## Overview
The data for this exercise are drawn from various sources.
Load data: | https://openei.org/datasets/files/961/pub/RESIDENTIAL_LOAD_DATA_E_PLUS_OUTPUT/BASE/
This is profile load data provided by OpenEI for a typical home in Boston, MA
Solar Data: | https://pvwatts.nrel.gov/pvwatts.php
This is a solar output model produced by NREL, for location Lat, Lon: 42.37, -71.06, near Logan Airport.
Wind Data: | https://www.ncdc.noaa.gov/cdo-web/datatools/lcd
This is climatalogical data from NOAA, showing wind speeds at 80 meters at location Lat,Lon: 42.3606°, -71.0097°, also near Logan.
These wind speed data are then run through the power curve for a GE model 1.5sle wind turbine.
The battery storage algorithm is a standard myopic ("greedy") algorithm, which starts out full and then discharges to meet any energy deficit, and stores any surplus. Any escess generation that cannot be stored is assumed to be curtailed.
Annualized costs use Excel's PMT function to calculate the annuity payment for a calculated upfront cost, an interest rate (5%) and a useful life (20 years for the wind and solar, 10 years for the battery).

## Hourly Model
Note: | Only shaded cells can be changed. (You can change anything you like if you go into Tools:Protection and Unprotect the sheet; there is no password)
The View Month (orange shaded) is set by default to the Worst Month. You can change it to view any month you like
The Solar, Wind, and Battery cells turn greeen when the combination meets the load requirement.
[10 empty] | Objective: |  | Select the amount of Solar, Wind, and Battery necessary to meet the load requirements. The upper graph shows the load (blue), solar output (orange) and wind output (green) in the worst month. The lower graph shows the battery level. If the battery ever gets empty, then you are not satisfying the load requirement.
| Load (kWH) | Solar (kW) | Wind (kW) | Battery (kWH) | [5 empty] | Questions: | 1) | How much energy does your system generate? How much gets curtailed?
| 10000 | 10 | 10 | 10 | [6 empty] | 2) | Can you design a system that does not curtail any energy? How?
| Cost per unit | [9 empty] | 3) | Now add a cost per unit of $800 for solar, $1900 for wind, and $400 for battery storage
| Cost per Year | 0 | 0 | 0 | Total: | 0 |  | Cost per MWh Generated: | 0 |  | 4) | What is the cost of the system with no curtailment?
| Cost per MWH Generated: | 0 | 0 |  |  |  |  | Cost per MWh Consumed: | 0 |  | 5) | Can you find the lowest cost system that meets the load requirement?
Total kWH | 10000 | 14989.8981 | 20912.1133 |  | Hours Curtailed: | 25902.0115 | 72.15% |  |  |  | 6) | For your lowest cost system, what is the cost of energy per kWH generated? Per kWH consumed?
[5 empty] | Hours Dark: | 530 | 6.05% |  |  |  | 7) | Using only solar and battery, calculate the cost per MWh consumed for a system that meets the load
in every hour. What would be the cost if you were willing to go dark in 5% of the hours?
| Worst Day: | 2019-01-03 |  | View Month | 1 | 2017-01-01
| Worst Month: | 1 |  | 48 | -20034.8541 | FALSE
|  |  |  | Offset | 0
Date-Hour | Load (W) | Solar Output (W) | Wind Output (W) | Battery Storage (WH)
2019-01-01 | 1042.0208 | 0 | 2773.3333 | 10000
2019-01-01 01:00 | 893.3192 | 0 | 4266.6667 | 10000
2019-01-01 02:00 | 839.8014 | 0 | 2773.3333 | 10000
2019-01-01 03:00 | 821.5169 | 0 | 4266.6667 | 10000
2019-01-01 04:00 | 816.1413 | 0 | 6160 | 10000
2019-01-01 05:00 | 873.2033 | 0 | 2773.3333 | 10000
2019-01-01 06:00 | 1122.6479 | 0 | 2773.3333 | 10000
2019-01-01 07:00 | 1499.8922 | 0 | 2773.3333 | 10000
2019-01-01 08:00 | 1448.3726 | 708.2896 | 4266.6667 | 10000
2019-01-01 09:00 | 1236.4919 | 1129.5231 | 7873.3333 | 10000
2019-01-01 10:00 | 1252.2673 | 1224.4694 | 7873.3333 | 10000
2019-01-01 11:00 | 1215.4377 | 1659.0774 | 9573.3333 | 10000
2019-01-01 12:00 | 1168.2547 | 2055.2789 | 9060 | 10000
2019-01-01 13:00 | 1136.2649 | 1889.7156 | 7873.3333 | 10000
2019-01-01 14:00 | 1138.8866 | 628.8913 | 9060 | 10000
2019-01-01 15:00 | 1226.292 | 394.1476 | 1666.6667 | 10000
2019-01-01 16:00 | 1536.5213 | 0 | 873.3333 | 10000
2019-01-01 17:00 | 2126.095 | 0 | 873.3333 | 9336.812
2019-01-01 18:00 | 2488.3215 | 0 | 286.6667 | 8084.0504
2019-01-01 19:00 | 2454.9812 | 0 | 873.3333 | 5882.3955
2019-01-01 20:00 | 2299.757 | 0 | 286.6667 | 4300.7476
2019-01-01 21:00 | 2130.1209 | 0 | 286.6667 | 2287.6573
2019-01-01 22:00 | 1783.9856 | 0 | 286.6667 | 444.2031
2019-01-01 23:00 | 1433.6875 | 0 | 286.6667 | 0
2019-01-02 | 1079.4076 | 0 | 286.6667 | 0
2019-01-02 01:00 | 952.1266 | 0 | 0 | 0
2019-01-02 02:00 | 911.2734 | 0 | 0 | 0
2019-01-02 03:00 | 893.1193 | 0 | 0 | 0
2019-01-02 04:00 | 897.4218 | 0 | 0 | 0
2019-01-02 05:00 | 961.3495 | 0 | 0 | 0
2019-01-02 06:00 | 1205.3234 | 0 | 0 | 0
2019-01-02 07:00 | 1571.0671 | 0 | 0 | 0
2019-01-02 08:00 | 1476.0105 | 56.3028 | 0 | 0
2019-01-02 09:00 | 1238.1063 | 576.1557 | 286.6667 | 0
2019-01-02 10:00 | 1263.1562 | 1431.367 | 0 | 0
2019-01-02 11:00 | 1240.8118 | 1858.0987 | 0 | 168.2108
2019-01-02 12:00 | 1199.2196 | 1415.5718 | 0 | 785.4977
2019-01-02 13:00 | 1145.3117 | 1486.8292 | 0 | 1001.8499
2019-01-02 14:00 | 1146.5493 | 781.2559 | 0 | 1343.3674
2019-01-02 15:00 | 1232.2918 | 233.3545 | 0 | 978.074
2019-01-02 16:00 | 1530.4 | 0 | 0 | 0
2019-01-02 17:00 | 2112.549 | 0 | 286.6667 | 0
2019-01-02 18:00 | 2455.9215 | 0 | 873.3333 | 0
2019-01-02 19:00 | 2413.3347 | 0 | 286.6667 | 0
2019-01-02 20:00 | 2242.7475 | 0 | 286.6667 | 0
2019-01-02 21:00 | 2055.1301 | 0 | 286.6667 | 0
2019-01-02 22:00 | 1705.7544 | 0 | 873.3333 | 0
2019-01-02 23:00 | 1362.2701 | 0 | 873.3333 | 0
2019-01-03 | 1019.1125 | 0 | 1666.6667 | 0
2019-01-03 01:00 | 882.2924 | 0 | 1666.6667 | 647.5542
2019-01-03 02:00 | 827.7665 | 0 | 286.6667 | 1431.9285
2019-01-03 03:00 | 815.8933 | 0 | 1666.6667 | 890.8286
2019-01-03 04:00 | 809.4685 | 0 | 2773.3333 | 1741.602
2019-01-03 05:00 | 862.3635 | 0 | 4266.6667 | 3705.4668
2019-01-03 06:00 | 1099.3037 | 0 | 7873.3333 | 7109.7699
2019-01-03 07:00 | 1463.6729 | 0 | 9060 | 10000
2019-01-03 08:00 | 1397.2756 | 2298.1554 | 7873.3333 | 10000
2019-01-03 09:00 | 1193.6693 | 355.7939 | 7873.3333 | 10000
2019-01-03 10:00 | 1210.2789 | 794.3579 | 7873.3333 | 10000
2019-01-03 11:00 | 1196.5668 | 1494.9402 | 7873.3333 | 10000
2019-01-03 12:00 | 1169.7933 | 2408.8038 | 7873.3333 | 10000
2019-01-03 13:00 | 1141.3569 | 1058.008 | 7873.3333 | 10000
2019-01-03 14:00 | 1139.9138 | 140.9877 | 7873.3333 | 10000
2019-01-03 15:00 | 1218.3248 | 591.491 | 9060 | 10000
2019-01-03 16:00 | 1506.9759 | 0 | 9573.3333 | 10000
2019-01-03 17:00 | 2037.4872 | 0 | 9060 | 10000
2019-01-03 18:00 | 2436.5917 | 0 | 9060 | 10000
2019-01-03 19:00 | 2369.5303 | 0 | 6160 | 10000
2019-01-03 20:00 | 2201.5219 | 0 | 7873.3333 | 10000
2019-01-03 21:00 | 2010.361 | 0 | 7873.3333 | 10000
2019-01-03 22:00 | 1662.7543 | 0 | 9060 | 10000
2019-01-03 23:00 | 1325.8165 | 0 | 9060 | 10000
2019-01-04 | 990.4983 | 0 | 2773.3333 | 10000
2019-01-04 01:00 | 861.2787 | 0 | 873.3333 | 10000
2019-01-04 02:00 | 811.391 | 0 | 286.6667 | 10000
2019-01-04 03:00 | 801.9284 | 0 | 2773.3333 | 9475.2757
2019-01-04 04:00 | 804.1801 | 0 | 1666.6667 | 10000
2019-01-04 05:00 | 867.4404 | 0 | 873.3333 | 10000
2019-01-04 06:00 | 1119.6275 | 0 | 873.3333 | 10000
2019-01-04 07:00 | 1446.7352 | 733.6448 | 286.6667 | 9753.7058
2019-01-04 08:00 | 1402.3409 | 3144.2943 | 286.6667 | 9327.2821
2019-01-04 09:00 | 1221.9481 | 5160.0902 | 2773.3333 | 10000
2019-01-04 10:00 | 1209.5577 | 3703.1104 | 2773.3333 | 10000
2019-01-04 11:00 | 1204.1012 | 3526.8016 | 4266.6667 | 10000
2019-01-04 12:00 | 1169.0455 | 3210.4377 | 1666.6667 | 10000
2019-01-04 13:00 | 1131.7361 | 3272.2894 | 2773.3333 | 10000
2019-01-04 14:00 | 1138.8976 | 4464.185 | 873.3333 | 10000
2019-01-04 15:00 | 1228.0748 | 2245.505 | 1666.6667 | 10000
2019-01-04 16:00 | 1551.8261 | 0 | 873.3333 | 10000
2019-01-04 17:00 | 2138.284 | 0 | 1666.6667 | 9321.5072
2019-01-04 18:00 | 2490.7181 | 0 | 4266.6667 | 8849.8899
2019-01-04 19:00 | 2454.1603 | 0 | 6160 | 10000
2019-01-04 20:00 | 2298.0408 | 0 | 7873.3333 | 10000
2019-01-04 21:00 | 2115.7759 | 0 | 6160 | 10000
2019-01-04 22:00 | 1770.7263 | 0 | 7873.3333 | 10000
2019-01-04 23:00 | 1435.3098 | 0 | 4266.6667 | 10000
2019-01-05 | 1108.1231 | 0 | 7873.3333 | 10000
2019-01-05 01:00 | 977.69 | 0 | 6160 | 10000
2019-01-05 02:00 | 934.1205 | 0 | 9060 | 10000
2019-01-05 03:00 | 921.89 | 0 | 4266.6667 | 10000
2019-01-05 04:00 | 938.3732 | 0 | 6160 | 10000
2019-01-05 05:00 | 1000.0422 | 0 | 7873.3333 | 10000
2019-01-05 06:00 | 1251.0793 | 0 | 6160 | 10000
2019-01-05 07:00 | 1593.9334 | 707.3707 | 4266.6667 | 10000
2019-01-05 08:00 | 1511.5761 | 3028.0374 | 6160 | 10000
2019-01-05 09:00 | 1285.8132 | 655.6265 | 7873.3333 | 10000
2019-01-05 10:00 | 1296.9823 | 1927.0918 | 7873.3333 | 10000
2019-01-05 11:00 | 1253.0589 | 3099.8158 | 9060 | 10000
2019-01-05 12:00 | 1202.8901 | 2959.3812 | 4266.6667 | 10000
2019-01-05 13:00 | 1160.6337 | 2077.6314 | 1666.6667 | 10000
2019-01-05 14:00 | 1166.9031 | 2572.4649 | 6160 | 10000
2019-01-05 15:00 | 1265.0815 | 2092.4733 | 2773.3333 | 10000
2019-01-05 16:00 | 1573.6313 | 0 | 1666.6667 | 10000
2019-01-05 17:00 | 2171.8176 | 0 | 286.6667 | 10000
2019-01-05 18:00 | 2522.1304 | 0 | 873.3333 | 8114.8491
2019-01-05 19:00 | 2487.6218 | 0 | 873.3333 | 6466.0521
2019-01-05 20:00 | 2325.2633 | 0 | 873.3333 | 4851.7636
2019-01-05 21:00 | 2145.8022 | 0 | 286.6667 | 3399.8337
2019-01-05 22:00 | 1802.0216 | 0 | 286.6667 | 1540.6982
2019-01-05 23:00 | 1461.3819 | 0 | 1666.6667 | 25.3432
2019-01-06 | 1129.743 | 0 | 286.6667 | 230.628
2019-01-06 01:00 | 990.0455 | 0 | 286.6667 | 0
2019-01-06 02:00 | 940.1069 | 0 | 873.3333 | 0
2019-01-06 03:00 | 933.8959 | 0 | 873.3333 | 0
2019-01-06 04:00 | 931.2571 | 0 | 286.6667 | 0
2019-01-06 05:00 | 992.2818 | 0 | 286.6667 | 0
2019-01-06 06:00 | 1234.5975 | 0 | 0 | 0
2019-01-06 07:00 | 1574.0274 | 726.1974 | 0 | 0
2019-01-06 08:00 | 1495.3606 | 3066.0667 | 0 | 0
2019-01-06 09:00 | 1254.2489 | 5005.4969 | 0 | 1570.7062
2019-01-06 10:00 | 1256.5931 | 6386.134 | 0 | 5321.9542
2019-01-06 11:00 | 1214.7196 | 6955.9417 | 286.6667 | 10000
2019-01-06 12:00 | 1172.1534 | 6795.2833 | 286.6667 | 10000
2019-01-06 13:00 | 1131.0846 | 5947.2825 | 286.6667 | 10000
2019-01-06 14:00 | 1141.6182 | 2867.7998 | 873.3333 | 10000
2019-01-06 15:00 | 1226.4254 | 1499.5413 | 873.3333 | 10000
2019-01-06 16:00 | 1531.0673 | 0 | 873.3333 | 10000
2019-01-06 17:00 | 2112.311 | 0 | 1666.6667 | 9342.266
2019-01-06 18:00 | 2461.3628 | 0 | 286.6667 | 8896.6217
2019-01-06 19:00 | 2421.6762 | 0 | 873.3333 | 6721.9255
2019-01-06 20:00 | 2254.9516 | 0 | 873.3333 | 5173.5827
2019-01-06 21:00 | 2073.3565 | 0 | 286.6667 | 3791.9645
2019-01-06 22:00 | 1726.4627 | 0 | 286.6667 | 2005.2747
2019-01-06 23:00 | 1386.7211 | 0 | 873.3333 | 565.4786
2019-01-07 | 1053.7304 | 0 | 1666.6667 | 52.0908
2019-01-07 01:00 | 914.2289 | 0 | 873.3333 | 665.027
2019-01-07 02:00 | 859.6796 | 0 | 873.3333 | 624.1314
2019-01-07 03:00 | 840.5408 | 0 | 286.6667 | 637.7852
2019-01-07 04:00 | 835.563 | 0 | 286.6667 | 83.911
2019-01-07 05:00 | 894.051 | 0 | 286.6667 | 0
2019-01-07 06:00 | 1139.0025 | 0 | 873.3333 | 0
2019-01-07 07:00 | 1498.2187 | 173.4545 | 873.3333 | 0
2019-01-07 08:00 | 1446.7904 | 3075.5278 | 873.3333 | 0
2019-01-07 09:00 | 1237.1264 | 5064.7897 | 2773.3333 | 2502.0707
2019-01-07 10:00 | 1250.1037 | 6355.6268 | 2773.3333 | 9103.0674
2019-01-07 11:00 | 1232.5755 | 6946.422 | 1666.6667 | 10000
2019-01-07 12:00 | 1195.4708 | 6827.9594 | 2773.3333 | 10000
2019-01-07 13:00 | 1152.4164 | 5979.8079 | 4266.6667 | 10000
2019-01-07 14:00 | 1153.606 | 4377.5842 | 6160 | 10000
2019-01-07 15:00 | 1232.5736 | 2281.1331 | 4266.6667 | 10000
2019-01-07 16:00 | 1523.9281 | 0 | 6160 | 10000
2019-01-07 17:00 | 2092.4904 | 0 | 9060 | 10000
2019-01-07 18:00 | 2439.7012 | 0 | 9060 | 10000
2019-01-07 19:00 | 2393.0598 | 0 | 9573.3333 | 10000
2019-01-07 20:00 | 2221.3541 | 0 | 9060 | 10000
2019-01-07 21:00 | 2035.6386 | 0 | 6160 | 10000
2019-01-07 22:00 | 1677.6564 | 0 | 4266.6667 | 10000
2019-01-07 23:00 | 1320.8098 | 0 | 4266.6667 | 10000
2019-01-08 | 971.7899 | 0 | 4266.6667 | 10000
2019-01-08 01:00 | 832.3694 | 0 | 4266.6667 | 10000
2019-01-08 02:00 | 780.3847 | 0 | 2773.3333 | 10000
2019-01-08 03:00 | 776.5227 | 0 | 2773.3333 | 10000
2019-01-08 04:00 | 779.5976 | 0 | 2773.3333 | 10000
2019-01-08 05:00 | 843.6749 | 0 | 2773.3333 | 10000
2019-01-08 06:00 | 1092.6993 | 0 | 873.3333 | 10000
2019-01-08 07:00 | 1468.5789 | 26.2648 | 1666.6667 | 9780.634
2019-01-08 08:00 | 1417.516 | 311.8742 | 4266.6667 | 10000
2019-01-08 09:00 | 1234.5601 | 2820.7211 | 4266.6667 | 10000
2019-01-08 10:00 | 1264.5128 | 1591.439 | 2773.3333 | 10000
2019-01-08 11:00 | 1254.5346 | 4101.598 | 2773.3333 | 10000
2019-01-08 12:00 | 1224.6702 | 682.5583 | 4266.6667 | 10000
2019-01-08 13:00 | 1195.1458 | 932.5568 | 2773.3333 | 10000
2019-01-08 14:00 | 1200.6413 | 812.8832 | 2773.3333 | 10000
2019-01-08 15:00 | 1285.8584 | 477.2833 | 4266.6667 | 10000
2019-01-08 16:00 | 1588.8933 | 0 | 2773.3333 | 10000
2019-01-08 17:00 | 2173.9246 | 0 | 2773.3333 | 10000
2019-01-08 18:00 | 2531.0058 | 0 | 2773.3333 | 10000
2019-01-08 19:00 | 2493.8456 | 0 | 1666.6667 | 10000
2019-01-08 20:00 | 2337.2326 | 0 | 2773.3333 | 9172.8211
2019-01-08 21:00 | 2153.3967 | 0 | 4266.6667 | 9608.9218
2019-01-08 22:00 | 1804.3532 | 0 | 2773.3333 | 10000
2019-01-08 23:00 | 1453.3781 | 0 | 2773.3333 | 10000
2019-01-09 | 1100.1168 | 0 | 873.3333 | 10000
2019-01-09 01:00 | 968.9644 | 0 | 1666.6667 | 9773.2165
2019-01-09 02:00 | 931.9764 | 0 | 4266.6667 | 10000
2019-01-09 03:00 | 932.7078 | 0 | 2773.3333 | 10000
2019-01-09 04:00 | 931.5577 | 0 | 1666.6667 | 10000
2019-01-09 05:00 | 993.6304 | 0 | 4266.6667 | 10000
2019-01-09 06:00 | 1261.6405 | 0 | 2773.3333 | 10000
2019-01-09 07:00 | 1614.2213 | 760.1132 | 2773.3333 | 10000
2019-01-09 08:00 | 1517.4772 | 3231.9393 | 2773.3333 | 10000
2019-01-09 09:00 | 1285.4932 | 5361.0067 | 286.6667 | 10000
2019-01-09 10:00 | 1290.7479 | 6734.8232 | 873.3333 | 10000
2019-01-09 11:00 | 1238.0291 | 7324.5248 | 286.6667 | 10000
2019-01-09 12:00 | 1190.6351 | 7204.1899 | 0 | 10000
2019-01-09 13:00 | 1148.2085 | 6368.6068 | 0 | 10000
2019-01-09 14:00 | 1161.7449 | 4803.1038 | 873.3333 | 10000
2019-01-09 15:00 | 1257.9821 | 2573.5114 | 1666.6667 | 10000
2019-01-09 16:00 | 1564.8568 | 0 | 1666.6667 | 10000
2019-01-09 17:00 | 2155.2275 | 0 | 2773.3333 | 10000
2019-01-09 18:00 | 2498.5406 | 0 | 2773.3333 | 10000
2019-01-09 19:00 | 2461.1569 | 0 | 1666.6667 | 10000
2019-01-09 20:00 | 2294.6091 | 0 | 873.3333 | 9205.5097
2019-01-09 21:00 | 2121.1985 | 0 | 286.6667 | 7784.234
2019-01-09 22:00 | 1776.9825 | 0 | 286.6667 | 5949.7022
2019-01-09 23:00 | 1437.8816 | 0 | 286.6667 | 4459.3863
2019-01-10 | 1099.1459 | 0 | 873.3333 | 3308.1714
2019-01-10 01:00 | 967.9049 | 0 | 873.3333 | 3082.3588
2019-01-10 02:00 | 919.2615 | 0 | 1666.6667 | 2987.7872
2019-01-10 03:00 | 911.3138 | 0 | 873.3333 | 3735.1923
2019-01-10 04:00 | 911.9384 | 0 | 286.6667 | 3697.2119
2019-01-10 05:00 | 970.4012 | 0 | 0 | 3071.9401
2019-01-10 06:00 | 1237.6796 | 0 | 0 | 2101.5389
2019-01-10 07:00 | 1583.6504 | 802.1273 | 0 | 863.8593
2019-01-10 08:00 | 1486.9945 | 3259.0839 | 0 | 82.3362
2019-01-10 09:00 | 1253.0934 | 5286.7892 | 286.6667 | 1854.4256
2019-01-10 10:00 | 1253.8638 | 6545.0858 | 0 | 6174.7881
2019-01-10 11:00 | 1216.162 | 7076.3352 | 286.6667 | 10000
2019-01-10 12:00 | 1186.9317 | 6975.3641 | 0 | 10000
2019-01-10 13:00 | 1156.0461 | 6166.6968 | 0 | 10000
2019-01-10 14:00 | 1167.2865 | 4671.0654 | 0 | 10000
2019-01-10 15:00 | 1258.7129 | 2523.353 | 0 | 10000
2019-01-10 16:00 | 1564.9035 | 0 | 0 | 10000
2019-01-10 17:00 | 2159.2321 | 0 | 2773.3333 | 8435.0965
2019-01-10 18:00 | 2504.3254 | 0 | 6160 | 9049.1978
2019-01-10 19:00 | 2467.3409 | 0 | 9060 | 10000
2019-01-10 20:00 | 2313.3317 | 0 | 4266.6667 | 10000
2019-01-10 21:00 | 2137.6896 | 0 | 1666.6667 | 10000
2019-01-10 22:00 | 1805.6335 | 0 | 2773.3333 | 9528.977
2019-01-10 23:00 | 1468.8726 | 0 | 2773.3333 | 10000
2019-01-11 | 1134.9702 | 0 | 873.3333 | 10000
2019-01-11 01:00 | 1009.5438 | 0 | 2773.3333 | 9738.3631
2019-01-11 02:00 | 957.5205 | 0 | 4266.6667 | 10000
2019-01-11 03:00 | 952.7863 | 0 | 9060 | 10000
2019-01-11 04:00 | 951.3375 | 0 | 9060 | 10000
2019-01-11 05:00 | 1014.0059 | 0 | 9873.3333 | 10000
2019-01-11 06:00 | 1282.0857 | 0 | 9960 | 10000
2019-01-11 07:00 | 1630.5214 | 593.6886 | 9873.3333 | 10000
2019-01-11 08:00 | 1537.4837 | 2954.4558 | 9060 | 10000
2019-01-11 09:00 | 1303.4911 | 4912.0341 | 9060 | 10000
2019-01-11 10:00 | 1324.9925 | 6182.2735 | 9060 | 10000
2019-01-11 11:00 | 1293.5942 | 6740.089 | 4266.6667 | 10000
2019-01-11 12:00 | 1263.5404 | 6638.7465 | 6160 | 10000
2019-01-11 13:00 | 1228.4431 | 5848.8195 | 2773.3333 | 10000
2019-01-11 14:00 | 1233.5561 | 4354.4842 | 4266.6667 | 10000
2019-01-11 15:00 | 1316.1137 | 2237.9138 | 286.6667 | 10000
2019-01-11 16:00 | 1604.9263 | 0 | 0 | 10000
2019-01-11 17:00 | 2135.7964 | 0 | 873.3333 | 8395.0737
2019-01-11 18:00 | 2553.0007 | 0 | 286.6667 | 7132.6106
2019-01-11 19:00 | 2473.1916 | 0 | 873.3333 | 4866.2765
2019-01-11 20:00 | 2294.4682 | 0 | 873.3333 | 3266.4182
2019-01-11 21:00 | 2111.0057 | 0 | 873.3333 | 1845.2834
2019-01-11 22:00 | 1762.9842 | 0 | 873.3333 | 607.6111
2019-01-11 23:00 | 1420.9287 | 0 | 286.6667 | 0
2019-01-12 | 1091.0769 | 0 | 286.6667 | 0
2019-01-12 01:00 | 969.5585 | 0 | 0 | 0
2019-01-12 02:00 | 922.8738 | 0 | 286.6667 | 0
2019-01-12 03:00 | 916.4785 | 0 | 873.3333 | 0
2019-01-12 04:00 | 916.4849 | 0 | 6160 | 0
2019-01-12 05:00 | 991.0524 | 0 | 6160 | 5243.5151
2019-01-12 06:00 | 1234.3075 | 0 | 6160 | 10000
2019-01-12 07:00 | 1599.9252 | 89.4378 | 7873.3333 | 10000
2019-01-12 08:00 | 1536.2566 | 835.4554 | 4266.6667 | 10000
2019-01-12 09:00 | 1328.6617 | 1429.2396 | 7873.3333 | 10000
2019-01-12 10:00 | 1363.3813 | 2151.3993 | 7873.3333 | 10000
2019-01-12 11:00 | 1321.792 | 3307.2298 | 7873.3333 | 10000
2019-01-12 12:00 | 1285.1337 | 6902.875 | 4266.6667 | 10000
2019-01-12 13:00 | 1245.9316 | 6076.6908 | 4266.6667 | 10000
2019-01-12 14:00 | 1242.9141 | 4640.8687 | 2773.3333 | 10000
2019-01-12 15:00 | 1326.9046 | 2528.9535 | 2773.3333 | 10000
2019-01-12 16:00 | 1620.2033 | 0 | 873.3333 | 10000
2019-01-12 17:00 | 2204.0909 | 0 | 286.6667 | 9253.13
2019-01-12 18:00 | 2539.9982 | 0 | 1666.6667 | 7335.7058
2019-01-12 19:00 | 2489.553 | 0 | 873.3333 | 6462.3743
2019-01-12 20:00 | 2317.242 | 0 | 6160 | 4846.1546
2019-01-12 21:00 | 2133.2084 | 0 | 7873.3333 | 8688.9126
2019-01-12 22:00 | 1782.0521 | 0 | 6160 | 10000
2019-01-12 23:00 | 1442.1133 | 0 | 4266.6667 | 10000
2019-01-13 | 1106.5453 | 0 | 1666.6667 | 10000
2019-01-13 01:00 | 967.0336 | 0 | 2773.3333 | 10000
2019-01-13 02:00 | 928.3393 | 0 | 2773.3333 | 10000
2019-01-13 03:00 | 926.4689 | 0 | 4266.6667 | 10000
2019-01-13 04:00 | 917.5191 | 0 | 6160 | 10000
2019-01-13 05:00 | 974.9294 | 0 | 4266.6667 | 10000
2019-01-13 06:00 | 1245.7623 | 0 | 9573.3333 | 10000
2019-01-13 07:00 | 1593.6157 | 804.2042 | 7873.3333 | 10000
2019-01-13 08:00 | 1498.5987 | 3287.3773 | 6160 | 10000
2019-01-13 09:00 | 1262.9549 | 5366.8706 | 9573.3333 | 10000
2019-01-13 10:00 | 1254.7644 | 6655.226 | 9060 | 10000
2019-01-13 11:00 | 1204.4716 | 7193.7479 | 9060 | 10000
2019-01-13 12:00 | 1154.2388 | 7020.7305 | 7873.3333 | 10000
2019-01-13 13:00 | 1111.2412 | 4976.0281 | 7873.3333 | 10000
2019-01-13 14:00 | 1115.894 | 4538.1093 | 7873.3333 | 10000
2019-01-13 15:00 | 1202.5254 | 2385.6451 | 6160 | 10000
2019-01-13 16:00 | 1498.5686 | 0 | 6160 | 10000
2019-01-13 17:00 | 2078.403 | 0 | 2773.3333 | 10000
2019-01-13 18:00 | 2427.3876 | 0 | 2773.3333 | 10000
2019-01-13 19:00 | 2381.2042 | 0 | 1666.6667 | 10000
2019-01-13 20:00 | 2211.9885 | 0 | 4266.6667 | 9285.4625
2019-01-13 21:00 | 2020.156 | 0 | 2773.3333 | 10000
2019-01-13 22:00 | 1676.4262 | 0 | 2773.3333 | 10000
2019-01-13 23:00 | 1321.8451 | 0 | 873.3333 | 10000
2019-01-14 | 980.7033 | 0 | 4266.6667 | 9551.4883
2019-01-14 01:00 | 836.6575 | 0 | 2773.3333 | 10000
2019-01-14 02:00 | 790.8116 | 0 | 1666.6667 | 10000
2019-01-14 03:00 | 759.5663 | 0 | 873.3333 | 10000
2019-01-14 04:00 | 751.1711 | 0 | 873.3333 | 10000
2019-01-14 05:00 | 799.5044 | 0 | 286.6667 | 10000
2019-01-14 06:00 | 1051.333 | 0 | 873.3333 | 9487.1622
2019-01-14 07:00 | 1431.8255 | 230.8119 | 286.6667 | 9309.1626
2019-01-14 08:00 | 1389.5915 | 3152.6767 | 0 | 8394.8157
2019-01-14 09:00 | 1178.3947 | 5061.9217 | 0 | 10000
2019-01-14 10:00 | 1175.7576 | 6320.2068 | 0 | 10000
2019-01-14 11:00 | 1183.7616 | 6892.8803 | 0 | 10000
2019-01-14 12:00 | 1145.4295 | 6756.442 | 286.6667 | 10000
2019-01-14 13:00 | 1122.9399 | 5998.4207 | 286.6667 | 10000
2019-01-14 14:00 | 1097.7804 | 4589.4729 | 1666.6667 | 10000
2019-01-14 15:00 | 1190.9402 | 2468.3232 | 873.3333 | 10000
2019-01-14 16:00 | 1502.9951 | 0 | 873.3333 | 10000
2019-01-14 17:00 | 2089.7165 | 0 | 2773.3333 | 9370.3382
2019-01-14 18:00 | 2445.2593 | 0 | 1666.6667 | 10000
2019-01-14 19:00 | 2414.326 | 0 | 873.3333 | 9221.4074
2019-01-14 20:00 | 2249.8169 | 0 | 2773.3333 | 7680.4147
2019-01-14 21:00 | 2073.1239 | 0 | 2773.3333 | 8203.9311
2019-01-14 22:00 | 1720.3067 | 0 | 1666.6667 | 8904.1405
2019-01-14 23:00 | 1376.5154 | 0 | 873.3333 | 8850.5005
2019-01-15 | 1021.2685 | 0 | 1666.6667 | 8347.3184
2019-01-15 01:00 | 884.8755 | 0 | 873.3333 | 8992.7166
2019-01-15 02:00 | 846.5273 | 0 | 286.6667 | 8981.1744
2019-01-15 03:00 | 838.1416 | 0 | 4266.6667 | 8421.3137
2019-01-15 04:00 | 837.0028 | 0 | 2773.3333 | 10000
2019-01-15 05:00 | 897.1803 | 0 | 873.3333 | 10000
2019-01-15 06:00 | 1152.9911 | 0 | 873.3333 | 9976.1531
2019-01-15 07:00 | 1516.9659 | 35.3176 | 873.3333 | 9696.4953
2019-01-15 08:00 | 1446.6477 | 1489.6697 | 286.6667 | 9088.1803
2019-01-15 09:00 | 1240.2874 | 1712.2867 | 873.3333 | 9417.869
2019-01-15 10:00 | 1279.727 | 3710.9408 | 873.3333 | 10000
2019-01-15 11:00 | 1257.1741 | 4715.7532 | 873.3333 | 10000
2019-01-15 12:00 | 1238.0586 | 5274.2082 | 2773.3333 | 10000
2019-01-15 13:00 | 1199.1964 | 4127.0257 | 2773.3333 | 10000
2019-01-15 14:00 | 1197.1765 | 2187.7772 | 873.3333 | 10000
2019-01-15 15:00 | 1284.0345 | 2224.0678 | 873.3333 | 10000
2019-01-15 16:00 | 1590.4354 | 0 | 873.3333 | 10000
2019-01-15 17:00 | 2170.2063 | 0 | 286.6667 | 9282.8979
2019-01-15 18:00 | 2524.9814 | 0 | 286.6667 | 7399.3583
2019-01-15 19:00 | 2485.5055 | 0 | 286.6667 | 5161.0436
2019-01-15 20:00 | 2313.7149 | 0 | 0 | 2962.2048
2019-01-15 21:00 | 2131.4109 | 0 | 0 | 648.4898
2019-01-15 22:00 | 1780.8071 | 0 | 0 | 0
2019-01-15 23:00 | 1426.4938 | 0 | 0 | 0
2019-01-16 | 1064.1937 | 0 | 0 | 0
2019-01-16 01:00 | 925.3398 | 0 | 0 | 0
2019-01-16 02:00 | 874.5328 | 0 | 0 | 0
2019-01-16 03:00 | 863.5571 | 0 | 0 | 0
2019-01-16 04:00 | 861.2195 | 0 | 0 | 0
2019-01-16 05:00 | 920.675 | 0 | 0 | 0
2019-01-16 06:00 | 1161.3779 | 0 | 0 | 0
2019-01-16 07:00 | 1506.7941 | 236.4802 | 0 | 0
2019-01-16 08:00 | 1452.801 | 3024.5242 | 0 | 0
2019-01-16 09:00 | 1247.5783 | 4974.9287 | 1666.6667 | 1571.7232
2019-01-16 10:00 | 1261.3221 | 6205.1355 | 1666.6667 | 6965.7402
2019-01-16 11:00 | 1237.4988 | 6758.2429 | 6160 | 10000
2019-01-16 12:00 | 1203.0897 | 6647.0057 | 4266.6667 | 10000
2019-01-16 13:00 | 1160.826 | 5910.1869 | 4266.6667 | 10000
2019-01-16 14:00 | 1156.3318 | 4532.0821 | 2773.3333 | 10000
2019-01-16 15:00 | 1232.9217 | 2472.8392 | 4266.6667 | 10000
2019-01-16 16:00 | 1524.3101 | 0 | 2773.3333 | 10000
2019-01-16 17:00 | 2087.6373 | 0 | 2773.3333 | 10000
2019-01-16 18:00 | 2462.035 | 0 | 2773.3333 | 10000
2019-01-16 19:00 | 2383.6495 | 0 | 2773.3333 | 10000
2019-01-16 20:00 | 2206.3424 | 0 | 2773.3333 | 10000
2019-01-16 21:00 | 2015.4962 | 0 | 2773.3333 | 10000
2019-01-16 22:00 | 1667.4942 | 0 | 4266.6667 | 10000
2019-01-16 23:00 | 1329.3998 | 0 | 2773.3333 | 10000
2019-01-17 | 994.1555 | 0 | 2773.3333 | 10000
2019-01-17 01:00 | 865.2969 | 0 | 873.3333 | 10000
2019-01-17 02:00 | 819.7261 | 0 | 873.3333 | 10000
2019-01-17 03:00 | 815.039 | 0 | 0 | 10000
2019-01-17 04:00 | 816.2918 | 0 | 0 | 9184.961
2019-01-17 05:00 | 880.9404 | 0 | 286.6667 | 8368.6692
2019-01-17 06:00 | 1140.3784 | 0 | 0 | 7774.3955
2019-01-17 07:00 | 1492.1999 | 66.6448 | 286.6667 | 6634.0171
2019-01-17 08:00 | 1435.1415 | 2464.2292 | 873.3333 | 5495.1287
2019-01-17 09:00 | 1220.4165 | 3486.4044 | 286.6667 | 7397.5497
2019-01-17 10:00 | 1241.3648 | 5145.6865 | 286.6667 | 9950.2043
2019-01-17 11:00 | 1196.13 | 4836.3319 | 286.6667 | 10000
2019-01-17 12:00 | 1162.6076 | 3121.3311 | 4266.6667 | 10000
2019-01-17 13:00 | 1134.351 | 1053.8749 | 2773.3333 | 10000
2019-01-17 14:00 | 1143.5175 | 461.3926 | 873.3333 | 10000
2019-01-17 15:00 | 1249.7695 | 229.7217 | 873.3333 | 10000
2019-01-17 16:00 | 1561.9174 | 0 | 873.3333 | 9853.2856
2019-01-17 17:00 | 2167.9562 | 0 | 4266.6667 | 9164.7015
2019-01-17 18:00 | 2529.1432 | 0 | 4266.6667 | 10000
2019-01-17 19:00 | 2479.0587 | 0 | 6160 | 10000
2019-01-17 20:00 | 2327.4386 | 0 | 7873.3333 | 10000
2019-01-17 21:00 | 2146.3039 | 0 | 4266.6667 | 10000
2019-01-17 22:00 | 1805.2376 | 0 | 6160 | 10000
2019-01-17 23:00 | 1476.4142 | 0 | 4266.6667 | 10000
2019-01-18 | 1142.3495 | 0 | 4266.6667 | 10000
2019-01-18 01:00 | 1011.2487 | 0 | 4266.6667 | 10000
2019-01-18 02:00 | 965.5616 | 0 | 9060 | 10000
2019-01-18 03:00 | 963.567 | 0 | 7873.3333 | 10000
2019-01-18 04:00 | 967.1993 | 0 | 6160 | 10000
2019-01-18 05:00 | 1032.7226 | 0 | 6160 | 10000
2019-01-18 06:00 | 1302.4447 | 0 | 6160 | 10000
2019-01-18 07:00 | 1653.0783 | 0 | 4266.6667 | 10000
2019-01-18 08:00 | 1566.9229 | 107.1271 | 2773.3333 | 10000
2019-01-18 09:00 | 1327.7309 | 416.6415 | 4266.6667 | 10000
2019-01-18 10:00 | 1337.411 | 1209.662 | 4266.6667 | 10000
2019-01-18 11:00 | 1277.2035 | 302.5949 | 4266.6667 | 10000
2019-01-18 12:00 | 1234.4014 | 560.2156 | 6160 | 10000
2019-01-18 13:00 | 1183.1775 | 1246.5574 | 4266.6667 | 10000
2019-01-18 14:00 | 1183.6735 | 4347.6015 | 4266.6667 | 10000
2019-01-18 15:00 | 1286.4846 | 2268.6314 | 1666.6667 | 10000
2019-01-18 16:00 | 1597.853 | 0 | 873.3333 | 10000
2019-01-18 17:00 | 2209.4723 | 0 | 873.3333 | 9275.4804
2019-01-18 18:00 | 2561.6335 | 0 | 1666.6667 | 7939.3414
2019-01-18 19:00 | 2521.7886 | 0 | 873.3333 | 7044.3745
2019-01-18 20:00 | 2366.897 | 0 | 0 | 5395.9193
2019-01-18 21:00 | 2190.6705 | 0 | 286.6667 | 3029.0222
2019-01-18 22:00 | 1845.9155 | 0 | 873.3333 | 1125.0184
2019-01-18 23:00 | 1516.2844 | 0 | 286.6667 | 152.4362
2019-01-19 | 1174.1528 | 0 | 873.3333 | 0
2019-01-19 01:00 | 1038.6212 | 0 | 286.6667 | 0
2019-01-19 02:00 | 990.0507 | 0 | 286.6667 | 0
2019-01-19 03:00 | 982.597 | 0 | 0 | 0
2019-01-19 04:00 | 977.2347 | 0 | 0 | 0
2019-01-19 05:00 | 1039.0727 | 0 | 0 | 0
2019-01-19 06:00 | 1282.1593 | 0 | 0 | 0
2019-01-19 07:00 | 1654.9666 | 334.5614 | 0 | 0
2019-01-19 08:00 | 1557.2568 | 128.6677 | 0 | 0
2019-01-19 09:00 | 1303.4426 | 243.1767 | 0 | 0
2019-01-19 10:00 | 1302.9389 | 1029.8595 | 0 | 0
2019-01-19 11:00 | 1237.0056 | 1583.2476 | 1666.6667 | 0
2019-01-19 12:00 | 1187.972 | 902.359 | 1666.6667 | 2012.9086
2019-01-19 13:00 | 1147.105 | 219.8766 | 1666.6667 | 3393.9623
2019-01-19 14:00 | 1145.6303 | 139.227 | 2773.3333 | 4133.4005
2019-01-19 15:00 | 1236.0177 | 35.1969 | 286.6667 | 5900.3306
2019-01-19 16:00 | 1545.6045 | 0 | 0 | 4986.1765
2019-01-19 17:00 | 2146.225 | 0 | 873.3333 | 3440.572
2019-01-19 18:00 | 2492.804 | 0 | 1666.6667 | 2167.6803
2019-01-19 19:00 | 2453.2607 | 0 | 1666.6667 | 1341.5429
2019-01-19 20:00 | 2285.5781 | 0 | 873.3333 | 554.9489
2019-01-19 21:00 | 2103.3648 | 0 | 1666.6667 | 0
2019-01-19 22:00 | 1763.1147 | 0 | 1666.6667 | 0
2019-01-19 23:00 | 1423.5258 | 0 | 286.6667 | 0
2019-01-20 | 1083.3644 | 0 | 0 | 0
2019-01-20 01:00 | 948.8806 | 0 | 0 | 0
2019-01-20 02:00 | 897.4717 | 0 | 286.6667 | 0
2019-01-20 03:00 | 882.9725 | 0 | 873.3333 | 0
2019-01-20 04:00 | 878.691 | 0 | 286.6667 | 0
2019-01-20 05:00 | 933.6678 | 0 | 0 | 0
2019-01-20 06:00 | 1181.0944 | 0 | 0 | 0
2019-01-20 07:00 | 1510.473 | 402.8461 | 0 | 0
2019-01-20 08:00 | 1449.0384 | 2649.8461 | 0 | 0
2019-01-20 09:00 | 1240.1077 | 1690.1699 | 0 | 1200.8077
2019-01-20 10:00 | 1242.5125 | 1520.5093 | 0 | 1650.8699
2019-01-20 11:00 | 1223.68 | 1411.3904 | 0 | 1928.8667
2019-01-20 12:00 | 1201.76 | 892.2125 | 0 | 2116.5771
2019-01-20 13:00 | 1167.2337 | 1113.6807 | 0 | 1807.0296
2019-01-20 14:00 | 1171.4244 | 2763.335 | 0 | 1753.4767
2019-01-20 15:00 | 1253.9191 | 2127.7484 | 0 | 3345.3873
2019-01-20 16:00 | 1540.1594 | 64.3529 | 286.6667 | 4219.2166
2019-01-20 17:00 | 2113.9344 | 0 | 286.6667 | 3030.0767
2019-01-20 18:00 | 2460.6605 | 0 | 286.6667 | 1202.809
2019-01-20 19:00 | 2414.062 | 0 | 0 | 0
2019-01-20 20:00 | 2250.3254 | 0 | 286.6667 | 0
2019-01-20 21:00 | 2063.7319 | 0 | 0 | 0
2019-01-20 22:00 | 1715.8068 | 0 | 0 | 0
2019-01-20 23:00 | 1376.4285 | 0 | 286.6667 | 0
2019-01-21 | 1044.5197 | 0 | 873.3333 | 0
2019-01-21 01:00 | 907.7362 | 0 | 286.6667 | 0
2019-01-21 02:00 | 856.5391 | 0 | 0 | 0
2019-01-21 03:00 | 844.718 | 0 | 0 | 0
2019-01-21 04:00 | 853.2605 | 0 | 0 | 0
2019-01-21 05:00 | 910.8369 | 0 | 0 | 0
2019-01-21 06:00 | 1162.7189 | 0 | 0 | 0
2019-01-21 07:00 | 1539.8908 | 858.3657 | 286.6667 | 0
2019-01-21 08:00 | 1455.4819 | 3273.9281 | 873.3333 | 0
2019-01-21 09:00 | 1235.2849 | 5249.3164 | 0 | 2691.7796
2019-01-21 10:00 | 1243.062 | 6543.0319 | 0 | 6705.8112
2019-01-21 11:00 | 1217.9629 | 7153.3841 | 286.6667 | 10000
2019-01-21 12:00 | 1197.8194 | 7044.5446 | 2773.3333 | 10000
2019-01-21 13:00 | 1165.8059 | 6292.8483 | 873.3333 | 10000
2019-01-21 14:00 | 1166.6776 | 4892.5013 | 286.6667 | 10000
2019-01-21 15:00 | 1245.7464 | 2843.8902 | 2773.3333 | 10000
2019-01-21 16:00 | 1541.5534 | 531.3448 | 1666.6667 | 10000
2019-01-21 17:00 | 2118.6245 | 0 | 1666.6667 | 10000
2019-01-21 18:00 | 2465.5942 | 0 | 286.6667 | 9548.0421
2019-01-21 19:00 | 2420.9017 | 0 | 286.6667 | 7369.1146
2019-01-21 20:00 | 2252.8064 | 0 | 286.6667 | 5234.8796
2019-01-21 21:00 | 2068.3448 | 0 | 286.6667 | 3268.7398
2019-01-21 22:00 | 1710.6804 | 0 | 0 | 1487.0617
2019-01-21 23:00 | 1360.8709 | 0 | 0 | 0
2019-01-22 | 1012.4045 | 0 | 0 | 0
2019-01-22 01:00 | 877.0126 | 0 | 0 | 0
2019-01-22 02:00 | 826.4 | 0 | 0 | 0
2019-01-22 03:00 | 816.8215 | 0 | 0 | 0
2019-01-22 04:00 | 819.2013 | 0 | 0 | 0
2019-01-22 05:00 | 885.1944 | 0 | 0 | 0
2019-01-22 06:00 | 1136.96 | 0 | 0 | 0
2019-01-22 07:00 | 1514.9863 | 294.0929 | 0 | 0
2019-01-22 08:00 | 1466.688 | 2479.5725 | 0 | 0
2019-01-22 09:00 | 1266.5131 | 4543.3487 | 286.6667 | 1012.8845
2019-01-22 10:00 | 1273.9204 | 5775.4943 | 873.3333 | 4576.3868
2019-01-22 11:00 | 1241.5184 | 6403.4909 | 2773.3333 | 9951.294
2019-01-22 12:00 | 1246.3218 | 6203.5255 | 2773.3333 | 10000
2019-01-22 13:00 | 1242.4496 | 4838.0638 | 4266.6667 | 10000
2019-01-22 14:00 | 1268.2631 | 4069.367 | 6160 | 10000
2019-01-22 15:00 | 1351.2652 | 1541.5934 | 6160 | 10000
2019-01-22 16:00 | 1674.3772 | 65.3085 | 6160 | 10000
2019-01-22 17:00 | 2272.5749 | 0 | 7873.3333 | 10000
2019-01-22 18:00 | 2645.158 | 0 | 6160 | 10000
2019-01-22 19:00 | 2653.2846 | 0 | 7873.3333 | 10000
2019-01-22 20:00 | 2475.9969 | 0 | 6160 | 10000
2019-01-22 21:00 | 2311.9676 | 0 | 6160 | 10000
2019-01-22 22:00 | 1972.1364 | 0 | 7873.3333 | 10000
2019-01-22 23:00 | 1637.7704 | 0 | 7873.3333 | 10000
2019-01-23 | 1286.8751 | 0 | 9060 | 10000
2019-01-23 01:00 | 1140.9131 | 0 | 9060 | 10000
2019-01-23 02:00 | 1087.6222 | 0 | 9060 | 10000
2019-01-23 03:00 | 1078.6953 | 0 | 9573.3333 | 10000
2019-01-23 04:00 | 1064.7714 | 0 | 9873.3333 | 10000
2019-01-23 05:00 | 1133.2132 | 0 | 7873.3333 | 10000
2019-01-23 06:00 | 1394.5648 | 0 | 9060 | 10000
2019-01-23 07:00 | 1698.7745 | 1018.317 | 9573.3333 | 10000
2019-01-23 08:00 | 1619.1588 | 3490.756 | 9573.3333 | 10000
2019-01-23 09:00 | 1369.6154 | 5510.2664 | 9573.3333 | 10000
2019-01-23 10:00 | 1378.0664 | 6800.824 | 9060 | 10000
2019-01-23 11:00 | 1325.5733 | 7384.6778 | 9960 | 10000
2019-01-23 12:00 | 1270.673 | 7294.9146 | 9573.3333 | 10000
2019-01-23 13:00 | 1232.3321 | 6558.2844 | 9873.3333 | 10000
2019-01-23 14:00 | 1225.5876 | 5172.5505 | 10000 | 10000
2019-01-23 15:00 | 1313.1156 | 3076.7847 | 9573.3333 | 10000
2019-01-23 16:00 | 1623.0013 | 699.783 | 9873.3333 | 10000
2019-01-23 17:00 | 2219.6949 | 0 | 10000 | 10000
2019-01-23 18:00 | 2564.2211 | 0 | 10000 | 10000
2019-01-23 19:00 | 2522.6271 | 0 | 10000 | 10000
2019-01-23 20:00 | 2357.8716 | 0 | 10000 | 10000
2019-01-23 21:00 | 2176.7949 | 0 | 10000 | 10000
2019-01-23 22:00 | 1825.4166 | 0 | 10000 | 10000
2019-01-23 23:00 | 1481.0469 | 0 | 9960 | 10000
2019-01-24 | 1146.775 | 0 | 9960 | 10000
2019-01-24 01:00 | 1012.1422 | 0 | 10000 | 10000
2019-01-24 02:00 | 958.178 | 0 | 10000 | 10000
2019-01-24 03:00 | 943.623 | 0 | 10000 | 10000
2019-01-24 04:00 | 940.696 | 0 | 10000 | 10000
2019-01-24 05:00 | 997.3008 | 0 | 10000 | 10000
2019-01-24 06:00 | 1236.1758 | 0 | 10000 | 10000
2019-01-24 07:00 | 1607.1438 | 690.828 | 10000 | 10000
2019-01-24 08:00 | 1532.2539 | 2444.5193 | 9960 | 10000
2019-01-24 09:00 | 1325.324 | 3842.7963 | 9960 | 10000
2019-01-24 10:00 | 1362.5857 | 3880.9406 | 10000 | 10000
2019-01-24 11:00 | 1326.9383 | 4343.6662 | 10000 | 10000
2019-01-24 12:00 | 1291.7765 | 4142.8244 | 10000 | 10000
2019-01-24 13:00 | 1259.1784 | 3139.9094 | 9960 | 10000
2019-01-24 14:00 | 1259.3985 | 1342.8285 | 9573.3333 | 10000
2019-01-24 15:00 | 1334.8979 | 85.407 | 9060 | 10000
2019-01-24 16:00 | 1627.3925 | 0 | 9573.3333 | 10000
2019-01-24 17:00 | 2208.8502 | 0 | 6160 | 10000
2019-01-24 18:00 | 2540.7739 | 0 | 4266.6667 | 10000
2019-01-24 19:00 | 2490.2724 | 0 | 2773.3333 | 10000
2019-01-24 20:00 | 2318.4458 | 0 | 4266.6667 | 10000
2019-01-24 21:00 | 2137.7022 | 0 | 6160 | 10000
2019-01-24 22:00 | 1786.957 | 0 | 4266.6667 | 10000
2019-01-24 23:00 | 1443.1652 | 0 | 4266.6667 | 10000
2019-01-25 | 1102.4695 | 0 | 2773.3333 | 10000
2019-01-25 01:00 | 968.0245 | 0 | 2773.3333 | 10000
2019-01-25 02:00 | 914.5121 | 0 | 2773.3333 | 10000
2019-01-25 03:00 | 899.3305 | 0 | 4266.6667 | 10000
2019-01-25 04:00 | 896.3437 | 0 | 4266.6667 | 10000
2019-01-25 05:00 | 956.9103 | 0 | 2773.3333 | 10000
2019-01-25 06:00 | 1215.3361 | 0 | 7873.3333 | 10000
2019-01-25 07:00 | 1537.4715 | 0 | 7873.3333 | 10000
2019-01-25 08:00 | 1464.2614 | 32.6565 | 7873.3333 | 10000
2019-01-25 09:00 | 1235.7892 | 233.9077 | 9060 | 10000
2019-01-25 10:00 | 1253.5029 | 660.9774 | 9060 | 10000
2019-01-25 11:00 | 1230.6477 | 499.1299 | 9573.3333 | 10000
2019-01-25 12:00 | 1195.7628 | 368.2196 | 7873.3333 | 10000
2019-01-25 13:00 | 1162.4777 | 10.7341 | 1666.6667 | 10000
2019-01-25 14:00 | 1155.6555 | 0 | 7873.3333 | 10000
2019-01-25 15:00 | 1239.1712 | 0.50025 | 4266.6667 | 10000
2019-01-25 16:00 | 1536.3834 | 0 | 4266.6667 | 10000
2019-01-25 17:00 | 2116.4573 | 0 | 2773.3333 | 10000
2019-01-25 18:00 | 2458.0514 | 0 | 2773.3333 | 10000
2019-01-25 19:00 | 2406.4321 | 0 | 1666.6667 | 10000
2019-01-25 20:00 | 2233.1742 | 0 | 1666.6667 | 9260.2345
2019-01-25 21:00 | 2043.6667 | 0 | 873.3333 | 8693.727
2019-01-25 22:00 | 1695.2938 | 0 | 286.6667 | 7523.3937
2019-01-25 23:00 | 1347.5914 | 0 | 286.6667 | 6114.7665
2019-01-26 | 1004.3397 | 0 | 873.3333 | 5053.8418
2019-01-26 01:00 | 863.1574 | 0 | 873.3333 | 4922.8354
2019-01-26 02:00 | 809.8609 | 0 | 873.3333 | 4933.0114
2019-01-26 03:00 | 795.9519 | 0 | 873.3333 | 4996.4838
2019-01-26 04:00 | 786.9748 | 0 | 286.6667 | 5073.8652
2019-01-26 05:00 | 844.2034 | 0 | 873.3333 | 4573.5571
2019-01-26 06:00 | 1082.3061 | 0 | 0 | 4602.687
2019-01-26 07:00 | 1445.1917 | 76.9649 | 0 | 3520.3809
2019-01-26 08:00 | 1373.4371 | 596.4693 | 873.3333 | 2152.1541
2019-01-26 09:00 | 1176.8673 | 3859.5679 | 873.3333 | 2248.5197
2019-01-26 10:00 | 1193.6198 | 6363.6136 | 4266.6667 | 5804.5536
2019-01-26 11:00 | 1173.5659 | 6914.9029 | 4266.6667 | 10000
2019-01-26 12:00 | 1143.9622 | 4356.8704 | 4266.6667 | 10000
2019-01-26 13:00 | 1112.9298 | 1267.392 | 7873.3333 | 10000
2019-01-26 14:00 | 1110.1004 | 2863.6346 | 6160 | 10000
2019-01-26 15:00 | 1187.069 | 2828.3249 | 9060 | 10000
2019-01-26 16:00 | 1481.0084 | 225.109 | 4266.6667 | 10000
2019-01-26 17:00 | 2053.1912 | 0 | 4266.6667 | 10000
2019-01-26 18:00 | 2399.1319 | 0 | 4266.6667 | 10000
2019-01-26 19:00 | 2357.4158 | 0 | 4266.6667 | 10000
2019-01-26 20:00 | 2188.2032 | 0 | 4266.6667 | 10000
2019-01-26 21:00 | 2002.5932 | 0 | 4266.6667 | 10000
2019-01-26 22:00 | 1653.2331 | 0 | 7873.3333 | 10000
2019-01-26 23:00 | 1307.8693 | 0 | 9060 | 10000
2019-01-27 | 964.0521 | 0 | 4266.6667 | 10000
2019-01-27 01:00 | 812.9373 | 0 | 2773.3333 | 10000
2019-01-27 02:00 | 751.122 | 0 | 4266.6667 | 10000
2019-01-27 03:00 | 735.998 | 0 | 7873.3333 | 10000
2019-01-27 04:00 | 728.5807 | 0 | 6160 | 10000
2019-01-27 05:00 | 779.7277 | 0 | 4266.6667 | 10000
2019-01-27 06:00 | 1017.552 | 0 | 873.3333 | 10000
2019-01-27 07:00 | 1369.2532 | 897.0713 | 2773.3333 | 9855.7814
2019-01-27 08:00 | 1306.6954 | 3200.427 | 2773.3333 | 10000
2019-01-27 09:00 | 1105.7016 | 5195.6436 | 9873.3333 | 10000
2019-01-27 10:00 | 1106.6311 | 6542.4294 | 9573.3333 | 10000
2019-01-27 11:00 | 1108.8422 | 7134.0917 | 9960 | 10000
2019-01-27 12:00 | 1082.8504 | 7038.3185 | 9060 | 10000
2019-01-27 13:00 | 1060.5898 | 6154.1249 | 9060 | 10000
2019-01-27 14:00 | 1062.0479 | 2365.2395 | 9060 | 10000
2019-01-27 15:00 | 1142.0533 | 1770.5814 | 6160 | 10000
2019-01-27 16:00 | 1433.1679 | 281.0761 | 6160 | 10000
2019-01-27 17:00 | 1990.3296 | 0 | 6160 | 10000
2019-01-27 18:00 | 2365.4897 | 0 | 4266.6667 | 10000
2019-01-27 19:00 | 2302.7784 | 0 | 4266.6667 | 10000
2019-01-27 20:00 | 2128.5062 | 0 | 4266.6667 | 10000
2019-01-27 21:00 | 1938.3175 | 0 | 4266.6667 | 10000
2019-01-27 22:00 | 1585.3487 | 0 | 4266.6667 | 10000
2019-01-27 23:00 | 1241.4877 | 0 | 6160 | 10000
2019-01-28 | 917.6138 | 0 | 6160 | 10000
2019-01-28 01:00 | 780.2961 | 0 | 4266.6667 | 10000
2019-01-28 02:00 | 736.7804 | 0 | 6160 | 10000
2019-01-28 03:00 | 731.9534 | 0 | 4266.6667 | 10000
2019-01-28 04:00 | 735.6987 | 0 | 1666.6667 | 10000
2019-01-28 05:00 | 795.0888 | 0 | 873.3333 | 10000
2019-01-28 06:00 | 1060.5679 | 0 | 873.3333 | 10000
2019-01-28 07:00 | 1413.7599 | 756.0733 | 2773.3333 | 9812.7654
2019-01-28 08:00 | 1378.1132 | 1108.0664 | 2773.3333 | 10000
2019-01-28 09:00 | 1197.819 | 1857.8825 | 9060 | 10000
2019-01-28 10:00 | 1223.886 | 6569.4911 | 7873.3333 | 10000
2019-01-28 11:00 | 1253.7416 | 4771.3592 | 4266.6667 | 10000
2019-01-28 12:00 | 1203.0159 | 6987.5863 | 7873.3333 | 10000
2019-01-28 13:00 | 1154.5071 | 646.6691 | 7873.3333 | 10000
2019-01-28 14:00 | 1159.9189 | 2356.7479 | 9060 | 10000
2019-01-28 15:00 | 1232.5716 | 54.0109 | 4266.6667 | 10000
2019-01-28 16:00 | 1537.1242 | 426.2751 | 4266.6667 | 10000
2019-01-28 17:00 | 2120.1088 | 0 | 4266.6667 | 10000
2019-01-28 18:00 | 2479.0492 | 0 | 2773.3333 | 10000
2019-01-28 19:00 | 2438.347 | 0 | 1666.6667 | 10000
2019-01-28 20:00 | 2275.1822 | 0 | 2773.3333 | 9228.3197
2019-01-28 21:00 | 2095.7377 | 0 | 2773.3333 | 9726.4708
2019-01-28 22:00 | 1739.3605 | 0 | 2773.3333 | 10000
2019-01-28 23:00 | 1385.1879 | 0 | 2773.3333 | 10000
2019-01-29 | 1036.3004 | 0 | 2773.3333 | 10000
2019-01-29 01:00 | 896.7224 | 0 | 1666.6667 | 10000
2019-01-29 02:00 | 843.5519 | 0 | 873.3333 | 10000
2019-01-29 03:00 | 831.8732 | 0 | 2773.3333 | 10000
2019-01-29 04:00 | 829.6349 | 0 | 1666.6667 | 10000
2019-01-29 05:00 | 886.9388 | 0 | 873.3333 | 10000
2019-01-29 06:00 | 1129.8136 | 0 | 1666.6667 | 9986.3945
2019-01-29 07:00 | 1507.9069 | 1170.9116 | 1666.6667 | 10000
2019-01-29 08:00 | 1448.6848 | 3887.3496 | 2773.3333 | 10000
2019-01-29 09:00 | 1246.9369 | 6161.0571 | 4266.6667 | 10000
2019-01-29 10:00 | 1241.8035 | 7622.951 | 2773.3333 | 10000
2019-01-29 11:00 | 1206.4906 | 8309.9011 | 2773.3333 | 10000
2019-01-29 12:00 | 1177.6434 | 8255.3233 | 6160 | 10000
2019-01-29 13:00 | 1143.8723 | 7376.5255 | 4266.6667 | 10000
2019-01-29 14:00 | 1145.2487 | 5818.8459 | 873.3333 | 10000
2019-01-29 15:00 | 1234.9285 | 3563.2025 | 2773.3333 | 10000
2019-01-29 16:00 | 1524.0564 | 965.8356 | 1666.6667 | 10000
2019-01-29 17:00 | 2097.5615 | 0 | 286.6667 | 10000
2019-01-29 18:00 | 2449.7931 | 0 | 286.6667 | 8189.1051
2019-01-29 19:00 | 2403.8072 | 0 | 286.6667 | 6025.9787
2019-01-29 20:00 | 2234.9994 | 0 | 873.3333 | 3908.8382
2019-01-29 21:00 | 2049.7907 | 0 | 873.3333 | 2547.1721
2019-01-29 22:00 | 1691.7112 | 0 | 286.6667 | 1370.7147
2019-01-29 23:00 | 1341.183 | 0 | 286.6667 | 0
2019-01-30 | 989.0102 | 0 | 873.3333 | 0
2019-01-30 01:00 | 861.0135 | 0 | 286.6667 | 0
2019-01-30 02:00 | 818.3529 | 0 | 286.6667 | 0
2019-01-30 03:00 | 809.9062 | 0 | 873.3333 | 0
2019-01-30 04:00 | 813.1561 | 0 | 873.3333 | 63.4271
2019-01-30 05:00 | 877.9137 | 0 | 873.3333 | 123.6043
2019-01-30 06:00 | 1136.9463 | 0 | 286.6667 | 119.0239
2019-01-30 07:00 | 1485.9642 | 1176.7524 | 0 | 0
2019-01-30 08:00 | 1399.612 | 3822.5459 | 873.3333 | 0
2019-01-30 09:00 | 1169.9742 | 5959.3598 | 286.6667 | 3296.2673
2019-01-30 10:00 | 1173.7355 | 7151.8155 | 0 | 8372.3196
2019-01-30 11:00 | 1154.9907 | 6743.6506 | 0 | 10000
2019-01-30 12:00 | 1128.5623 | 7665.4343 | 286.6667 | 10000
2019-01-30 13:00 | 1104.6879 | 5993.3158 | 873.3333 | 10000
2019-01-30 14:00 | 1112.4942 | 3890.8537 | 1666.6667 | 10000
2019-01-30 15:00 | 1207.002 | 1044.9716 | 2773.3333 | 10000
2019-01-30 16:00 | 1508.1507 | 132.626 | 873.3333 | 10000
2019-01-30 17:00 | 2092.0525 | 0 | 286.6667 | 9497.8086
2019-01-30 18:00 | 2441.2049 | 0 | 4266.6667 | 7692.4228
2019-01-30 19:00 | 2402.3179 | 0 | 4266.6667 | 9517.8846
2019-01-30 20:00 | 2240.2838 | 0 | 2773.3333 | 10000
2019-01-30 21:00 | 2061.5464 | 0 | 2773.3333 | 10000
2019-01-30 22:00 | 1720.4238 | 0 | 2773.3333 | 10000
2019-01-30 23:00 | 1385.1798 | 0 | 4266.6667 | 10000
2019-01-31 | 1054.0378 | 0 | 4266.6667 | 10000
2019-01-31 01:00 | 921.4298 | 0 | 4266.6667 | 10000
2019-01-31 02:00 | 876.8591 | 0 | 4266.6667 | 10000
2019-01-31 03:00 | 871.5935 | 0 | 2773.3333 | 10000
2019-01-31 04:00 | 874.8927 | 0 | 1666.6667 | 10000
2019-01-31 05:00 | 940.7039 | 0 | 2773.3333 | 10000
2019-01-31 06:00 | 1205.3787 | 0 | 1666.6667 | 10000
2019-01-31 07:00 | 1552.6316 | 1141.8787 | 873.3333 | 10000
2019-01-31 08:00 | 1456.0062 | 3663.8011 | 286.6667 | 10000
2019-01-31 09:00 | 1225.0165 | 5592.2936 | 0 | 10000
2019-01-31 10:00 | 1225.0856 | 6874.9795 | 0 | 10000
2019-01-31 11:00 | 1181.3611 | 7646.5915 | 0 | 10000
2019-01-31 12:00 | 1139.69 | 7576.8854 | 0 | 10000
2019-01-31 13:00 | 1108.6061 | 6796.101 | 0 | 10000
2019-01-31 14:00 | 1115.7237 | 5360.0994 | 0 | 10000
2019-01-31 15:00 | 1205.0264 | 3227.2875 | 0 | 10000
2019-01-31 16:00 | 1508.9029 | 908.0768 | 0 | 10000
2019-01-31 17:00 | 2091.8662 | 0 | 0 | 9399.1739
2019-01-31 18:00 | 2443.7305 | 0 | 0 | 7307.3077
2019-01-31 19:00 | 2404.0791 | 0 | 0 | 4863.5772
2019-01-31 20:00 | 2236.941 | 0 | 0 | 2459.498
2019-01-31 21:00 | 2058.18 | 0 | 0 | 222.557
2019-01-31 22:00 | 1718.4208 | 0 | 0 | 0
2019-01-31 23:00 | 1386.1312 | 0 | 0 | 0
Formulas:
Solar (kW) = OFFSET('8760'!A2,[Battery (kWH), row below],0)

## 8760
Date-Hour | Load | Solar | Wind | Battery at Start | Net Energy | Energy to/from Battery | Deficit
2019-01-01 | 1042.0208 | 0 | 2773.3333 | 10000 | 1731.3126 | 0 | 0
2019-01-01 01:00 | 893.3192 | 0 | 4266.6667 | 10000 | 3373.3475 | 0 | 0
2019-01-01 02:00 | 839.8014 | 0 | 2773.3333 | 10000 | 1933.5319 | 0 | 0
2019-01-01 03:00 | 821.5169 | 0 | 4266.6667 | 10000 | 3445.1498 | 0 | 0
2019-01-01 04:00 | 816.1413 | 0 | 6160 | 10000 | 5343.8587 | 0 | 0
2019-01-01 05:00 | 873.2033 | 0 | 2773.3333 | 10000 | 1900.13 | 0 | 0
2019-01-01 06:00 | 1122.6479 | 0 | 2773.3333 | 10000 | 1650.6854 | 0 | 0
2019-01-01 07:00 | 1499.8922 | 0 | 2773.3333 | 10000 | 1273.4411 | 0 | 0
2019-01-01 08:00 | 1448.3726 | 708.2896 | 4266.6667 | 10000 | 3526.5837 | 0 | 0
2019-01-01 09:00 | 1236.4919 | 1129.5231 | 7873.3333 | 10000 | 7766.3645 | 0 | 0
2019-01-01 10:00 | 1252.2673 | 1224.4694 | 7873.3333 | 10000 | 7845.5355 | 0 | 0
2019-01-01 11:00 | 1215.4377 | 1659.0774 | 9573.3333 | 10000 | 10016.973 | 0 | 0
2019-01-01 12:00 | 1168.2547 | 2055.2789 | 9060 | 10000 | 9947.0241 | 0 | 0
2019-01-01 13:00 | 1136.2649 | 1889.7156 | 7873.3333 | 10000 | 8626.7841 | 0 | 0
2019-01-01 14:00 | 1138.8866 | 628.8913 | 9060 | 10000 | 8550.0047 | 0 | 0
2019-01-01 15:00 | 1226.292 | 394.1476 | 1666.6667 | 10000 | 834.5222 | 0 | 0
2019-01-01 16:00 | 1536.5213 | 0 | 873.3333 | 10000 | -663.188 | -663.188 | 0
2019-01-01 17:00 | 2126.095 | 0 | 873.3333 | 9336.812 | -1252.7617 | -1252.7617 | 0
2019-01-01 18:00 | 2488.3215 | 0 | 286.6667 | 8084.0504 | -2201.6549 | -2201.6549 | 0
2019-01-01 19:00 | 2454.9812 | 0 | 873.3333 | 5882.3955 | -1581.6479 | -1581.6479 | 0
2019-01-01 20:00 | 2299.757 | 0 | 286.6667 | 4300.7476 | -2013.0903 | -2013.0903 | 0
2019-01-01 21:00 | 2130.1209 | 0 | 286.6667 | 2287.6573 | -1843.4542 | -1843.4542 | 0
2019-01-01 22:00 | 1783.9856 | 0 | 286.6667 | 444.2031 | -1497.3189 | -444.2031 | -1053.1158
2019-01-01 23:00 | 1433.6875 | 0 | 286.6667 | 0 | -1147.0208 | 0 | -2200.1366
2019-01-02 | 1079.4076 | 0 | 286.6667 | 0 | -792.7409 | 0 | -2992.8775
2019-01-02 01:00 | 952.1266 | 0 | 0 | 0 | -952.1266 | 0 | -3945.0041
2019-01-02 02:00 | 911.2734 | 0 | 0 | 0 | -911.2734 | 0 | -4856.2775
2019-01-02 03:00 | 893.1193 | 0 | 0 | 0 | -893.1193 | 0 | -5749.3968
2019-01-02 04:00 | 897.4218 | 0 | 0 | 0 | -897.4218 | 0 | -6646.8186
2019-01-02 05:00 | 961.3495 | 0 | 0 | 0 | -961.3495 | 0 | -7608.1681
2019-01-02 06:00 | 1205.3234 | 0 | 0 | 0 | -1205.3234 | 0 | -8813.4915
2019-01-02 07:00 | 1571.0671 | 0 | 0 | 0 | -1571.0671 | 0 | -10384.5586
2019-01-02 08:00 | 1476.0105 | 56.3028 | 0 | 0 | -1419.7076 | 0 | -11804.2662
2019-01-02 09:00 | 1238.1063 | 576.1557 | 286.6667 | 0 | -375.2839 | 0 | -12179.5501
2019-01-02 10:00 | 1263.1562 | 1431.367 | 0 | 0 | 168.2108 | 168.2108 | -12011.3393
2019-01-02 11:00 | 1240.8118 | 1858.0987 | 0 | 168.2108 | 617.2869 | 617.2869 | -11225.8416
2019-01-02 12:00 | 1199.2196 | 1415.5718 | 0 | 785.4977 | 216.3522 | 216.3522 | -10223.9918
2019-01-02 13:00 | 1145.3117 | 1486.8292 | 0 | 1001.8499 | 341.5175 | 341.5175 | -8880.6243
2019-01-02 14:00 | 1146.5493 | 781.2559 | 0 | 1343.3674 | -365.2934 | -365.2934 | -7902.5503
2019-01-02 15:00 | 1232.2918 | 233.3545 | 0 | 978.074 | -998.9372 | -978.074 | -7923.4135
2019-01-02 16:00 | 1530.4 | 0 | 0 | 0 | -1530.4 | 0 | -9453.8135
2019-01-02 17:00 | 2112.549 | 0 | 286.6667 | 0 | -1825.8823 | 0 | -11279.6958
2019-01-02 18:00 | 2455.9215 | 0 | 873.3333 | 0 | -1582.5882 | 0 | -12862.284
2019-01-02 19:00 | 2413.3347 | 0 | 286.6667 | 0 | -2126.6681 | 0 | -14988.952
2019-01-02 20:00 | 2242.7475 | 0 | 286.6667 | 0 | -1956.0808 | 0 | -16945.0329
2019-01-02 21:00 | 2055.1301 | 0 | 286.6667 | 0 | -1768.4634 | 0 | -18713.4963
2019-01-02 22:00 | 1705.7544 | 0 | 873.3333 | 0 | -832.4211 | 0 | -19545.9174
2019-01-02 23:00 | 1362.2701 | 0 | 873.3333 | 0 | -488.9368 | 0 | -20034.8541
2019-01-03 | 1019.1125 | 0 | 1666.6667 | 0 | 647.5542 | 647.5542 | -19387.3
2019-01-03 01:00 | 882.2924 | 0 | 1666.6667 | 647.5542 | 784.3743 | 784.3743 | -17955.3715
2019-01-03 02:00 | 827.7665 | 0 | 286.6667 | 1431.9285 | -541.0998 | -541.0998 | -17064.5429
2019-01-03 03:00 | 815.8933 | 0 | 1666.6667 | 890.8286 | 850.7734 | 850.7734 | -15322.9409
2019-01-03 04:00 | 809.4685 | 0 | 2773.3333 | 1741.602 | 1963.8648 | 1963.8648 | -11617.4741
2019-01-03 05:00 | 862.3635 | 0 | 4266.6667 | 3705.4668 | 3404.3032 | 3404.3032 | -4507.7042
2019-01-03 06:00 | 1099.3037 | 0 | 7873.3333 | 7109.7699 | 6774.0297 | 2890.2301 | 0
2019-01-03 07:00 | 1463.6729 | 0 | 9060 | 10000 | 7596.3271 | 0 | 0
2019-01-03 08:00 | 1397.2756 | 2298.1554 | 7873.3333 | 10000 | 8774.2131 | 0 | 0
2019-01-03 09:00 | 1193.6693 | 355.7939 | 7873.3333 | 10000 | 7035.458 | 0 | 0
2019-01-03 10:00 | 1210.2789 | 794.3579 | 7873.3333 | 10000 | 7457.4124 | 0 | 0
2019-01-03 11:00 | 1196.5668 | 1494.9402 | 7873.3333 | 10000 | 8171.7067 | 0 | 0
2019-01-03 12:00 | 1169.7933 | 2408.8038 | 7873.3333 | 10000 | 9112.3439 | 0 | 0
2019-01-03 13:00 | 1141.3569 | 1058.008 | 7873.3333 | 10000 | 7789.9845 | 0 | 0
2019-01-03 14:00 | 1139.9138 | 140.9877 | 7873.3333 | 10000 | 6874.4072 | 0 | 0
2019-01-03 15:00 | 1218.3248 | 591.491 | 9060 | 10000 | 8433.1662 | 0 | 0
2019-01-03 16:00 | 1506.9759 | 0 | 9573.3333 | 10000 | 8066.3575 | 0 | 0
2019-01-03 17:00 | 2037.4872 | 0 | 9060 | 10000 | 7022.5128 | 0 | 0
2019-01-03 18:00 | 2436.5917 | 0 | 9060 | 10000 | 6623.4083 | 0 | 0
2019-01-03 19:00 | 2369.5303 | 0 | 6160 | 10000 | 3790.4697 | 0 | 0
2019-01-03 20:00 | 2201.5219 | 0 | 7873.3333 | 10000 | 5671.8114 | 0 | 0
2019-01-03 21:00 | 2010.361 | 0 | 7873.3333 | 10000 | 5862.9723 | 0 | 0
2019-01-03 22:00 | 1662.7543 | 0 | 9060 | 10000 | 7397.2457 | 0 | 0
2019-01-03 23:00 | 1325.8165 | 0 | 9060 | 10000 | 7734.1835 | 0 | 0
2019-01-04 | 990.4983 | 0 | 2773.3333 | 10000 | 1782.835 | 0 | 0
2019-01-04 01:00 | 861.2787 | 0 | 873.3333 | 10000 | 12.0546 | 0 | 0
2019-01-04 02:00 | 811.391 | 0 | 286.6667 | 10000 | -524.7243 | -524.7243 | 0
2019-01-04 03:00 | 801.9284 | 0 | 2773.3333 | 9475.2757 | 1971.405 | 524.7243 | 0
2019-01-04 04:00 | 804.1801 | 0 | 1666.6667 | 10000 | 862.4866 | 0 | 0
2019-01-04 05:00 | 867.4404 | 0 | 873.3333 | 10000 | 5.8929 | 0 | 0
2019-01-04 06:00 | 1119.6275 | 0 | 873.3333 | 10000 | -246.2942 | -246.2942 | 0
2019-01-04 07:00 | 1446.7352 | 733.6448 | 286.6667 | 9753.7058 | -426.4237 | -426.4237 | 0
2019-01-04 08:00 | 1402.3409 | 3144.2943 | 286.6667 | 9327.2821 | 2028.6202 | 672.7179 | 0
2019-01-04 09:00 | 1221.9481 | 5160.0902 | 2773.3333 | 10000 | 6711.4754 | 0 | 0
2019-01-04 10:00 | 1209.5577 | 3703.1104 | 2773.3333 | 10000 | 5266.8861 | 0 | 0
2019-01-04 11:00 | 1204.1012 | 3526.8016 | 4266.6667 | 10000 | 6589.3671 | 0 | 0
2019-01-04 12:00 | 1169.0455 | 3210.4377 | 1666.6667 | 10000 | 3708.059 | 0 | 0
2019-01-04 13:00 | 1131.7361 | 3272.2894 | 2773.3333 | 10000 | 4913.8865 | 0 | 0
2019-01-04 14:00 | 1138.8976 | 4464.185 | 873.3333 | 10000 | 4198.6208 | 0 | 0
2019-01-04 15:00 | 1228.0748 | 2245.505 | 1666.6667 | 10000 | 2684.0968 | 0 | 0
2019-01-04 16:00 | 1551.8261 | 0 | 873.3333 | 10000 | -678.4928 | -678.4928 | 0
2019-01-04 17:00 | 2138.284 | 0 | 1666.6667 | 9321.5072 | -471.6173 | -471.6173 | 0
2019-01-04 18:00 | 2490.7181 | 0 | 4266.6667 | 8849.8899 | 1775.9485 | 1150.1101 | 0
2019-01-04 19:00 | 2454.1603 | 0 | 6160 | 10000 | 3705.8397 | 0 | 0
2019-01-04 20:00 | 2298.0408 | 0 | 7873.3333 | 10000 | 5575.2925 | 0 | 0
2019-01-04 21:00 | 2115.7759 | 0 | 6160 | 10000 | 4044.2241 | 0 | 0
2019-01-04 22:00 | 1770.7263 | 0 | 7873.3333 | 10000 | 6102.6071 | 0 | 0
2019-01-04 23:00 | 1435.3098 | 0 | 4266.6667 | 10000 | 2831.3569 | 0 | 0
2019-01-05 | 1108.1231 | 0 | 7873.3333 | 10000 | 6765.2102 | 0 | 0
2019-01-05 01:00 | 977.69 | 0 | 6160 | 10000 | 5182.31 | 0 | 0
2019-01-05 02:00 | 934.1205 | 0 | 9060 | 10000 | 8125.8795 | 0 | 0
2019-01-05 03:00 | 921.89 | 0 | 4266.6667 | 10000 | 3344.7767 | 0 | 0
2019-01-05 04:00 | 938.3732 | 0 | 6160 | 10000 | 5221.6268 | 0 | 0
2019-01-05 05:00 | 1000.0422 | 0 | 7873.3333 | 10000 | 6873.2912 | 0 | 0
2019-01-05 06:00 | 1251.0793 | 0 | 6160 | 10000 | 4908.9207 | 0 | 0
2019-01-05 07:00 | 1593.9334 | 707.3707 | 4266.6667 | 10000 | 3380.104 | 0 | 0
2019-01-05 08:00 | 1511.5761 | 3028.0374 | 6160 | 10000 | 7676.4613 | 0 | 0
2019-01-05 09:00 | 1285.8132 | 655.6265 | 7873.3333 | 10000 | 7243.1466 | 0 | 0
2019-01-05 10:00 | 1296.9823 | 1927.0918 | 7873.3333 | 10000 | 8503.4429 | 0 | 0
2019-01-05 11:00 | 1253.0589 | 3099.8158 | 9060 | 10000 | 10906.7569 | 0 | 0
2019-01-05 12:00 | 1202.8901 | 2959.3812 | 4266.6667 | 10000 | 6023.1578 | 0 | 0
2019-01-05 13:00 | 1160.6337 | 2077.6314 | 1666.6667 | 10000 | 2583.6644 | 0 | 0
2019-01-05 14:00 | 1166.9031 | 2572.4649 | 6160 | 10000 | 7565.5618 | 0 | 0
2019-01-05 15:00 | 1265.0815 | 2092.4733 | 2773.3333 | 10000 | 3600.7251 | 0 | 0
2019-01-05 16:00 | 1573.6313 | 0 | 1666.6667 | 10000 | 93.0354 | 0 | 0
2019-01-05 17:00 | 2171.8176 | 0 | 286.6667 | 10000 | -1885.1509 | -1885.1509 | 0
2019-01-05 18:00 | 2522.1304 | 0 | 873.3333 | 8114.8491 | -1648.797 | -1648.797 | 0
2019-01-05 19:00 | 2487.6218 | 0 | 873.3333 | 6466.0521 | -1614.2884 | -1614.2884 | 0
2019-01-05 20:00 | 2325.2633 | 0 | 873.3333 | 4851.7636 | -1451.93 | -1451.93 | 0
2019-01-05 21:00 | 2145.8022 | 0 | 286.6667 | 3399.8337 | -1859.1355 | -1859.1355 | 0
2019-01-05 22:00 | 1802.0216 | 0 | 286.6667 | 1540.6982 | -1515.355 | -1515.355 | 0
2019-01-05 23:00 | 1461.3819 | 0 | 1666.6667 | 25.3432 | 205.2848 | 205.2848 | 0
2019-01-06 | 1129.743 | 0 | 286.6667 | 230.628 | -843.0763 | -230.628 | -612.4484
2019-01-06 01:00 | 990.0455 | 0 | 286.6667 | 0 | -703.3788 | 0 | -1315.8272
2019-01-06 02:00 | 940.1069 | 0 | 873.3333 | 0 | -66.7735 | 0 | -1382.6007
2019-01-06 03:00 | 933.8959 | 0 | 873.3333 | 0 | -60.5626 | 0 | -1443.1633
2019-01-06 04:00 | 931.2571 | 0 | 286.6667 | 0 | -644.5905 | 0 | -2087.7538
2019-01-06 05:00 | 992.2818 | 0 | 286.6667 | 0 | -705.6151 | 0 | -2793.3689
2019-01-06 06:00 | 1234.5975 | 0 | 0 | 0 | -1234.5975 | 0 | -4027.9664
2019-01-06 07:00 | 1574.0274 | 726.1974 | 0 | 0 | -847.83 | 0 | -4875.7964
2019-01-06 08:00 | 1495.3606 | 3066.0667 | 0 | 0 | 1570.7062 | 1570.7062 | -3305.0902
2019-01-06 09:00 | 1254.2489 | 5005.4969 | 0 | 1570.7062 | 3751.248 | 3751.248 | 0
2019-01-06 10:00 | 1256.5931 | 6386.134 | 0 | 5321.9542 | 5129.5409 | 4678.0458 | 0
2019-01-06 11:00 | 1214.7196 | 6955.9417 | 286.6667 | 10000 | 6027.8888 | 0 | 0
2019-01-06 12:00 | 1172.1534 | 6795.2833 | 286.6667 | 10000 | 5909.7966 | 0 | 0
2019-01-06 13:00 | 1131.0846 | 5947.2825 | 286.6667 | 10000 | 5102.8645 | 0 | 0
2019-01-06 14:00 | 1141.6182 | 2867.7998 | 873.3333 | 10000 | 2599.515 | 0 | 0
2019-01-06 15:00 | 1226.4254 | 1499.5413 | 873.3333 | 10000 | 1146.4493 | 0 | 0
2019-01-06 16:00 | 1531.0673 | 0 | 873.3333 | 10000 | -657.734 | -657.734 | 0
2019-01-06 17:00 | 2112.311 | 0 | 1666.6667 | 9342.266 | -445.6444 | -445.6444 | 0
2019-01-06 18:00 | 2461.3628 | 0 | 286.6667 | 8896.6217 | -2174.6961 | -2174.6961 | 0
2019-01-06 19:00 | 2421.6762 | 0 | 873.3333 | 6721.9255 | -1548.3428 | -1548.3428 | 0
2019-01-06 20:00 | 2254.9516 | 0 | 873.3333 | 5173.5827 | -1381.6182 | -1381.6182 | 0
2019-01-06 21:00 | 2073.3565 | 0 | 286.6667 | 3791.9645 | -1786.6898 | -1786.6898 | 0
2019-01-06 22:00 | 1726.4627 | 0 | 286.6667 | 2005.2747 | -1439.7961 | -1439.7961 | 0
2019-01-06 23:00 | 1386.7211 | 0 | 873.3333 | 565.4786 | -513.3878 | -513.3878 | 0
2019-01-07 | 1053.7304 | 0 | 1666.6667 | 52.0908 | 612.9363 | 612.9363 | 0
2019-01-07 01:00 | 914.2289 | 0 | 873.3333 | 665.027 | -40.8956 | -40.8956 | 0
2019-01-07 02:00 | 859.6796 | 0 | 873.3333 | 624.1314 | 13.6537 | 13.6537 | 0
2019-01-07 03:00 | 840.5408 | 0 | 286.6667 | 637.7852 | -553.8741 | -553.8741 | 0
2019-01-07 04:00 | 835.563 | 0 | 286.6667 | 83.911 | -548.8963 | -83.911 | -464.9853
2019-01-07 05:00 | 894.051 | 0 | 286.6667 | 0 | -607.3843 | 0 | -1072.3696
2019-01-07 06:00 | 1139.0025 | 0 | 873.3333 | 0 | -265.6691 | 0 | -1338.0387
2019-01-07 07:00 | 1498.2187 | 173.4545 | 873.3333 | 0 | -451.4309 | 0 | -1789.4696
2019-01-07 08:00 | 1446.7904 | 3075.5278 | 873.3333 | 0 | 2502.0707 | 2502.0707 | 0
2019-01-07 09:00 | 1237.1264 | 5064.7897 | 2773.3333 | 2502.0707 | 6600.9967 | 6600.9967 | 0
2019-01-07 10:00 | 1250.1037 | 6355.6268 | 2773.3333 | 9103.0674 | 7878.8565 | 896.9326 | 0
2019-01-07 11:00 | 1232.5755 | 6946.422 | 1666.6667 | 10000 | 7380.5132 | 0 | 0
2019-01-07 12:00 | 1195.4708 | 6827.9594 | 2773.3333 | 10000 | 8405.8219 | 0 | 0
2019-01-07 13:00 | 1152.4164 | 5979.8079 | 4266.6667 | 10000 | 9094.0582 | 0 | 0
2019-01-07 14:00 | 1153.606 | 4377.5842 | 6160 | 10000 | 9383.9782 | 0 | 0
2019-01-07 15:00 | 1232.5736 | 2281.1331 | 4266.6667 | 10000 | 5315.2262 | 0 | 0
2019-01-07 16:00 | 1523.9281 | 0 | 6160 | 10000 | 4636.0719 | 0 | 0
2019-01-07 17:00 | 2092.4904 | 0 | 9060 | 10000 | 6967.5096 | 0 | 0
2019-01-07 18:00 | 2439.7012 | 0 | 9060 | 10000 | 6620.2988 | 0 | 0
2019-01-07 19:00 | 2393.0598 | 0 | 9573.3333 | 10000 | 7180.2735 | 0 | 0
2019-01-07 20:00 | 2221.3541 | 0 | 9060 | 10000 | 6838.6459 | 0 | 0
2019-01-07 21:00 | 2035.6386 | 0 | 6160 | 10000 | 4124.3614 | 0 | 0
2019-01-07 22:00 | 1677.6564 | 0 | 4266.6667 | 10000 | 2589.0102 | 0 | 0
2019-01-07 23:00 | 1320.8098 | 0 | 4266.6667 | 10000 | 2945.8569 | 0 | 0
2019-01-08 | 971.7899 | 0 | 4266.6667 | 10000 | 3294.8767 | 0 | 0
2019-01-08 01:00 | 832.3694 | 0 | 4266.6667 | 10000 | 3434.2973 | 0 | 0
2019-01-08 02:00 | 780.3847 | 0 | 2773.3333 | 10000 | 1992.9487 | 0 | 0
2019-01-08 03:00 | 776.5227 | 0 | 2773.3333 | 10000 | 1996.8106 | 0 | 0
2019-01-08 04:00 | 779.5976 | 0 | 2773.3333 | 10000 | 1993.7357 | 0 | 0
2019-01-08 05:00 | 843.6749 | 0 | 2773.3333 | 10000 | 1929.6584 | 0 | 0
2019-01-08 06:00 | 1092.6993 | 0 | 873.3333 | 10000 | -219.366 | -219.366 | 0
2019-01-08 07:00 | 1468.5789 | 26.2648 | 1666.6667 | 9780.634 | 224.3526 | 219.366 | 0
2019-01-08 08:00 | 1417.516 | 311.8742 | 4266.6667 | 10000 | 3161.0249 | 0 | 0
2019-01-08 09:00 | 1234.5601 | 2820.7211 | 4266.6667 | 10000 | 5852.8277 | 0 | 0
2019-01-08 10:00 | 1264.5128 | 1591.439 | 2773.3333 | 10000 | 3100.2595 | 0 | 0
2019-01-08 11:00 | 1254.5346 | 4101.598 | 2773.3333 | 10000 | 5620.3968 | 0 | 0
2019-01-08 12:00 | 1224.6702 | 682.5583 | 4266.6667 | 10000 | 3724.5548 | 0 | 0
2019-01-08 13:00 | 1195.1458 | 932.5568 | 2773.3333 | 10000 | 2510.7444 | 0 | 0
2019-01-08 14:00 | 1200.6413 | 812.8832 | 2773.3333 | 10000 | 2385.5753 | 0 | 0
2019-01-08 15:00 | 1285.8584 | 477.2833 | 4266.6667 | 10000 | 3458.0916 | 0 | 0
2019-01-08 16:00 | 1588.8933 | 0 | 2773.3333 | 10000 | 1184.44 | 0 | 0
2019-01-08 17:00 | 2173.9246 | 0 | 2773.3333 | 10000 | 599.4088 | 0 | 0
2019-01-08 18:00 | 2531.0058 | 0 | 2773.3333 | 10000 | 242.3276 | 0 | 0
2019-01-08 19:00 | 2493.8456 | 0 | 1666.6667 | 10000 | -827.1789 | -827.1789 | 0
2019-01-08 20:00 | 2337.2326 | 0 | 2773.3333 | 9172.8211 | 436.1008 | 436.1008 | 0
2019-01-08 21:00 | 2153.3967 | 0 | 4266.6667 | 9608.9218 | 2113.27 | 391.0782 | 0
2019-01-08 22:00 | 1804.3532 | 0 | 2773.3333 | 10000 | 968.9801 | 0 | 0
2019-01-08 23:00 | 1453.3781 | 0 | 2773.3333 | 10000 | 1319.9552 | 0 | 0
2019-01-09 | 1100.1168 | 0 | 873.3333 | 10000 | -226.7835 | -226.7835 | 0
2019-01-09 01:00 | 968.9644 | 0 | 1666.6667 | 9773.2165 | 697.7022 | 226.7835 | 0
2019-01-09 02:00 | 931.9764 | 0 | 4266.6667 | 10000 | 3334.6903 | 0 | 0
2019-01-09 03:00 | 932.7078 | 0 | 2773.3333 | 10000 | 1840.6256 | 0 | 0
2019-01-09 04:00 | 931.5577 | 0 | 1666.6667 | 10000 | 735.1089 | 0 | 0
2019-01-09 05:00 | 993.6304 | 0 | 4266.6667 | 10000 | 3273.0363 | 0 | 0
2019-01-09 06:00 | 1261.6405 | 0 | 2773.3333 | 10000 | 1511.6928 | 0 | 0
2019-01-09 07:00 | 1614.2213 | 760.1132 | 2773.3333 | 10000 | 1919.2253 | 0 | 0
2019-01-09 08:00 | 1517.4772 | 3231.9393 | 2773.3333 | 10000 | 4487.7955 | 0 | 0
2019-01-09 09:00 | 1285.4932 | 5361.0067 | 286.6667 | 10000 | 4362.1803 | 0 | 0
2019-01-09 10:00 | 1290.7479 | 6734.8232 | 873.3333 | 10000 | 6317.4086 | 0 | 0
2019-01-09 11:00 | 1238.0291 | 7324.5248 | 286.6667 | 10000 | 6373.1624 | 0 | 0
2019-01-09 12:00 | 1190.6351 | 7204.1899 | 0 | 10000 | 6013.5549 | 0 | 0
2019-01-09 13:00 | 1148.2085 | 6368.6068 | 0 | 10000 | 5220.3984 | 0 | 0
2019-01-09 14:00 | 1161.7449 | 4803.1038 | 873.3333 | 10000 | 4514.6923 | 0 | 0
2019-01-09 15:00 | 1257.9821 | 2573.5114 | 1666.6667 | 10000 | 2982.196 | 0 | 0
2019-01-09 16:00 | 1564.8568 | 0 | 1666.6667 | 10000 | 101.8099 | 0 | 0
2019-01-09 17:00 | 2155.2275 | 0 | 2773.3333 | 10000 | 618.1058 | 0 | 0
2019-01-09 18:00 | 2498.5406 | 0 | 2773.3333 | 10000 | 274.7928 | 0 | 0
2019-01-09 19:00 | 2461.1569 | 0 | 1666.6667 | 10000 | -794.4903 | -794.4903 | 0
2019-01-09 20:00 | 2294.6091 | 0 | 873.3333 | 9205.5097 | -1421.2757 | -1421.2757 | 0
2019-01-09 21:00 | 2121.1985 | 0 | 286.6667 | 7784.234 | -1834.5318 | -1834.5318 | 0
2019-01-09 22:00 | 1776.9825 | 0 | 286.6667 | 5949.7022 | -1490.3159 | -1490.3159 | 0
2019-01-09 23:00 | 1437.8816 | 0 | 286.6667 | 4459.3863 | -1151.215 | -1151.215 | 0
2019-01-10 | 1099.1459 | 0 | 873.3333 | 3308.1714 | -225.8126 | -225.8126 | 0
2019-01-10 01:00 | 967.9049 | 0 | 873.3333 | 3082.3588 | -94.5716 | -94.5716 | 0
2019-01-10 02:00 | 919.2615 | 0 | 1666.6667 | 2987.7872 | 747.4051 | 747.4051 | 0
2019-01-10 03:00 | 911.3138 | 0 | 873.3333 | 3735.1923 | -37.9804 | -37.9804 | 0
2019-01-10 04:00 | 911.9384 | 0 | 286.6667 | 3697.2119 | -625.2718 | -625.2718 | 0
2019-01-10 05:00 | 970.4012 | 0 | 0 | 3071.9401 | -970.4012 | -970.4012 | 0
2019-01-10 06:00 | 1237.6796 | 0 | 0 | 2101.5389 | -1237.6796 | -1237.6796 | 0
2019-01-10 07:00 | 1583.6504 | 802.1273 | 0 | 863.8593 | -781.5231 | -781.5231 | 0
2019-01-10 08:00 | 1486.9945 | 3259.0839 | 0 | 82.3362 | 1772.0894 | 1772.0894 | 0
2019-01-10 09:00 | 1253.0934 | 5286.7892 | 286.6667 | 1854.4256 | 4320.3625 | 4320.3625 | 0
2019-01-10 10:00 | 1253.8638 | 6545.0858 | 0 | 6174.7881 | 5291.2221 | 3825.2119 | 0
2019-01-10 11:00 | 1216.162 | 7076.3352 | 286.6667 | 10000 | 6146.8399 | 0 | 0
2019-01-10 12:00 | 1186.9317 | 6975.3641 | 0 | 10000 | 5788.4324 | 0 | 0
2019-01-10 13:00 | 1156.0461 | 6166.6968 | 0 | 10000 | 5010.6506 | 0 | 0
2019-01-10 14:00 | 1167.2865 | 4671.0654 | 0 | 10000 | 3503.7789 | 0 | 0
2019-01-10 15:00 | 1258.7129 | 2523.353 | 0 | 10000 | 1264.6401 | 0 | 0
2019-01-10 16:00 | 1564.9035 | 0 | 0 | 10000 | -1564.9035 | -1564.9035 | 0
2019-01-10 17:00 | 2159.2321 | 0 | 2773.3333 | 8435.0965 | 614.1013 | 614.1013 | 0
2019-01-10 18:00 | 2504.3254 | 0 | 6160 | 9049.1978 | 3655.6746 | 950.8022 | 0
2019-01-10 19:00 | 2467.3409 | 0 | 9060 | 10000 | 6592.6591 | 0 | 0
2019-01-10 20:00 | 2313.3317 | 0 | 4266.6667 | 10000 | 1953.335 | 0 | 0
2019-01-10 21:00 | 2137.6896 | 0 | 1666.6667 | 10000 | -471.023 | -471.023 | 0
2019-01-10 22:00 | 1805.6335 | 0 | 2773.3333 | 9528.977 | 967.6998 | 471.023 | 0
2019-01-10 23:00 | 1468.8726 | 0 | 2773.3333 | 10000 | 1304.4607 | 0 | 0
2019-01-11 | 1134.9702 | 0 | 873.3333 | 10000 | -261.6369 | -261.6369 | 0
2019-01-11 01:00 | 1009.5438 | 0 | 2773.3333 | 9738.3631 | 1763.7895 | 261.6369 | 0
2019-01-11 02:00 | 957.5205 | 0 | 4266.6667 | 10000 | 3309.1462 | 0 | 0
2019-01-11 03:00 | 952.7863 | 0 | 9060 | 10000 | 8107.2137 | 0 | 0
2019-01-11 04:00 | 951.3375 | 0 | 9060 | 10000 | 8108.6625 | 0 | 0
2019-01-11 05:00 | 1014.0059 | 0 | 9873.3333 | 10000 | 8859.3274 | 0 | 0
2019-01-11 06:00 | 1282.0857 | 0 | 9960 | 10000 | 8677.9143 | 0 | 0
2019-01-11 07:00 | 1630.5214 | 593.6886 | 9873.3333 | 10000 | 8836.5006 | 0 | 0
2019-01-11 08:00 | 1537.4837 | 2954.4558 | 9060 | 10000 | 10476.9721 | 0 | 0
2019-01-11 09:00 | 1303.4911 | 4912.0341 | 9060 | 10000 | 12668.543 | 0 | 0
2019-01-11 10:00 | 1324.9925 | 6182.2735 | 9060 | 10000 | 13917.281 | 0 | 0
2019-01-11 11:00 | 1293.5942 | 6740.089 | 4266.6667 | 10000 | 9713.1616 | 0 | 0
2019-01-11 12:00 | 1263.5404 | 6638.7465 | 6160 | 10000 | 11535.2061 | 0 | 0
2019-01-11 13:00 | 1228.4431 | 5848.8195 | 2773.3333 | 10000 | 7393.7098 | 0 | 0
2019-01-11 14:00 | 1233.5561 | 4354.4842 | 4266.6667 | 10000 | 7387.5947 | 0 | 0
2019-01-11 15:00 | 1316.1137 | 2237.9138 | 286.6667 | 10000 | 1208.4668 | 0 | 0
2019-01-11 16:00 | 1604.9263 | 0 | 0 | 10000 | -1604.9263 | -1604.9263 | 0
2019-01-11 17:00 | 2135.7964 | 0 | 873.3333 | 8395.0737 | -1262.4631 | -1262.4631 | 0
2019-01-11 18:00 | 2553.0007 | 0 | 286.6667 | 7132.6106 | -2266.3341 | -2266.3341 | 0
2019-01-11 19:00 | 2473.1916 | 0 | 873.3333 | 4866.2765 | -1599.8583 | -1599.8583 | 0
2019-01-11 20:00 | 2294.4682 | 0 | 873.3333 | 3266.4182 | -1421.1348 | -1421.1348 | 0
2019-01-11 21:00 | 2111.0057 | 0 | 873.3333 | 1845.2834 | -1237.6723 | -1237.6723 | 0
2019-01-11 22:00 | 1762.9842 | 0 | 873.3333 | 607.6111 | -889.6509 | -607.6111 | -282.0398
2019-01-11 23:00 | 1420.9287 | 0 | 286.6667 | 0 | -1134.262 | 0 | -1416.3019
2019-01-12 | 1091.0769 | 0 | 286.6667 | 0 | -804.4102 | 0 | -2220.7121
2019-01-12 01:00 | 969.5585 | 0 | 0 | 0 | -969.5585 | 0 | -3190.2706
2019-01-12 02:00 | 922.8738 | 0 | 286.6667 | 0 | -636.2072 | 0 | -3826.4777
2019-01-12 03:00 | 916.4785 | 0 | 873.3333 | 0 | -43.1452 | 0 | -3869.623
2019-01-12 04:00 | 916.4849 | 0 | 6160 | 0 | 5243.5151 | 5243.5151 | 0
2019-01-12 05:00 | 991.0524 | 0 | 6160 | 5243.5151 | 5168.9476 | 4756.4849 | 0
2019-01-12 06:00 | 1234.3075 | 0 | 6160 | 10000 | 4925.6925 | 0 | 0
2019-01-12 07:00 | 1599.9252 | 89.4378 | 7873.3333 | 10000 | 6362.8459 | 0 | 0
2019-01-12 08:00 | 1536.2566 | 835.4554 | 4266.6667 | 10000 | 3565.8656 | 0 | 0
2019-01-12 09:00 | 1328.6617 | 1429.2396 | 7873.3333 | 10000 | 7973.9112 | 0 | 0
2019-01-12 10:00 | 1363.3813 | 2151.3993 | 7873.3333 | 10000 | 8661.3514 | 0 | 0
2019-01-12 11:00 | 1321.792 | 3307.2298 | 7873.3333 | 10000 | 9858.7711 | 0 | 0
2019-01-12 12:00 | 1285.1337 | 6902.875 | 4266.6667 | 10000 | 9884.408 | 0 | 0
2019-01-12 13:00 | 1245.9316 | 6076.6908 | 4266.6667 | 10000 | 9097.426 | 0 | 0
2019-01-12 14:00 | 1242.9141 | 4640.8687 | 2773.3333 | 10000 | 6171.2879 | 0 | 0
2019-01-12 15:00 | 1326.9046 | 2528.9535 | 2773.3333 | 10000 | 3975.3822 | 0 | 0
2019-01-12 16:00 | 1620.2033 | 0 | 873.3333 | 10000 | -746.87 | -746.87 | 0
2019-01-12 17:00 | 2204.0909 | 0 | 286.6667 | 9253.13 | -1917.4243 | -1917.4243 | 0
2019-01-12 18:00 | 2539.9982 | 0 | 1666.6667 | 7335.7058 | -873.3315 | -873.3315 | 0
2019-01-12 19:00 | 2489.553 | 0 | 873.3333 | 6462.3743 | -1616.2197 | -1616.2197 | 0
2019-01-12 20:00 | 2317.242 | 0 | 6160 | 4846.1546 | 3842.758 | 3842.758 | 0
2019-01-12 21:00 | 2133.2084 | 0 | 7873.3333 | 8688.9126 | 5740.1249 | 1311.0874 | 0
2019-01-12 22:00 | 1782.0521 | 0 | 6160 | 10000 | 4377.9479 | 0 | 0
2019-01-12 23:00 | 1442.1133 | 0 | 4266.6667 | 10000 | 2824.5533 | 0 | 0
2019-01-13 | 1106.5453 | 0 | 1666.6667 | 10000 | 560.1214 | 0 | 0
2019-01-13 01:00 | 967.0336 | 0 | 2773.3333 | 10000 | 1806.2997 | 0 | 0
2019-01-13 02:00 | 928.3393 | 0 | 2773.3333 | 10000 | 1844.9941 | 0 | 0
2019-01-13 03:00 | 926.4689 | 0 | 4266.6667 | 10000 | 3340.1978 | 0 | 0
2019-01-13 04:00 | 917.5191 | 0 | 6160 | 10000 | 5242.4809 | 0 | 0
2019-01-13 05:00 | 974.9294 | 0 | 4266.6667 | 10000 | 3291.7372 | 0 | 0
2019-01-13 06:00 | 1245.7623 | 0 | 9573.3333 | 10000 | 8327.571 | 0 | 0
2019-01-13 07:00 | 1593.6157 | 804.2042 | 7873.3333 | 10000 | 7083.9218 | 0 | 0
2019-01-13 08:00 | 1498.5987 | 3287.3773 | 6160 | 10000 | 7948.7787 | 0 | 0
2019-01-13 09:00 | 1262.9549 | 5366.8706 | 9573.3333 | 10000 | 13677.249 | 0 | 0
2019-01-13 10:00 | 1254.7644 | 6655.226 | 9060 | 10000 | 14460.4615 | 0 | 0
2019-01-13 11:00 | 1204.4716 | 7193.7479 | 9060 | 10000 | 15049.2763 | 0 | 0
2019-01-13 12:00 | 1154.2388 | 7020.7305 | 7873.3333 | 10000 | 13739.8249 | 0 | 0
2019-01-13 13:00 | 1111.2412 | 4976.0281 | 7873.3333 | 10000 | 11738.1203 | 0 | 0
2019-01-13 14:00 | 1115.894 | 4538.1093 | 7873.3333 | 10000 | 11295.5486 | 0 | 0
2019-01-13 15:00 | 1202.5254 | 2385.6451 | 6160 | 10000 | 7343.1197 | 0 | 0
2019-01-13 16:00 | 1498.5686 | 0 | 6160 | 10000 | 4661.4314 | 0 | 0
2019-01-13 17:00 | 2078.403 | 0 | 2773.3333 | 10000 | 694.9304 | 0 | 0
2019-01-13 18:00 | 2427.3876 | 0 | 2773.3333 | 10000 | 345.9458 | 0 | 0
2019-01-13 19:00 | 2381.2042 | 0 | 1666.6667 | 10000 | -714.5375 | -714.5375 | 0
2019-01-13 20:00 | 2211.9885 | 0 | 4266.6667 | 9285.4625 | 2054.6781 | 714.5375 | 0
2019-01-13 21:00 | 2020.156 | 0 | 2773.3333 | 10000 | 753.1773 | 0 | 0
2019-01-13 22:00 | 1676.4262 | 0 | 2773.3333 | 10000 | 1096.9071 | 0 | 0
2019-01-13 23:00 | 1321.8451 | 0 | 873.3333 | 10000 | -448.5117 | -448.5117 | 0
2019-01-14 | 980.7033 | 0 | 4266.6667 | 9551.4883 | 3285.9634 | 448.5117 | 0
2019-01-14 01:00 | 836.6575 | 0 | 2773.3333 | 10000 | 1936.6759 | 0 | 0
2019-01-14 02:00 | 790.8116 | 0 | 1666.6667 | 10000 | 875.8551 | 0 | 0
2019-01-14 03:00 | 759.5663 | 0 | 873.3333 | 10000 | 113.7671 | 0 | 0
2019-01-14 04:00 | 751.1711 | 0 | 873.3333 | 10000 | 122.1622 | 0 | 0
2019-01-14 05:00 | 799.5044 | 0 | 286.6667 | 10000 | -512.8378 | -512.8378 | 0
2019-01-14 06:00 | 1051.333 | 0 | 873.3333 | 9487.1622 | -177.9996 | -177.9996 | 0
2019-01-14 07:00 | 1431.8255 | 230.8119 | 286.6667 | 9309.1626 | -914.3469 | -914.3469 | 0
2019-01-14 08:00 | 1389.5915 | 3152.6767 | 0 | 8394.8157 | 1763.0852 | 1605.1843 | 0
2019-01-14 09:00 | 1178.3947 | 5061.9217 | 0 | 10000 | 3883.5269 | 0 | 0
2019-01-14 10:00 | 1175.7576 | 6320.2068 | 0 | 10000 | 5144.4492 | 0 | 0
2019-01-14 11:00 | 1183.7616 | 6892.8803 | 0 | 10000 | 5709.1188 | 0 | 0
2019-01-14 12:00 | 1145.4295 | 6756.442 | 286.6667 | 10000 | 5897.6792 | 0 | 0
2019-01-14 13:00 | 1122.9399 | 5998.4207 | 286.6667 | 10000 | 5162.1475 | 0 | 0
2019-01-14 14:00 | 1097.7804 | 4589.4729 | 1666.6667 | 10000 | 5158.3591 | 0 | 0
2019-01-14 15:00 | 1190.9402 | 2468.3232 | 873.3333 | 10000 | 2150.7164 | 0 | 0
2019-01-14 16:00 | 1502.9951 | 0 | 873.3333 | 10000 | -629.6618 | -629.6618 | 0
2019-01-14 17:00 | 2089.7165 | 0 | 2773.3333 | 9370.3382 | 683.6168 | 629.6618 | 0
2019-01-14 18:00 | 2445.2593 | 0 | 1666.6667 | 10000 | -778.5926 | -778.5926 | 0
2019-01-14 19:00 | 2414.326 | 0 | 873.3333 | 9221.4074 | -1540.9926 | -1540.9926 | 0
2019-01-14 20:00 | 2249.8169 | 0 | 2773.3333 | 7680.4147 | 523.5164 | 523.5164 | 0
2019-01-14 21:00 | 2073.1239 | 0 | 2773.3333 | 8203.9311 | 700.2094 | 700.2094 | 0
2019-01-14 22:00 | 1720.3067 | 0 | 1666.6667 | 8904.1405 | -53.6401 | -53.6401 | 0
2019-01-14 23:00 | 1376.5154 | 0 | 873.3333 | 8850.5005 | -503.1821 | -503.1821 | 0
2019-01-15 | 1021.2685 | 0 | 1666.6667 | 8347.3184 | 645.3981 | 645.3981 | 0
2019-01-15 01:00 | 884.8755 | 0 | 873.3333 | 8992.7166 | -11.5422 | -11.5422 | 0
2019-01-15 02:00 | 846.5273 | 0 | 286.6667 | 8981.1744 | -559.8606 | -559.8606 | 0
2019-01-15 03:00 | 838.1416 | 0 | 4266.6667 | 8421.3137 | 3428.525 | 1578.6863 | 0
2019-01-15 04:00 | 837.0028 | 0 | 2773.3333 | 10000 | 1936.3306 | 0 | 0
2019-01-15 05:00 | 897.1803 | 0 | 873.3333 | 10000 | -23.8469 | -23.8469 | 0
2019-01-15 06:00 | 1152.9911 | 0 | 873.3333 | 9976.1531 | -279.6578 | -279.6578 | 0
2019-01-15 07:00 | 1516.9659 | 35.3176 | 873.3333 | 9696.4953 | -608.315 | -608.315 | 0
2019-01-15 08:00 | 1446.6477 | 1489.6697 | 286.6667 | 9088.1803 | 329.6887 | 329.6887 | 0
2019-01-15 09:00 | 1240.2874 | 1712.2867 | 873.3333 | 9417.869 | 1345.3327 | 582.131 | 0
2019-01-15 10:00 | 1279.727 | 3710.9408 | 873.3333 | 10000 | 3304.5471 | 0 | 0
2019-01-15 11:00 | 1257.1741 | 4715.7532 | 873.3333 | 10000 | 4331.9125 | 0 | 0
2019-01-15 12:00 | 1238.0586 | 5274.2082 | 2773.3333 | 10000 | 6809.4829 | 0 | 0
2019-01-15 13:00 | 1199.1964 | 4127.0257 | 2773.3333 | 10000 | 5701.1627 | 0 | 0
2019-01-15 14:00 | 1197.1765 | 2187.7772 | 873.3333 | 10000 | 1863.9341 | 0 | 0
2019-01-15 15:00 | 1284.0345 | 2224.0678 | 873.3333 | 10000 | 1813.3667 | 0 | 0
2019-01-15 16:00 | 1590.4354 | 0 | 873.3333 | 10000 | -717.1021 | -717.1021 | 0
2019-01-15 17:00 | 2170.2063 | 0 | 286.6667 | 9282.8979 | -1883.5396 | -1883.5396 | 0
2019-01-15 18:00 | 2524.9814 | 0 | 286.6667 | 7399.3583 | -2238.3147 | -2238.3147 | 0
2019-01-15 19:00 | 2485.5055 | 0 | 286.6667 | 5161.0436 | -2198.8389 | -2198.8389 | 0
2019-01-15 20:00 | 2313.7149 | 0 | 0 | 2962.2048 | -2313.7149 | -2313.7149 | 0
2019-01-15 21:00 | 2131.4109 | 0 | 0 | 648.4898 | -2131.4109 | -648.4898 | -1482.9211
2019-01-15 22:00 | 1780.8071 | 0 | 0 | 0 | -1780.8071 | 0 | -3263.7282
2019-01-15 23:00 | 1426.4938 | 0 | 0 | 0 | -1426.4938 | 0 | -4690.222
2019-01-16 | 1064.1937 | 0 | 0 | 0 | -1064.1937 | 0 | -5754.4157
2019-01-16 01:00 | 925.3398 | 0 | 0 | 0 | -925.3398 | 0 | -6679.7555
2019-01-16 02:00 | 874.5328 | 0 | 0 | 0 | -874.5328 | 0 | -7554.2884
2019-01-16 03:00 | 863.5571 | 0 | 0 | 0 | -863.5571 | 0 | -8417.8455
2019-01-16 04:00 | 861.2195 | 0 | 0 | 0 | -861.2195 | 0 | -9279.065
2019-01-16 05:00 | 920.675 | 0 | 0 | 0 | -920.675 | 0 | -10199.7401
2019-01-16 06:00 | 1161.3779 | 0 | 0 | 0 | -1161.3779 | 0 | -11361.1179
2019-01-16 07:00 | 1506.7941 | 236.4802 | 0 | 0 | -1270.3138 | 0 | -12631.4317
2019-01-16 08:00 | 1452.801 | 3024.5242 | 0 | 0 | 1571.7232 | 1571.7232 | -11059.7085
2019-01-16 09:00 | 1247.5783 | 4974.9287 | 1666.6667 | 1571.7232 | 5394.0171 | 5394.0171 | -4093.9683
2019-01-16 10:00 | 1261.3221 | 6205.1355 | 1666.6667 | 6965.7402 | 6610.4801 | 3034.2598 | 0
2019-01-16 11:00 | 1237.4988 | 6758.2429 | 6160 | 10000 | 11680.7441 | 0 | 0
2019-01-16 12:00 | 1203.0897 | 6647.0057 | 4266.6667 | 10000 | 9710.5827 | 0 | 0
2019-01-16 13:00 | 1160.826 | 5910.1869 | 4266.6667 | 10000 | 9016.0276 | 0 | 0
2019-01-16 14:00 | 1156.3318 | 4532.0821 | 2773.3333 | 10000 | 6149.0837 | 0 | 0
2019-01-16 15:00 | 1232.9217 | 2472.8392 | 4266.6667 | 10000 | 5506.5842 | 0 | 0
2019-01-16 16:00 | 1524.3101 | 0 | 2773.3333 | 10000 | 1249.0232 | 0 | 0
2019-01-16 17:00 | 2087.6373 | 0 | 2773.3333 | 10000 | 685.696 | 0 | 0
2019-01-16 18:00 | 2462.035 | 0 | 2773.3333 | 10000 | 311.2983 | 0 | 0
2019-01-16 19:00 | 2383.6495 | 0 | 2773.3333 | 10000 | 389.6838 | 0 | 0
2019-01-16 20:00 | 2206.3424 | 0 | 2773.3333 | 10000 | 566.9909 | 0 | 0
2019-01-16 21:00 | 2015.4962 | 0 | 2773.3333 | 10000 | 757.8371 | 0 | 0
2019-01-16 22:00 | 1667.4942 | 0 | 4266.6667 | 10000 | 2599.1725 | 0 | 0
2019-01-16 23:00 | 1329.3998 | 0 | 2773.3333 | 10000 | 1443.9335 | 0 | 0
2019-01-17 | 994.1555 | 0 | 2773.3333 | 10000 | 1779.1778 | 0 | 0
2019-01-17 01:00 | 865.2969 | 0 | 873.3333 | 10000 | 8.0364 | 0 | 0
2019-01-17 02:00 | 819.7261 | 0 | 873.3333 | 10000 | 53.6072 | 0 | 0
2019-01-17 03:00 | 815.039 | 0 | 0 | 10000 | -815.039 | -815.039 | 0
2019-01-17 04:00 | 816.2918 | 0 | 0 | 9184.961 | -816.2918 | -816.2918 | 0
2019-01-17 05:00 | 880.9404 | 0 | 286.6667 | 8368.6692 | -594.2737 | -594.2737 | 0
2019-01-17 06:00 | 1140.3784 | 0 | 0 | 7774.3955 | -1140.3784 | -1140.3784 | 0
2019-01-17 07:00 | 1492.1999 | 66.6448 | 286.6667 | 6634.0171 | -1138.8884 | -1138.8884 | 0
2019-01-17 08:00 | 1435.1415 | 2464.2292 | 873.3333 | 5495.1287 | 1902.421 | 1902.421 | 0
2019-01-17 09:00 | 1220.4165 | 3486.4044 | 286.6667 | 7397.5497 | 2552.6545 | 2552.6545 | 0
2019-01-17 10:00 | 1241.3648 | 5145.6865 | 286.6667 | 9950.2043 | 4190.9884 | 49.7957 | 0
2019-01-17 11:00 | 1196.13 | 4836.3319 | 286.6667 | 10000 | 3926.8686 | 0 | 0
2019-01-17 12:00 | 1162.6076 | 3121.3311 | 4266.6667 | 10000 | 6225.3902 | 0 | 0
2019-01-17 13:00 | 1134.351 | 1053.8749 | 2773.3333 | 10000 | 2692.8573 | 0 | 0
2019-01-17 14:00 | 1143.5175 | 461.3926 | 873.3333 | 10000 | 191.2085 | 0 | 0
2019-01-17 15:00 | 1249.7695 | 229.7217 | 873.3333 | 10000 | -146.7144 | -146.7144 | 0
2019-01-17 16:00 | 1561.9174 | 0 | 873.3333 | 9853.2856 | -688.5841 | -688.5841 | 0
2019-01-17 17:00 | 2167.9562 | 0 | 4266.6667 | 9164.7015 | 2098.7105 | 835.2985 | 0
2019-01-17 18:00 | 2529.1432 | 0 | 4266.6667 | 10000 | 1737.5234 | 0 | 0
2019-01-17 19:00 | 2479.0587 | 0 | 6160 | 10000 | 3680.9413 | 0 | 0
2019-01-17 20:00 | 2327.4386 | 0 | 7873.3333 | 10000 | 5545.8947 | 0 | 0
2019-01-17 21:00 | 2146.3039 | 0 | 4266.6667 | 10000 | 2120.3627 | 0 | 0
2019-01-17 22:00 | 1805.2376 | 0 | 6160 | 10000 | 4354.7624 | 0 | 0
2019-01-17 23:00 | 1476.4142 | 0 | 4266.6667 | 10000 | 2790.2525 | 0 | 0
2019-01-18 | 1142.3495 | 0 | 4266.6667 | 10000 | 3124.3171 | 0 | 0
2019-01-18 01:00 | 1011.2487 | 0 | 4266.6667 | 10000 | 3255.418 | 0 | 0
2019-01-18 02:00 | 965.5616 | 0 | 9060 | 10000 | 8094.4384 | 0 | 0
2019-01-18 03:00 | 963.567 | 0 | 7873.3333 | 10000 | 6909.7663 | 0 | 0
2019-01-18 04:00 | 967.1993 | 0 | 6160 | 10000 | 5192.8007 | 0 | 0
2019-01-18 05:00 | 1032.7226 | 0 | 6160 | 10000 | 5127.2774 | 0 | 0
2019-01-18 06:00 | 1302.4447 | 0 | 6160 | 10000 | 4857.5553 | 0 | 0
2019-01-18 07:00 | 1653.0783 | 0 | 4266.6667 | 10000 | 2613.5884 | 0 | 0
2019-01-18 08:00 | 1566.9229 | 107.1271 | 2773.3333 | 10000 | 1313.5375 | 0 | 0
2019-01-18 09:00 | 1327.7309 | 416.6415 | 4266.6667 | 10000 | 3355.5773 | 0 | 0
2019-01-18 10:00 | 1337.411 | 1209.662 | 4266.6667 | 10000 | 4138.9177 | 0 | 0
2019-01-18 11:00 | 1277.2035 | 302.5949 | 4266.6667 | 10000 | 3292.058 | 0 | 0
2019-01-18 12:00 | 1234.4014 | 560.2156 | 6160 | 10000 | 5485.8142 | 0 | 0
2019-01-18 13:00 | 1183.1775 | 1246.5574 | 4266.6667 | 10000 | 4330.0466 | 0 | 0
2019-01-18 14:00 | 1183.6735 | 4347.6015 | 4266.6667 | 10000 | 7430.5946 | 0 | 0
2019-01-18 15:00 | 1286.4846 | 2268.6314 | 1666.6667 | 10000 | 2648.8135 | 0 | 0
2019-01-18 16:00 | 1597.853 | 0 | 873.3333 | 10000 | -724.5196 | -724.5196 | 0
2019-01-18 17:00 | 2209.4723 | 0 | 873.3333 | 9275.4804 | -1336.1389 | -1336.1389 | 0
2019-01-18 18:00 | 2561.6335 | 0 | 1666.6667 | 7939.3414 | -894.9669 | -894.9669 | 0
2019-01-18 19:00 | 2521.7886 | 0 | 873.3333 | 7044.3745 | -1648.4553 | -1648.4553 | 0
2019-01-18 20:00 | 2366.897 | 0 | 0 | 5395.9193 | -2366.897 | -2366.897 | 0
2019-01-18 21:00 | 2190.6705 | 0 | 286.6667 | 3029.0222 | -1904.0039 | -1904.0039 | 0
2019-01-18 22:00 | 1845.9155 | 0 | 873.3333 | 1125.0184 | -972.5822 | -972.5822 | 0
2019-01-18 23:00 | 1516.2844 | 0 | 286.6667 | 152.4362 | -1229.6177 | -152.4362 | -1077.1815
2019-01-19 | 1174.1528 | 0 | 873.3333 | 0 | -300.8194 | 0 | -1378.001
2019-01-19 01:00 | 1038.6212 | 0 | 286.6667 | 0 | -751.9546 | 0 | -2129.9555
2019-01-19 02:00 | 990.0507 | 0 | 286.6667 | 0 | -703.384 | 0 | -2833.3395
2019-01-19 03:00 | 982.597 | 0 | 0 | 0 | -982.597 | 0 | -3815.9365
2019-01-19 04:00 | 977.2347 | 0 | 0 | 0 | -977.2347 | 0 | -4793.1712
2019-01-19 05:00 | 1039.0727 | 0 | 0 | 0 | -1039.0727 | 0 | -5832.2439
2019-01-19 06:00 | 1282.1593 | 0 | 0 | 0 | -1282.1593 | 0 | -7114.4032
2019-01-19 07:00 | 1654.9666 | 334.5614 | 0 | 0 | -1320.4051 | 0 | -8434.8083
2019-01-19 08:00 | 1557.2568 | 128.6677 | 0 | 0 | -1428.589 | 0 | -9863.3973
2019-01-19 09:00 | 1303.4426 | 243.1767 | 0 | 0 | -1060.2659 | 0 | -10923.6633
2019-01-19 10:00 | 1302.9389 | 1029.8595 | 0 | 0 | -273.0794 | 0 | -11196.7427
2019-01-19 11:00 | 1237.0056 | 1583.2476 | 1666.6667 | 0 | 2012.9086 | 2012.9086 | -9183.8341
2019-01-19 12:00 | 1187.972 | 902.359 | 1666.6667 | 2012.9086 | 1381.0536 | 1381.0536 | -5789.8718
2019-01-19 13:00 | 1147.105 | 219.8766 | 1666.6667 | 3393.9623 | 739.4382 | 739.4382 | -1656.4713
2019-01-19 14:00 | 1145.6303 | 139.227 | 2773.3333 | 4133.4005 | 1766.9301 | 1766.9301 | 0
2019-01-19 15:00 | 1236.0177 | 35.1969 | 286.6667 | 5900.3306 | -914.1541 | -914.1541 | 0
2019-01-19 16:00 | 1545.6045 | 0 | 0 | 4986.1765 | -1545.6045 | -1545.6045 | 0
2019-01-19 17:00 | 2146.225 | 0 | 873.3333 | 3440.572 | -1272.8917 | -1272.8917 | 0
2019-01-19 18:00 | 2492.804 | 0 | 1666.6667 | 2167.6803 | -826.1373 | -826.1373 | 0
2019-01-19 19:00 | 2453.2607 | 0 | 1666.6667 | 1341.5429 | -786.594 | -786.594 | 0
2019-01-19 20:00 | 2285.5781 | 0 | 873.3333 | 554.9489 | -1412.2447 | -554.9489 | -857.2958
2019-01-19 21:00 | 2103.3648 | 0 | 1666.6667 | 0 | -436.6982 | 0 | -1293.994
2019-01-19 22:00 | 1763.1147 | 0 | 1666.6667 | 0 | -96.448 | 0 | -1390.442
2019-01-19 23:00 | 1423.5258 | 0 | 286.6667 | 0 | -1136.8592 | 0 | -2527.3012
2019-01-20 | 1083.3644 | 0 | 0 | 0 | -1083.3644 | 0 | -3610.6656
2019-01-20 01:00 | 948.8806 | 0 | 0 | 0 | -948.8806 | 0 | -4559.5461
2019-01-20 02:00 | 897.4717 | 0 | 286.6667 | 0 | -610.805 | 0 | -5170.3512
2019-01-20 03:00 | 882.9725 | 0 | 873.3333 | 0 | -9.6391 | 0 | -5179.9903
2019-01-20 04:00 | 878.691 | 0 | 286.6667 | 0 | -592.0243 | 0 | -5772.0146
2019-01-20 05:00 | 933.6678 | 0 | 0 | 0 | -933.6678 | 0 | -6705.6824
2019-01-20 06:00 | 1181.0944 | 0 | 0 | 0 | -1181.0944 | 0 | -7886.7769
2019-01-20 07:00 | 1510.473 | 402.8461 | 0 | 0 | -1107.6269 | 0 | -8994.4038
2019-01-20 08:00 | 1449.0384 | 2649.8461 | 0 | 0 | 1200.8077 | 1200.8077 | -7793.5961
2019-01-20 09:00 | 1240.1077 | 1690.1699 | 0 | 1200.8077 | 450.0622 | 450.0622 | -6142.7262
2019-01-20 10:00 | 1242.5125 | 1520.5093 | 0 | 1650.8699 | 277.9968 | 277.9968 | -4213.8595
2019-01-20 11:00 | 1223.68 | 1411.3904 | 0 | 1928.8667 | 187.7104 | 187.7104 | -2097.2824
2019-01-20 12:00 | 1201.76 | 892.2125 | 0 | 2116.5771 | -309.5474 | -309.5474 | -290.2528
2019-01-20 13:00 | 1167.2337 | 1113.6807 | 0 | 1807.0296 | -53.553 | -53.553 | 0
2019-01-20 14:00 | 1171.4244 | 2763.335 | 0 | 1753.4767 | 1591.9106 | 1591.9106 | 0
2019-01-20 15:00 | 1253.9191 | 2127.7484 | 0 | 3345.3873 | 873.8293 | 873.8293 | 0
2019-01-20 16:00 | 1540.1594 | 64.3529 | 286.6667 | 4219.2166 | -1189.1399 | -1189.1399 | 0
2019-01-20 17:00 | 2113.9344 | 0 | 286.6667 | 3030.0767 | -1827.2677 | -1827.2677 | 0
2019-01-20 18:00 | 2460.6605 | 0 | 286.6667 | 1202.809 | -2173.9939 | -1202.809 | -971.1849
2019-01-20 19:00 | 2414.062 | 0 | 0 | 0 | -2414.062 | 0 | -3385.2469
2019-01-20 20:00 | 2250.3254 | 0 | 286.6667 | 0 | -1963.6588 | 0 | -5348.9056
2019-01-20 21:00 | 2063.7319 | 0 | 0 | 0 | -2063.7319 | 0 | -7412.6375
2019-01-20 22:00 | 1715.8068 | 0 | 0 | 0 | -1715.8068 | 0 | -9128.4443
2019-01-20 23:00 | 1376.4285 | 0 | 286.6667 | 0 | -1089.7618 | 0 | -10218.2061
2019-01-21 | 1044.5197 | 0 | 873.3333 | 0 | -171.1864 | 0 | -10389.3925
2019-01-21 01:00 | 907.7362 | 0 | 286.6667 | 0 | -621.0695 | 0 | -11010.462
2019-01-21 02:00 | 856.5391 | 0 | 0 | 0 | -856.5391 | 0 | -11867.0011
2019-01-21 03:00 | 844.718 | 0 | 0 | 0 | -844.718 | 0 | -12711.7191
2019-01-21 04:00 | 853.2605 | 0 | 0 | 0 | -853.2605 | 0 | -13564.9796
2019-01-21 05:00 | 910.8369 | 0 | 0 | 0 | -910.8369 | 0 | -14475.8166
2019-01-21 06:00 | 1162.7189 | 0 | 0 | 0 | -1162.7189 | 0 | -15638.5355
2019-01-21 07:00 | 1539.8908 | 858.3657 | 286.6667 | 0 | -394.8584 | 0 | -16033.3938
2019-01-21 08:00 | 1455.4819 | 3273.9281 | 873.3333 | 0 | 2691.7796 | 2691.7796 | -13341.6143
2019-01-21 09:00 | 1235.2849 | 5249.3164 | 0 | 2691.7796 | 4014.0316 | 4014.0316 | -6635.8031
2019-01-21 10:00 | 1243.062 | 6543.0319 | 0 | 6705.8112 | 5299.97 | 3294.1888 | 0
2019-01-21 11:00 | 1217.9629 | 7153.3841 | 286.6667 | 10000 | 6222.0878 | 0 | 0
2019-01-21 12:00 | 1197.8194 | 7044.5446 | 2773.3333 | 10000 | 8620.0586 | 0 | 0
2019-01-21 13:00 | 1165.8059 | 6292.8483 | 873.3333 | 10000 | 6000.3757 | 0 | 0
2019-01-21 14:00 | 1166.6776 | 4892.5013 | 286.6667 | 10000 | 4012.4905 | 0 | 0
2019-01-21 15:00 | 1245.7464 | 2843.8902 | 2773.3333 | 10000 | 4371.4771 | 0 | 0
2019-01-21 16:00 | 1541.5534 | 531.3448 | 1666.6667 | 10000 | 656.4581 | 0 | 0
2019-01-21 17:00 | 2118.6245 | 0 | 1666.6667 | 10000 | -451.9579 | -451.9579 | 0
2019-01-21 18:00 | 2465.5942 | 0 | 286.6667 | 9548.0421 | -2178.9275 | -2178.9275 | 0
2019-01-21 19:00 | 2420.9017 | 0 | 286.6667 | 7369.1146 | -2134.235 | -2134.235 | 0
2019-01-21 20:00 | 2252.8064 | 0 | 286.6667 | 5234.8796 | -1966.1398 | -1966.1398 | 0
2019-01-21 21:00 | 2068.3448 | 0 | 286.6667 | 3268.7398 | -1781.6781 | -1781.6781 | 0
2019-01-21 22:00 | 1710.6804 | 0 | 0 | 1487.0617 | -1710.6804 | -1487.0617 | -223.6187
2019-01-21 23:00 | 1360.8709 | 0 | 0 | 0 | -1360.8709 | 0 | -1584.4896
2019-01-22 | 1012.4045 | 0 | 0 | 0 | -1012.4045 | 0 | -2596.8941
2019-01-22 01:00 | 877.0126 | 0 | 0 | 0 | -877.0126 | 0 | -3473.9067
2019-01-22 02:00 | 826.4 | 0 | 0 | 0 | -826.4 | 0 | -4300.3068
2019-01-22 03:00 | 816.8215 | 0 | 0 | 0 | -816.8215 | 0 | -5117.1283
2019-01-22 04:00 | 819.2013 | 0 | 0 | 0 | -819.2013 | 0 | -5936.3296
2019-01-22 05:00 | 885.1944 | 0 | 0 | 0 | -885.1944 | 0 | -6821.5239
2019-01-22 06:00 | 1136.96 | 0 | 0 | 0 | -1136.96 | 0 | -7958.4839
2019-01-22 07:00 | 1514.9863 | 294.0929 | 0 | 0 | -1220.8934 | 0 | -9179.3773
2019-01-22 08:00 | 1466.688 | 2479.5725 | 0 | 0 | 1012.8845 | 1012.8845 | -8166.4928
2019-01-22 09:00 | 1266.5131 | 4543.3487 | 286.6667 | 1012.8845 | 3563.5023 | 3563.5023 | -3590.106
2019-01-22 10:00 | 1273.9204 | 5775.4943 | 873.3333 | 4576.3868 | 5374.9073 | 5374.9073 | 0
2019-01-22 11:00 | 1241.5184 | 6403.4909 | 2773.3333 | 9951.294 | 7935.3059 | 48.706 | 0
2019-01-22 12:00 | 1246.3218 | 6203.5255 | 2773.3333 | 10000 | 7730.537 | 0 | 0
2019-01-22 13:00 | 1242.4496 | 4838.0638 | 4266.6667 | 10000 | 7862.2809 | 0 | 0
2019-01-22 14:00 | 1268.2631 | 4069.367 | 6160 | 10000 | 8961.1039 | 0 | 0
2019-01-22 15:00 | 1351.2652 | 1541.5934 | 6160 | 10000 | 6350.3282 | 0 | 0
2019-01-22 16:00 | 1674.3772 | 65.3085 | 6160 | 10000 | 4550.9313 | 0 | 0
2019-01-22 17:00 | 2272.5749 | 0 | 7873.3333 | 10000 | 5600.7585 | 0 | 0
2019-01-22 18:00 | 2645.158 | 0 | 6160 | 10000 | 3514.842 | 0 | 0
2019-01-22 19:00 | 2653.2846 | 0 | 7873.3333 | 10000 | 5220.0487 | 0 | 0
2019-01-22 20:00 | 2475.9969 | 0 | 6160 | 10000 | 3684.0031 | 0 | 0
2019-01-22 21:00 | 2311.9676 | 0 | 6160 | 10000 | 3848.0324 | 0 | 0
2019-01-22 22:00 | 1972.1364 | 0 | 7873.3333 | 10000 | 5901.197 | 0 | 0
2019-01-22 23:00 | 1637.7704 | 0 | 7873.3333 | 10000 | 6235.563 | 0 | 0
2019-01-23 | 1286.8751 | 0 | 9060 | 10000 | 7773.1249 | 0 | 0
2019-01-23 01:00 | 1140.9131 | 0 | 9060 | 10000 | 7919.0869 | 0 | 0
2019-01-23 02:00 | 1087.6222 | 0 | 9060 | 10000 | 7972.3778 | 0 | 0
2019-01-23 03:00 | 1078.6953 | 0 | 9573.3333 | 10000 | 8494.638 | 0 | 0
2019-01-23 04:00 | 1064.7714 | 0 | 9873.3333 | 10000 | 8808.5619 | 0 | 0
2019-01-23 05:00 | 1133.2132 | 0 | 7873.3333 | 10000 | 6740.1201 | 0 | 0
2019-01-23 06:00 | 1394.5648 | 0 | 9060 | 10000 | 7665.4352 | 0 | 0
2019-01-23 07:00 | 1698.7745 | 1018.317 | 9573.3333 | 10000 | 8892.8758 | 0 | 0
2019-01-23 08:00 | 1619.1588 | 3490.756 | 9573.3333 | 10000 | 11444.9306 | 0 | 0
2019-01-23 09:00 | 1369.6154 | 5510.2664 | 9573.3333 | 10000 | 13713.9843 | 0 | 0
2019-01-23 10:00 | 1378.0664 | 6800.824 | 9060 | 10000 | 14482.7576 | 0 | 0
2019-01-23 11:00 | 1325.5733 | 7384.6778 | 9960 | 10000 | 16019.1046 | 0 | 0
2019-01-23 12:00 | 1270.673 | 7294.9146 | 9573.3333 | 10000 | 15597.575 | 0 | 0
2019-01-23 13:00 | 1232.3321 | 6558.2844 | 9873.3333 | 10000 | 15199.2857 | 0 | 0
2019-01-23 14:00 | 1225.5876 | 5172.5505 | 10000 | 10000 | 13946.9629 | 0 | 0
2019-01-23 15:00 | 1313.1156 | 3076.7847 | 9573.3333 | 10000 | 11337.0025 | 0 | 0
2019-01-23 16:00 | 1623.0013 | 699.783 | 9873.3333 | 10000 | 8950.115 | 0 | 0
2019-01-23 17:00 | 2219.6949 | 0 | 10000 | 10000 | 7780.3051 | 0 | 0
2019-01-23 18:00 | 2564.2211 | 0 | 10000 | 10000 | 7435.7789 | 0 | 0
2019-01-23 19:00 | 2522.6271 | 0 | 10000 | 10000 | 7477.3729 | 0 | 0
2019-01-23 20:00 | 2357.8716 | 0 | 10000 | 10000 | 7642.1284 | 0 | 0
2019-01-23 21:00 | 2176.7949 | 0 | 10000 | 10000 | 7823.2051 | 0 | 0
2019-01-23 22:00 | 1825.4166 | 0 | 10000 | 10000 | 8174.5834 | 0 | 0
2019-01-23 23:00 | 1481.0469 | 0 | 9960 | 10000 | 8478.9531 | 0 | 0
2019-01-24 | 1146.775 | 0 | 9960 | 10000 | 8813.225 | 0 | 0
2019-01-24 01:00 | 1012.1422 | 0 | 10000 | 10000 | 8987.8578 | 0 | 0
2019-01-24 02:00 | 958.178 | 0 | 10000 | 10000 | 9041.822 | 0 | 0
2019-01-24 03:00 | 943.623 | 0 | 10000 | 10000 | 9056.377 | 0 | 0
2019-01-24 04:00 | 940.696 | 0 | 10000 | 10000 | 9059.304 | 0 | 0
2019-01-24 05:00 | 997.3008 | 0 | 10000 | 10000 | 9002.6992 | 0 | 0
2019-01-24 06:00 | 1236.1758 | 0 | 10000 | 10000 | 8763.8242 | 0 | 0
2019-01-24 07:00 | 1607.1438 | 690.828 | 10000 | 10000 | 9083.6842 | 0 | 0
2019-01-24 08:00 | 1532.2539 | 2444.5193 | 9960 | 10000 | 10872.2654 | 0 | 0
2019-01-24 09:00 | 1325.324 | 3842.7963 | 9960 | 10000 | 12477.4723 | 0 | 0
2019-01-24 10:00 | 1362.5857 | 3880.9406 | 10000 | 10000 | 12518.355 | 0 | 0
2019-01-24 11:00 | 1326.9383 | 4343.6662 | 10000 | 10000 | 13016.7279 | 0 | 0
2019-01-24 12:00 | 1291.7765 | 4142.8244 | 10000 | 10000 | 12851.0479 | 0 | 0
2019-01-24 13:00 | 1259.1784 | 3139.9094 | 9960 | 10000 | 11840.731 | 0 | 0
2019-01-24 14:00 | 1259.3985 | 1342.8285 | 9573.3333 | 10000 | 9656.7633 | 0 | 0
2019-01-24 15:00 | 1334.8979 | 85.407 | 9060 | 10000 | 7810.5092 | 0 | 0
2019-01-24 16:00 | 1627.3925 | 0 | 9573.3333 | 10000 | 7945.9408 | 0 | 0
2019-01-24 17:00 | 2208.8502 | 0 | 6160 | 10000 | 3951.1498 | 0 | 0
2019-01-24 18:00 | 2540.7739 | 0 | 4266.6667 | 10000 | 1725.8928 | 0 | 0
2019-01-24 19:00 | 2490.2724 | 0 | 2773.3333 | 10000 | 283.0609 | 0 | 0
2019-01-24 20:00 | 2318.4458 | 0 | 4266.6667 | 10000 | 1948.2208 | 0 | 0
2019-01-24 21:00 | 2137.7022 | 0 | 6160 | 10000 | 4022.2978 | 0 | 0
2019-01-24 22:00 | 1786.957 | 0 | 4266.6667 | 10000 | 2479.7097 | 0 | 0
2019-01-24 23:00 | 1443.1652 | 0 | 4266.6667 | 10000 | 2823.5014 | 0 | 0
2019-01-25 | 1102.4695 | 0 | 2773.3333 | 10000 | 1670.8638 | 0 | 0
2019-01-25 01:00 | 968.0245 | 0 | 2773.3333 | 10000 | 1805.3088 | 0 | 0
2019-01-25 02:00 | 914.5121 | 0 | 2773.3333 | 10000 | 1858.8212 | 0 | 0
2019-01-25 03:00 | 899.3305 | 0 | 4266.6667 | 10000 | 3367.3362 | 0 | 0
2019-01-25 04:00 | 896.3437 | 0 | 4266.6667 | 10000 | 3370.3229 | 0 | 0
2019-01-25 05:00 | 956.9103 | 0 | 2773.3333 | 10000 | 1816.423 | 0 | 0
2019-01-25 06:00 | 1215.3361 | 0 | 7873.3333 | 10000 | 6657.9972 | 0 | 0
2019-01-25 07:00 | 1537.4715 | 0 | 7873.3333 | 10000 | 6335.8618 | 0 | 0
2019-01-25 08:00 | 1464.2614 | 32.6565 | 7873.3333 | 10000 | 6441.7285 | 0 | 0
2019-01-25 09:00 | 1235.7892 | 233.9077 | 9060 | 10000 | 8058.1185 | 0 | 0
2019-01-25 10:00 | 1253.5029 | 660.9774 | 9060 | 10000 | 8467.4746 | 0 | 0
2019-01-25 11:00 | 1230.6477 | 499.1299 | 9573.3333 | 10000 | 8841.8155 | 0 | 0
2019-01-25 12:00 | 1195.7628 | 368.2196 | 7873.3333 | 10000 | 7045.7901 | 0 | 0
2019-01-25 13:00 | 1162.4777 | 10.7341 | 1666.6667 | 10000 | 514.923 | 0 | 0
2019-01-25 14:00 | 1155.6555 | 0 | 7873.3333 | 10000 | 6717.6779 | 0 | 0
2019-01-25 15:00 | 1239.1712 | 0.50025 | 4266.6667 | 10000 | 3027.9958 | 0 | 0
2019-01-25 16:00 | 1536.3834 | 0 | 4266.6667 | 10000 | 2730.2832 | 0 | 0
2019-01-25 17:00 | 2116.4573 | 0 | 2773.3333 | 10000 | 656.876 | 0 | 0
2019-01-25 18:00 | 2458.0514 | 0 | 2773.3333 | 10000 | 315.2819 | 0 | 0
2019-01-25 19:00 | 2406.4321 | 0 | 1666.6667 | 10000 | -739.7655 | -739.7655 | 0
2019-01-25 20:00 | 2233.1742 | 0 | 1666.6667 | 9260.2345 | -566.5075 | -566.5075 | 0
2019-01-25 21:00 | 2043.6667 | 0 | 873.3333 | 8693.727 | -1170.3334 | -1170.3334 | 0
2019-01-25 22:00 | 1695.2938 | 0 | 286.6667 | 7523.3937 | -1408.6272 | -1408.6272 | 0
2019-01-25 23:00 | 1347.5914 | 0 | 286.6667 | 6114.7665 | -1060.9247 | -1060.9247 | 0
2019-01-26 | 1004.3397 | 0 | 873.3333 | 5053.8418 | -131.0064 | -131.0064 | 0
2019-01-26 01:00 | 863.1574 | 0 | 873.3333 | 4922.8354 | 10.176 | 10.176 | 0
2019-01-26 02:00 | 809.8609 | 0 | 873.3333 | 4933.0114 | 63.4724 | 63.4724 | 0
2019-01-26 03:00 | 795.9519 | 0 | 873.3333 | 4996.4838 | 77.3814 | 77.3814 | 0
2019-01-26 04:00 | 786.9748 | 0 | 286.6667 | 5073.8652 | -500.3082 | -500.3082 | 0
2019-01-26 05:00 | 844.2034 | 0 | 873.3333 | 4573.5571 | 29.1299 | 29.1299 | 0
2019-01-26 06:00 | 1082.3061 | 0 | 0 | 4602.687 | -1082.3061 | -1082.3061 | 0
2019-01-26 07:00 | 1445.1917 | 76.9649 | 0 | 3520.3809 | -1368.2268 | -1368.2268 | 0
2019-01-26 08:00 | 1373.4371 | 596.4693 | 873.3333 | 2152.1541 | 96.3656 | 96.3656 | 0
2019-01-26 09:00 | 1176.8673 | 3859.5679 | 873.3333 | 2248.5197 | 3556.0339 | 3556.0339 | 0
2019-01-26 10:00 | 1193.6198 | 6363.6136 | 4266.6667 | 5804.5536 | 9436.6604 | 4195.4464 | 0
2019-01-26 11:00 | 1173.5659 | 6914.9029 | 4266.6667 | 10000 | 10008.0037 | 0 | 0
2019-01-26 12:00 | 1143.9622 | 4356.8704 | 4266.6667 | 10000 | 7479.5749 | 0 | 0
2019-01-26 13:00 | 1112.9298 | 1267.392 | 7873.3333 | 10000 | 8027.7955 | 0 | 0
2019-01-26 14:00 | 1110.1004 | 2863.6346 | 6160 | 10000 | 7913.5341 | 0 | 0
2019-01-26 15:00 | 1187.069 | 2828.3249 | 9060 | 10000 | 10701.2559 | 0 | 0
2019-01-26 16:00 | 1481.0084 | 225.109 | 4266.6667 | 10000 | 3010.7673 | 0 | 0
2019-01-26 17:00 | 2053.1912 | 0 | 4266.6667 | 10000 | 2213.4755 | 0 | 0
2019-01-26 18:00 | 2399.1319 | 0 | 4266.6667 | 10000 | 1867.5348 | 0 | 0
2019-01-26 19:00 | 2357.4158 | 0 | 4266.6667 | 10000 | 1909.2508 | 0 | 0
2019-01-26 20:00 | 2188.2032 | 0 | 4266.6667 | 10000 | 2078.4634 | 0 | 0
2019-01-26 21:00 | 2002.5932 | 0 | 4266.6667 | 10000 | 2264.0734 | 0 | 0
2019-01-26 22:00 | 1653.2331 | 0 | 7873.3333 | 10000 | 6220.1003 | 0 | 0
2019-01-26 23:00 | 1307.8693 | 0 | 9060 | 10000 | 7752.1307 | 0 | 0
2019-01-27 | 964.0521 | 0 | 4266.6667 | 10000 | 3302.6146 | 0 | 0
2019-01-27 01:00 | 812.9373 | 0 | 2773.3333 | 10000 | 1960.396 | 0 | 0
2019-01-27 02:00 | 751.122 | 0 | 4266.6667 | 10000 | 3515.5447 | 0 | 0
2019-01-27 03:00 | 735.998 | 0 | 7873.3333 | 10000 | 7137.3353 | 0 | 0
2019-01-27 04:00 | 728.5807 | 0 | 6160 | 10000 | 5431.4193 | 0 | 0
2019-01-27 05:00 | 779.7277 | 0 | 4266.6667 | 10000 | 3486.939 | 0 | 0
2019-01-27 06:00 | 1017.552 | 0 | 873.3333 | 10000 | -144.2186 | -144.2186 | 0
2019-01-27 07:00 | 1369.2532 | 897.0713 | 2773.3333 | 9855.7814 | 2301.1514 | 144.2186 | 0
2019-01-27 08:00 | 1306.6954 | 3200.427 | 2773.3333 | 10000 | 4667.0649 | 0 | 0
2019-01-27 09:00 | 1105.7016 | 5195.6436 | 9873.3333 | 10000 | 13963.2754 | 0 | 0
2019-01-27 10:00 | 1106.6311 | 6542.4294 | 9573.3333 | 10000 | 15009.1315 | 0 | 0
2019-01-27 11:00 | 1108.8422 | 7134.0917 | 9960 | 10000 | 15985.2495 | 0 | 0
2019-01-27 12:00 | 1082.8504 | 7038.3185 | 9060 | 10000 | 15015.4682 | 0 | 0
2019-01-27 13:00 | 1060.5898 | 6154.1249 | 9060 | 10000 | 14153.5352 | 0 | 0
2019-01-27 14:00 | 1062.0479 | 2365.2395 | 9060 | 10000 | 10363.1916 | 0 | 0
2019-01-27 15:00 | 1142.0533 | 1770.5814 | 6160 | 10000 | 6788.5281 | 0 | 0
2019-01-27 16:00 | 1433.1679 | 281.0761 | 6160 | 10000 | 5007.9082 | 0 | 0
2019-01-27 17:00 | 1990.3296 | 0 | 6160 | 10000 | 4169.6704 | 0 | 0
2019-01-27 18:00 | 2365.4897 | 0 | 4266.6667 | 10000 | 1901.177 | 0 | 0
2019-01-27 19:00 | 2302.7784 | 0 | 4266.6667 | 10000 | 1963.8883 | 0 | 0
2019-01-27 20:00 | 2128.5062 | 0 | 4266.6667 | 10000 | 2138.1604 | 0 | 0
2019-01-27 21:00 | 1938.3175 | 0 | 4266.6667 | 10000 | 2328.3492 | 0 | 0
2019-01-27 22:00 | 1585.3487 | 0 | 4266.6667 | 10000 | 2681.318 | 0 | 0
2019-01-27 23:00 | 1241.4877 | 0 | 6160 | 10000 | 4918.5123 | 0 | 0
2019-01-28 | 917.6138 | 0 | 6160 | 10000 | 5242.3862 | 0 | 0
2019-01-28 01:00 | 780.2961 | 0 | 4266.6667 | 10000 | 3486.3706 | 0 | 0
2019-01-28 02:00 | 736.7804 | 0 | 6160 | 10000 | 5423.2196 | 0 | 0
2019-01-28 03:00 | 731.9534 | 0 | 4266.6667 | 10000 | 3534.7133 | 0 | 0
2019-01-28 04:00 | 735.6987 | 0 | 1666.6667 | 10000 | 930.968 | 0 | 0
2019-01-28 05:00 | 795.0888 | 0 | 873.3333 | 10000 | 78.2445 | 0 | 0
2019-01-28 06:00 | 1060.5679 | 0 | 873.3333 | 10000 | -187.2346 | -187.2346 | 0
2019-01-28 07:00 | 1413.7599 | 756.0733 | 2773.3333 | 9812.7654 | 2115.6467 | 187.2346 | 0
2019-01-28 08:00 | 1378.1132 | 1108.0664 | 2773.3333 | 10000 | 2503.2865 | 0 | 0
2019-01-28 09:00 | 1197.819 | 1857.8825 | 9060 | 10000 | 9720.0635 | 0 | 0
2019-01-28 10:00 | 1223.886 | 6569.4911 | 7873.3333 | 10000 | 13218.9385 | 0 | 0
2019-01-28 11:00 | 1253.7416 | 4771.3592 | 4266.6667 | 10000 | 7784.2842 | 0 | 0
2019-01-28 12:00 | 1203.0159 | 6987.5863 | 7873.3333 | 10000 | 13657.9038 | 0 | 0
2019-01-28 13:00 | 1154.5071 | 646.6691 | 7873.3333 | 10000 | 7365.4953 | 0 | 0
2019-01-28 14:00 | 1159.9189 | 2356.7479 | 9060 | 10000 | 10256.829 | 0 | 0
2019-01-28 15:00 | 1232.5716 | 54.0109 | 4266.6667 | 10000 | 3088.106 | 0 | 0
2019-01-28 16:00 | 1537.1242 | 426.2751 | 4266.6667 | 10000 | 3155.8176 | 0 | 0
2019-01-28 17:00 | 2120.1088 | 0 | 4266.6667 | 10000 | 2146.5579 | 0 | 0
2019-01-28 18:00 | 2479.0492 | 0 | 2773.3333 | 10000 | 294.2842 | 0 | 0
2019-01-28 19:00 | 2438.347 | 0 | 1666.6667 | 10000 | -771.6803 | -771.6803 | 0
2019-01-28 20:00 | 2275.1822 | 0 | 2773.3333 | 9228.3197 | 498.1511 | 498.1511 | 0
2019-01-28 21:00 | 2095.7377 | 0 | 2773.3333 | 9726.4708 | 677.5956 | 273.5292 | 0
2019-01-28 22:00 | 1739.3605 | 0 | 2773.3333 | 10000 | 1033.9729 | 0 | 0
2019-01-28 23:00 | 1385.1879 | 0 | 2773.3333 | 10000 | 1388.1454 | 0 | 0
2019-01-29 | 1036.3004 | 0 | 2773.3333 | 10000 | 1737.033 | 0 | 0
2019-01-29 01:00 | 896.7224 | 0 | 1666.6667 | 10000 | 769.9443 | 0 | 0
2019-01-29 02:00 | 843.5519 | 0 | 873.3333 | 10000 | 29.7814 | 0 | 0
2019-01-29 03:00 | 831.8732 | 0 | 2773.3333 | 10000 | 1941.4601 | 0 | 0
2019-01-29 04:00 | 829.6349 | 0 | 1666.6667 | 10000 | 837.0317 | 0 | 0
2019-01-29 05:00 | 886.9388 | 0 | 873.3333 | 10000 | -13.6055 | -13.6055 | 0
2019-01-29 06:00 | 1129.8136 | 0 | 1666.6667 | 9986.3945 | 536.8531 | 13.6055 | 0
2019-01-29 07:00 | 1507.9069 | 1170.9116 | 1666.6667 | 10000 | 1329.6714 | 0 | 0
2019-01-29 08:00 | 1448.6848 | 3887.3496 | 2773.3333 | 10000 | 5211.9981 | 0 | 0
2019-01-29 09:00 | 1246.9369 | 6161.0571 | 4266.6667 | 10000 | 9180.787 | 0 | 0
2019-01-29 10:00 | 1241.8035 | 7622.951 | 2773.3333 | 10000 | 9154.4807 | 0 | 0
2019-01-29 11:00 | 1206.4906 | 8309.9011 | 2773.3333 | 10000 | 9876.7439 | 0 | 0
2019-01-29 12:00 | 1177.6434 | 8255.3233 | 6160 | 10000 | 13237.6799 | 0 | 0
2019-01-29 13:00 | 1143.8723 | 7376.5255 | 4266.6667 | 10000 | 10499.3199 | 0 | 0
2019-01-29 14:00 | 1145.2487 | 5818.8459 | 873.3333 | 10000 | 5546.9305 | 0 | 0
2019-01-29 15:00 | 1234.9285 | 3563.2025 | 2773.3333 | 10000 | 5101.6074 | 0 | 0
2019-01-29 16:00 | 1524.0564 | 965.8356 | 1666.6667 | 10000 | 1108.4458 | 0 | 0
2019-01-29 17:00 | 2097.5615 | 0 | 286.6667 | 10000 | -1810.8949 | -1810.8949 | 0
2019-01-29 18:00 | 2449.7931 | 0 | 286.6667 | 8189.1051 | -2163.1264 | -2163.1264 | 0
2019-01-29 19:00 | 2403.8072 | 0 | 286.6667 | 6025.9787 | -2117.1405 | -2117.1405 | 0
2019-01-29 20:00 | 2234.9994 | 0 | 873.3333 | 3908.8382 | -1361.6661 | -1361.6661 | 0
2019-01-29 21:00 | 2049.7907 | 0 | 873.3333 | 2547.1721 | -1176.4573 | -1176.4573 | 0
2019-01-29 22:00 | 1691.7112 | 0 | 286.6667 | 1370.7147 | -1405.0446 | -1370.7147 | -34.3298
2019-01-29 23:00 | 1341.183 | 0 | 286.6667 | 0 | -1054.5163 | 0 | -1088.8462
2019-01-30 | 989.0102 | 0 | 873.3333 | 0 | -115.6769 | 0 | -1204.523
2019-01-30 01:00 | 861.0135 | 0 | 286.6667 | 0 | -574.3468 | 0 | -1778.8698
2019-01-30 02:00 | 818.3529 | 0 | 286.6667 | 0 | -531.6863 | 0 | -2310.5561
2019-01-30 03:00 | 809.9062 | 0 | 873.3333 | 0 | 63.4271 | 63.4271 | -2247.129
2019-01-30 04:00 | 813.1561 | 0 | 873.3333 | 63.4271 | 60.1772 | 60.1772 | -2123.5246
2019-01-30 05:00 | 877.9137 | 0 | 873.3333 | 123.6043 | -4.5804 | -4.5804 | -2004.5007
2019-01-30 06:00 | 1136.9463 | 0 | 286.6667 | 119.0239 | -850.2796 | -119.0239 | -2735.7564
2019-01-30 07:00 | 1485.9642 | 1176.7524 | 0 | 0 | -309.2118 | 0 | -3044.9682
2019-01-30 08:00 | 1399.612 | 3822.5459 | 873.3333 | 0 | 3296.2673 | 3296.2673 | 0
2019-01-30 09:00 | 1169.9742 | 5959.3598 | 286.6667 | 3296.2673 | 5076.0523 | 5076.0523 | 0
2019-01-30 10:00 | 1173.7355 | 7151.8155 | 0 | 8372.3196 | 5978.08 | 1627.6804 | 0
2019-01-30 11:00 | 1154.9907 | 6743.6506 | 0 | 10000 | 5588.6599 | 0 | 0
2019-01-30 12:00 | 1128.5623 | 7665.4343 | 286.6667 | 10000 | 6823.5387 | 0 | 0
2019-01-30 13:00 | 1104.6879 | 5993.3158 | 873.3333 | 10000 | 5761.9612 | 0 | 0
2019-01-30 14:00 | 1112.4942 | 3890.8537 | 1666.6667 | 10000 | 4445.0261 | 0 | 0
2019-01-30 15:00 | 1207.002 | 1044.9716 | 2773.3333 | 10000 | 2611.303 | 0 | 0
2019-01-30 16:00 | 1508.1507 | 132.626 | 873.3333 | 10000 | -502.1914 | -502.1914 | 0
2019-01-30 17:00 | 2092.0525 | 0 | 286.6667 | 9497.8086 | -1805.3858 | -1805.3858 | 0
2019-01-30 18:00 | 2441.2049 | 0 | 4266.6667 | 7692.4228 | 1825.4618 | 1825.4618 | 0
2019-01-30 19:00 | 2402.3179 | 0 | 4266.6667 | 9517.8846 | 1864.3487 | 482.1154 | 0
2019-01-30 20:00 | 2240.2838 | 0 | 2773.3333 | 10000 | 533.0496 | 0 | 0
2019-01-30 21:00 | 2061.5464 | 0 | 2773.3333 | 10000 | 711.787 | 0 | 0
2019-01-30 22:00 | 1720.4238 | 0 | 2773.3333 | 10000 | 1052.9095 | 0 | 0
2019-01-30 23:00 | 1385.1798 | 0 | 4266.6667 | 10000 | 2881.4869 | 0 | 0
2019-01-31 | 1054.0378 | 0 | 4266.6667 | 10000 | 3212.6289 | 0 | 0
2019-01-31 01:00 | 921.4298 | 0 | 4266.6667 | 10000 | 3345.2369 | 0 | 0
2019-01-31 02:00 | 876.8591 | 0 | 4266.6667 | 10000 | 3389.8076 | 0 | 0
2019-01-31 03:00 | 871.5935 | 0 | 2773.3333 | 10000 | 1901.7399 | 0 | 0
2019-01-31 04:00 | 874.8927 | 0 | 1666.6667 | 10000 | 791.774 | 0 | 0
2019-01-31 05:00 | 940.7039 | 0 | 2773.3333 | 10000 | 1832.6295 | 0 | 0
2019-01-31 06:00 | 1205.3787 | 0 | 1666.6667 | 10000 | 461.288 | 0 | 0
2019-01-31 07:00 | 1552.6316 | 1141.8787 | 873.3333 | 10000 | 462.5804 | 0 | 0
2019-01-31 08:00 | 1456.0062 | 3663.8011 | 286.6667 | 10000 | 2494.4615 | 0 | 0
2019-01-31 09:00 | 1225.0165 | 5592.2936 | 0 | 10000 | 4367.2771 | 0 | 0
2019-01-31 10:00 | 1225.0856 | 6874.9795 | 0 | 10000 | 5649.8938 | 0 | 0
2019-01-31 11:00 | 1181.3611 | 7646.5915 | 0 | 10000 | 6465.2304 | 0 | 0
2019-01-31 12:00 | 1139.69 | 7576.8854 | 0 | 10000 | 6437.1954 | 0 | 0
2019-01-31 13:00 | 1108.6061 | 6796.101 | 0 | 10000 | 5687.4948 | 0 | 0
2019-01-31 14:00 | 1115.7237 | 5360.0994 | 0 | 10000 | 4244.3757 | 0 | 0
2019-01-31 15:00 | 1205.0264 | 3227.2875 | 0 | 10000 | 2022.2611 | 0 | 0
2019-01-31 16:00 | 1508.9029 | 908.0768 | 0 | 10000 | -600.8261 | -600.8261 | 0
2019-01-31 17:00 | 2091.8662 | 0 | 0 | 9399.1739 | -2091.8662 | -2091.8662 | 0
2019-01-31 18:00 | 2443.7305 | 0 | 0 | 7307.3077 | -2443.7305 | -2443.7305 | 0
2019-01-31 19:00 | 2404.0791 | 0 | 0 | 4863.5772 | -2404.0791 | -2404.0791 | 0
2019-01-31 20:00 | 2236.941 | 0 | 0 | 2459.498 | -2236.941 | -2236.941 | 0
2019-01-31 21:00 | 2058.18 | 0 | 0 | 222.557 | -2058.18 | -222.557 | -1835.6229
2019-01-31 22:00 | 1718.4208 | 0 | 0 | 0 | -1718.4208 | 0 | -3554.0437
2019-01-31 23:00 | 1386.1312 | 0 | 0 | 0 | -1386.1312 | 0 | -4940.1749
2019-02-01 | 1055.5094 | 0 | 0 | 0 | -1055.5094 | 0 | -5995.6843
2019-02-01 01:00 | 934.2521 | 0 | 286.6667 | 0 | -647.5854 | 0 | -6643.2698
2019-02-01 02:00 | 893.139 | 0 | 0 | 0 | -893.139 | 0 | -7536.4088
2019-02-01 03:00 | 896.1835 | 0 | 286.6667 | 0 | -609.5168 | 0 | -8145.9256
2019-02-01 04:00 | 902.5338 | 0 | 0 | 0 | -902.5338 | 0 | -9048.4594
2019-02-01 05:00 | 972.1991 | 0 | 0 | 0 | -972.1991 | 0 | -10020.6585
2019-02-01 06:00 | 1194.229 | 0 | 0 | 0 | -1194.229 | 0 | -11214.8875
2019-02-01 07:00 | 1498.3768 | 683.7796 | 286.6667 | 0 | -527.9305 | 0 | -11742.818
2019-02-01 08:00 | 1422.2581 | 1928.8191 | 1666.6667 | 0 | 2173.2276 | 2173.2276 | -9569.5903
2019-02-01 09:00 | 1224.9464 | 4471.8831 | 873.3333 | 2173.2276 | 4120.27 | 4120.27 | -3276.0927
2019-02-01 10:00 | 1233.9941 | 6489.8076 | 286.6667 | 6293.4976 | 5542.4803 | 3706.5024 | 0
2019-02-01 11:00 | 1192.1004 | 7016.817 | 2773.3333 | 10000 | 8598.05 | 0 | 0
2019-02-01 12:00 | 1141.6891 | 5863.7603 | 6160 | 10000 | 10882.0712 | 0 | 0
2019-02-01 13:00 | 1132.2413 | 5115.4587 | 4266.6667 | 10000 | 8249.8841 | 0 | 0
2019-02-01 14:00 | 1140.1556 | 3984.0864 | 9573.3333 | 10000 | 12417.2642 | 0 | 0
2019-02-01 15:00 | 1215.0334 | 1033.5441 | 9573.3333 | 10000 | 9391.844 | 0 | 0
2019-02-01 16:00 | 1447.1433 | 137.4215 | 7873.3333 | 10000 | 6563.6116 | 0 | 0
2019-02-01 17:00 | 1931.6224 | 0 | 1666.6667 | 10000 | -264.9558 | -264.9558 | 0
2019-02-01 18:00 | 2275.4567 | 0 | 286.6667 | 9735.0442 | -1988.79 | -1988.79 | 0
2019-02-01 19:00 | 2403.9234 | 0 | 286.6667 | 7746.2542 | -2117.2567 | -2117.2567 | 0
2019-02-01 20:00 | 2327.3621 | 0 | 286.6667 | 5628.9975 | -2040.6955 | -2040.6955 | 0
2019-02-01 21:00 | 2133.3777 | 0 | 4266.6667 | 3588.3021 | 2133.289 | 2133.289 | 0
2019-02-01 22:00 | 1784.4004 | 0 | 2773.3333 | 5721.591 | 988.9329 | 988.9329 | 0
2019-02-01 23:00 | 1459.4457 | 0 | 873.3333 | 6710.5239 | -586.1124 | -586.1124 | 0
2019-02-02 | 1121.7581 | 0 | 2773.3333 | 6124.4116 | 1651.5752 | 1651.5752 | 0
2019-02-02 01:00 | 985.7646 | 0 | 1666.6667 | 7775.9868 | 680.9021 | 680.9021 | 0
2019-02-02 02:00 | 930.2966 | 0 | 286.6667 | 8456.8889 | -643.6299 | -643.6299 | 0
2019-02-02 03:00 | 920.8762 | 0 | 873.3333 | 7813.259 | -47.5428 | -47.5428 | 0
2019-02-02 04:00 | 931.3621 | 0 | 873.3333 | 7765.7162 | -58.0287 | -58.0287 | 0
2019-02-02 05:00 | 1005.6866 | 0 | 873.3333 | 7707.6874 | -132.3532 | -132.3532 | 0
2019-02-02 06:00 | 1218.7982 | 0 | 873.3333 | 7575.3342 | -345.4649 | -345.4649 | 0
2019-02-02 07:00 | 1522.9691 | 181.2664 | 1666.6667 | 7229.8693 | 324.964 | 324.964 | 0
2019-02-02 08:00 | 1419.5629 | 1490.4816 | 873.3333 | 7554.8333 | 944.2521 | 944.2521 | 0
2019-02-02 09:00 | 1228.2721 | 2766.3652 | 873.3333 | 8499.0854 | 2411.4265 | 1500.9146 | 0
2019-02-02 10:00 | 1244.6626 | 4332.5249 | 1666.6667 | 10000 | 4754.529 | 0 | 0
2019-02-02 11:00 | 1201.521 | 2714.1644 | 4266.6667 | 10000 | 5779.3101 | 0 | 0
2019-02-02 12:00 | 1151.8455 | 3682.2402 | 6160 | 10000 | 8690.3947 | 0 | 0
2019-02-02 13:00 | 1117.3109 | 414.8361 | 6160 | 10000 | 5457.5252 | 0 | 0
2019-02-02 14:00 | 1108.484 | 215.8205 | 6160 | 10000 | 5267.3365 | 0 | 0
2019-02-02 15:00 | 1175.6783 | 831.6374 | 4266.6667 | 10000 | 3922.6258 | 0 | 0
2019-02-02 16:00 | 1413.9492 | 126.6817 | 2773.3333 | 10000 | 1486.0659 | 0 | 0
2019-02-02 17:00 | 1906.9693 | 0 | 7873.3333 | 10000 | 5966.364 | 0 | 0
2019-02-02 18:00 | 2259.1901 | 0 | 2773.3333 | 10000 | 514.1432 | 0 | 0
2019-02-02 19:00 | 2386.5173 | 0 | 1666.6667 | 10000 | -719.8506 | -719.8506 | 0
2019-02-02 20:00 | 2306.3588 | 0 | 2773.3333 | 9280.1494 | 466.9745 | 466.9745 | 0
2019-02-02 21:00 | 2111.061 | 0 | 6160 | 9747.1239 | 4048.939 | 252.8761 | 0
2019-02-02 22:00 | 1758.5457 | 0 | 7873.3333 | 10000 | 6114.7877 | 0 | 0
2019-02-02 23:00 | 1430.5059 | 0 | 2773.3333 | 10000 | 1342.8274 | 0 | 0
2019-02-03 | 1085.3408 | 0 | 4266.6667 | 10000 | 3181.3259 | 0 | 0
2019-02-03 01:00 | 957.5744 | 0 | 1666.6667 | 10000 | 709.0923 | 0 | 0
2019-02-03 02:00 | 903.644 | 0 | 4266.6667 | 10000 | 3363.0226 | 0 | 0
2019-02-03 03:00 | 892.6671 | 0 | 1666.6667 | 10000 | 773.9996 | 0 | 0
2019-02-03 04:00 | 888.4193 | 0 | 1666.6667 | 10000 | 778.2474 | 0 | 0
2019-02-03 05:00 | 950.8042 | 0 | 1666.6667 | 10000 | 715.8624 | 0 | 0
2019-02-03 06:00 | 1181.8825 | 0 | 1666.6667 | 10000 | 484.7842 | 0 | 0
2019-02-03 07:00 | 1474.3566 | 66.478 | 873.3333 | 10000 | -534.5452 | -534.5452 | 0
2019-02-03 08:00 | 1398.0474 | 367.5319 | 286.6667 | 9465.4548 | -743.8488 | -743.8488 | 0
2019-02-03 09:00 | 1217.2482 | 387.3568 | 286.6667 | 8721.606 | -543.2247 | -543.2247 | 0
2019-02-03 10:00 | 1230.0507 | 765.8563 | 286.6667 | 8178.3813 | -177.5277 | -177.5277 | 0
2019-02-03 11:00 | 1196.9201 | 1215.42 | 286.6667 | 8000.8536 | 305.1666 | 305.1666 | 0
2019-02-03 12:00 | 1162.5654 | 978.1084 | 873.3333 | 8306.0202 | 688.8763 | 688.8763 | 0
2019-02-03 13:00 | 1124.1689 | 1292.5275 | 873.3333 | 8994.8965 | 1041.692 | 1005.1035 | 0
2019-02-03 14:00 | 1121.1999 | 292.0965 | 2773.3333 | 10000 | 1944.2299 | 0 | 0
2019-02-03 15:00 | 1179.6905 | 0 | 2773.3333 | 10000 | 1593.6429 | 0 | 0
2019-02-03 16:00 | 1404.1803 | 0 | 1666.6667 | 10000 | 262.4864 | 0 | 0
2019-02-03 17:00 | 1876.9881 | 0 | 1666.6667 | 10000 | -210.3214 | -210.3214 | 0
2019-02-03 18:00 | 2225.0194 | 0 | 2773.3333 | 9789.6786 | 548.314 | 210.3214 | 0
2019-02-03 19:00 | 2345.6264 | 0 | 4266.6667 | 10000 | 1921.0402 | 0 | 0
2019-02-03 20:00 | 2255.8228 | 0 | 2773.3333 | 10000 | 517.5105 | 0 | 0
2019-02-03 21:00 | 2056.5892 | 0 | 2773.3333 | 10000 | 716.7441 | 0 | 0
2019-02-03 22:00 | 1702.4944 | 0 | 2773.3333 | 10000 | 1070.8389 | 0 | 0
2019-02-03 23:00 | 1372.6557 | 0 | 2773.3333 | 10000 | 1400.6776 | 0 | 0
2019-02-04 | 1034.5651 | 0 | 6160 | 10000 | 5125.4349 | 0 | 0
2019-02-04 01:00 | 900.5178 | 0 | 6160 | 10000 | 5259.4822 | 0 | 0
2019-02-04 02:00 | 846.7175 | 0 | 6160 | 10000 | 5313.2825 | 0 | 0
2019-02-04 03:00 | 837.8158 | 0 | 4266.6667 | 10000 | 3428.8508 | 0 | 0
2019-02-04 04:00 | 836.8607 | 0 | 4266.6667 | 10000 | 3429.806 | 0 | 0
2019-02-04 05:00 | 917.4926 | 0 | 2773.3333 | 10000 | 1855.8407 | 0 | 0
2019-02-04 06:00 | 1147.775 | 0 | 4266.6667 | 10000 | 3118.8917 | 0 | 0
2019-02-04 07:00 | 1471.4783 | 368.3277 | 2773.3333 | 10000 | 1670.1828 | 0 | 0
2019-02-04 08:00 | 1384.2196 | 1894.771 | 2773.3333 | 10000 | 3283.8848 | 0 | 0
2019-02-04 09:00 | 1207.1536 | 5674.8751 | 2773.3333 | 10000 | 7241.0548 | 0 | 0
2019-02-04 10:00 | 1235.3853 | 6919.7938 | 2773.3333 | 10000 | 8457.7419 | 0 | 0
2019-02-04 11:00 | 1197.6932 | 7515.672 | 4266.6667 | 10000 | 10584.6455 | 0 | 0
2019-02-04 12:00 | 1144.3476 | 7464.4073 | 4266.6667 | 10000 | 10586.7264 | 0 | 0
2019-02-04 13:00 | 1104.6534 | 6712.2648 | 6160 | 10000 | 11767.6114 | 0 | 0
2019-02-04 14:00 | 1093.165 | 4875.6354 | 286.6667 | 10000 | 4069.1371 | 0 | 0
2019-02-04 15:00 | 1161.9819 | 1964.944 | 2773.3333 | 10000 | 3576.2954 | 0 | 0
2019-02-04 16:00 | 1403.0768 | 429.9332 | 1666.6667 | 10000 | 693.5231 | 0 | 0
2019-02-04 17:00 | 1887.8124 | 0 | 4266.6667 | 10000 | 2378.8543 | 0 | 0
2019-02-04 18:00 | 2239.1647 | 0 | 873.3333 | 10000 | -1365.8314 | -1365.8314 | 0
2019-02-04 19:00 | 2365.2082 | 0 | 286.6667 | 8634.1686 | -2078.5415 | -2078.5415 | 0
2019-02-04 20:00 | 2280.741 | 0 | 286.6667 | 6555.6271 | -1994.0743 | -1994.0743 | 0
2019-02-04 21:00 | 2084.8919 | 0 | 286.6667 | 4561.5528 | -1798.2252 | -1798.2252 | 0
2019-02-04 22:00 | 1727.1724 | 0 | 873.3333 | 2763.3276 | -853.8391 | -853.8391 | 0
2019-02-04 23:00 | 1380.2824 | 0 | 873.3333 | 1909.4885 | -506.949 | -506.949 | 0
2019-02-05 | 1024.0888 | 0 | 286.6667 | 1402.5395 | -737.4221 | -737.4221 | 0
2019-02-05 01:00 | 893.3937 | 0 | 286.6667 | 665.1173 | -606.7271 | -606.7271 | 0
2019-02-05 02:00 | 842.1718 | 0 | 873.3333 | 58.3903 | 31.1616 | 31.1616 | 0
2019-02-05 03:00 | 835.9096 | 0 | 873.3333 | 89.5518 | 37.4237 | 37.4237 | 0
2019-02-05 04:00 | 835.1986 | 0 | 286.6667 | 126.9755 | -548.532 | -126.9755 | -421.5564
2019-02-05 05:00 | 904.6218 | 0 | 873.3333 | 0 | -31.2884 | 0 | -452.8449
2019-02-05 06:00 | 1121.4366 | 0 | 4266.6667 | 0 | 3145.2301 | 3145.2301 | 0
2019-02-05 07:00 | 1467.8013 | 14.7131 | 4266.6667 | 3145.2301 | 2813.5785 | 2813.5785 | 0
2019-02-05 08:00 | 1385.3015 | 160.272 | 2773.3333 | 5958.8086 | 1548.3039 | 1548.3039 | 0
2019-02-05 09:00 | 1225.7037 | 529.5911 | 4266.6667 | 7507.1125 | 3570.5541 | 2492.8875 | 0
2019-02-05 10:00 | 1261.2833 | 837.2126 | 1666.6667 | 10000 | 1242.596 | 0 | 0
2019-02-05 11:00 | 1244.4624 | 2845.0448 | 9060 | 10000 | 10660.5824 | 0 | 0
2019-02-05 12:00 | 1203.7138 | 1255.8725 | 4266.6667 | 10000 | 4318.8253 | 0 | 0
2019-02-05 13:00 | 1170.8142 | 1093.3464 | 7873.3333 | 10000 | 7795.8656 | 0 | 0
2019-02-05 14:00 | 1167.1409 | 487.286 | 9060 | 10000 | 8380.1452 | 0 | 0
2019-02-05 15:00 | 1225.9146 | 168.9246 | 6160 | 10000 | 5103.0101 | 0 | 0
2019-02-05 16:00 | 1450.3137 | 864.5746 | 4266.6667 | 10000 | 3680.9276 | 0 | 0
2019-02-05 17:00 | 1930.4843 | 0 | 6160 | 10000 | 4229.5157 | 0 | 0
2019-02-05 18:00 | 2276.7038 | 0 | 2773.3333 | 10000 | 496.6295 | 0 | 0
2019-02-05 19:00 | 2402.1959 | 0 | 4266.6667 | 10000 | 1864.4708 | 0 | 0
2019-02-05 20:00 | 2314.8956 | 0 | 286.6667 | 10000 | -2028.229 | -2028.229 | 0
2019-02-05 21:00 | 2122.0012 | 0 | 1666.6667 | 7971.771 | -455.3346 | -455.3346 | 0
2019-02-05 22:00 | 1757.526 | 0 | 1666.6667 | 7516.4365 | -90.8593 | -90.8593 | 0
2019-02-05 23:00 | 1410.3548 | 0 | 2773.3333 | 7425.5772 | 1362.9785 | 1362.9785 | 0
2019-02-06 | 1046.3835 | 0 | 873.3333 | 8788.5557 | -173.0502 | -173.0502 | 0
2019-02-06 01:00 | 915.5226 | 0 | 2773.3333 | 8615.5055 | 1857.8107 | 1384.4945 | 0
2019-02-06 02:00 | 878.0776 | 0 | 6160 | 10000 | 5281.9224 | 0 | 0
2019-02-06 03:00 | 877.9834 | 0 | 9573.3333 | 10000 | 8695.35 | 0 | 0
2019-02-06 04:00 | 878.1645 | 0 | 9060 | 10000 | 8181.8355 | 0 | 0
2019-02-06 05:00 | 959.1211 | 0 | 4266.6667 | 10000 | 3307.5455 | 0 | 0
2019-02-06 06:00 | 1195.0335 | 0 | 4266.6667 | 10000 | 3071.6332 | 0 | 0
2019-02-06 07:00 | 1512.7444 | 1227.5445 | 4266.6667 | 10000 | 3981.4668 | 0 | 0
2019-02-06 08:00 | 1400.3941 | 3817.5227 | 1666.6667 | 10000 | 4083.7953 | 0 | 0
2019-02-06 09:00 | 1202.7233 | 4303.461 | 9060 | 10000 | 12160.7377 | 0 | 0
2019-02-06 10:00 | 1224.697 | 5638.6064 | 7873.3333 | 10000 | 12287.2427 | 0 | 0
2019-02-06 11:00 | 1185.5683 | 3654.0215 | 7873.3333 | 10000 | 10341.7866 | 0 | 0
2019-02-06 12:00 | 1149.0696 | 7878.42 | 6160 | 10000 | 12889.3504 | 0 | 0
2019-02-06 13:00 | 1108.3898 | 7065.3608 | 6160 | 10000 | 12116.971 | 0 | 0
2019-02-06 14:00 | 1111.2533 | 5666.9298 | 6160 | 10000 | 10715.6764 | 0 | 0
2019-02-06 15:00 | 1197.7056 | 3587.8447 | 6160 | 10000 | 8550.1391 | 0 | 0
2019-02-06 16:00 | 1460.1168 | 1120.8245 | 4266.6667 | 10000 | 3927.3744 | 0 | 0
2019-02-06 17:00 | 1947.6574 | 0 | 1666.6667 | 10000 | -280.9907 | -280.9907 | 0
2019-02-06 18:00 | 2300.2165 | 0 | 873.3333 | 9719.0093 | -1426.8831 | -1426.8831 | 0
2019-02-06 19:00 | 2431.1841 | 0 | 873.3333 | 8292.1262 | -1557.8508 | -1557.8508 | 0
2019-02-06 20:00 | 2344.4003 | 0 | 0 | 6734.2754 | -2344.4003 | -2344.4003 | 0
2019-02-06 21:00 | 2150.6771 | 0 | 0 | 4389.8751 | -2150.6771 | -2150.6771 | 0
2019-02-06 22:00 | 1794.2546 | 0 | 0 | 2239.1979 | -1794.2546 | -1794.2546 | 0
2019-02-06 23:00 | 1467.2426 | 0 | 0 | 444.9433 | -1467.2426 | -444.9433 | -1022.2993
2019-02-07 | 1121.9813 | 0 | 0 | 0 | -1121.9813 | 0 | -2144.2806
2019-02-07 01:00 | 990.1545 | 0 | 0 | 0 | -990.1545 | 0 | -3134.4351
2019-02-07 02:00 | 931.2572 | 0 | 873.3333 | 0 | -57.9238 | 0 | -3192.3589
2019-02-07 03:00 | 913.1829 | 0 | 873.3333 | 0 | -39.8496 | 0 | -3232.2085
2019-02-07 04:00 | 908.1286 | 0 | 2773.3333 | 0 | 1865.2047 | 1865.2047 | -1367.0038
2019-02-07 05:00 | 978.2115 | 0 | 4266.6667 | 1865.2047 | 3288.4552 | 3288.4552 | 0
2019-02-07 06:00 | 1183.8257 | 0 | 6160 | 5153.6599 | 4976.1743 | 4846.3401 | 0
2019-02-07 07:00 | 1499.469 | 1382.6128 | 4266.6667 | 10000 | 4149.8105 | 0 | 0
2019-02-07 08:00 | 1420.5609 | 3951.1849 | 6160 | 10000 | 8690.624 | 0 | 0
2019-02-07 09:00 | 1239.1387 | 5989.7738 | 6160 | 10000 | 10910.6352 | 0 | 0
2019-02-07 10:00 | 1248.977 | 7549.3107 | 7873.3333 | 10000 | 14173.6671 | 0 | 0
2019-02-07 11:00 | 1199.7724 | 8211.4312 | 7873.3333 | 10000 | 14884.9922 | 0 | 0
2019-02-07 12:00 | 1145.6492 | 8138.3154 | 9573.3333 | 10000 | 16565.9995 | 0 | 0
2019-02-07 13:00 | 1111.7321 | 7372.7201 | 9573.3333 | 10000 | 15834.3214 | 0 | 0
2019-02-07 14:00 | 1101.5788 | 5902.5705 | 9060 | 10000 | 13860.9917 | 0 | 0
2019-02-07 15:00 | 1169.4173 | 3652.3425 | 9573.3333 | 10000 | 12056.2586 | 0 | 0
2019-02-07 16:00 | 1415.0306 | 1218.0386 | 9573.3333 | 10000 | 9376.3414 | 0 | 0
2019-02-07 17:00 | 1910.2258 | 0 | 7873.3333 | 10000 | 5963.1076 | 0 | 0
2019-02-07 18:00 | 2258.4332 | 0 | 6160 | 10000 | 3901.5668 | 0 | 0
2019-02-07 19:00 | 2386.9919 | 0 | 9060 | 10000 | 6673.0081 | 0 | 0
2019-02-07 20:00 | 2312.2123 | 0 | 6160 | 10000 | 3847.7877 | 0 | 0
2019-02-07 21:00 | 2121.2702 | 0 | 4266.6667 | 10000 | 2145.3964 | 0 | 0
2019-02-07 22:00 | 1774.0893 | 0 | 4266.6667 | 10000 | 2492.5774 | 0 | 0
2019-02-07 23:00 | 1448.0762 | 0 | 873.3333 | 10000 | -574.7428 | -574.7428 | 0
2019-02-08 | 1103.7621 | 0 | 873.3333 | 9425.2572 | -230.4287 | -230.4287 | 0
2019-02-08 01:00 | 974.9776 | 0 | 1666.6667 | 9194.8284 | 691.689 | 691.689 | 0
2019-02-08 02:00 | 918.1642 | 0 | 286.6667 | 9886.5175 | -631.4976 | -631.4976 | 0
2019-02-08 03:00 | 905.2781 | 0 | 286.6667 | 9255.0199 | -618.6114 | -618.6114 | 0
2019-02-08 04:00 | 905.4545 | 0 | 873.3333 | 8636.4085 | -32.1211 | -32.1211 | 0
2019-02-08 05:00 | 978.3876 | 0 | 0 | 8604.2874 | -978.3876 | -978.3876 | 0
2019-02-08 06:00 | 1186.529 | 0 | 0 | 7625.8998 | -1186.529 | -1186.529 | 0
2019-02-08 07:00 | 1496.5129 | 1505.9951 | 0 | 6439.3708 | 9.4822 | 9.4822 | 0
2019-02-08 08:00 | 1398.6873 | 4139.0386 | 286.6667 | 6448.853 | 3027.018 | 3027.018 | 0
2019-02-08 09:00 | 1203.3583 | 6174.8238 | 0 | 9475.871 | 4971.4655 | 524.129 | 0
2019-02-08 10:00 | 1200.6879 | 7489.0196 | 286.6667 | 10000 | 6574.9984 | 0 | 0
2019-02-08 11:00 | 1159.1954 | 8056.2583 | 873.3333 | 10000 | 7770.3962 | 0 | 0
2019-02-08 12:00 | 1112.1168 | 7913.9033 | 1666.6667 | 10000 | 8468.4531 | 0 | 0
2019-02-08 13:00 | 1063.4142 | 5111.6672 | 873.3333 | 10000 | 4921.5863 | 0 | 0
2019-02-08 14:00 | 1065.1474 | 4044.4258 | 4266.6667 | 10000 | 7245.9451 | 0 | 0
2019-02-08 15:00 | 1132.8047 | 1764.8647 | 2773.3333 | 10000 | 3405.3934 | 0 | 0
2019-02-08 16:00 | 1375.8112 | 1131.3734 | 873.3333 | 10000 | 628.8956 | 0 | 0
2019-02-08 17:00 | 1869.1186 | 0 | 873.3333 | 10000 | -995.7853 | -995.7853 | 0
2019-02-08 18:00 | 2221.2972 | 0 | 1666.6667 | 9004.2147 | -554.6305 | -554.6305 | 0
2019-02-08 19:00 | 2351.8793 | 0 | 873.3333 | 8449.5842 | -1478.546 | -1478.546 | 0
2019-02-08 20:00 | 2273.7047 | 0 | 2773.3333 | 6971.0382 | 499.6287 | 499.6287 | 0
2019-02-08 21:00 | 2080.2912 | 0 | 2773.3333 | 7470.6669 | 693.0422 | 693.0422 | 0
2019-02-08 22:00 | 1728.5405 | 0 | 1666.6667 | 8163.7091 | -61.8739 | -61.8739 | 0
2019-02-08 23:00 | 1403.002 | 0 | 286.6667 | 8101.8352 | -1116.3353 | -1116.3353 | 0
2019-02-09 | 1056.337 | 0 | 0 | 6985.4999 | -1056.337 | -1056.337 | 0
2019-02-09 01:00 | 929.0471 | 0 | 0 | 5929.1629 | -929.0471 | -929.0471 | 0
2019-02-09 02:00 | 882.4319 | 0 | 0 | 5000.1158 | -882.4319 | -882.4319 | 0
2019-02-09 03:00 | 871.6107 | 0 | 0 | 4117.6839 | -871.6107 | -871.6107 | 0
2019-02-09 04:00 | 869.9804 | 0 | 1666.6667 | 3246.0732 | 796.6863 | 796.6863 | 0
2019-02-09 05:00 | 939.1171 | 0 | 7873.3333 | 4042.7595 | 6934.2162 | 5957.2405 | 0
2019-02-09 06:00 | 1151.9589 | 0 | 9060 | 10000 | 7908.0411 | 0 | 0
2019-02-09 07:00 | 1486.5177 | 1337.8927 | 9573.3333 | 10000 | 9424.7084 | 0 | 0
2019-02-09 08:00 | 1371.0583 | 1264.3525 | 9060 | 10000 | 8953.2942 | 0 | 0
2019-02-09 09:00 | 1176.8748 | 4088.9883 | 10000 | 10000 | 12912.1135 | 0 | 0
2019-02-09 10:00 | 1178.4835 | 4865.8305 | 10000 | 10000 | 13687.347 | 0 | 0
2019-02-09 11:00 | 1140.273 | 6401.4302 | 10000 | 10000 | 15261.1572 | 0 | 0
2019-02-09 12:00 | 1105.0125 | 5233.5293 | 9873.3333 | 10000 | 14001.8501 | 0 | 0
2019-02-09 13:00 | 1079.4192 | 5126.8196 | 9960 | 10000 | 14007.4004 | 0 | 0
2019-02-09 14:00 | 1077.5839 | 3453.2223 | 9573.3333 | 10000 | 11948.9717 | 0 | 0
2019-02-09 15:00 | 1140.8091 | 1960.4406 | 7873.3333 | 10000 | 8692.9649 | 0 | 0
2019-02-09 16:00 | 1376.1466 | 455.8048 | 7873.3333 | 10000 | 6952.9915 | 0 | 0
2019-02-09 17:00 | 1868.2515 | 0 | 4266.6667 | 10000 | 2398.4151 | 0 | 0
2019-02-09 18:00 | 2221.2512 | 0 | 9873.3333 | 10000 | 7652.0822 | 0 | 0
2019-02-09 19:00 | 2347.0838 | 0 | 9573.3333 | 10000 | 7226.2495 | 0 | 0
2019-02-09 20:00 | 2266.6082 | 0 | 9573.3333 | 10000 | 7306.7252 | 0 | 0
2019-02-09 21:00 | 2067.4598 | 0 | 9873.3333 | 10000 | 7805.8735 | 0 | 0
2019-02-09 22:00 | 1709.0378 | 0 | 10000 | 10000 | 8290.9622 | 0 | 0
2019-02-09 23:00 | 1371.5345 | 0 | 9060 | 10000 | 7688.4655 | 0 | 0
2019-02-10 | 1016.8805 | 0 | 7873.3333 | 10000 | 6856.4529 | 0 | 0
2019-02-10 01:00 | 882.2621 | 0 | 6160 | 10000 | 5277.7379 | 0 | 0
2019-02-10 02:00 | 826.2228 | 0 | 4266.6667 | 10000 | 3440.4438 | 0 | 0
2019-02-10 03:00 | 814.3819 | 0 | 2773.3333 | 10000 | 1958.9514 | 0 | 0
2019-02-10 04:00 | 810.2316 | 0 | 2773.3333 | 10000 | 1963.1017 | 0 | 0
2019-02-10 05:00 | 879.2419 | 0 | 873.3333 | 10000 | -5.9085 | -5.9085 | 0
2019-02-10 06:00 | 1088.9558 | 0 | 1666.6667 | 9994.0915 | 577.7109 | 5.9085 | 0
2019-02-10 07:00 | 1404.0988 | 1338.0641 | 2773.3333 | 10000 | 2707.2987 | 0 | 0
2019-02-10 08:00 | 1335.7395 | 3945.5936 | 2773.3333 | 10000 | 5383.1875 | 0 | 0
2019-02-10 09:00 | 1131.0008 | 6089.227 | 4266.6667 | 10000 | 9224.8929 | 0 | 0
2019-02-10 10:00 | 1124.7009 | 7449.7724 | 7873.3333 | 10000 | 14198.4049 | 0 | 0
2019-02-10 11:00 | 1103.6447 | 8137.8899 | 4266.6667 | 10000 | 11300.9119 | 0 | 0
2019-02-10 12:00 | 1063.2943 | 8108.8788 | 6160 | 10000 | 13205.5846 | 0 | 0
2019-02-10 13:00 | 1027.9692 | 7416.7962 | 6160 | 10000 | 12548.827 | 0 | 0
2019-02-10 14:00 | 1024.5947 | 5967.3569 | 2773.3333 | 10000 | 7716.0955 | 0 | 0
2019-02-10 15:00 | 1090.9604 | 3836.4115 | 4266.6667 | 10000 | 7012.1177 | 0 | 0
2019-02-10 16:00 | 1326.4499 | 1298.4742 | 2773.3333 | 10000 | 2745.3577 | 0 | 0
2019-02-10 17:00 | 1812.9692 | 0 | 286.6667 | 10000 | -1526.3026 | -1526.3026 | 0
2019-02-10 18:00 | 2171.4769 | 0 | 286.6667 | 8473.6974 | -1884.8103 | -1884.8103 | 0
2019-02-10 19:00 | 2305.2961 | 0 | 286.6667 | 6588.8872 | -2018.6295 | -2018.6295 | 0
2019-02-10 20:00 | 2224.1282 | 0 | 286.6667 | 4570.2577 | -1937.4615 | -1937.4615 | 0
2019-02-10 21:00 | 2030.7227 | 0 | 286.6667 | 2632.7962 | -1744.056 | -1744.056 | 0
2019-02-10 22:00 | 1684.6774 | 0 | 286.6667 | 888.7402 | -1398.0108 | -888.7402 | -509.2706
2019-02-10 23:00 | 1362.6762 | 0 | 0 | 0 | -1362.6762 | 0 | -1871.9468
2019-02-11 | 1028.2172 | 0 | 0 | 0 | -1028.2172 | 0 | -2900.164
2019-02-11 01:00 | 894.3859 | 0 | 0 | 0 | -894.3859 | 0 | -3794.5499
2019-02-11 02:00 | 837.5045 | 0 | 0 | 0 | -837.5045 | 0 | -4632.0543
2019-02-11 03:00 | 827.1001 | 0 | 873.3333 | 0 | 46.2333 | 46.2333 | -4585.8211
2019-02-11 04:00 | 829.1063 | 0 | 286.6667 | 46.2333 | -542.4397 | -46.2333 | -5082.0275
2019-02-11 05:00 | 900.3992 | 0 | 873.3333 | 0 | -27.0658 | 0 | -5109.0933
2019-02-11 06:00 | 1141.4599 | 0 | 873.3333 | 0 | -268.1266 | 0 | -5377.2199
2019-02-11 07:00 | 1446.6522 | 1536.4368 | 0 | 0 | 89.7846 | 89.7846 | -5287.4353
2019-02-11 08:00 | 1380.611 | 4213.3723 | 0 | 89.7846 | 2832.7613 | 2832.7613 | -2364.8894
2019-02-11 09:00 | 1189.0488 | 6338.1364 | 0 | 2922.5459 | 5149.0876 | 5149.0876 | 0
2019-02-11 10:00 | 1194.7559 | 7713.3306 | 873.3333 | 8071.6335 | 7391.908 | 1928.3665 | 0
2019-02-11 11:00 | 1183.9867 | 8369.984 | 873.3333 | 10000 | 8059.3307 | 0 | 0
2019-02-11 12:00 | 1129.815 | 8333.3312 | 1666.6667 | 10000 | 8870.1829 | 0 | 0
2019-02-11 13:00 | 1081.7201 | 7638.6507 | 1666.6667 | 10000 | 8223.5973 | 0 | 0
2019-02-11 14:00 | 1074.3941 | 6185.1508 | 1666.6667 | 10000 | 6777.4234 | 0 | 0
2019-02-11 15:00 | 1135.8461 | 4056.5169 | 873.3333 | 10000 | 3794.0042 | 0 | 0
2019-02-11 16:00 | 1366.1768 | 1457.6917 | 873.3333 | 10000 | 964.8483 | 0 | 0
2019-02-11 17:00 | 1851.9696 | 0 | 286.6667 | 10000 | -1565.303 | -1565.303 | 0
2019-02-11 18:00 | 2207.5523 | 0 | 873.3333 | 8434.697 | -1334.2189 | -1334.2189 | 0
2019-02-11 19:00 | 2328.6182 | 0 | 873.3333 | 7100.4781 | -1455.2848 | -1455.2848 | 0
2019-02-11 20:00 | 2240.9199 | 0 | 873.3333 | 5645.1933 | -1367.5865 | -1367.5865 | 0
2019-02-11 21:00 | 2041.8803 | 0 | 873.3333 | 4277.6067 | -1168.547 | -1168.547 | 0
2019-02-11 22:00 | 1676.3132 | 0 | 1666.6667 | 3109.0597 | -9.6465 | -9.6465 | 0
2019-02-11 23:00 | 1318.9587 | 0 | 873.3333 | 3099.4132 | -445.6254 | -445.6254 | 0
2019-02-12 | 964.5416 | 0 | 286.6667 | 2653.7879 | -677.8749 | -677.8749 | 0
2019-02-12 01:00 | 836.4689 | 0 | 873.3333 | 1975.9129 | 36.8645 | 36.8645 | 0
2019-02-12 02:00 | 783.9719 | 0 | 1666.6667 | 2012.7774 | 882.6947 | 882.6947 | 0
2019-02-12 03:00 | 774.1326 | 0 | 1666.6667 | 2895.4721 | 892.534 | 892.534 | 0
2019-02-12 04:00 | 775.1458 | 0 | 873.3333 | 3788.0062 | 98.1875 | 98.1875 | 0
2019-02-12 05:00 | 843.0295 | 0 | 873.3333 | 3886.1936 | 30.3038 | 30.3038 | 0
2019-02-12 06:00 | 1074.9257 | 0 | 873.3333 | 3916.4975 | -201.5923 | -201.5923 | 0
2019-02-12 07:00 | 1383.4114 | 1729.5839 | 1666.6667 | 3714.9051 | 2012.8392 | 2012.8392 | 0
2019-02-12 08:00 | 1321.8876 | 4375.7949 | 873.3333 | 5727.7443 | 3927.2406 | 3927.2406 | 0
2019-02-12 09:00 | 1159.1162 | 6419.1344 | 0 | 9654.9848 | 5260.0182 | 345.0152 | 0
2019-02-12 10:00 | 1176.0516 | 7745.4328 | 2773.3333 | 10000 | 9342.7146 | 0 | 0
2019-02-12 11:00 | 1138.0798 | 8313.1246 | 9573.3333 | 10000 | 16748.3782 | 0 | 0
2019-02-12 12:00 | 1094.492 | 8267.4109 | 9060 | 10000 | 16232.9189 | 0 | 0
2019-02-12 13:00 | 1060.2426 | 6410.6428 | 9573.3333 | 10000 | 14923.7335 | 0 | 0
2019-02-12 14:00 | 1067.7617 | 4886.4247 | 9573.3333 | 10000 | 13391.9964 | 0 | 0
2019-02-12 15:00 | 1129.821 | 2876.7319 | 6160 | 10000 | 7906.9109 | 0 | 0
2019-02-12 16:00 | 1358.2761 | 807.7082 | 4266.6667 | 10000 | 3716.0988 | 0 | 0
2019-02-12 17:00 | 1838.8149 | 0 | 4266.6667 | 10000 | 2427.8518 | 0 | 0
2019-02-12 18:00 | 2198.542 | 0 | 4266.6667 | 10000 | 2068.1247 | 0 | 0
2019-02-12 19:00 | 2326.7486 | 0 | 2773.3333 | 10000 | 446.5848 | 0 | 0
2019-02-12 20:00 | 2244.2241 | 0 | 6160 | 10000 | 3915.7759 | 0 | 0
2019-02-12 21:00 | 2053.2475 | 0 | 6160 | 10000 | 4106.7525 | 0 | 0
2019-02-12 22:00 | 1691.6667 | 0 | 4266.6667 | 10000 | 2574.9999 | 0 | 0
2019-02-12 23:00 | 1348.164 | 0 | 873.3333 | 10000 | -474.8306 | -474.8306 | 0
2019-02-13 | 985.7325 | 0 | 286.6667 | 9525.1694 | -699.0658 | -699.0658 | 0
2019-02-13 01:00 | 854.1892 | 0 | 2773.3333 | 8826.1035 | 1919.1441 | 1173.8965 | 0
2019-02-13 02:00 | 803.6126 | 0 | 6160 | 10000 | 5356.3874 | 0 | 0
2019-02-13 03:00 | 794.673 | 0 | 6160 | 10000 | 5365.327 | 0 | 0
2019-02-13 04:00 | 796.9295 | 0 | 7873.3333 | 10000 | 7076.4038 | 0 | 0
2019-02-13 05:00 | 863.8534 | 0 | 4266.6667 | 10000 | 3402.8132 | 0 | 0
2019-02-13 06:00 | 1073.8728 | 0 | 6160 | 10000 | 5086.1272 | 0 | 0
2019-02-13 07:00 | 1404.1233 | 192.7193 | 7873.3333 | 10000 | 6661.9293 | 0 | 0
2019-02-13 08:00 | 1312.9262 | 385.6973 | 4266.6667 | 10000 | 3339.4378 | 0 | 0
2019-02-13 09:00 | 1144.4439 | 937.8215 | 4266.6667 | 10000 | 4060.0443 | 0 | 0
2019-02-13 10:00 | 1160.1108 | 898.2201 | 9060 | 10000 | 8798.1093 | 0 | 0
2019-02-13 11:00 | 1145.244 | 970.6241 | 9873.3333 | 10000 | 9698.7135 | 0 | 0
2019-02-13 12:00 | 1120.3832 | 917.7839 | 9960 | 10000 | 9757.4008 | 0 | 0
2019-02-13 13:00 | 1089.15 | 743.3795 | 9960 | 10000 | 9614.2295 | 0 | 0
2019-02-13 14:00 | 1083.574 | 733.3734 | 9873.3333 | 10000 | 9523.1327 | 0 | 0
2019-02-13 15:00 | 1140.5004 | 230.3737 | 9573.3333 | 10000 | 8663.2067 | 0 | 0
2019-02-13 16:00 | 1368.6876 | 34.37 | 9573.3333 | 10000 | 8239.0158 | 0 | 0
2019-02-13 17:00 | 1847.0118 | 0 | 9060 | 10000 | 7212.9882 | 0 | 0
2019-02-13 18:00 | 2191.7617 | 0 | 9060 | 10000 | 6868.2383 | 0 | 0
2019-02-13 19:00 | 2311.2348 | 0 | 9060 | 10000 | 6748.7652 | 0 | 0
2019-02-13 20:00 | 2221.7468 | 0 | 9060 | 10000 | 6838.2532 | 0 | 0
2019-02-13 21:00 | 2021.9593 | 0 | 7873.3333 | 10000 | 5851.374 | 0 | 0
2019-02-13 22:00 | 1663.3131 | 0 | 6160 | 10000 | 4496.6869 | 0 | 0
2019-02-13 23:00 | 1328.4263 | 0 | 6160 | 10000 | 4831.5737 | 0 | 0
2019-02-14 | 984.7724 | 0 | 4266.6667 | 10000 | 3281.8943 | 0 | 0
2019-02-14 01:00 | 854.2666 | 0 | 2773.3333 | 10000 | 1919.0667 | 0 | 0
2019-02-14 02:00 | 803.5312 | 0 | 2773.3333 | 10000 | 1969.8022 | 0 | 0
2019-02-14 03:00 | 794.9667 | 0 | 2773.3333 | 10000 | 1978.3667 | 0 | 0
2019-02-14 04:00 | 799.0806 | 0 | 4266.6667 | 10000 | 3467.5861 | 0 | 0
2019-02-14 05:00 | 868.7637 | 0 | 2773.3333 | 10000 | 1904.5696 | 0 | 0
2019-02-14 06:00 | 1080.4264 | 0 | 2773.3333 | 10000 | 1692.9069 | 0 | 0
2019-02-14 07:00 | 1391.404 | 506.8728 | 1666.6667 | 10000 | 782.1355 | 0 | 0
2019-02-14 08:00 | 1298.599 | 1516.4912 | 873.3333 | 10000 | 1091.2256 | 0 | 0
2019-02-14 09:00 | 1103.4694 | 3626.5422 | 873.3333 | 10000 | 3396.4062 | 0 | 0
2019-02-14 10:00 | 1109.8291 | 4074.7283 | 873.3333 | 10000 | 3838.2325 | 0 | 0
2019-02-14 11:00 | 1104.335 | 5097.0116 | 0 | 10000 | 3992.6766 | 0 | 0
2019-02-14 12:00 | 1053.8017 | 6011.5192 | 0 | 10000 | 4957.7175 | 0 | 0
2019-02-14 13:00 | 1011.5796 | 3544.2931 | 0 | 10000 | 2532.7135 | 0 | 0
2019-02-14 14:00 | 1013.771 | 4133.0597 | 0 | 10000 | 3119.2888 | 0 | 0
2019-02-14 15:00 | 1082.4806 | 3917.4807 | 286.6667 | 10000 | 3121.6668 | 0 | 0
2019-02-14 16:00 | 1316.668 | 1395.6791 | 873.3333 | 10000 | 952.3444 | 0 | 0
2019-02-14 17:00 | 1795.0562 | 0 | 873.3333 | 10000 | -921.7229 | -921.7229 | 0
2019-02-14 18:00 | 2156.2907 | 0 | 286.6667 | 9078.2771 | -1869.624 | -1869.624 | 0
2019-02-14 19:00 | 2292.6892 | 0 | 286.6667 | 7208.6531 | -2006.0225 | -2006.0225 | 0
2019-02-14 20:00 | 2212.7911 | 0 | 873.3333 | 5202.6305 | -1339.4578 | -1339.4578 | 0
2019-02-14 21:00 | 2019.0114 | 0 | 1666.6667 | 3863.1728 | -352.3447 | -352.3447 | 0
2019-02-14 22:00 | 1667.3974 | 0 | 873.3333 | 3510.8281 | -794.064 | -794.064 | 0
2019-02-14 23:00 | 1337.7263 | 0 | 0 | 2716.764 | -1337.7263 | -1337.7263 | 0
2019-02-15 | 992.1156 | 0 | 286.6667 | 1379.0378 | -705.449 | -705.449 | 0
2019-02-15 01:00 | 861.6387 | 0 | 286.6667 | 673.5888 | -574.9721 | -574.9721 | 0
2019-02-15 02:00 | 807.6888 | 0 | 1666.6667 | 98.6167 | 858.9779 | 858.9779 | 0
2019-02-15 03:00 | 797.4795 | 0 | 873.3333 | 957.5946 | 75.8538 | 75.8538 | 0
2019-02-15 04:00 | 798.0958 | 0 | 873.3333 | 1033.4484 | 75.2375 | 75.2375 | 0
2019-02-15 05:00 | 864.841 | 0 | 286.6667 | 1108.6859 | -578.1743 | -578.1743 | 0
2019-02-15 06:00 | 1076.143 | 0 | 0 | 530.5116 | -1076.143 | -530.5116 | -545.6314
2019-02-15 07:00 | 1404.5294 | 205.3394 | 0 | 0 | -1199.19 | 0 | -1744.8214
2019-02-15 08:00 | 1315.9888 | 778.4902 | 0 | 0 | -537.4986 | 0 | -2282.32
2019-02-15 09:00 | 1145.0434 | 4129.8075 | 0 | 0 | 2984.7642 | 2984.7642 | 0
2019-02-15 10:00 | 1175.3167 | 4498.0858 | 0 | 2984.7642 | 3322.7691 | 3322.7691 | 0
2019-02-15 11:00 | 1152.9893 | 4168.5487 | 0 | 6307.5333 | 3015.5595 | 3015.5595 | 0
2019-02-15 12:00 | 1123.0198 | 1814.4217 | 0 | 9323.0928 | 691.4019 | 676.9072 | 0
2019-02-15 13:00 | 1093.4553 | 1910.5939 | 0 | 10000 | 817.1386 | 0 | 0
2019-02-15 14:00 | 1099.9492 | 1084.6317 | 286.6667 | 10000 | 271.3491 | 0 | 0
2019-02-15 15:00 | 1161.2567 | 436.042 | 0 | 10000 | -725.2146 | -725.2146 | 0
2019-02-15 16:00 | 1389.6616 | 106.9672 | 0 | 9274.7854 | -1282.6944 | -1282.6944 | 0
2019-02-15 17:00 | 1877.075 | 0 | 286.6667 | 7992.091 | -1590.4083 | -1590.4083 | 0
2019-02-15 18:00 | 2237.1616 | 0 | 0 | 6401.6827 | -2237.1616 | -2237.1616 | 0
2019-02-15 19:00 | 2360.0773 | 0 | 0 | 4164.5211 | -2360.0773 | -2360.0773 | 0
2019-02-15 20:00 | 2279.3492 | 0 | 873.3333 | 1804.4438 | -1406.0159 | -1406.0159 | 0
2019-02-15 21:00 | 2080.6297 | 0 | 2773.3333 | 398.4279 | 692.7036 | 692.7036 | 0
2019-02-15 22:00 | 1738.9273 | 0 | 1666.6667 | 1091.1316 | -72.2607 | -72.2607 | 0
2019-02-15 23:00 | 1407.4522 | 0 | 4266.6667 | 1018.8709 | 2859.2145 | 2859.2145 | 0
2019-02-16 | 1068.1351 | 0 | 4266.6667 | 3878.0854 | 3198.5316 | 3198.5316 | 0
2019-02-16 01:00 | 940.5236 | 0 | 6160 | 7076.6169 | 5219.4764 | 2923.3831 | 0
2019-02-16 02:00 | 892.7496 | 0 | 2773.3333 | 10000 | 1880.5838 | 0 | 0
2019-02-16 03:00 | 888.0249 | 0 | 4266.6667 | 10000 | 3378.6418 | 0 | 0
2019-02-16 04:00 | 885.8277 | 0 | 2773.3333 | 10000 | 1887.5056 | 0 | 0
2019-02-16 05:00 | 956.5563 | 0 | 2773.3333 | 10000 | 1816.777 | 0 | 0
2019-02-16 06:00 | 1188.3196 | 0 | 2773.3333 | 10000 | 1585.0137 | 0 | 0
2019-02-16 07:00 | 1478.3373 | 1836.4108 | 2773.3333 | 10000 | 3131.4069 | 0 | 0
2019-02-16 08:00 | 1379.3351 | 4529.2083 | 2773.3333 | 10000 | 5923.2066 | 0 | 0
2019-02-16 09:00 | 1182.8217 | 6675.6419 | 2773.3333 | 10000 | 8266.1535 | 0 | 0
2019-02-16 10:00 | 1204.4851 | 5799.5109 | 4266.6667 | 10000 | 8861.6925 | 0 | 0
2019-02-16 11:00 | 1163.4882 | 6467.5528 | 4266.6667 | 10000 | 9570.7313 | 0 | 0
2019-02-16 12:00 | 1123.7152 | 8603.7721 | 4266.6667 | 10000 | 11746.7236 | 0 | 0
2019-02-16 13:00 | 1087.3898 | 6427.0809 | 4266.6667 | 10000 | 9606.3577 | 0 | 0
2019-02-16 14:00 | 1085.0627 | 4707.6043 | 6160 | 10000 | 9782.5417 | 0 | 0
2019-02-16 15:00 | 1159.6008 | 4110.8417 | 7873.3333 | 10000 | 10824.5743 | 0 | 0
2019-02-16 16:00 | 1396.5276 | 1609.3548 | 6160 | 10000 | 6372.8272 | 0 | 0
2019-02-16 17:00 | 1895.809 | 0 | 7873.3333 | 10000 | 5977.5243 | 0 | 0
2019-02-16 18:00 | 2248.9788 | 0 | 9060 | 10000 | 6811.0212 | 0 | 0
2019-02-16 19:00 | 2386.2017 | 0 | 9060 | 10000 | 6673.7983 | 0 | 0
2019-02-16 20:00 | 2309.0029 | 0 | 7873.3333 | 10000 | 5564.3305 | 0 | 0
2019-02-16 21:00 | 2119.8312 | 0 | 6160 | 10000 | 4040.1688 | 0 | 0
2019-02-16 22:00 | 1773.5053 | 0 | 4266.6667 | 10000 | 2493.1614 | 0 | 0
2019-02-16 23:00 | 1445.8384 | 0 | 2773.3333 | 10000 | 1327.4949 | 0 | 0
2019-02-17 | 1105.0146 | 0 | 4266.6667 | 10000 | 3161.6521 | 0 | 0
2019-02-17 01:00 | 987.5338 | 0 | 2773.3333 | 10000 | 1785.7995 | 0 | 0
2019-02-17 02:00 | 948.1033 | 0 | 2773.3333 | 10000 | 1825.23 | 0 | 0
2019-02-17 03:00 | 947.2589 | 0 | 4266.6667 | 10000 | 3319.4077 | 0 | 0
2019-02-17 04:00 | 949.2302 | 0 | 4266.6667 | 10000 | 3317.4364 | 0 | 0
2019-02-17 05:00 | 1023.6148 | 0 | 1666.6667 | 10000 | 643.0519 | 0 | 0
2019-02-17 06:00 | 1261.4749 | 0 | 873.3333 | 10000 | -388.1416 | -388.1416 | 0
2019-02-17 07:00 | 1547.8297 | 1985.1472 | 1666.6667 | 9611.8584 | 2103.9842 | 388.1416 | 0
2019-02-17 08:00 | 1446.2703 | 4765.9473 | 6160 | 10000 | 9479.677 | 0 | 0
2019-02-17 09:00 | 1251.1595 | 6929.1686 | 2773.3333 | 10000 | 8451.3425 | 0 | 0
2019-02-17 10:00 | 1265.4673 | 8272.8711 | 4266.6667 | 10000 | 11274.0705 | 0 | 0
2019-02-17 11:00 | 1217.3209 | 8848.2242 | 7873.3333 | 10000 | 15504.2367 | 0 | 0
2019-02-17 12:00 | 1172.0512 | 8761.5901 | 4266.6667 | 10000 | 11856.2055 | 0 | 0
2019-02-17 13:00 | 1129.2908 | 8071.306 | 2773.3333 | 10000 | 9715.3486 | 0 | 0
2019-02-17 14:00 | 1124.0574 | 6620.4614 | 1666.6667 | 10000 | 7163.0707 | 0 | 0
2019-02-17 15:00 | 1194.087 | 4462.5531 | 6160 | 10000 | 9428.4661 | 0 | 0
2019-02-17 16:00 | 1428.9417 | 1790.5304 | 4266.6667 | 10000 | 4628.2554 | 0 | 0
2019-02-17 17:00 | 1927.3274 | 0 | 4266.6667 | 10000 | 2339.3393 | 0 | 0
2019-02-17 18:00 | 2275.1252 | 0 | 4266.6667 | 10000 | 1991.5414 | 0 | 0
2019-02-17 19:00 | 2403.009 | 0 | 2773.3333 | 10000 | 370.3243 | 0 | 0
2019-02-17 20:00 | 2318.1552 | 0 | 2773.3333 | 10000 | 455.1781 | 0 | 0
2019-02-17 21:00 | 2125.723 | 0 | 873.3333 | 10000 | -1252.3897 | -1252.3897 | 0
2019-02-17 22:00 | 1777.2 | 0 | 873.3333 | 8747.6103 | -903.8667 | -903.8667 | 0
2019-02-17 23:00 | 1448.9987 | 0 | 2773.3333 | 7843.7436 | 1324.3347 | 1324.3347 | 0
2019-02-18 | 1113.17 | 0 | 873.3333 | 9168.0783 | -239.8367 | -239.8367 | 0
2019-02-18 01:00 | 982.9078 | 0 | 873.3333 | 8928.2416 | -109.5745 | -109.5745 | 0
2019-02-18 02:00 | 927.4296 | 0 | 1666.6667 | 8818.6671 | 739.237 | 739.237 | 0
2019-02-18 03:00 | 917.657 | 0 | 286.6667 | 9557.9042 | -630.9903 | -630.9903 | 0
2019-02-18 04:00 | 917.5026 | 0 | 286.6667 | 8926.9138 | -630.8359 | -630.8359 | 0
2019-02-18 05:00 | 985.7114 | 0 | 873.3333 | 8296.0779 | -112.3781 | -112.3781 | 0
2019-02-18 06:00 | 1202.2062 | 0 | 286.6667 | 8183.6998 | -915.5395 | -915.5395 | 0
2019-02-18 07:00 | 1513.1335 | 47.6043 | 873.3333 | 7268.1603 | -592.1959 | -592.1959 | 0
2019-02-18 08:00 | 1425.9594 | 813.947 | 286.6667 | 6675.9644 | -325.3457 | -325.3457 | 0
2019-02-18 09:00 | 1236.7546 | 701.784 | 873.3333 | 6350.6187 | 338.3628 | 338.3628 | 0
2019-02-18 10:00 | 1240.6269 | 2648.6685 | 2773.3333 | 6688.9815 | 4181.3749 | 3311.0185 | 0
2019-02-18 11:00 | 1204.0601 | 1880.6559 | 6160 | 10000 | 6836.5958 | 0 | 0
2019-02-18 12:00 | 1154.816 | 2476.4158 | 7873.3333 | 10000 | 9194.9331 | 0 | 0
2019-02-18 13:00 | 1109.802 | 1542.6514 | 7873.3333 | 10000 | 8306.1827 | 0 | 0
2019-02-18 14:00 | 1101.4454 | 650.1019 | 9060 | 10000 | 8608.6565 | 0 | 0
2019-02-18 15:00 | 1165.0715 | 656.7639 | 4266.6667 | 10000 | 3758.359 | 0 | 0
2019-02-18 16:00 | 1418.2608 | 3.7237 | 2773.3333 | 10000 | 1358.7962 | 0 | 0
2019-02-18 17:00 | 1917.5699 | 0 | 4266.6667 | 10000 | 2349.0967 | 0 | 0
2019-02-18 18:00 | 2264.6169 | 0 | 6160 | 10000 | 3895.3831 | 0 | 0
2019-02-18 19:00 | 2394.622 | 0 | 6160 | 10000 | 3765.378 | 0 | 0
2019-02-18 20:00 | 2315.9424 | 0 | 2773.3333 | 10000 | 457.391 | 0 | 0
2019-02-18 21:00 | 2120.6632 | 0 | 6160 | 10000 | 4039.3368 | 0 | 0
2019-02-18 22:00 | 1766.443 | 0 | 4266.6667 | 10000 | 2500.2237 | 0 | 0
2019-02-18 23:00 | 1423.2324 | 0 | 4266.6667 | 10000 | 2843.4343 | 0 | 0
2019-02-19 | 1067.8058 | 0 | 2773.3333 | 10000 | 1705.5275 | 0 | 0
2019-02-19 01:00 | 935.3464 | 0 | 1666.6667 | 10000 | 731.3202 | 0 | 0
2019-02-19 02:00 | 884.861 | 0 | 2773.3333 | 10000 | 1888.4723 | 0 | 0
2019-02-19 03:00 | 874.3151 | 0 | 873.3333 | 10000 | -0.98174 | -0.98174 | 0
2019-02-19 04:00 | 870.0568 | 0 | 286.6667 | 9999.0183 | -583.3901 | -583.3901 | 0
2019-02-19 05:00 | 936.4786 | 0 | 873.3333 | 9415.6282 | -63.1453 | -63.1453 | 0
2019-02-19 06:00 | 1167.0637 | 0 | 1666.6667 | 9352.4829 | 499.603 | 499.603 | 0
2019-02-19 07:00 | 1469.6576 | 1655.3353 | 873.3333 | 9852.0858 | 1059.0111 | 147.9142 | 0
2019-02-19 08:00 | 1396.4509 | 4120.9974 | 1666.6667 | 10000 | 4391.2132 | 0 | 0
2019-02-19 09:00 | 1234.555 | 3989.2407 | 1666.6667 | 10000 | 4421.3524 | 0 | 0
2019-02-19 10:00 | 1252.2254 | 4712.9484 | 873.3333 | 10000 | 4334.0563 | 0 | 0
2019-02-19 11:00 | 1227.8876 | 3501.9834 | 2773.3333 | 10000 | 5047.4291 | 0 | 0
2019-02-19 12:00 | 1192.5418 | 3450.023 | 9060 | 10000 | 11317.4812 | 0 | 0
2019-02-19 13:00 | 1151.023 | 1589.9888 | 6160 | 10000 | 6598.9658 | 0 | 0
2019-02-19 14:00 | 1145.6231 | 636.3525 | 6160 | 10000 | 5650.7294 | 0 | 0
2019-02-19 15:00 | 1204.4618 | 819.5291 | 2773.3333 | 10000 | 2388.4006 | 0 | 0
2019-02-19 16:00 | 1424.9824 | 516.0464 | 1666.6667 | 10000 | 757.7307 | 0 | 0
2019-02-19 17:00 | 1900.0891 | 0 | 286.6667 | 10000 | -1613.4225 | -1613.4225 | 0
2019-02-19 18:00 | 2243.7938 | 0 | 0 | 8386.5775 | -2243.7938 | -2243.7938 | 0
2019-02-19 19:00 | 2369.7194 | 0 | 0 | 6142.7838 | -2369.7194 | -2369.7194 | 0
2019-02-19 20:00 | 2285.8245 | 0 | 286.6667 | 3773.0643 | -1999.1578 | -1999.1578 | 0
2019-02-19 21:00 | 2094.5076 | 0 | 873.3333 | 1773.9065 | -1221.1743 | -1221.1743 | 0
2019-02-19 22:00 | 1730.1678 | 0 | 873.3333 | 552.7322 | -856.8345 | -552.7322 | -304.1023
2019-02-19 23:00 | 1382.5971 | 0 | 286.6667 | 0 | -1095.9304 | 0 | -1400.0327
2019-02-20 | 1020.1327 | 0 | 286.6667 | 0 | -733.4661 | 0 | -2133.4987
2019-02-20 01:00 | 901.3676 | 0 | 873.3333 | 0 | -28.0342 | 0 | -2161.533
2019-02-20 02:00 | 843.2639 | 0 | 873.3333 | 0 | 30.0694 | 30.0694 | -2131.4636
2019-02-20 03:00 | 835.1149 | 0 | 1666.6667 | 30.0694 | 831.5517 | 831.5517 | -1269.8424
2019-02-20 04:00 | 834.6369 | 0 | 873.3333 | 861.6212 | 38.6964 | 38.6964 | -369.5248
2019-02-20 05:00 | 903.1749 | 0 | 1666.6667 | 900.3176 | 763.4917 | 763.4917 | 0
2019-02-20 06:00 | 1113.5258 | 0 | 1666.6667 | 1663.8093 | 553.1409 | 553.1409 | 0
2019-02-20 07:00 | 1422.3596 | 1898.2084 | 1666.6667 | 2216.9502 | 2142.5155 | 2142.5155 | 0
2019-02-20 08:00 | 1341.8636 | 4380.2488 | 4266.6667 | 4359.4657 | 7305.0519 | 5640.5343 | 0
2019-02-20 09:00 | 1169.7194 | 6300.6085 | 1666.6667 | 10000 | 6797.5558 | 0 | 0
2019-02-20 10:00 | 1182.6419 | 7505.8499 | 873.3333 | 10000 | 7196.5414 | 0 | 0
2019-02-20 11:00 | 1173.7149 | 8078.1761 | 873.3333 | 10000 | 7777.7945 | 0 | 0
2019-02-20 12:00 | 1148.4179 | 8064.0357 | 2773.3333 | 10000 | 9688.9511 | 0 | 0
2019-02-20 13:00 | 1119.8665 | 5798.2862 | 2773.3333 | 10000 | 7451.753 | 0 | 0
2019-02-20 14:00 | 1122.893 | 4973.0715 | 2773.3333 | 10000 | 6623.5118 | 0 | 0
2019-02-20 15:00 | 1184.4491 | 1216.079 | 4266.6667 | 10000 | 4298.2965 | 0 | 0
2019-02-20 16:00 | 1402.5478 | 177.9659 | 2773.3333 | 10000 | 1548.7515 | 0 | 0
2019-02-20 17:00 | 1883.9797 | 0 | 873.3333 | 10000 | -1010.6464 | -1010.6464 | 0
2019-02-20 18:00 | 2242.8959 | 0 | 1666.6667 | 8989.3536 | -576.2293 | -576.2293 | 0
2019-02-20 19:00 | 2356.2264 | 0 | 873.3333 | 8413.1243 | -1482.893 | -1482.893 | 0
2019-02-20 20:00 | 2267.328 | 0 | 873.3333 | 6930.2313 | -1393.9947 | -1393.9947 | 0
2019-02-20 21:00 | 2067.7832 | 0 | 873.3333 | 5536.2366 | -1194.4498 | -1194.4498 | 0
2019-02-20 22:00 | 1712.28 | 0 | 873.3333 | 4341.7868 | -838.9467 | -838.9467 | 0
2019-02-20 23:00 | 1376.8812 | 0 | 286.6667 | 3502.8401 | -1090.2146 | -1090.2146 | 0
2019-02-21 | 1027.7779 | 0 | 286.6667 | 2412.6256 | -741.1112 | -741.1112 | 0
2019-02-21 01:00 | 895.2698 | 0 | 286.6667 | 1671.5143 | -608.6031 | -608.6031 | 0
2019-02-21 02:00 | 843.7302 | 0 | 286.6667 | 1062.9112 | -557.0635 | -557.0635 | 0
2019-02-21 03:00 | 833.4174 | 0 | 286.6667 | 505.8477 | -546.7507 | -505.8477 | -40.903
2019-02-21 04:00 | 829.3902 | 0 | 286.6667 | 0 | -542.7235 | 0 | -583.6265
2019-02-21 05:00 | 895.0808 | 0 | 286.6667 | 0 | -608.4142 | 0 | -1192.0407
2019-02-21 06:00 | 1105.2494 | 0 | 286.6667 | 0 | -818.5827 | 0 | -2010.6234
2019-02-21 07:00 | 1433.514 | 0 | 286.6667 | 0 | -1146.8473 | 0 | -3157.4707
2019-02-21 08:00 | 1326.4802 | 137.3997 | 0 | 0 | -1189.0805 | 0 | -4346.5512
2019-02-21 09:00 | 1138.6682 | 1176.2603 | 286.6667 | 0 | 324.2587 | 324.2587 | -4022.2925
2019-02-21 10:00 | 1150.5138 | 736.9039 | 286.6667 | 324.2587 | -126.9432 | -126.9432 | -3824.977
2019-02-21 11:00 | 1126.7433 | 443.9058 | 0 | 197.3155 | -682.8376 | -197.3155 | -4310.4991
2019-02-21 12:00 | 1098.619 | 1343.7301 | 873.3333 | 0 | 1118.4445 | 1118.4445 | -3192.0547
2019-02-21 13:00 | 1075.535 | 1256.4428 | 1666.6667 | 1118.4445 | 1847.5745 | 1847.5745 | -226.0357
2019-02-21 14:00 | 1079.8653 | 1470.735 | 2773.3333 | 2966.019 | 3164.2031 | 3164.2031 | 0
2019-02-21 15:00 | 1148.3755 | 518.1889 | 2773.3333 | 6130.222 | 2143.1467 | 2143.1467 | 0
2019-02-21 16:00 | 1397.6754 | 84.379 | 1666.6667 | 8273.3687 | 353.3702 | 353.3702 | 0
2019-02-21 17:00 | 1875.9175 | 0 | 873.3333 | 8626.7389 | -1002.5841 | -1002.5841 | 0
2019-02-21 18:00 | 2245.107 | 0 | 873.3333 | 7624.1548 | -1371.7736 | -1371.7736 | 0
2019-02-21 19:00 | 2366.2726 | 0 | 873.3333 | 6252.3811 | -1492.9393 | -1492.9393 | 0
2019-02-21 20:00 | 2302.764 | 0 | 873.3333 | 4759.4418 | -1429.4307 | -1429.4307 | 0
2019-02-21 21:00 | 2121.3239 | 0 | 873.3333 | 3330.0112 | -1247.9905 | -1247.9905 | 0
2019-02-21 22:00 | 1772.3662 | 0 | 1666.6667 | 2082.0207 | -105.6995 | -105.6995 | 0
2019-02-21 23:00 | 1431.311 | 0 | 873.3333 | 1976.3211 | -557.9777 | -557.9777 | 0
2019-02-22 | 1082.339 | 0 | 1666.6667 | 1418.3434 | 584.3276 | 584.3276 | 0
2019-02-22 01:00 | 964.2137 | 0 | 873.3333 | 2002.671 | -90.8804 | -90.8804 | 0
2019-02-22 02:00 | 907.1309 | 0 | 1666.6667 | 1911.7907 | 759.5358 | 759.5358 | 0
2019-02-22 03:00 | 904.0244 | 0 | 2773.3333 | 2671.3265 | 1869.3089 | 1869.3089 | 0
2019-02-22 04:00 | 899.5784 | 0 | 1666.6667 | 4540.6354 | 767.0883 | 767.0883 | 0
2019-02-22 05:00 | 972.2513 | 0 | 873.3333 | 5307.7237 | -98.9179 | -98.9179 | 0
2019-02-22 06:00 | 1208.3748 | 0 | 873.3333 | 5208.8057 | -335.0415 | -335.0415 | 0
2019-02-22 07:00 | 1495.0602 | 580.4694 | 873.3333 | 4873.7643 | -41.2574 | -41.2574 | 0
2019-02-22 08:00 | 1391.5535 | 4397.6149 | 286.6667 | 4832.5068 | 3292.7281 | 3292.7281 | 0
2019-02-22 09:00 | 1214.416 | 6235.507 | 0 | 8125.2349 | 5021.091 | 1874.7651 | 0
2019-02-22 10:00 | 1219.7067 | 7514.8532 | 286.6667 | 10000 | 6581.8132 | 0 | 0
2019-02-22 11:00 | 1193.7871 | 8050.422 | 0 | 10000 | 6856.6349 | 0 | 0
2019-02-22 12:00 | 1160.3678 | 8164.1835 | 0 | 10000 | 7003.8157 | 0 | 0
2019-02-22 13:00 | 1128.6125 | 7607.5548 | 0 | 10000 | 6478.9422 | 0 | 0
2019-02-22 14:00 | 1120.132 | 6239.8954 | 1666.6667 | 10000 | 6786.4301 | 0 | 0
2019-02-22 15:00 | 1166.4567 | 4182.9341 | 286.6667 | 10000 | 3303.144 | 0 | 0
2019-02-22 16:00 | 1386.1751 | 1722.7092 | 0 | 10000 | 336.5341 | 0 | 0
2019-02-22 17:00 | 1868.6449 | 0 | 286.6667 | 10000 | -1581.9782 | -1581.9782 | 0
2019-02-22 18:00 | 2220.9807 | 0 | 286.6667 | 8418.0218 | -1934.314 | -1934.314 | 0
2019-02-22 19:00 | 2341.5662 | 0 | 0 | 6483.7078 | -2341.5662 | -2341.5662 | 0
2019-02-22 20:00 | 2251.279 | 0 | 0 | 4142.1415 | -2251.279 | -2251.279 | 0
2019-02-22 21:00 | 2053.7532 | 0 | 0 | 1890.8625 | -2053.7532 | -1890.8625 | -162.8907
2019-02-22 22:00 | 1706.0125 | 0 | 0 | 0 | -1706.0125 | 0 | -1868.9032
2019-02-22 23:00 | 1367.9103 | 0 | 286.6667 | 0 | -1081.2436 | 0 | -2950.1468
2019-02-23 | 1017.0657 | 0 | 0 | 0 | -1017.0657 | 0 | -3967.2125
2019-02-23 01:00 | 882.5261 | 0 | 0 | 0 | -882.5261 | 0 | -4849.7385
2019-02-23 02:00 | 827.3953 | 0 | 873.3333 | 0 | 45.938 | 45.938 | -4803.8005
2019-02-23 03:00 | 815.7154 | 0 | 0 | 45.938 | -815.7154 | -45.938 | -5573.5779
2019-02-23 04:00 | 813.5452 | 0 | 0 | 0 | -813.5452 | 0 | -6387.1231
2019-02-23 05:00 | 883.5141 | 0 | 873.3333 | 0 | -10.1808 | 0 | -6397.3039
2019-02-23 06:00 | 1096.1741 | 0 | 0 | 0 | -1096.1741 | 0 | -7493.478
2019-02-23 07:00 | 1406.4393 | 356.6196 | 0 | 0 | -1049.8197 | 0 | -8543.2977
2019-02-23 08:00 | 1319.7867 | 3267.0396 | 286.6667 | 0 | 2233.9195 | 2233.9195 | -6309.3782
2019-02-23 09:00 | 1128.7277 | 4879.9778 | 286.6667 | 2233.9195 | 4037.9168 | 4037.9168 | -37.5419
2019-02-23 10:00 | 1138.4534 | 6243.7536 | 873.3333 | 6271.8363 | 5978.6336 | 3728.1637 | 0
2019-02-23 11:00 | 1115.8111 | 6188.9239 | 1666.6667 | 10000 | 6739.7795 | 0 | 0
2019-02-23 12:00 | 1092.7292 | 4780.9283 | 4266.6667 | 10000 | 7954.8659 | 0 | 0
2019-02-23 13:00 | 1067.8252 | 3158.805 | 7873.3333 | 10000 | 9964.3132 | 0 | 0
2019-02-23 14:00 | 1076.3868 | 3139.3769 | 9060 | 10000 | 11122.9902 | 0 | 0
2019-02-23 15:00 | 1140.564 | 1877.7372 | 4266.6667 | 10000 | 5003.8399 | 0 | 0
2019-02-23 16:00 | 1371.8901 | 743.1691 | 4266.6667 | 10000 | 3637.9457 | 0 | 0
2019-02-23 17:00 | 1859.2868 | 0 | 7873.3333 | 10000 | 6014.0465 | 0 | 0
2019-02-23 18:00 | 2208.2207 | 0 | 7873.3333 | 10000 | 5665.1127 | 0 | 0
2019-02-23 19:00 | 2330.8284 | 0 | 7873.3333 | 10000 | 5542.505 | 0 | 0
2019-02-23 20:00 | 2243.1014 | 0 | 6160 | 10000 | 3916.8986 | 0 | 0
2019-02-23 21:00 | 2047.3071 | 0 | 6160 | 10000 | 4112.6929 | 0 | 0
2019-02-23 22:00 | 1689.7644 | 0 | 6160 | 10000 | 4470.2356 | 0 | 0
2019-02-23 23:00 | 1357.5855 | 0 | 2773.3333 | 10000 | 1415.7478 | 0 | 0
2019-02-24 | 1016.0778 | 0 | 286.6667 | 10000 | -729.4111 | -729.4111 | 0
2019-02-24 01:00 | 885.7536 | 0 | 286.6667 | 9270.5889 | -599.087 | -599.087 | 0
2019-02-24 02:00 | 832.8554 | 0 | 286.6667 | 8671.5019 | -546.1888 | -546.1888 | 0
2019-02-24 03:00 | 822.6774 | 0 | 0 | 8125.3132 | -822.6774 | -822.6774 | 0
2019-02-24 04:00 | 817.8406 | 0 | 0 | 7302.6358 | -817.8406 | -817.8406 | 0
2019-02-24 05:00 | 885.2275 | 0 | 0 | 6484.7952 | -885.2275 | -885.2275 | 0
2019-02-24 06:00 | 1094.6676 | 0 | 0 | 5599.5676 | -1094.6676 | -1094.6676 | 0
2019-02-24 07:00 | 1403.629 | 2138.0478 | 0 | 4504.9 | 734.4188 | 734.4188 | 0
2019-02-24 08:00 | 1332.6872 | 4777.2253 | 873.3333 | 5239.3188 | 4317.8715 | 4317.8715 | 0
2019-02-24 09:00 | 1176.8519 | 6819.9715 | 873.3333 | 9557.1903 | 6516.4529 | 442.8097 | 0
2019-02-24 10:00 | 1200.4678 | 7019.2205 | 873.3333 | 10000 | 6692.086 | 0 | 0
2019-02-24 11:00 | 1185.9434 | 7068.2381 | 1666.6667 | 10000 | 7548.9614 | 0 | 0
2019-02-24 12:00 | 1157.4011 | 7460.809 | 7873.3333 | 10000 | 14176.7413 | 0 | 0
2019-02-24 13:00 | 1123.3111 | 6554.011 | 9060 | 10000 | 14490.6999 | 0 | 0
2019-02-24 14:00 | 1122.9062 | 5774.7399 | 9060 | 10000 | 13711.8338 | 0 | 0
2019-02-24 15:00 | 1181.7866 | 3527.5985 | 7873.3333 | 10000 | 10219.1452 | 0 | 0
2019-02-24 16:00 | 1404.4931 | 1818.3743 | 7873.3333 | 10000 | 8287.2145 | 0 | 0
2019-02-24 17:00 | 1884.1222 | 0 | 6160 | 10000 | 4275.8778 | 0 | 0
2019-02-24 18:00 | 2262.2874 | 0 | 4266.6667 | 10000 | 2004.3793 | 0 | 0
2019-02-24 19:00 | 2351.7706 | 0 | 2773.3333 | 10000 | 421.5628 | 0 | 0
2019-02-24 20:00 | 2249.9789 | 0 | 2773.3333 | 10000 | 523.3544 | 0 | 0
2019-02-24 21:00 | 2038.359 | 0 | 873.3333 | 10000 | -1165.0256 | -1165.0256 | 0
2019-02-24 22:00 | 1676.0176 | 0 | 873.3333 | 8834.9744 | -802.6843 | -802.6843 | 0
2019-02-24 23:00 | 1340.3596 | 0 | 4266.6667 | 8032.2901 | 2926.3071 | 1967.7099 | 0
2019-02-25 | 994.3558 | 0 | 1666.6667 | 10000 | 672.3109 | 0 | 0
2019-02-25 01:00 | 874.6147 | 0 | 873.3333 | 10000 | -1.2813 | -1.2813 | 0
2019-02-25 02:00 | 821.6119 | 0 | 286.6667 | 9998.7187 | -534.9452 | -534.9452 | 0
2019-02-25 03:00 | 810.1552 | 0 | 286.6667 | 9463.7735 | -523.4886 | -523.4886 | 0
2019-02-25 04:00 | 786.5605 | 0 | 286.6667 | 8940.2849 | -499.8938 | -499.8938 | 0
2019-02-25 05:00 | 847.1689 | 0 | 286.6667 | 8440.391 | -560.5023 | -560.5023 | 0
2019-02-25 06:00 | 1104.1411 | 0 | 286.6667 | 7879.8888 | -817.4744 | -817.4744 | 0
2019-02-25 07:00 | 1426.949 | 2249.6541 | 873.3333 | 7062.4144 | 1696.0385 | 1696.0385 | 0
2019-02-25 08:00 | 1343.0065 | 4253.3187 | 873.3333 | 8758.4529 | 3783.6455 | 1241.5471 | 0
2019-02-25 09:00 | 1169.1801 | 4305.1204 | 286.6667 | 10000 | 3422.607 | 0 | 0
2019-02-25 10:00 | 1176.9271 | 6849.7324 | 873.3333 | 10000 | 6546.1386 | 0 | 0
2019-02-25 11:00 | 1163.1349 | 7512.7717 | 873.3333 | 10000 | 7222.9701 | 0 | 0
2019-02-25 12:00 | 1128.9263 | 6701.3662 | 6160 | 10000 | 11732.44 | 0 | 0
2019-02-25 13:00 | 1093.3544 | 7079.6932 | 4266.6667 | 10000 | 10253.0055 | 0 | 0
2019-02-25 14:00 | 1083.5654 | 5773.0103 | 1666.6667 | 10000 | 6356.1116 | 0 | 0
2019-02-25 15:00 | 1146.4203 | 3468.776 | 6160 | 10000 | 8482.3558 | 0 | 0
2019-02-25 16:00 | 1373.2122 | 1927.1021 | 2773.3333 | 10000 | 3327.2233 | 0 | 0
2019-02-25 17:00 | 1841.4519 | 0 | 6160 | 10000 | 4318.5481 | 0 | 0
2019-02-25 18:00 | 2197.1825 | 0 | 873.3333 | 10000 | -1323.8491 | -1323.8491 | 0
2019-02-25 19:00 | 2332.6186 | 0 | 286.6667 | 8676.1509 | -2045.952 | -2045.952 | 0
2019-02-25 20:00 | 2243.8531 | 0 | 873.3333 | 6630.1989 | -1370.5198 | -1370.5198 | 0
2019-02-25 21:00 | 2047.8272 | 0 | 873.3333 | 5259.6791 | -1174.4938 | -1174.4938 | 0
2019-02-25 22:00 | 1684.2791 | 0 | 4266.6667 | 4085.1853 | 2582.3876 | 2582.3876 | 0
2019-02-25 23:00 | 1337.4856 | 0 | 4266.6667 | 6667.5729 | 2929.1811 | 2929.1811 | 0
2019-02-26 | 975.2552 | 0 | 7873.3333 | 9596.7539 | 6898.0782 | 403.2461 | 0
2019-02-26 01:00 | 841.0063 | 0 | 6160 | 10000 | 5318.9937 | 0 | 0
2019-02-26 02:00 | 786.5796 | 0 | 6160 | 10000 | 5373.4204 | 0 | 0
2019-02-26 03:00 | 773.1768 | 0 | 7873.3333 | 10000 | 7100.1566 | 0 | 0
2019-02-26 04:00 | 775.8002 | 0 | 7873.3333 | 10000 | 7097.5332 | 0 | 0
2019-02-26 05:00 | 841.3008 | 0 | 6160 | 10000 | 5318.6992 | 0 | 0
2019-02-26 06:00 | 1074.2782 | 0 | 6160 | 10000 | 5085.7218 | 0 | 0
2019-02-26 07:00 | 1382.0529 | 1082.2477 | 6160 | 10000 | 5860.1948 | 0 | 0
2019-02-26 08:00 | 1300.5499 | 1846.4457 | 4266.6667 | 10000 | 4812.5625 | 0 | 0
2019-02-26 09:00 | 1134.4113 | 3375.3685 | 2773.3333 | 10000 | 5014.2905 | 0 | 0
2019-02-26 10:00 | 1162.1938 | 5421.6646 | 6160 | 10000 | 10419.4709 | 0 | 0
2019-02-26 11:00 | 1153.0999 | 8848.9142 | 9060 | 10000 | 16755.8143 | 0 | 0
2019-02-26 12:00 | 1110.6455 | 7218.956 | 6160 | 10000 | 12268.3105 | 0 | 0
2019-02-26 13:00 | 1060.3776 | 1321.1441 | 7873.3333 | 10000 | 8134.0999 | 0 | 0
2019-02-26 14:00 | 1053.4291 | 5306.2713 | 7873.3333 | 10000 | 12126.1756 | 0 | 0
2019-02-26 15:00 | 1118.01 | 3479.3929 | 7873.3333 | 10000 | 10234.7162 | 0 | 0
2019-02-26 16:00 | 1354.9028 | 1932.0138 | 9060 | 10000 | 9637.111 | 0 | 0
2019-02-26 17:00 | 1834.2145 | 0 | 6160 | 10000 | 4325.7855 | 0 | 0
2019-02-26 18:00 | 2192.5797 | 0 | 6160 | 10000 | 3967.4203 | 0 | 0
2019-02-26 19:00 | 2323.7074 | 0 | 6160 | 10000 | 3836.2926 | 0 | 0
2019-02-26 20:00 | 2242.0222 | 0 | 873.3333 | 10000 | -1368.6889 | -1368.6889 | 0
2019-02-26 21:00 | 2046.2873 | 0 | 2773.3333 | 8631.3111 | 727.046 | 727.046 | 0
2019-02-26 22:00 | 1688.4475 | 0 | 1666.6667 | 9358.3572 | -21.7808 | -21.7808 | 0
2019-02-26 23:00 | 1347.5649 | 0 | 2773.3333 | 9336.5764 | 1425.7684 | 663.4236 | 0
2019-02-27 | 985.3666 | 0 | 873.3333 | 10000 | -112.0333 | -112.0333 | 0
2019-02-27 01:00 | 851.8539 | 0 | 873.3333 | 9887.9667 | 21.4795 | 21.4795 | 0
2019-02-27 02:00 | 802.6537 | 0 | 2773.3333 | 9909.4462 | 1970.6797 | 90.5538 | 0
2019-02-27 03:00 | 796.5829 | 0 | 873.3333 | 10000 | 76.7504 | 0 | 0
2019-02-27 04:00 | 794.8828 | 0 | 1666.6667 | 10000 | 871.7839 | 0 | 0
2019-02-27 05:00 | 865.2988 | 0 | 6160 | 10000 | 5294.7012 | 0 | 0
2019-02-27 06:00 | 1076.182 | 0 | 9060 | 10000 | 7983.818 | 0 | 0
2019-02-27 07:00 | 1380.0091 | 2420.3003 | 9060 | 10000 | 10100.2912 | 0 | 0
2019-02-27 08:00 | 1285.9836 | 5014.3024 | 6160 | 10000 | 9888.3189 | 0 | 0
2019-02-27 09:00 | 1123.4791 | 5670.604 | 4266.6667 | 10000 | 8813.7916 | 0 | 0
2019-02-27 10:00 | 1143.5581 | 7257.8018 | 4266.6667 | 10000 | 10380.9104 | 0 | 0
2019-02-27 11:00 | 1134.8232 | 8876.9535 | 2773.3333 | 10000 | 10515.4636 | 0 | 0
2019-02-27 12:00 | 1107.7535 | 7767.8728 | 9573.3333 | 10000 | 16233.4526 | 0 | 0
2019-02-27 13:00 | 1082.074 | 4405.3464 | 9573.3333 | 10000 | 12896.6057 | 0 | 0
2019-02-27 14:00 | 1083.0425 | 2719.7604 | 9060 | 10000 | 10696.7178 | 0 | 0
2019-02-27 15:00 | 1143.3443 | 1105.7606 | 9573.3333 | 10000 | 9535.7497 | 0 | 0
2019-02-27 16:00 | 1371.7498 | 1287.2283 | 9573.3333 | 10000 | 9488.8119 | 0 | 0
2019-02-27 17:00 | 1848.0596 | 0 | 9573.3333 | 10000 | 7725.2737 | 0 | 0
2019-02-27 18:00 | 2194.7935 | 0 | 7873.3333 | 10000 | 5678.5398 | 0 | 0
2019-02-27 19:00 | 2312.7158 | 0 | 6160 | 10000 | 3847.2842 | 0 | 0
2019-02-27 20:00 | 2222.1174 | 0 | 2773.3333 | 10000 | 551.2159 | 0 | 0
2019-02-27 21:00 | 2020.3038 | 0 | 1666.6667 | 10000 | -353.6372 | -353.6372 | 0
2019-02-27 22:00 | 1662.605 | 0 | 1666.6667 | 9646.3628 | 4.0616 | 4.0616 | 0
2019-02-27 23:00 | 1322.8724 | 0 | 2773.3333 | 9650.4245 | 1450.4609 | 349.5755 | 0
2019-02-28 | 975.3234 | 0 | 2773.3333 | 10000 | 1798.01 | 0 | 0
2019-02-28 01:00 | 843.6096 | 0 | 1666.6667 | 10000 | 823.0571 | 0 | 0
2019-02-28 02:00 | 791.8669 | 0 | 873.3333 | 10000 | 81.4664 | 0 | 0
2019-02-28 03:00 | 778.6324 | 0 | 873.3333 | 10000 | 94.701 | 0 | 0
2019-02-28 04:00 | 775.4775 | 0 | 873.3333 | 10000 | 97.8559 | 0 | 0
2019-02-28 05:00 | 840.8306 | 0 | 286.6667 | 10000 | -554.1639 | -554.1639 | 0
2019-02-28 06:00 | 1051.4324 | 0 | 0 | 9445.8361 | -1051.4324 | -1051.4324 | 0
2019-02-28 07:00 | 1380.8756 | 2563.0475 | 0 | 8394.4037 | 1182.172 | 1182.172 | 0
2019-02-28 08:00 | 1281.6092 | 5312.7171 | 0 | 9576.5757 | 4031.1079 | 423.4243 | 0
2019-02-28 09:00 | 1095.3877 | 7414.0454 | 0 | 10000 | 6318.6577 | 0 | 0
2019-02-28 10:00 | 1097.6747 | 8636.1838 | 0 | 10000 | 7538.509 | 0 | 0
2019-02-28 11:00 | 1076.0005 | 9217.0626 | 286.6667 | 10000 | 8427.7288 | 0 | 0
2019-02-28 12:00 | 1042.8947 | 9142.5472 | 286.6667 | 10000 | 8386.3192 | 0 | 0
2019-02-28 13:00 | 1008.3718 | 8424.9667 | 873.3333 | 10000 | 8289.9282 | 0 | 0
2019-02-28 14:00 | 1011.5324 | 6969.9924 | 1666.6667 | 10000 | 7625.1267 | 0 | 0
2019-02-28 15:00 | 1083.3383 | 4689.3113 | 286.6667 | 10000 | 3892.6397 | 0 | 0
2019-02-28 16:00 | 1327.4933 | 2110.3121 | 286.6667 | 10000 | 1069.4855 | 0 | 0
2019-02-28 17:00 | 1819.2384 | 0 | 286.6667 | 10000 | -1532.5717 | -1532.5717 | 0
2019-02-28 18:00 | 2180.5381 | 0 | 0 | 8467.4283 | -2180.5381 | -2180.5381 | 0
2019-02-28 19:00 | 2317.9788 | 0 | 286.6667 | 6286.8902 | -2031.3121 | -2031.3121 | 0
2019-02-28 20:00 | 2239.6388 | 0 | 286.6667 | 4255.5781 | -1952.9722 | -1952.9722 | 0
2019-02-28 21:00 | 2044.3892 | 0 | 286.6667 | 2302.6059 | -1757.7226 | -1757.7226 | 0
2019-02-28 22:00 | 1690.3217 | 0 | 286.6667 | 544.8834 | -1403.6551 | -544.8834 | -858.7717
2019-02-28 23:00 | 1355.317 | 0 | 286.6667 | 0 | -1068.6504 | 0 | -1927.4221
2019-03-01 | 958.0488 | 0 | 286.6667 | 0 | -671.3821 | 0 | -2598.8042
2019-03-01 01:00 | 826.864 | 0 | 286.6667 | 0 | -540.1973 | 0 | -3139.0015
2019-03-01 02:00 | 769.678 | 0 | 286.6667 | 0 | -483.0113 | 0 | -3622.0128
2019-03-01 03:00 | 755.1802 | 0 | 873.3333 | 0 | 118.1531 | 118.1531 | -3503.8597
2019-03-01 04:00 | 751.9414 | 0 | 873.3333 | 118.1531 | 121.3919 | 121.3919 | -3264.3146
2019-03-01 05:00 | 809.7061 | 0 | 873.3333 | 239.5451 | 63.6273 | 63.6273 | -2961.1423
2019-03-01 06:00 | 972.26 | 129.3485 | 2773.3333 | 303.1723 | 1930.4219 | 1930.4219 | -727.5481
2019-03-01 07:00 | 1200.0219 | 2161.3801 | 2773.3333 | 2233.5942 | 3734.6915 | 3734.6915 | 0
2019-03-01 08:00 | 1108.963 | 1093.3245 | 2773.3333 | 5968.2857 | 2757.6949 | 2757.6949 | 0
2019-03-01 09:00 | 1015.3083 | 1392.1808 | 2773.3333 | 8725.9806 | 3150.2058 | 1274.0194 | 0
2019-03-01 10:00 | 1035.7423 | 2523.5531 | 1666.6667 | 10000 | 3154.4774 | 0 | 0
2019-03-01 11:00 | 1020.2572 | 1545.3562 | 4266.6667 | 10000 | 4791.7656 | 0 | 0
2019-03-01 12:00 | 979.6636 | 2598.6745 | 4266.6667 | 10000 | 5885.6777 | 0 | 0
2019-03-01 13:00 | 934.4509 | 1198.5288 | 6160 | 10000 | 6424.078 | 0 | 0
2019-03-01 14:00 | 922.6531 | 1000.4321 | 7873.3333 | 10000 | 7951.1124 | 0 | 0
2019-03-01 15:00 | 970.1345 | 379.3494 | 6160 | 10000 | 5569.2148 | 0 | 0
2019-03-01 16:00 | 1157.1991 | 96.1009 | 4266.6667 | 10000 | 3205.5685 | 0 | 0
2019-03-01 17:00 | 1539.5626 | 0 | 6160 | 10000 | 4620.4374 | 0 | 0
2019-03-01 18:00 | 1843.348 | 0 | 7873.3333 | 10000 | 6029.9853 | 0 | 0
2019-03-01 19:00 | 2043.3776 | 0 | 6160 | 10000 | 4116.6224 | 0 | 0
2019-03-01 20:00 | 2100.0646 | 0 | 9060 | 10000 | 6959.9354 | 0 | 0
2019-03-01 21:00 | 1926.6909 | 0 | 9060 | 10000 | 7133.3091 | 0 | 0
2019-03-01 22:00 | 1595.1349 | 0 | 9060 | 10000 | 7464.8651 | 0 | 0
2019-03-01 23:00 | 1275.8202 | 0 | 4266.6667 | 10000 | 2990.8465 | 0 | 0
2019-03-02 | 939.332 | 0 | 6160 | 10000 | 5220.668 | 0 | 0
2019-03-02 01:00 | 816.6882 | 0 | 4266.6667 | 10000 | 3449.9785 | 0 | 0
2019-03-02 02:00 | 767.7008 | 0 | 2773.3333 | 10000 | 2005.6326 | 0 | 0
2019-03-02 03:00 | 758.7987 | 0 | 4266.6667 | 10000 | 3507.868 | 0 | 0
2019-03-02 04:00 | 759.4543 | 0 | 4266.6667 | 10000 | 3507.2124 | 0 | 0
2019-03-02 05:00 | 819.9219 | 0 | 9960 | 10000 | 9140.0781 | 0 | 0
2019-03-02 06:00 | 985.5835 | 188.1653 | 9060 | 10000 | 8262.5818 | 0 | 0
2019-03-02 07:00 | 1219.9024 | 2243.9156 | 9060 | 10000 | 10084.0133 | 0 | 0
2019-03-02 08:00 | 1131.1237 | 4630.3818 | 9060 | 10000 | 12559.2582 | 0 | 0
2019-03-02 09:00 | 1009.6326 | 6478.6423 | 10000 | 10000 | 15469.0097 | 0 | 0
2019-03-02 10:00 | 1021.7244 | 7466.8304 | 10000 | 10000 | 16445.106 | 0 | 0
2019-03-02 11:00 | 1009.7512 | 3426.8746 | 10000 | 10000 | 12417.1234 | 0 | 0
2019-03-02 12:00 | 989.2784 | 3464.8396 | 9873.3333 | 10000 | 12348.8945 | 0 | 0
2019-03-02 13:00 | 963.3063 | 3081.3939 | 9873.3333 | 10000 | 11991.421 | 0 | 0
2019-03-02 14:00 | 956.7481 | 1090.484 | 10000 | 10000 | 10133.736 | 0 | 0
2019-03-02 15:00 | 1009.4749 | 1145.9807 | 9573.3333 | 10000 | 9709.8392 | 0 | 0
2019-03-02 16:00 | 1188.0838 | 1737.8984 | 9873.3333 | 10000 | 10423.1479 | 0 | 0
2019-03-02 17:00 | 1566.6161 | 0 | 9873.3333 | 10000 | 8306.7172 | 0 | 0
2019-03-02 18:00 | 1865.2946 | 0 | 9060 | 10000 | 7194.7054 | 0 | 0
2019-03-02 19:00 | 2064.2887 | 0 | 9060 | 10000 | 6995.7113 | 0 | 0
2019-03-02 20:00 | 2116.2725 | 0 | 7873.3333 | 10000 | 5757.0608 | 0 | 0
2019-03-02 21:00 | 1940.5563 | 0 | 4266.6667 | 10000 | 2326.1104 | 0 | 0
2019-03-02 22:00 | 1601.8626 | 0 | 2773.3333 | 10000 | 1171.4707 | 0 | 0
2019-03-02 23:00 | 1287.2609 | 0 | 6160 | 10000 | 4872.7391 | 0 | 0
2019-03-03 | 956.5491 | 0 | 4266.6667 | 10000 | 3310.1176 | 0 | 0
2019-03-03 01:00 | 833.6411 | 0 | 2773.3333 | 10000 | 1939.6922 | 0 | 0
2019-03-03 02:00 | 783.4787 | 0 | 1666.6667 | 10000 | 883.1879 | 0 | 0
2019-03-03 03:00 | 777.5675 | 0 | 1666.6667 | 10000 | 889.0992 | 0 | 0
2019-03-03 04:00 | 781.448 | 0 | 873.3333 | 10000 | 91.8854 | 0 | 0
2019-03-03 05:00 | 845.2655 | 0 | 4266.6667 | 10000 | 3421.4011 | 0 | 0
2019-03-03 06:00 | 1012.9372 | 0 | 4266.6667 | 10000 | 3253.7295 | 0 | 0
2019-03-03 07:00 | 1241.9306 | 752.1678 | 6160 | 10000 | 5670.2372 | 0 | 0
2019-03-03 08:00 | 1157.9753 | 1976.9351 | 7873.3333 | 10000 | 8692.2931 | 0 | 0
2019-03-03 09:00 | 1044.0404 | 4266.1274 | 4266.6667 | 10000 | 7488.7536 | 0 | 0
2019-03-03 10:00 | 1061.0734 | 5095.0014 | 2773.3333 | 10000 | 6807.2614 | 0 | 0
2019-03-03 11:00 | 1029.5488 | 5617.9121 | 4266.6667 | 10000 | 8855.03 | 0 | 0
2019-03-03 12:00 | 1004.4662 | 5387.0543 | 873.3333 | 10000 | 5255.9214 | 0 | 0
2019-03-03 13:00 | 973.8864 | 4182.6132 | 873.3333 | 10000 | 4082.0601 | 0 | 0
2019-03-03 14:00 | 971.6957 | 3945.3901 | 873.3333 | 10000 | 3847.0277 | 0 | 0
2019-03-03 15:00 | 1032.6059 | 1508.8368 | 0 | 10000 | 476.2309 | 0 | 0
2019-03-03 16:00 | 1218.5772 | 682.9838 | 873.3333 | 10000 | 337.74 | 0 | 0
2019-03-03 17:00 | 1613.9293 | 0 | 2773.3333 | 10000 | 1159.4041 | 0 | 0
2019-03-03 18:00 | 1922.6885 | 0 | 1666.6667 | 10000 | -256.0218 | -256.0218 | 0
2019-03-03 19:00 | 2127.3493 | 0 | 6160 | 9743.9782 | 4032.6507 | 256.0218 | 0
2019-03-03 20:00 | 2180.5508 | 0 | 6160 | 10000 | 3979.4492 | 0 | 0
2019-03-03 21:00 | 2018.343 | 0 | 9573.3333 | 10000 | 7554.9903 | 0 | 0
2019-03-03 22:00 | 1680.3139 | 0 | 9060 | 10000 | 7379.6861 | 0 | 0
2019-03-03 23:00 | 1365.594 | 0 | 6160 | 10000 | 4794.406 | 0 | 0
2019-03-04 | 1040.8873 | 0 | 9060 | 10000 | 8019.1127 | 0 | 0
2019-03-04 01:00 | 914.398 | 0 | 7873.3333 | 10000 | 6958.9353 | 0 | 0
2019-03-04 02:00 | 862.4089 | 0 | 9573.3333 | 10000 | 8710.9245 | 0 | 0
2019-03-04 03:00 | 847.8498 | 0 | 6160 | 10000 | 5312.1502 | 0 | 0
2019-03-04 04:00 | 849.4686 | 0 | 7873.3333 | 10000 | 7023.8647 | 0 | 0
2019-03-04 05:00 | 912.8229 | 0 | 2773.3333 | 10000 | 1860.5104 | 0 | 0
2019-03-04 06:00 | 1086.2319 | 312.7045 | 2773.3333 | 10000 | 1999.806 | 0 | 0
2019-03-04 07:00 | 1331.7782 | 2439.9676 | 2773.3333 | 10000 | 3881.5228 | 0 | 0
2019-03-04 08:00 | 1236.1175 | 4898.2651 | 2773.3333 | 10000 | 6435.481 | 0 | 0
2019-03-04 09:00 | 1128.8436 | 4775.4417 | 6160 | 10000 | 9806.5981 | 0 | 0
2019-03-04 10:00 | 1144.6612 | 5832.1571 | 4266.6667 | 10000 | 8954.1626 | 0 | 0
2019-03-04 11:00 | 1104.9167 | 5196.099 | 9573.3333 | 10000 | 13664.5156 | 0 | 0
2019-03-04 12:00 | 1054.688 | 5839.915 | 9573.3333 | 10000 | 14358.5604 | 0 | 0
2019-03-04 13:00 | 1006.1442 | 3767.3448 | 9573.3333 | 10000 | 12334.5339 | 0 | 0
2019-03-04 14:00 | 989.2379 | 3669.1405 | 9060 | 10000 | 11739.9026 | 0 | 0
2019-03-04 15:00 | 1032.5143 | 2466.3659 | 9573.3333 | 10000 | 11007.185 | 0 | 0
2019-03-04 16:00 | 1214.778 | 790.5813 | 9573.3333 | 10000 | 9149.1367 | 0 | 0
2019-03-04 17:00 | 1597.9705 | 0 | 9060 | 10000 | 7462.0295 | 0 | 0
2019-03-04 18:00 | 1900.7189 | 0 | 7873.3333 | 10000 | 5972.6144 | 0 | 0
2019-03-04 19:00 | 2100.8642 | 0 | 9060 | 10000 | 6959.1358 | 0 | 0
2019-03-04 20:00 | 2156.7911 | 0 | 9060 | 10000 | 6903.2089 | 0 | 0
2019-03-04 21:00 | 1979.7665 | 0 | 7873.3333 | 10000 | 5893.5668 | 0 | 0
2019-03-04 22:00 | 1641.2587 | 0 | 9060 | 10000 | 7418.7413 | 0 | 0
2019-03-04 23:00 | 1310.3075 | 0 | 4266.6667 | 10000 | 2956.3592 | 0 | 0
2019-03-05 | 969.1305 | 0 | 9060 | 10000 | 8090.8695 | 0 | 0
2019-03-05 01:00 | 845.4868 | 0 | 9060 | 10000 | 8214.5132 | 0 | 0
2019-03-05 02:00 | 797.9097 | 0 | 9873.3333 | 10000 | 9075.4236 | 0 | 0
2019-03-05 03:00 | 792.113 | 0 | 9573.3333 | 10000 | 8781.2203 | 0 | 0
2019-03-05 04:00 | 797.2586 | 0 | 9573.3333 | 10000 | 8776.0747 | 0 | 0
2019-03-05 05:00 | 861.3515 | 0 | 7873.3333 | 10000 | 7011.9818 | 0 | 0
2019-03-05 06:00 | 1038.9237 | 320.3888 | 4266.6667 | 10000 | 3548.1319 | 0 | 0
2019-03-05 07:00 | 1283.5997 | 961.3379 | 4266.6667 | 10000 | 3944.4049 | 0 | 0
2019-03-05 08:00 | 1197.6417 | 2530.0264 | 4266.6667 | 10000 | 5599.0514 | 0 | 0
2019-03-05 09:00 | 1100.1924 | 3141.3089 | 6160 | 10000 | 8201.1165 | 0 | 0
2019-03-05 10:00 | 1128.765 | 3798.0141 | 7873.3333 | 10000 | 10542.5825 | 0 | 0
2019-03-05 11:00 | 1109.8552 | 3067.9493 | 6160 | 10000 | 8118.0941 | 0 | 0
2019-03-05 12:00 | 1079.5446 | 3820.1792 | 7873.3333 | 10000 | 10613.968 | 0 | 0
2019-03-05 13:00 | 1039.5473 | 1558.7054 | 7873.3333 | 10000 | 8392.4915 | 0 | 0
2019-03-05 14:00 | 1028.2295 | 2943.456 | 4266.6667 | 10000 | 6181.8932 | 0 | 0
2019-03-05 15:00 | 1077.0823 | 323.1684 | 9060 | 10000 | 8306.0861 | 0 | 0
2019-03-05 16:00 | 1262.2984 | 1595.901 | 7873.3333 | 10000 | 8206.9359 | 0 | 0
2019-03-05 17:00 | 1650.2919 | 0 | 4266.6667 | 10000 | 2616.3748 | 0 | 0
2019-03-05 18:00 | 1948.0271 | 0 | 6160 | 10000 | 4211.9729 | 0 | 0
2019-03-05 19:00 | 2142.1662 | 0 | 4266.6667 | 10000 | 2124.5004 | 0 | 0
2019-03-05 20:00 | 2196.5137 | 0 | 4266.6667 | 10000 | 2070.153 | 0 | 0
2019-03-05 21:00 | 2016.9215 | 0 | 1666.6667 | 10000 | -350.2548 | -350.2548 | 0
2019-03-05 22:00 | 1669.8304 | 0 | 1666.6667 | 9649.7452 | -3.1638 | -3.1638 | 0
2019-03-05 23:00 | 1330.346 | 0 | 873.3333 | 9646.5814 | -457.0127 | -457.0127 | 0
2019-03-06 | 974.6215 | 0 | 2773.3333 | 9189.5687 | 1798.7119 | 810.4313 | 0
2019-03-06 01:00 | 847.8996 | 0 | 2773.3333 | 10000 | 1925.4337 | 0 | 0
2019-03-06 02:00 | 793.5957 | 0 | 286.6667 | 10000 | -506.929 | -506.929 | 0
2019-03-06 03:00 | 781.9186 | 0 | 1666.6667 | 9493.071 | 884.748 | 506.929 | 0
2019-03-06 04:00 | 778.2309 | 0 | 1666.6667 | 10000 | 888.4357 | 0 | 0
2019-03-06 05:00 | 833.1355 | 0 | 873.3333 | 10000 | 40.1979 | 0 | 0
2019-03-06 06:00 | 997.7395 | 0 | 0 | 10000 | -997.7395 | -997.7395 | 0
2019-03-06 07:00 | 1252.2199 | 146.7745 | 0 | 9002.2605 | -1105.4454 | -1105.4454 | 0
2019-03-06 08:00 | 1162.8176 | 1019.4278 | 0 | 7896.8151 | -143.3898 | -143.3898 | 0
2019-03-06 09:00 | 1062.9528 | 978.7155 | 0 | 7753.4253 | -84.2373 | -84.2373 | 0
2019-03-06 10:00 | 1094.6419 | 2398.0375 | 0 | 7669.1881 | 1303.3956 | 1303.3956 | 0
2019-03-06 11:00 | 1076.3766 | 3469.4936 | 0 | 8972.5836 | 2393.117 | 1027.4164 | 0
2019-03-06 12:00 | 1046.7088 | 2697.3595 | 0 | 10000 | 1650.6507 | 0 | 0
2019-03-06 13:00 | 1018.4048 | 1950.5334 | 0 | 10000 | 932.1286 | 0 | 0
2019-03-06 14:00 | 1014.3874 | 1013.4915 | 873.3333 | 10000 | 872.4375 | 0 | 0
2019-03-06 15:00 | 1055.1773 | 812.4002 | 873.3333 | 10000 | 630.5562 | 0 | 0
2019-03-06 16:00 | 1226.4156 | 157.2406 | 873.3333 | 10000 | -195.8416 | -195.8416 | 0
2019-03-06 17:00 | 1607.1934 | 0 | 873.3333 | 9804.1584 | -733.86 | -733.86 | 0
2019-03-06 18:00 | 1906.6181 | 0 | 286.6667 | 9070.2983 | -1619.9514 | -1619.9514 | 0
2019-03-06 19:00 | 2097.0978 | 0 | 286.6667 | 7450.3469 | -1810.4311 | -1810.4311 | 0
2019-03-06 20:00 | 2146.7495 | 0 | 286.6667 | 5639.9158 | -1860.0829 | -1860.0829 | 0
2019-03-06 21:00 | 1966.1737 | 0 | 286.6667 | 3779.833 | -1679.507 | -1679.507 | 0
2019-03-06 22:00 | 1627.9873 | 0 | 286.6667 | 2100.326 | -1341.3207 | -1341.3207 | 0
2019-03-06 23:00 | 1299.7919 | 0 | 286.6667 | 759.0053 | -1013.1252 | -759.0053 | -254.1199
2019-03-07 | 958.7558 | 0 | 286.6667 | 0 | -672.0891 | 0 | -926.2091
2019-03-07 01:00 | 831.6674 | 0 | 286.6667 | 0 | -545.0007 | 0 | -1471.2098
2019-03-07 02:00 | 777.217 | 0 | 286.6667 | 0 | -490.5504 | 0 | -1961.7601
2019-03-07 03:00 | 766.2449 | 0 | 286.6667 | 0 | -479.5783 | 0 | -2441.3384
2019-03-07 04:00 | 765.2387 | 0 | 286.6667 | 0 | -478.572 | 0 | -2919.9104
2019-03-07 05:00 | 826.7604 | 0 | 0 | 0 | -826.7604 | 0 | -3746.6708
2019-03-07 06:00 | 994.0012 | 24.0821 | 286.6667 | 0 | -683.2524 | 0 | -4429.9232
2019-03-07 07:00 | 1247.092 | 489.0524 | 286.6667 | 0 | -471.3729 | 0 | -4901.2961
2019-03-07 08:00 | 1160.9117 | 1613.8847 | 1666.6667 | 0 | 2119.6397 | 2119.6397 | -2781.6565
2019-03-07 09:00 | 1066.3842 | 3051.1018 | 2773.3333 | 2119.6397 | 4758.0509 | 4758.0509 | 0
2019-03-07 10:00 | 1099.4435 | 3240.7115 | 1666.6667 | 6877.6906 | 3807.9347 | 3122.3094 | 0
2019-03-07 11:00 | 1086.4105 | 5132.6892 | 873.3333 | 10000 | 4919.6121 | 0 | 0
2019-03-07 12:00 | 1057.1703 | 3730.7001 | 873.3333 | 10000 | 3546.863 | 0 | 0
2019-03-07 13:00 | 1031.9749 | 4097.1498 | 1666.6667 | 10000 | 4731.8416 | 0 | 0
2019-03-07 14:00 | 1022.043 | 2209.8595 | 4266.6667 | 10000 | 5454.4832 | 0 | 0
2019-03-07 15:00 | 1069.3412 | 1789.546 | 2773.3333 | 10000 | 3493.5381 | 0 | 0
2019-03-07 16:00 | 1249.0691 | 599.7388 | 873.3333 | 10000 | 224.003 | 0 | 0
2019-03-07 17:00 | 1625.5038 | 0 | 873.3333 | 10000 | -752.1705 | -752.1705 | 0
2019-03-07 18:00 | 1916.056 | 0 | 873.3333 | 9247.8295 | -1042.7227 | -1042.7227 | 0
2019-03-07 19:00 | 2104.7413 | 0 | 873.3333 | 8205.1068 | -1231.408 | -1231.408 | 0
2019-03-07 20:00 | 2154.3291 | 0 | 873.3333 | 6973.6989 | -1280.9958 | -1280.9958 | 0
2019-03-07 21:00 | 1968.8211 | 0 | 873.3333 | 5692.7031 | -1095.4878 | -1095.4878 | 0
2019-03-07 22:00 | 1628.8587 | 0 | 873.3333 | 4597.2153 | -755.5254 | -755.5254 | 0
2019-03-07 23:00 | 1302.5465 | 0 | 873.3333 | 3841.6899 | -429.2132 | -429.2132 | 0
2019-03-08 | 962.2615 | 0 | 2773.3333 | 3412.4767 | 1811.0718 | 1811.0718 | 0
2019-03-08 01:00 | 830.4283 | 0 | 1666.6667 | 5223.5486 | 836.2384 | 836.2384 | 0
2019-03-08 02:00 | 777.3047 | 0 | 1666.6667 | 6059.787 | 889.362 | 889.362 | 0
2019-03-08 03:00 | 767.0574 | 0 | 2773.3333 | 6949.149 | 2006.2759 | 2006.2759 | 0
2019-03-08 04:00 | 768.228 | 0 | 2773.3333 | 8955.4249 | 2005.1053 | 1044.5751 | 0
2019-03-08 05:00 | 827.2949 | 0 | 2773.3333 | 10000 | 1946.0385 | 0 | 0
2019-03-08 06:00 | 988.2455 | 0 | 4266.6667 | 10000 | 3278.4211 | 0 | 0
2019-03-08 07:00 | 1229.9701 | 137.7803 | 4266.6667 | 10000 | 3174.4769 | 0 | 0
2019-03-08 08:00 | 1147.6105 | 1053.5656 | 4266.6667 | 10000 | 4172.6218 | 0 | 0
2019-03-08 09:00 | 1059.398 | 1667.14 | 4266.6667 | 10000 | 4874.4087 | 0 | 0
2019-03-08 10:00 | 1092.2298 | 1344.7076 | 1666.6667 | 10000 | 1919.1445 | 0 | 0
2019-03-08 11:00 | 1065.497 | 3453.059 | 4266.6667 | 10000 | 6654.2287 | 0 | 0
2019-03-08 12:00 | 1040.4139 | 2872.4711 | 6160 | 10000 | 7992.0573 | 0 | 0
2019-03-08 13:00 | 1009.158 | 3280.3876 | 4266.6667 | 10000 | 6537.8964 | 0 | 0
2019-03-08 14:00 | 999.2259 | 901.9507 | 6160 | 10000 | 6062.7248 | 0 | 0
2019-03-08 15:00 | 1043.4292 | 362.6329 | 6160 | 10000 | 5479.2037 | 0 | 0
2019-03-08 16:00 | 1220.5531 | 65.067 | 4266.6667 | 10000 | 3111.1806 | 0 | 0
2019-03-08 17:00 | 1605.2871 | 0 | 2773.3333 | 10000 | 1168.0463 | 0 | 0
2019-03-08 18:00 | 1898.6288 | 0 | 873.3333 | 10000 | -1025.2954 | -1025.2954 | 0
2019-03-08 19:00 | 2091.2209 | 0 | 1666.6667 | 8974.7046 | -424.5543 | -424.5543 | 0
2019-03-08 20:00 | 2143.508 | 0 | 2773.3333 | 8550.1503 | 629.8254 | 629.8254 | 0
2019-03-08 21:00 | 1958.4845 | 0 | 4266.6667 | 9179.9756 | 2308.1822 | 820.0244 | 0
2019-03-08 22:00 | 1620.5265 | 0 | 4266.6667 | 10000 | 2646.1401 | 0 | 0
2019-03-08 23:00 | 1297.8767 | 0 | 6160 | 10000 | 4862.1233 | 0 | 0
2019-03-09 | 959.3068 | 0 | 1666.6667 | 10000 | 707.3599 | 0 | 0
2019-03-09 01:00 | 830.5748 | 0 | 1666.6667 | 10000 | 836.0918 | 0 | 0
2019-03-09 02:00 | 777.0241 | 0 | 1666.6667 | 10000 | 889.6425 | 0 | 0
2019-03-09 03:00 | 766.567 | 0 | 1666.6667 | 10000 | 900.0996 | 0 | 0
2019-03-09 04:00 | 764.6741 | 0 | 1666.6667 | 10000 | 901.9926 | 0 | 0
2019-03-09 05:00 | 824.0727 | 0 | 1666.6667 | 10000 | 842.594 | 0 | 0
2019-03-09 06:00 | 993.3088 | 483.6291 | 873.3333 | 10000 | 363.6536 | 0 | 0
2019-03-09 07:00 | 1220.665 | 2859.7901 | 1666.6667 | 10000 | 3305.7918 | 0 | 0
2019-03-09 08:00 | 1136.1549 | 5412.7061 | 9873.3333 | 10000 | 14149.8846 | 0 | 0
2019-03-09 09:00 | 1035.3872 | 7340.9985 | 10000 | 10000 | 16305.6113 | 0 | 0
2019-03-09 10:00 | 1063.2493 | 8557.6503 | 9873.3333 | 10000 | 17367.7343 | 0 | 0
2019-03-09 11:00 | 1043.3717 | 9093.9803 | 9573.3333 | 10000 | 17623.942 | 0 | 0
2019-03-09 12:00 | 1007.6346 | 9016.9867 | 10000 | 10000 | 18009.3521 | 0 | 0
2019-03-09 13:00 | 967.927 | 8249.5768 | 10000 | 10000 | 17281.6497 | 0 | 0
2019-03-09 14:00 | 957.9531 | 6876.9827 | 9573.3333 | 10000 | 15492.363 | 0 | 0
2019-03-09 15:00 | 1002.7821 | 4737.8792 | 9960 | 10000 | 13695.0972 | 0 | 0
2019-03-09 16:00 | 1179.9819 | 2281.6471 | 9573.3333 | 10000 | 10674.9985 | 0 | 0
2019-03-09 17:00 | 1560.241 | 228.7143 | 2773.3333 | 10000 | 1441.8066 | 0 | 0
2019-03-09 18:00 | 1862.7441 | 0 | 4266.6667 | 10000 | 2403.9225 | 0 | 0
2019-03-09 19:00 | 2060.8885 | 0 | 4266.6667 | 10000 | 2205.7782 | 0 | 0
2019-03-09 20:00 | 2113.3059 | 0 | 6160 | 10000 | 4046.6941 | 0 | 0
2019-03-09 21:00 | 1932.8819 | 0 | 6160 | 10000 | 4227.1181 | 0 | 0
2019-03-09 22:00 | 1595.0655 | 0 | 4266.6667 | 10000 | 2671.6011 | 0 | 0
2019-03-09 23:00 | 1275.1324 | 0 | 4266.6667 | 10000 | 2991.5342 | 0 | 0
2019-03-10 | 938.3697 | 0 | 1666.6667 | 10000 | 728.2969 | 0 | 0
2019-03-10 01:00 | 810.8701 | 0 | 873.3333 | 10000 | 62.4632 | 0 | 0
2019-03-10 02:00 | 759.3318 | 0 | 0 | 10000 | -759.3318 | -759.3318 | 0
2019-03-10 03:00 | 749.7701 | 0 | 0 | 9240.6682 | -749.7701 | -749.7701 | 0
2019-03-10 04:00 | 750.2035 | 0 | 0 | 8490.8981 | -750.2035 | -750.2035 | 0
2019-03-10 05:00 | 811.1254 | 0 | 0 | 7740.6946 | -811.1254 | -811.1254 | 0
2019-03-10 06:00 | 980.2069 | 462.9291 | 286.6667 | 6929.5692 | -230.6111 | -230.6111 | 0
2019-03-10 07:00 | 1206.1935 | 1107.5293 | 0 | 6698.9581 | -98.6641 | -98.6641 | 0
2019-03-10 08:00 | 1125.1662 | 2910.5442 | 0 | 6600.2939 | 1785.378 | 1785.378 | 0
2019-03-10 09:00 | 1026.0156 | 3983.0894 | 0 | 8385.6719 | 2957.0738 | 1614.3281 | 0
2019-03-10 10:00 | 1048.7925 | 5626.9051 | 0 | 10000 | 4578.1127 | 0 | 0
2019-03-10 11:00 | 1030.8849 | 6781.0544 | 0 | 10000 | 5750.1694 | 0 | 0
2019-03-10 12:00 | 1003.1266 | 7199.4968 | 0 | 10000 | 6196.3702 | 0 | 0
2019-03-10 13:00 | 973.2526 | 7843.9867 | 0 | 10000 | 6870.7341 | 0 | 0
2019-03-10 14:00 | 964.4722 | 6552.9288 | 0 | 10000 | 5588.4566 | 0 | 0
2019-03-10 15:00 | 1006.2454 | 4627.3838 | 0 | 10000 | 3621.1384 | 0 | 0
2019-03-10 16:00 | 1186.666 | 2194.9463 | 0 | 10000 | 1008.2803 | 0 | 0
2019-03-10 17:00 | 1562.984 | 197.5654 | 0 | 10000 | -1365.4186 | -1365.4186 | 0
2019-03-10 18:00 | 1862.644 | 0 | 0 | 8634.5814 | -1862.644 | -1862.644 | 0
2019-03-10 19:00 | 2058.443 | 0 | 1666.6667 | 6771.9375 | -391.7764 | -391.7764 | 0
2019-03-10 20:00 | 2108.73 | 0 | 9573.3333 | 6380.1611 | 7464.6033 | 3619.8389 | 0
2019-03-10 21:00 | 1930.1291 | 0 | 9573.3333 | 10000 | 7643.2042 | 0 | 0
2019-03-10 22:00 | 1598.0107 | 0 | 6160 | 10000 | 4561.9893 | 0 | 0
2019-03-10 23:00 | 1278.1876 | 0 | 4266.6667 | 10000 | 2988.4791 | 0 | 0
2019-03-11 | 953.209 | 0 | 2773.3333 | 10000 | 1820.1243 | 0 | 0
2019-03-11 01:00 | 826.7487 | 0 | 2773.3333 | 10000 | 1946.5846 | 0 | 0
2019-03-11 02:00 | 775.0608 | 0 | 6160 | 10000 | 5384.9392 | 0 | 0
2019-03-11 03:00 | 765.8966 | 0 | 7873.3333 | 10000 | 7107.4367 | 0 | 0
2019-03-11 04:00 | 771.4159 | 0 | 9873.3333 | 10000 | 9101.9174 | 0 | 0
2019-03-11 05:00 | 833.3665 | 0 | 9573.3333 | 10000 | 8739.9669 | 0 | 0
2019-03-11 06:00 | 1020.0516 | 419.8569 | 6160 | 10000 | 5559.8054 | 0 | 0
2019-03-11 07:00 | 1254.8985 | 1400.6206 | 9060 | 10000 | 9205.7221 | 0 | 0
2019-03-11 08:00 | 1175.0983 | 4871.6599 | 9060 | 10000 | 12756.5616 | 0 | 0
2019-03-11 09:00 | 1082.6226 | 5628.0045 | 6160 | 10000 | 10705.382 | 0 | 0
2019-03-11 10:00 | 1114.034 | 7120.4216 | 6160 | 10000 | 12166.3877 | 0 | 0
2019-03-11 11:00 | 1106.8396 | 7267.494 | 9573.3333 | 10000 | 15733.9877 | 0 | 0
2019-03-11 12:00 | 1077.8169 | 5012.252 | 6160 | 10000 | 10094.4351 | 0 | 0
2019-03-11 13:00 | 1035.078 | 6742.0693 | 6160 | 10000 | 11866.9914 | 0 | 0
2019-03-11 14:00 | 1019.6578 | 5312.7608 | 9060 | 10000 | 13353.103 | 0 | 0
2019-03-11 15:00 | 1060.4388 | 3790.331 | 9873.3333 | 10000 | 12603.2255 | 0 | 0
2019-03-11 16:00 | 1237.716 | 1134.0495 | 9060 | 10000 | 8956.3335 | 0 | 0
2019-03-11 17:00 | 1616.2522 | 22.7608 | 9060 | 10000 | 7466.5086 | 0 | 0
2019-03-11 18:00 | 1914.1059 | 0 | 4266.6667 | 10000 | 2352.5607 | 0 | 0
2019-03-11 19:00 | 2108.387 | 0 | 4266.6667 | 10000 | 2158.2797 | 0 | 0
2019-03-11 20:00 | 2167.6451 | 0 | 6160 | 10000 | 3992.3549 | 0 | 0
2019-03-11 21:00 | 1987.2862 | 0 | 9573.3333 | 10000 | 7586.0472 | 0 | 0
2019-03-11 22:00 | 1646.4861 | 0 | 9060 | 10000 | 7413.5139 | 0 | 0
2019-03-11 23:00 | 1314.3226 | 0 | 2773.3333 | 10000 | 1459.0107 | 0 | 0
2019-03-12 | 977.206 | 0 | 873.3333 | 10000 | -103.8726 | -103.8726 | 0
2019-03-12 01:00 | 849.04 | 0 | 1666.6667 | 9896.1274 | 817.6267 | 103.8726 | 0
2019-03-12 02:00 | 802.2684 | 0 | 9060 | 10000 | 8257.7316 | 0 | 0
2019-03-12 03:00 | 791.2036 | 0 | 2773.3333 | 10000 | 1982.1297 | 0 | 0
2019-03-12 04:00 | 795.8746 | 0 | 2773.3333 | 10000 | 1977.4587 | 0 | 0
2019-03-12 05:00 | 856.5381 | 0 | 6160 | 10000 | 5303.4619 | 0 | 0
2019-03-12 06:00 | 1042.0129 | 33.2511 | 1666.6667 | 10000 | 657.9049 | 0 | 0
2019-03-12 07:00 | 1272.3076 | 848.1284 | 4266.6667 | 10000 | 3842.4875 | 0 | 0
2019-03-12 08:00 | 1191.0327 | 1087.9874 | 9060 | 10000 | 8956.9547 | 0 | 0
2019-03-12 09:00 | 1084.8248 | 2023.1513 | 6160 | 10000 | 7098.3265 | 0 | 0
2019-03-12 10:00 | 1108.471 | 3332.2377 | 4266.6667 | 10000 | 6490.4334 | 0 | 0
2019-03-12 11:00 | 1092.2413 | 3283.5835 | 6160 | 10000 | 8351.3422 | 0 | 0
2019-03-12 12:00 | 1063.7614 | 2671.2947 | 4266.6667 | 10000 | 5874.2 | 0 | 0
2019-03-12 13:00 | 1026.353 | 3177.128 | 4266.6667 | 10000 | 6417.4416 | 0 | 0
2019-03-12 14:00 | 1013.6932 | 1849.6393 | 9060 | 10000 | 9895.9461 | 0 | 0
2019-03-12 15:00 | 1056.2169 | 1040.9731 | 7873.3333 | 10000 | 7858.0895 | 0 | 0
2019-03-12 16:00 | 1237.8388 | 280.3171 | 7873.3333 | 10000 | 6915.8117 | 0 | 0
2019-03-12 17:00 | 1620.9005 | 0 | 4266.6667 | 10000 | 2645.7661 | 0 | 0
2019-03-12 18:00 | 1916.084 | 0 | 6160 | 10000 | 4243.916 | 0 | 0
2019-03-12 19:00 | 2111.903 | 0 | 6160 | 10000 | 4048.097 | 0 | 0
2019-03-12 20:00 | 2162.2229 | 0 | 4266.6667 | 10000 | 2104.4438 | 0 | 0
2019-03-12 21:00 | 1982.7296 | 0 | 2773.3333 | 10000 | 790.6037 | 0 | 0
2019-03-12 22:00 | 1636.9628 | 0 | 2773.3333 | 10000 | 1136.3706 | 0 | 0
2019-03-12 23:00 | 1300.5828 | 0 | 6160 | 10000 | 4859.4172 | 0 | 0
2019-03-13 | 948.2416 | 0 | 6160 | 10000 | 5211.7584 | 0 | 0
2019-03-13 01:00 | 825.6764 | 0 | 2773.3333 | 10000 | 1947.6569 | 0 | 0
2019-03-13 02:00 | 773.4204 | 0 | 4266.6667 | 10000 | 3493.2462 | 0 | 0
2019-03-13 03:00 | 770.053 | 0 | 2773.3333 | 10000 | 2003.2803 | 0 | 0
2019-03-13 04:00 | 768.7212 | 0 | 1666.6667 | 10000 | 897.9455 | 0 | 0
2019-03-13 05:00 | 822.3041 | 0 | 4266.6667 | 10000 | 3444.3625 | 0 | 0
2019-03-13 06:00 | 986.1657 | 511.206 | 4266.6667 | 10000 | 3791.707 | 0 | 0
2019-03-13 07:00 | 1213.6426 | 2820.605 | 2773.3333 | 10000 | 4380.2957 | 0 | 0
2019-03-13 08:00 | 1108.3834 | 4100.0593 | 2773.3333 | 10000 | 5765.0093 | 0 | 0
2019-03-13 09:00 | 985.221 | 5503.7942 | 873.3333 | 10000 | 5391.9065 | 0 | 0
2019-03-13 10:00 | 979.6857 | 6490.0388 | 286.6667 | 10000 | 5797.0198 | 0 | 0
2019-03-13 11:00 | 956.4655 | 7537.5554 | 0 | 10000 | 6581.0899 | 0 | 0
2019-03-13 12:00 | 923.9331 | 8110.6441 | 0 | 10000 | 7186.711 | 0 | 0
2019-03-13 13:00 | 908.2583 | 7468.5416 | 0 | 10000 | 6560.2833 | 0 | 0
2019-03-13 14:00 | 895.6154 | 6224.8982 | 0 | 10000 | 5329.2829 | 0 | 0
2019-03-13 15:00 | 945.3883 | 4415.6815 | 4266.6667 | 10000 | 7736.9598 | 0 | 0
2019-03-13 16:00 | 1128.6567 | 2157.4931 | 4266.6667 | 10000 | 5295.5031 | 0 | 0
2019-03-13 17:00 | 1501.9692 | 252.686 | 2773.3333 | 10000 | 1524.0502 | 0 | 0
2019-03-13 18:00 | 1817.3965 | 0 | 873.3333 | 10000 | -944.0631 | -944.0631 | 0
2019-03-13 19:00 | 2014.8473 | 0 | 873.3333 | 9055.9369 | -1141.514 | -1141.514 | 0
2019-03-13 20:00 | 2080.4764 | 0 | 873.3333 | 7914.4229 | -1207.1431 | -1207.1431 | 0
2019-03-13 21:00 | 1904.4634 | 0 | 873.3333 | 6707.2798 | -1031.1301 | -1031.1301 | 0
2019-03-13 22:00 | 1571.2993 | 0 | 873.3333 | 5676.1497 | -697.966 | -697.966 | 0
2019-03-13 23:00 | 1251.965 | 0 | 286.6667 | 4978.1838 | -965.2983 | -965.2983 | 0
2019-03-14 | 915.6857 | 0 | 286.6667 | 4012.8855 | -629.019 | -629.019 | 0
2019-03-14 01:00 | 797.5291 | 0 | 286.6667 | 3383.8664 | -510.8624 | -510.8624 | 0
2019-03-14 02:00 | 747.6673 | 0 | 286.6667 | 2873.004 | -461.0006 | -461.0006 | 0
2019-03-14 03:00 | 746.3524 | 0 | 873.3333 | 2412.0034 | 126.981 | 126.981 | 0
2019-03-14 04:00 | 753.8149 | 0 | 286.6667 | 2538.9844 | -467.1482 | -467.1482 | 0
2019-03-14 05:00 | 820.1023 | 0 | 2773.3333 | 2071.8362 | 1953.231 | 1953.231 | 0
2019-03-14 06:00 | 1007.658 | 127.7811 | 6160 | 4025.0672 | 5280.1231 | 5280.1231 | 0
2019-03-14 07:00 | 1238.9668 | 743.13 | 7873.3333 | 9305.1902 | 7377.4965 | 694.8098 | 0
2019-03-14 08:00 | 1139.5429 | 2211.1372 | 10000 | 10000 | 11071.5943 | 0 | 0
2019-03-14 09:00 | 1026.6524 | 4011.2874 | 10000 | 10000 | 12984.635 | 0 | 0
2019-03-14 10:00 | 1054.64 | 7053.4192 | 10000 | 10000 | 15998.7792 | 0 | 0
2019-03-14 11:00 | 1056.2858 | 4105.684 | 10000 | 10000 | 13049.3982 | 0 | 0
2019-03-14 12:00 | 1023.1751 | 6210.629 | 10000 | 10000 | 15187.4539 | 0 | 0
2019-03-14 13:00 | 1012.2371 | 5643.1385 | 10000 | 10000 | 14630.9014 | 0 | 0
2019-03-14 14:00 | 1016.9915 | 5030.3081 | 10000 | 10000 | 14013.3166 | 0 | 0
2019-03-14 15:00 | 1075.9817 | 3604.4944 | 10000 | 10000 | 12528.5128 | 0 | 0
2019-03-14 16:00 | 1266.2266 | 1274.9348 | 10000 | 10000 | 10008.7083 | 0 | 0
2019-03-14 17:00 | 1652.9441 | 107.4261 | 10000 | 10000 | 8454.482 | 0 | 0
2019-03-14 18:00 | 1958.7169 | 0 | 4266.6667 | 10000 | 2307.9497 | 0 | 0
2019-03-14 19:00 | 2165.9949 | 0 | 873.3333 | 10000 | -1292.6615 | -1292.6615 | 0
2019-03-14 20:00 | 2231.481 | 0 | 10000 | 8707.3385 | 7768.519 | 1292.6615 | 0
2019-03-14 21:00 | 2049.6413 | 0 | 9573.3333 | 10000 | 7523.692 | 0 | 0
2019-03-14 22:00 | 1708.2892 | 0 | 9573.3333 | 10000 | 7865.0441 | 0 | 0
2019-03-14 23:00 | 1384.1291 | 0 | 9060 | 10000 | 7675.8709 | 0 | 0
2019-03-15 | 1059.7507 | 0 | 9060 | 10000 | 8000.2493 | 0 | 0
2019-03-15 01:00 | 929.8903 | 0 | 9573.3333 | 10000 | 8643.4431 | 0 | 0
2019-03-15 02:00 | 857.4676 | 0 | 6160 | 10000 | 5302.5324 | 0 | 0
2019-03-15 03:00 | 842.5747 | 0 | 6160 | 10000 | 5317.4253 | 0 | 0
2019-03-15 04:00 | 833.0251 | 0 | 6160 | 10000 | 5326.9749 | 0 | 0
2019-03-15 05:00 | 881.9376 | 0 | 6160 | 10000 | 5278.0624 | 0 | 0
2019-03-15 06:00 | 1045.4082 | 630.9383 | 6160 | 10000 | 5745.5301 | 0 | 0
2019-03-15 07:00 | 1257.3842 | 2519.8386 | 7873.3333 | 10000 | 9135.7877 | 0 | 0
2019-03-15 08:00 | 1149.0777 | 3805.3787 | 4266.6667 | 10000 | 6922.9677 | 0 | 0
2019-03-15 09:00 | 1021.3553 | 4957.7845 | 6160 | 10000 | 10096.4293 | 0 | 0
2019-03-15 10:00 | 1022.0488 | 5139.8951 | 6160 | 10000 | 10277.8463 | 0 | 0
2019-03-15 11:00 | 989.7649 | 7271.3131 | 9060 | 10000 | 15341.5483 | 0 | 0
2019-03-15 12:00 | 945.0784 | 6936.3561 | 7873.3333 | 10000 | 13864.611 | 0 | 0
2019-03-15 13:00 | 902.5971 | 4507.6239 | 6160 | 10000 | 9765.0268 | 0 | 0
2019-03-15 14:00 | 890.0037 | 6444.3803 | 7873.3333 | 10000 | 13427.71 | 0 | 0
2019-03-15 15:00 | 937.9468 | 4480.6289 | 6160 | 10000 | 9702.682 | 0 | 0
2019-03-15 16:00 | 1120.2881 | 2207.8827 | 6160 | 10000 | 7247.5946 | 0 | 0
2019-03-15 17:00 | 1497.211 | 229.931 | 9573.3333 | 10000 | 8306.0533 | 0 | 0
2019-03-15 18:00 | 1813.704 | 0 | 7873.3333 | 10000 | 6059.6293 | 0 | 0
2019-03-15 19:00 | 2019.8364 | 0 | 7873.3333 | 10000 | 5853.4969 | 0 | 0
2019-03-15 20:00 | 2076.4359 | 0 | 6160 | 10000 | 4083.5641 | 0 | 0
2019-03-15 21:00 | 1896.6327 | 0 | 9573.3333 | 10000 | 7676.7006 | 0 | 0
2019-03-15 22:00 | 1566.2489 | 0 | 9573.3333 | 10000 | 8007.0844 | 0 | 0
2019-03-15 23:00 | 1249.29 | 0 | 9060 | 10000 | 7810.71 | 0 | 0
2019-03-16 | 917.262 | 0 | 6160 | 10000 | 5242.738 | 0 | 0
2019-03-16 01:00 | 794.7957 | 0 | 4266.6667 | 10000 | 3471.871 | 0 | 0
2019-03-16 02:00 | 739.8903 | 0 | 6160 | 10000 | 5420.1097 | 0 | 0
2019-03-16 03:00 | 733.3201 | 0 | 2773.3333 | 10000 | 2040.0133 | 0 | 0
2019-03-16 04:00 | 736.023 | 0 | 4266.6667 | 10000 | 3530.6437 | 0 | 0
2019-03-16 05:00 | 797.5294 | 0 | 6160 | 10000 | 5362.4706 | 0 | 0
2019-03-16 06:00 | 977.1413 | 671.7173 | 6160 | 10000 | 5854.576 | 0 | 0
2019-03-16 07:00 | 1194.7385 | 3057.965 | 7873.3333 | 10000 | 9736.5598 | 0 | 0
2019-03-16 08:00 | 1107.1403 | 5372.2503 | 9060 | 10000 | 13325.11 | 0 | 0
2019-03-16 09:00 | 1002.5785 | 5486.0566 | 6160 | 10000 | 10643.4781 | 0 | 0
2019-03-16 10:00 | 1017.6289 | 5493.9076 | 4266.6667 | 10000 | 8742.9454 | 0 | 0
2019-03-16 11:00 | 1001.3811 | 5876.3171 | 4266.6667 | 10000 | 9141.6027 | 0 | 0
2019-03-16 12:00 | 978.5911 | 5995.3019 | 4266.6667 | 10000 | 9283.3775 | 0 | 0
2019-03-16 13:00 | 959.5756 | 5508.3425 | 7873.3333 | 10000 | 12422.1001 | 0 | 0
2019-03-16 14:00 | 959.4418 | 4687.4563 | 9573.3333 | 10000 | 13301.3479 | 0 | 0
2019-03-16 15:00 | 1004.9333 | 4670.6709 | 6160 | 10000 | 9825.7377 | 0 | 0
2019-03-16 16:00 | 1194.9671 | 2351.1612 | 6160 | 10000 | 7316.1941 | 0 | 0
2019-03-16 17:00 | 1600.9058 | 321.3203 | 2773.3333 | 10000 | 1493.7479 | 0 | 0
2019-03-16 18:00 | 1898.4355 | 0 | 873.3333 | 10000 | -1025.1022 | -1025.1022 | 0
2019-03-16 19:00 | 2098.0949 | 0 | 2773.3333 | 8974.8978 | 675.2384 | 675.2384 | 0
2019-03-16 20:00 | 2165.8233 | 0 | 1666.6667 | 9650.1363 | -499.1566 | -499.1566 | 0
2019-03-16 21:00 | 1989.0578 | 0 | 2773.3333 | 9150.9797 | 784.2755 | 784.2755 | 0
2019-03-16 22:00 | 1662.7364 | 0 | 1666.6667 | 9935.2552 | 3.9303 | 3.9303 | 0
2019-03-16 23:00 | 1350.0791 | 0 | 286.6667 | 9939.1854 | -1063.4124 | -1063.4124 | 0
2019-03-17 | 1020.8884 | 0 | 0 | 8875.773 | -1020.8884 | -1020.8884 | 0
2019-03-17 01:00 | 904.7743 | 0 | 0 | 7854.8846 | -904.7743 | -904.7743 | 0
2019-03-17 02:00 | 859.5447 | 0 | 2773.3333 | 6950.1104 | 1913.7886 | 1913.7886 | 0
2019-03-17 03:00 | 865.5476 | 0 | 873.3333 | 8863.899 | 7.7857 | 7.7857 | 0
2019-03-17 04:00 | 857.3537 | 0 | 1666.6667 | 8871.6847 | 809.3129 | 809.3129 | 0
2019-03-17 05:00 | 926.3649 | 0 | 873.3333 | 9680.9977 | -53.0316 | -53.0316 | 0
2019-03-17 06:00 | 1094.5528 | 710.0778 | 1666.6667 | 9627.9661 | 1282.1917 | 372.0339 | 0
2019-03-17 07:00 | 1324.2701 | 3167.5784 | 2773.3333 | 10000 | 4616.6417 | 0 | 0
2019-03-17 08:00 | 1226.4185 | 5520.6267 | 2773.3333 | 10000 | 7067.5416 | 0 | 0
2019-03-17 09:00 | 1101.523 | 7310.3499 | 2773.3333 | 10000 | 8982.1602 | 0 | 0
2019-03-17 10:00 | 1103.388 | 8452.4344 | 2773.3333 | 10000 | 10122.3797 | 0 | 0
2019-03-17 11:00 | 1067.5411 | 8991.8098 | 2773.3333 | 10000 | 10697.602 | 0 | 0
2019-03-17 12:00 | 1028.0108 | 7947.8788 | 4266.6667 | 10000 | 11186.5347 | 0 | 0
2019-03-17 13:00 | 988.9534 | 7441.6132 | 2773.3333 | 10000 | 9225.9932 | 0 | 0
2019-03-17 14:00 | 972.8359 | 6336.7024 | 2773.3333 | 10000 | 8137.1999 | 0 | 0
2019-03-17 15:00 | 1021.9649 | 4995.9358 | 286.6667 | 10000 | 4260.6376 | 0 | 0
2019-03-17 16:00 | 1203.7938 | 2514.5359 | 286.6667 | 10000 | 1597.4089 | 0 | 0
2019-03-17 17:00 | 1577.1257 | 360.9493 | 873.3333 | 10000 | -342.8431 | -342.8431 | 0
2019-03-17 18:00 | 1878.561 | 0 | 286.6667 | 9657.1569 | -1591.8943 | -1591.8943 | 0
2019-03-17 19:00 | 2082.2691 | 0 | 286.6667 | 8065.2627 | -1795.6024 | -1795.6024 | 0
2019-03-17 20:00 | 2146.9907 | 0 | 0 | 6269.6602 | -2146.9907 | -2146.9907 | 0
2019-03-17 21:00 | 1996.2877 | 0 | 286.6667 | 4122.6695 | -1709.621 | -1709.621 | 0
2019-03-17 22:00 | 1675.1161 | 0 | 0 | 2413.0484 | -1675.1161 | -1675.1161 | 0
2019-03-17 23:00 | 1363.4214 | 0 | 0 | 737.9323 | -1363.4214 | -737.9323 | -625.4891
2019-03-18 | 1060.0389 | 0 | 0 | 0 | -1060.0389 | 0 | -1685.528
2019-03-18 01:00 | 931.5217 | 0 | 0 | 0 | -931.5217 | 0 | -2617.0497
2019-03-18 02:00 | 887.1331 | 0 | 873.3333 | 0 | -13.7997 | 0 | -2630.8494
2019-03-18 03:00 | 888.3453 | 0 | 873.3333 | 0 | -15.012 | 0 | -2645.8614
2019-03-18 04:00 | 894.0201 | 0 | 873.3333 | 0 | -20.6868 | 0 | -2666.5481
2019-03-18 05:00 | 961.6114 | 0 | 873.3333 | 0 | -88.278 | 0 | -2754.8262
2019-03-18 06:00 | 1142.2809 | 794.3326 | 286.6667 | 0 | -61.2816 | 0 | -2816.1078
2019-03-18 07:00 | 1363.0656 | 2403.27 | 1666.6667 | 0 | 2706.8711 | 2706.8711 | -109.2367
2019-03-18 08:00 | 1278.2613 | 4387.9779 | 873.3333 | 2706.8711 | 3983.05 | 3983.05 | 0
2019-03-18 09:00 | 1160.0161 | 6276.4021 | 4266.6667 | 6689.9211 | 9383.0527 | 3310.0789 | 0
2019-03-18 10:00 | 1163.7823 | 7258.9334 | 2773.3333 | 10000 | 8868.4844 | 0 | 0
2019-03-18 11:00 | 1138.625 | 7848.7063 | 2773.3333 | 10000 | 9483.4146 | 0 | 0
2019-03-18 12:00 | 1096.0744 | 7150.7816 | 2773.3333 | 10000 | 8828.0406 | 0 | 0
2019-03-18 13:00 | 1040.5219 | 6860.5964 | 2773.3333 | 10000 | 8593.4078 | 0 | 0
2019-03-18 14:00 | 1028.8599 | 4568.9408 | 2773.3333 | 10000 | 6313.4142 | 0 | 0
2019-03-18 15:00 | 1084.3014 | 2441.3085 | 2773.3333 | 10000 | 4130.3405 | 0 | 0
2019-03-18 16:00 | 1267.2466 | 932.7236 | 2773.3333 | 10000 | 2438.8104 | 0 | 0
2019-03-18 17:00 | 1649.6602 | 96.9565 | 1666.6667 | 10000 | 113.963 | 0 | 0
2019-03-18 18:00 | 1953.2845 | 0 | 873.3333 | 10000 | -1079.9512 | -1079.9512 | 0
2019-03-18 19:00 | 2153.5997 | 0 | 1666.6667 | 8920.0488 | -486.933 | -486.933 | 0
2019-03-18 20:00 | 2206.1672 | 0 | 2773.3333 | 8433.1158 | 567.1661 | 567.1661 | 0
2019-03-18 21:00 | 2029.7497 | 0 | 4266.6667 | 9000.2819 | 2236.9169 | 999.7181 | 0
2019-03-18 22:00 | 1688.7791 | 0 | 2773.3333 | 10000 | 1084.5542 | 0 | 0
2019-03-18 23:00 | 1358.9055 | 0 | 6160 | 10000 | 4801.0945 | 0 | 0
2019-03-19 | 1015.146 | 0 | 6160 | 10000 | 5144.854 | 0 | 0
2019-03-19 01:00 | 891.862 | 0 | 6160 | 10000 | 5268.138 | 0 | 0
2019-03-19 02:00 | 845.2414 | 0 | 4266.6667 | 10000 | 3421.4253 | 0 | 0
2019-03-19 03:00 | 836.3199 | 0 | 2773.3333 | 10000 | 1937.0134 | 0 | 0
2019-03-19 04:00 | 842.172 | 0 | 2773.3333 | 10000 | 1931.1613 | 0 | 0
2019-03-19 05:00 | 906.4427 | 0 | 2773.3333 | 10000 | 1866.8906 | 0 | 0
2019-03-19 06:00 | 1099.1507 | 24.2535 | 2773.3333 | 10000 | 1698.4361 | 0 | 0
2019-03-19 07:00 | 1318.9393 | 697.2611 | 1666.6667 | 10000 | 1044.9885 | 0 | 0
2019-03-19 08:00 | 1227.0499 | 1192.1314 | 2773.3333 | 10000 | 2738.4148 | 0 | 0
2019-03-19 09:00 | 1117.874 | 1591.6667 | 6160 | 10000 | 6633.7927 | 0 | 0
2019-03-19 10:00 | 1136.4993 | 3666.9141 | 9060 | 10000 | 11590.4149 | 0 | 0
2019-03-19 11:00 | 1094.0341 | 4215.126 | 9060 | 10000 | 12181.092 | 0 | 0
2019-03-19 12:00 | 1062.0787 | 1739.7925 | 9873.3333 | 10000 | 10551.047 | 0 | 0
2019-03-19 13:00 | 1019.5414 | 2354.6146 | 9873.3333 | 10000 | 11208.4066 | 0 | 0
2019-03-19 14:00 | 1010.9249 | 1852.9984 | 9573.3333 | 10000 | 10415.4069 | 0 | 0
2019-03-19 15:00 | 1063.8899 | 4735.4976 | 6160 | 10000 | 9831.6077 | 0 | 0
2019-03-19 16:00 | 1247.7521 | 2337.3485 | 4266.6667 | 10000 | 5356.2631 | 0 | 0
2019-03-19 17:00 | 1649.1156 | 330.5169 | 4266.6667 | 10000 | 2948.068 | 0 | 0
2019-03-19 18:00 | 1950.5764 | 0 | 2773.3333 | 10000 | 822.7569 | 0 | 0
2019-03-19 19:00 | 2148.2131 | 0 | 2773.3333 | 10000 | 625.1202 | 0 | 0
2019-03-19 20:00 | 2212.0713 | 0 | 1666.6667 | 10000 | -545.4047 | -545.4047 | 0
2019-03-19 21:00 | 2027.8258 | 0 | 873.3333 | 9454.5953 | -1154.4925 | -1154.4925 | 0
2019-03-19 22:00 | 1683.7571 | 0 | 1666.6667 | 8300.1028 | -17.0904 | -17.0904 | 0
2019-03-19 23:00 | 1348.6299 | 0 | 2773.3333 | 8283.0124 | 1424.7034 | 1424.7034 | 0
2019-03-20 | 995.6487 | 0 | 1666.6667 | 9707.7158 | 671.018 | 292.2842 | 0
2019-03-20 01:00 | 867.5482 | 0 | 1666.6667 | 10000 | 799.1184 | 0 | 0
2019-03-20 02:00 | 813.5351 | 0 | 1666.6667 | 10000 | 853.1316 | 0 | 0
2019-03-20 03:00 | 808.2069 | 0 | 2773.3333 | 10000 | 1965.1265 | 0 | 0
2019-03-20 04:00 | 809.6224 | 0 | 2773.3333 | 10000 | 1963.7109 | 0 | 0
2019-03-20 05:00 | 871.0616 | 0 | 2773.3333 | 10000 | 1902.2717 | 0 | 0
2019-03-20 06:00 | 1046.9767 | 838.2281 | 2773.3333 | 10000 | 2564.5847 | 0 | 0
2019-03-20 07:00 | 1257.2996 | 3342.3657 | 2773.3333 | 10000 | 4858.3995 | 0 | 0
2019-03-20 08:00 | 1150.6901 | 5824.1727 | 6160 | 10000 | 10833.4826 | 0 | 0
2019-03-20 09:00 | 1051.9473 | 7707.7266 | 9060 | 10000 | 15715.7794 | 0 | 0
2019-03-20 10:00 | 1077.5196 | 6970.4962 | 6160 | 10000 | 12052.9765 | 0 | 0
2019-03-20 11:00 | 1046.0568 | 7338.2247 | 2773.3333 | 10000 | 9065.5012 | 0 | 0
2019-03-20 12:00 | 1010.8908 | 7412.5814 | 873.3333 | 10000 | 7275.024 | 0 | 0
2019-03-20 13:00 | 988.0966 | 8568.1336 | 1666.6667 | 10000 | 9246.7037 | 0 | 0
2019-03-20 14:00 | 990.503 | 7167.3577 | 2773.3333 | 10000 | 8950.1881 | 0 | 0
2019-03-20 15:00 | 1041.3068 | 5103.1917 | 873.3333 | 10000 | 4935.2182 | 0 | 0
2019-03-20 16:00 | 1219.3384 | 2602.4638 | 873.3333 | 10000 | 2256.4588 | 0 | 0
2019-03-20 17:00 | 1611.3037 | 415.9665 | 0 | 10000 | -1195.3372 | -1195.3372 | 0
2019-03-20 18:00 | 1908.7673 | 0 | 0 | 8804.6628 | -1908.7673 | -1908.7673 | 0
2019-03-20 19:00 | 2106.1378 | 0 | 0 | 6895.8954 | -2106.1378 | -2106.1378 | 0
2019-03-20 20:00 | 2155.4284 | 0 | 0 | 4789.7576 | -2155.4284 | -2155.4284 | 0
2019-03-20 21:00 | 1968.6715 | 0 | 0 | 2634.3292 | -1968.6715 | -1968.6715 | 0
2019-03-20 22:00 | 1634.9584 | 0 | 286.6667 | 665.6577 | -1348.2918 | -665.6577 | -682.634
2019-03-20 23:00 | 1316.2307 | 0 | 873.3333 | 0 | -442.8974 | 0 | -1125.5314
2019-03-21 | 977.9913 | 0 | 873.3333 | 0 | -104.6579 | 0 | -1230.1893
2019-03-21 01:00 | 851.1498 | 0 | 286.6667 | 0 | -564.4831 | 0 | -1794.6724
2019-03-21 02:00 | 800.8412 | 0 | 873.3333 | 0 | 72.4921 | 72.4921 | -1722.1803
2019-03-21 03:00 | 789.7089 | 0 | 873.3333 | 72.4921 | 83.6245 | 83.6245 | -1566.0638
2019-03-21 04:00 | 786.7125 | 0 | 286.6667 | 156.1166 | -500.0459 | -156.1166 | -1909.9931
2019-03-21 05:00 | 848.6543 | 0 | 286.6667 | 0 | -561.9876 | 0 | -2471.9807
2019-03-21 06:00 | 1013.2574 | 821.5324 | 286.6667 | 0 | 94.9417 | 94.9417 | -2377.039
2019-03-21 07:00 | 1249.6563 | 551.9126 | 286.6667 | 94.9417 | -411.077 | -94.9417 | -2693.1744
2019-03-21 08:00 | 1167.5696 | 3950.8848 | 286.6667 | 0 | 3069.9819 | 3069.9819 | 0
2019-03-21 09:00 | 1063.528 | 5298.1064 | 0 | 3069.9819 | 4234.5783 | 4234.5783 | 0
2019-03-21 10:00 | 1096.9881 | 3030.7606 | 286.6667 | 7304.5602 | 2220.4392 | 2220.4392 | 0
2019-03-21 11:00 | 1079.7409 | 5360.4363 | 286.6667 | 9524.9994 | 4567.3621 | 475.0006 | 0
2019-03-21 12:00 | 1055.8066 | 3156.9662 | 286.6667 | 10000 | 2387.8263 | 0 | 0
2019-03-21 13:00 | 1018.6513 | 4702.9664 | 286.6667 | 10000 | 3970.9818 | 0 | 0
2019-03-21 14:00 | 1006.8018 | 4820.7356 | 286.6667 | 10000 | 4100.6004 | 0 | 0
2019-03-21 15:00 | 1038.2282 | 1926.0051 | 0 | 10000 | 887.7768 | 0 | 0
2019-03-21 16:00 | 1213.017 | 421.9649 | 0 | 10000 | -791.0521 | -791.0521 | 0
2019-03-21 17:00 | 1597.5238 | 35.0255 | 873.3333 | 9208.9479 | -689.1649 | -689.1649 | 0
2019-03-21 18:00 | 1888.9117 | 0 | 4266.6667 | 8519.783 | 2377.755 | 1480.217 | 0
2019-03-21 19:00 | 2085.808 | 0 | 1666.6667 | 10000 | -419.1413 | -419.1413 | 0
2019-03-21 20:00 | 2137.825 | 0 | 2773.3333 | 9580.8587 | 635.5084 | 419.1413 | 0
2019-03-21 21:00 | 1952.5193 | 0 | 2773.3333 | 10000 | 820.814 | 0 | 0
2019-03-21 22:00 | 1611.1544 | 0 | 1666.6667 | 10000 | 55.5123 | 0 | 0
2019-03-21 23:00 | 1289.6365 | 0 | 1666.6667 | 10000 | 377.0301 | 0 | 0
2019-03-22 | 950.7928 | 0 | 286.6667 | 10000 | -664.1262 | -664.1262 | 0
2019-03-22 01:00 | 825.6078 | 0 | 0 | 9335.8738 | -825.6078 | -825.6078 | 0
2019-03-22 02:00 | 772.244 | 0 | 6160 | 8510.2661 | 5387.756 | 1489.7339 | 0
2019-03-22 03:00 | 762.9543 | 0 | 1666.6667 | 10000 | 903.7124 | 0 | 0
2019-03-22 04:00 | 765.939 | 0 | 4266.6667 | 10000 | 3500.7276 | 0 | 0
2019-03-22 05:00 | 829.7488 | 0 | 4266.6667 | 10000 | 3436.9179 | 0 | 0
2019-03-22 06:00 | 1011.4199 | 923.3798 | 4266.6667 | 10000 | 4178.6266 | 0 | 0
2019-03-22 07:00 | 1224.9301 | 3421.8768 | 7873.3333 | 10000 | 10070.28 | 0 | 0
2019-03-22 08:00 | 1125.8593 | 5811.5756 | 9060 | 10000 | 13745.7163 | 0 | 0
2019-03-22 09:00 | 1011.892 | 7592.8198 | 9060 | 10000 | 15640.9278 | 0 | 0
2019-03-22 10:00 | 1033.8558 | 8679.5054 | 9060 | 10000 | 16705.6496 | 0 | 0
2019-03-22 11:00 | 1012.0723 | 8198.5593 | 9060 | 10000 | 16246.487 | 0 | 0
2019-03-22 12:00 | 984.2772 | 6709.6071 | 9060 | 10000 | 14785.3299 | 0 | 0
2019-03-22 13:00 | 945.6524 | 7264.2855 | 9573.3333 | 10000 | 15891.9664 | 0 | 0
2019-03-22 14:00 | 939.4524 | 7186.9606 | 10000 | 10000 | 16247.5083 | 0 | 0
2019-03-22 15:00 | 990.2358 | 4160.2434 | 9960 | 10000 | 13130.0076 | 0 | 0
2019-03-22 16:00 | 1174.2741 | 952.6519 | 9873.3333 | 10000 | 9651.7112 | 0 | 0
2019-03-22 17:00 | 1562.9185 | 432.0711 | 9873.3333 | 10000 | 8742.4859 | 0 | 0
2019-03-22 18:00 | 1866.6302 | 0 | 9873.3333 | 10000 | 8006.7031 | 0 | 0
2019-03-22 19:00 | 2068.6548 | 0 | 9060 | 10000 | 6991.3452 | 0 | 0
2019-03-22 20:00 | 2121.8872 | 0 | 9573.3333 | 10000 | 7451.4462 | 0 | 0
2019-03-22 21:00 | 1948.5739 | 0 | 9873.3333 | 10000 | 7924.7595 | 0 | 0
2019-03-22 22:00 | 1613.4243 | 0 | 9873.3333 | 10000 | 8259.909 | 0 | 0
2019-03-22 23:00 | 1295.2049 | 0 | 9060 | 10000 | 7764.7951 | 0 | 0
2019-03-23 | 964.3729 | 0 | 7873.3333 | 10000 | 6908.9604 | 0 | 0
2019-03-23 01:00 | 843.3625 | 0 | 6160 | 10000 | 5316.6375 | 0 | 0
2019-03-23 02:00 | 789.7438 | 0 | 6160 | 10000 | 5370.2562 | 0 | 0
2019-03-23 03:00 | 775.3302 | 0 | 2773.3333 | 10000 | 1998.0031 | 0 | 0
2019-03-23 04:00 | 775.3057 | 0 | 1666.6667 | 10000 | 891.3609 | 0 | 0
2019-03-23 05:00 | 835.1767 | 0 | 2773.3333 | 10000 | 1938.1566 | 0 | 0
2019-03-23 06:00 | 1000.4187 | 984.6978 | 7873.3333 | 10000 | 7857.6124 | 0 | 0
2019-03-23 07:00 | 1228.5064 | 3581.6014 | 6160 | 10000 | 8513.095 | 0 | 0
2019-03-23 08:00 | 1135.2107 | 6021.7208 | 2773.3333 | 10000 | 7659.8435 | 0 | 0
2019-03-23 09:00 | 1025.3174 | 6921.229 | 6160 | 10000 | 12055.9116 | 0 | 0
2019-03-23 10:00 | 1050.9942 | 7828.9148 | 4266.6667 | 10000 | 11044.5873 | 0 | 0
2019-03-23 11:00 | 1024.3719 | 8448.92 | 1666.6667 | 10000 | 9091.2148 | 0 | 0
2019-03-23 12:00 | 988.9816 | 8252.3609 | 2773.3333 | 10000 | 10036.7126 | 0 | 0
2019-03-23 13:00 | 962.5336 | 7409.0463 | 2773.3333 | 10000 | 9219.846 | 0 | 0
2019-03-23 14:00 | 952.612 | 7226.3033 | 6160 | 10000 | 12433.6913 | 0 | 0
2019-03-23 15:00 | 1001.4088 | 5203.3877 | 9060 | 10000 | 13261.979 | 0 | 0
2019-03-23 16:00 | 1185.5381 | 2694.8605 | 7873.3333 | 10000 | 9382.6558 | 0 | 0
2019-03-23 17:00 | 1576.9098 | 444.4911 | 873.3333 | 10000 | -259.0853 | -259.0853 | 0
2019-03-23 18:00 | 1878.7567 | 0 | 2773.3333 | 9740.9147 | 894.5766 | 259.0853 | 0
2019-03-23 19:00 | 2079.0717 | 0 | 1666.6667 | 10000 | -412.405 | -412.405 | 0
2019-03-23 20:00 | 2133.6398 | 0 | 286.6667 | 9587.595 | -1846.9732 | -1846.9732 | 0
2019-03-23 21:00 | 1951.3866 | 0 | 0 | 7740.6218 | -1951.3866 | -1951.3866 | 0
2019-03-23 22:00 | 1619.1484 | 0 | 286.6667 | 5789.2352 | -1332.4817 | -1332.4817 | 0
2019-03-23 23:00 | 1298.661 | 0 | 873.3333 | 4456.7535 | -425.3276 | -425.3276 | 0
2019-03-24 | 961.7091 | 0 | 0 | 4031.4258 | -961.7091 | -961.7091 | 0
2019-03-24 01:00 | 836.7906 | 0 | 0 | 3069.7168 | -836.7906 | -836.7906 | 0
2019-03-24 02:00 | 786.055 | 0 | 0 | 2232.9262 | -786.055 | -786.055 | 0
2019-03-24 03:00 | 775.5322 | 0 | 0 | 1446.8712 | -775.5322 | -775.5322 | 0
2019-03-24 04:00 | 776.8709 | 0 | 0 | 671.339 | -776.8709 | -671.339 | -105.532
2019-03-24 05:00 | 839.4459 | 0 | 286.6667 | 0 | -552.7792 | 0 | -658.3112
2019-03-24 06:00 | 1017.4259 | 1023.2033 | 286.6667 | 0 | 292.4441 | 292.4441 | -365.8671
2019-03-24 07:00 | 1230.2615 | 3566.0131 | 286.6667 | 292.4441 | 2622.4183 | 2622.4183 | 0
2019-03-24 08:00 | 1125.6342 | 5978.3601 | 873.3333 | 2914.8624 | 5726.0593 | 5726.0593 | 0
2019-03-24 09:00 | 1011.5225 | 7759.5974 | 873.3333 | 8640.9216 | 7621.4082 | 1359.0784 | 0
2019-03-24 10:00 | 1023.9427 | 8553.915 | 1666.6667 | 10000 | 9196.6391 | 0 | 0
2019-03-24 11:00 | 993.9633 | 9029.9127 | 6160 | 10000 | 14195.9494 | 0 | 0
2019-03-24 12:00 | 953.4201 | 8876.6211 | 9060 | 10000 | 16983.2011 | 0 | 0
2019-03-24 13:00 | 921.9199 | 8189.2581 | 6160 | 10000 | 13427.3382 | 0 | 0
2019-03-24 14:00 | 916.2117 | 6870.882 | 873.3333 | 10000 | 6828.0036 | 0 | 0
2019-03-24 15:00 | 969.7096 | 4997.7712 | 6160 | 10000 | 10188.0616 | 0 | 0
2019-03-24 16:00 | 1154.1728 | 2659.6326 | 4266.6667 | 10000 | 5772.1265 | 0 | 0
2019-03-24 17:00 | 1546.8739 | 458.053 | 4266.6667 | 10000 | 3177.8458 | 0 | 0
2019-03-24 18:00 | 1847.0673 | 0 | 4266.6667 | 10000 | 2419.5994 | 0 | 0
2019-03-24 19:00 | 2049.8809 | 0 | 2773.3333 | 10000 | 723.4525 | 0 | 0
2019-03-24 20:00 | 2102.5977 | 0 | 873.3333 | 10000 | -1229.2643 | -1229.2643 | 0
2019-03-24 21:00 | 1921.1465 | 0 | 286.6667 | 8770.7357 | -1634.4798 | -1634.4798 | 0
2019-03-24 22:00 | 1588.5153 | 0 | 286.6667 | 7136.2559 | -1301.8486 | -1301.8486 | 0
2019-03-24 23:00 | 1265.5919 | 0 | 286.6667 | 5834.4073 | -978.9253 | -978.9253 | 0
2019-03-25 | 937.8548 | 0 | 0 | 4855.482 | -937.8548 | -937.8548 | 0
2019-03-25 01:00 | 807.9516 | 0 | 0 | 3917.6272 | -807.9516 | -807.9516 | 0
2019-03-25 02:00 | 758.8427 | 0 | 286.6667 | 3109.6757 | -472.176 | -472.176 | 0
2019-03-25 03:00 | 748.6029 | 0 | 873.3333 | 2637.4997 | 124.7304 | 124.7304 | 0
2019-03-25 04:00 | 753.4976 | 0 | 0 | 2762.23 | -753.4976 | -753.4976 | 0
2019-03-25 05:00 | 820.6931 | 0 | 0 | 2008.7324 | -820.6931 | -820.6931 | 0
2019-03-25 06:00 | 991.9259 | 896.6332 | 0 | 1188.0394 | -95.2928 | -95.2928 | 0
2019-03-25 07:00 | 1226.3258 | 3013.4358 | 286.6667 | 1092.7466 | 2073.7767 | 2073.7767 | 0
2019-03-25 08:00 | 1154.1637 | 5042.6695 | 286.6667 | 3166.5233 | 4175.1725 | 4175.1725 | 0
2019-03-25 09:00 | 1074.4664 | 5989.8198 | 873.3333 | 7341.6957 | 5788.6868 | 2658.3043 | 0
2019-03-25 10:00 | 1109.126 | 7735.598 | 286.6667 | 10000 | 6913.1388 | 0 | 0
2019-03-25 11:00 | 1110.842 | 8322.4212 | 286.6667 | 10000 | 7498.2459 | 0 | 0
2019-03-25 12:00 | 1090.9456 | 8554.8155 | 286.6667 | 10000 | 7750.5366 | 0 | 0
2019-03-25 13:00 | 1066.1611 | 7701.9134 | 286.6667 | 10000 | 6922.4189 | 0 | 0
2019-03-25 14:00 | 1052.4628 | 5777.7621 | 0 | 10000 | 4725.2993 | 0 | 0
2019-03-25 15:00 | 1094.1941 | 3550.8308 | 0 | 10000 | 2456.6367 | 0 | 0
2019-03-25 16:00 | 1270.3858 | 1233.4153 | 286.6667 | 10000 | 249.6961 | 0 | 0
2019-03-25 17:00 | 1652.4863 | 240.3097 | 0 | 10000 | -1412.1766 | -1412.1766 | 0
2019-03-25 18:00 | 1942.4946 | 0 | 286.6667 | 8587.8234 | -1655.8279 | -1655.8279 | 0
2019-03-25 19:00 | 2132.6935 | 0 | 0 | 6931.9955 | -2132.6935 | -2132.6935 | 0
2019-03-25 20:00 | 2181.7536 | 0 | 0 | 4799.302 | -2181.7536 | -2181.7536 | 0
2019-03-25 21:00 | 2001.2632 | 0 | 286.6667 | 2617.5484 | -1714.5965 | -1714.5965 | 0
2019-03-25 22:00 | 1655.5722 | 0 | 286.6667 | 902.9519 | -1368.9055 | -902.9519 | -465.9536
2019-03-25 23:00 | 1318.7131 | 0 | 873.3333 | 0 | -445.3797 | 0 | -911.3333
2019-03-26 | 978.934 | 0 | 0 | 0 | -978.934 | 0 | -1890.2673
2019-03-26 01:00 | 849.7179 | 0 | 286.6667 | 0 | -563.0513 | 0 | -2453.3186
2019-03-26 02:00 | 796.9043 | 0 | 873.3333 | 0 | 76.429 | 76.429 | -2376.8895
2019-03-26 03:00 | 780.5164 | 0 | 873.3333 | 76.429 | 92.8169 | 92.8169 | -2207.6436
2019-03-26 04:00 | 782.644 | 0 | 873.3333 | 169.2459 | 90.6893 | 90.6893 | -1947.7084
2019-03-26 05:00 | 844.9109 | 0 | 873.3333 | 259.9353 | 28.4225 | 28.4225 | -1659.3506
2019-03-26 06:00 | 1029.5957 | 169.74 | 873.3333 | 288.3577 | 13.4776 | 13.4776 | -1357.5153
2019-03-26 07:00 | 1254.7085 | 2445.9948 | 1666.6667 | 301.8353 | 2857.953 | 2857.953 | 0
2019-03-26 08:00 | 1161.2784 | 6034.5928 | 4266.6667 | 3159.7883 | 9139.981 | 6840.2117 | 0
2019-03-26 09:00 | 1058.9946 | 7551.6463 | 2773.3333 | 10000 | 9265.9851 | 0 | 0
2019-03-26 10:00 | 1060.2113 | 8604.2517 | 4266.6667 | 10000 | 11810.7071 | 0 | 0
2019-03-26 11:00 | 1040.7908 | 8962.8769 | 4266.6667 | 10000 | 12188.7528 | 0 | 0
2019-03-26 12:00 | 1007.0935 | 8850.6392 | 2773.3333 | 10000 | 10616.879 | 0 | 0
2019-03-26 13:00 | 965.5327 | 8178.2537 | 1666.6667 | 10000 | 8879.3877 | 0 | 0
2019-03-26 14:00 | 950.9031 | 6926.8375 | 2773.3333 | 10000 | 8749.2678 | 0 | 0
2019-03-26 15:00 | 985.0871 | 5021.0334 | 1666.6667 | 10000 | 5702.613 | 0 | 0
2019-03-26 16:00 | 1168.24 | 2656.9404 | 1666.6667 | 10000 | 3155.3671 | 0 | 0
2019-03-26 17:00 | 1554.0835 | 453.3116 | 873.3333 | 10000 | -227.4386 | -227.4386 | 0
2019-03-26 18:00 | 1867.1949 | 0 | 2773.3333 | 9772.5614 | 906.1384 | 227.4386 | 0
2019-03-26 19:00 | 2072.5344 | 0 | 2773.3333 | 10000 | 700.7989 | 0 | 0
2019-03-26 20:00 | 2135.0089 | 0 | 2773.3333 | 10000 | 638.3244 | 0 | 0
2019-03-26 21:00 | 1963.2123 | 0 | 1666.6667 | 10000 | -296.5456 | -296.5456 | 0
2019-03-26 22:00 | 1622.7369 | 0 | 873.3333 | 9703.4544 | -749.4036 | -749.4036 | 0
2019-03-26 23:00 | 1293.9228 | 0 | 286.6667 | 8954.0508 | -1007.2561 | -1007.2561 | 0
2019-03-27 | 948.5883 | 0 | 873.3333 | 7946.7947 | -75.255 | -75.255 | 0
2019-03-27 01:00 | 820.2894 | 0 | 873.3333 | 7871.5397 | 53.044 | 53.044 | 0
2019-03-27 02:00 | 768.4075 | 0 | 1666.6667 | 7924.5837 | 898.2592 | 898.2592 | 0
2019-03-27 03:00 | 761.2942 | 0 | 873.3333 | 8822.8429 | 112.0392 | 112.0392 | 0
2019-03-27 04:00 | 760.9382 | 0 | 1666.6667 | 8934.8821 | 905.7285 | 905.7285 | 0
2019-03-27 05:00 | 816.4041 | 0 | 873.3333 | 9840.6106 | 56.9293 | 56.9293 | 0
2019-03-27 06:00 | 991.3834 | 1101.8391 | 2773.3333 | 9897.5399 | 2883.789 | 102.4601 | 0
2019-03-27 07:00 | 1214.3566 | 3532.3446 | 2773.3333 | 10000 | 5091.3213 | 0 | 0
2019-03-27 08:00 | 1134.3102 | 5669.3482 | 873.3333 | 10000 | 5408.3713 | 0 | 0
2019-03-27 09:00 | 1037.6181 | 7234.7213 | 286.6667 | 10000 | 6483.7699 | 0 | 0
2019-03-27 10:00 | 1066.8975 | 8192.7115 | 0 | 10000 | 7125.814 | 0 | 0
2019-03-27 11:00 | 1057.1904 | 2355.4415 | 0 | 10000 | 1298.2511 | 0 | 0
2019-03-27 12:00 | 1035.7324 | 3688.6238 | 0 | 10000 | 2652.8915 | 0 | 0
2019-03-27 13:00 | 1009.4073 | 2765.359 | 286.6667 | 10000 | 2042.6183 | 0 | 0
2019-03-27 14:00 | 997.48 | 1408.5326 | 0 | 10000 | 411.0527 | 0 | 0
2019-03-27 15:00 | 1031.927 | 2400.6066 | 0 | 10000 | 1368.6796 | 0 | 0
2019-03-27 16:00 | 1201.9385 | 2552.0259 | 0 | 10000 | 1350.0874 | 0 | 0
2019-03-27 17:00 | 1577.2981 | 431.4202 | 873.3333 | 10000 | -272.5445 | -272.5445 | 0
2019-03-27 18:00 | 1873.0402 | 0 | 873.3333 | 9727.4555 | -999.7069 | -999.7069 | 0
2019-03-27 19:00 | 2063.0791 | 0 | 873.3333 | 8727.7486 | -1189.7457 | -1189.7457 | 0
2019-03-27 20:00 | 2112.6464 | 0 | 873.3333 | 7538.0029 | -1239.3131 | -1239.3131 | 0
2019-03-27 21:00 | 1930.5862 | 0 | 286.6667 | 6298.6898 | -1643.9195 | -1643.9195 | 0
2019-03-27 22:00 | 1594.9869 | 0 | 0 | 4654.7702 | -1594.9869 | -1594.9869 | 0
2019-03-27 23:00 | 1274.4882 | 0 | 0 | 3059.7834 | -1274.4882 | -1274.4882 | 0
2019-03-28 | 944.0769 | 0 | 0 | 1785.2951 | -944.0769 | -944.0769 | 0
2019-03-28 01:00 | 819.5321 | 0 | 0 | 841.2182 | -819.5321 | -819.5321 | 0
2019-03-28 02:00 | 768.7343 | 0 | 0 | 21.6862 | -768.7343 | -21.6862 | -747.0481
2019-03-28 03:00 | 764.3308 | 0 | 0 | 0 | -764.3308 | 0 | -1511.3789
2019-03-28 04:00 | 766.142 | 0 | 0 | 0 | -766.142 | 0 | -2277.5209
2019-03-28 05:00 | 829.7657 | 0 | 0 | 0 | -829.7657 | 0 | -3107.2866
2019-03-28 06:00 | 1006.701 | 343.8143 | 0 | 0 | -662.8867 | 0 | -3770.1733
2019-03-28 07:00 | 1212.9683 | 1198.4368 | 0 | 0 | -14.5314 | 0 | -3784.7047
2019-03-28 08:00 | 1117.6566 | 4409.5853 | 286.6667 | 0 | 3578.5953 | 3578.5953 | -206.1094
2019-03-28 09:00 | 1003.0719 | 3624.0237 | 0 | 3578.5953 | 2620.9518 | 2620.9518 | 0
2019-03-28 10:00 | 1019.2547 | 3087.6867 | 286.6667 | 6199.5472 | 2355.0987 | 2355.0987 | 0
2019-03-28 11:00 | 989.0261 | 2194.1563 | 286.6667 | 8554.6459 | 1491.7968 | 1445.3541 | 0
2019-03-28 12:00 | 946.9211 | 1556.3226 | 873.3333 | 10000 | 1482.7348 | 0 | 0
2019-03-28 13:00 | 912.9774 | 3013.9108 | 286.6667 | 10000 | 2387.6001 | 0 | 0
2019-03-28 14:00 | 905.178 | 1994.6474 | 286.6667 | 10000 | 1376.1361 | 0 | 0
2019-03-28 15:00 | 953.7223 | 181.2814 | 286.6667 | 10000 | -485.7742 | -485.7742 | 0
2019-03-28 16:00 | 1130.5738 | 702.5212 | 286.6667 | 9514.2258 | -141.3859 | -141.3859 | 0
2019-03-28 17:00 | 1502.5895 | 165.9507 | 286.6667 | 9372.8399 | -1049.9721 | -1049.9721 | 0
2019-03-28 18:00 | 1814.2277 | 0 | 286.6667 | 8322.8678 | -1527.5611 | -1527.5611 | 0
2019-03-28 19:00 | 2015.9971 | 0 | 0 | 6795.3067 | -2015.9971 | -2015.9971 | 0
2019-03-28 20:00 | 2072.6718 | 0 | 286.6667 | 4779.3096 | -1786.0052 | -1786.0052 | 0
2019-03-28 21:00 | 1896.8084 | 0 | 0 | 2993.3045 | -1896.8084 | -1896.8084 | 0
2019-03-28 22:00 | 1562.6397 | 0 | 286.6667 | 1096.496 | -1275.9731 | -1096.496 | -179.477
2019-03-28 23:00 | 1242.5675 | 0 | 286.6667 | 0 | -955.9008 | 0 | -1135.3778
2019-03-29 | 907.5419 | 0 | 286.6667 | 0 | -620.8752 | 0 | -1756.2531
2019-03-29 01:00 | 779.8043 | 0 | 286.6667 | 0 | -493.1376 | 0 | -2249.3906
2019-03-29 02:00 | 732.2114 | 0 | 873.3333 | 0 | 141.1219 | 141.1219 | -2108.2688
2019-03-29 03:00 | 724.0539 | 0 | 873.3333 | 141.1219 | 149.2794 | 149.2794 | -1817.8675
2019-03-29 04:00 | 724.8923 | 0 | 873.3333 | 290.4013 | 148.4411 | 148.4411 | -1379.0251
2019-03-29 05:00 | 782.5426 | 0 | 873.3333 | 438.8424 | 90.7908 | 90.7908 | -849.392
2019-03-29 06:00 | 956.7052 | 1138.8174 | 873.3333 | 529.6331 | 1055.4455 | 1055.4455 | 0
2019-03-29 07:00 | 1184.4404 | 3514.3632 | 873.3333 | 1585.0787 | 3203.2561 | 3203.2561 | 0
2019-03-29 08:00 | 1094.8933 | 4010.295 | 1666.6667 | 4788.3348 | 4582.0683 | 4582.0683 | 0
2019-03-29 09:00 | 978.5799 | 4484.0133 | 1666.6667 | 9370.403 | 5172.1 | 629.597 | 0
2019-03-29 10:00 | 970.1526 | 4713.3888 | 873.3333 | 10000 | 4616.5696 | 0 | 0
2019-03-29 11:00 | 951.5103 | 5815.1785 | 873.3333 | 10000 | 5737.0016 | 0 | 0
2019-03-29 12:00 | 900.4493 | 5463.9766 | 873.3333 | 10000 | 5436.8606 | 0 | 0
2019-03-29 13:00 | 849.1813 | 5031.0016 | 2773.3333 | 10000 | 6955.1536 | 0 | 0
2019-03-29 14:00 | 829.1612 | 4157.7985 | 4266.6667 | 10000 | 7595.304 | 0 | 0
2019-03-29 15:00 | 868.4395 | 1298.6226 | 9060 | 10000 | 9490.183 | 0 | 0
2019-03-29 16:00 | 1044.0694 | 1378.5177 | 9060 | 10000 | 9394.4482 | 0 | 0
2019-03-29 17:00 | 1395.8735 | 0 | 9060 | 10000 | 7664.1265 | 0 | 0
2019-03-29 18:00 | 1721.358 | 0 | 6160 | 10000 | 4438.642 | 0 | 0
2019-03-29 19:00 | 1924.6579 | 0 | 4266.6667 | 10000 | 2342.0088 | 0 | 0
2019-03-29 20:00 | 1979.8111 | 0 | 4266.6667 | 10000 | 2286.8556 | 0 | 0
2019-03-29 21:00 | 1800.9046 | 0 | 4266.6667 | 10000 | 2465.762 | 0 | 0
2019-03-29 22:00 | 1466.4238 | 0 | 4266.6667 | 10000 | 2800.2428 | 0 | 0
2019-03-29 23:00 | 1146.8865 | 0 | 4266.6667 | 10000 | 3119.7802 | 0 | 0
2019-03-30 | 812.5412 | 0 | 4266.6667 | 10000 | 3454.1255 | 0 | 0
2019-03-30 01:00 | 691.2593 | 0 | 1666.6667 | 10000 | 975.4073 | 0 | 0
2019-03-30 02:00 | 642.9315 | 0 | 2773.3333 | 10000 | 2130.4018 | 0 | 0
2019-03-30 03:00 | 638.148 | 0 | 2773.3333 | 10000 | 2135.1853 | 0 | 0
2019-03-30 04:00 | 642.7667 | 0 | 1666.6667 | 10000 | 1023.9 | 0 | 0
2019-03-30 05:00 | 710.0113 | 0 | 873.3333 | 10000 | 163.3221 | 0 | 0
2019-03-30 06:00 | 876.5428 | 1174.0592 | 2773.3333 | 10000 | 3070.8497 | 0 | 0
2019-03-30 07:00 | 1109.8103 | 3524.9789 | 2773.3333 | 10000 | 5188.5019 | 0 | 0
2019-03-30 08:00 | 1012.9356 | 5653.668 | 2773.3333 | 10000 | 7414.0657 | 0 | 0
2019-03-30 09:00 | 900.5339 | 7192.2253 | 873.3333 | 10000 | 7165.0248 | 0 | 0
2019-03-30 10:00 | 886.9243 | 6051.3724 | 873.3333 | 10000 | 6037.7814 | 0 | 0
2019-03-30 11:00 | 886.1634 | 6607.2065 | 1666.6667 | 10000 | 7387.7099 | 0 | 0
2019-03-30 12:00 | 864.3453 | 8437.9226 | 286.6667 | 10000 | 7860.2439 | 0 | 0
2019-03-30 13:00 | 839.3428 | 7719.0564 | 1666.6667 | 10000 | 8546.3803 | 0 | 0
2019-03-30 14:00 | 837.9684 | 6513.8771 | 1666.6667 | 10000 | 7342.5754 | 0 | 0
2019-03-30 15:00 | 890.6082 | 4737.0972 | 873.3333 | 10000 | 4719.8224 | 0 | 0
2019-03-30 16:00 | 1083.3903 | 2579.0682 | 873.3333 | 10000 | 2369.0112 | 0 | 0
2019-03-30 17:00 | 1455.9485 | 493.2591 | 1666.6667 | 10000 | 703.9773 | 0 | 0
2019-03-30 18:00 | 1778.2257 | 0 | 873.3333 | 10000 | -904.8923 | -904.8923 | 0
2019-03-30 19:00 | 1980.5517 | 0 | 873.3333 | 9095.1077 | -1107.2184 | -1107.2184 | 0
2019-03-30 20:00 | 2032.1285 | 0 | 286.6667 | 7987.8893 | -1745.4619 | -1745.4619 | 0
2019-03-30 21:00 | 1850.6813 | 0 | 286.6667 | 6242.4274 | -1564.0147 | -1564.0147 | 0
2019-03-30 22:00 | 1512.7725 | 0 | 286.6667 | 4678.4127 | -1226.1058 | -1226.1058 | 0
2019-03-30 23:00 | 1190.24 | 0 | 0 | 3452.3069 | -1190.24 | -1190.24 | 0
2019-03-31 | 854.8861 | 0 | 0 | 2262.0669 | -854.8861 | -854.8861 | 0
2019-03-31 01:00 | 725.8337 | 0 | 0 | 1407.1808 | -725.8337 | -725.8337 | 0
2019-03-31 02:00 | 671.3775 | 0 | 0 | 681.3471 | -671.3775 | -671.3775 | 0
2019-03-31 03:00 | 666.5549 | 0 | 0 | 9.9696 | -666.5549 | -9.9696 | -656.5853
2019-03-31 04:00 | 662.8602 | 0 | 0 | 0 | -662.8602 | 0 | -1319.4455
2019-03-31 05:00 | 721.8097 | 0 | 0 | 0 | -721.8097 | 0 | -2041.2552
2019-03-31 06:00 | 893.1282 | 1232.7966 | 286.6667 | 0 | 626.335 | 626.335 | -1414.9201
2019-03-31 07:00 | 1123.2862 | 2850.8937 | 1666.6667 | 626.335 | 3394.2742 | 3394.2742 | 0
2019-03-31 08:00 | 1025.07 | 4548.2086 | 4266.6667 | 4020.6092 | 7789.8053 | 5979.3908 | 0
2019-03-31 09:00 | 929.0973 | 6112.9227 | 4266.6667 | 10000 | 9450.4921 | 0 | 0
2019-03-31 10:00 | 911.1264 | 6728.8156 | 4266.6667 | 10000 | 10084.3558 | 0 | 0
2019-03-31 11:00 | 917.2179 | 6985.0931 | 2773.3333 | 10000 | 8841.2086 | 0 | 0
2019-03-31 12:00 | 885.1141 | 6556.2086 | 1666.6667 | 10000 | 7337.7612 | 0 | 0
2019-03-31 13:00 | 844.9201 | 5612.391 | 1666.6667 | 10000 | 6434.1376 | 0 | 0
2019-03-31 14:00 | 837.613 | 4394.3018 | 873.3333 | 10000 | 4430.0222 | 0 | 0
2019-03-31 15:00 | 881.7927 | 3040.4562 | 873.3333 | 10000 | 3031.9968 | 0 | 0
2019-03-31 16:00 | 1060.7139 | 1536.745 | 1666.6667 | 10000 | 2142.6978 | 0 | 0
2019-03-31 17:00 | 1418.3876 | 192.0166 | 2773.3333 | 10000 | 1546.9624 | 0 | 0
2019-03-31 18:00 | 1759.1867 | 0 | 4266.6667 | 10000 | 2507.48 | 0 | 0
2019-03-31 19:00 | 1963.9133 | 0 | 6160 | 10000 | 4196.0867 | 0 | 0
2019-03-31 20:00 | 2022.1345 | 0 | 6160 | 10000 | 4137.8655 | 0 | 0
2019-03-31 21:00 | 1849.7816 | 0 | 9060 | 10000 | 7210.2184 | 0 | 0
2019-03-31 22:00 | 1523.0334 | 0 | 9573.3333 | 10000 | 8050.2999 | 0 | 0
2019-03-31 23:00 | 1211.0383 | 0 | 9060 | 10000 | 7848.9617 | 0 | 0
2019-04-01 | 890.3315 | 0 | 9873.3333 | 10000 | 8983.0019 | 0 | 0
2019-04-01 01:00 | 775.7832 | 0 | 9573.3333 | 10000 | 8797.5502 | 0 | 0
2019-04-01 02:00 | 729.6024 | 0 | 9873.3333 | 10000 | 9143.7309 | 0 | 0
2019-04-01 03:00 | 730.2055 | 0 | 9573.3333 | 10000 | 8843.1278 | 0 | 0
2019-04-01 04:00 | 740.7839 | 0 | 9573.3333 | 10000 | 8832.5494 | 0 | 0
2019-04-01 05:00 | 809.6262 | 0 | 9573.3333 | 10000 | 8763.7071 | 0 | 0
2019-04-01 06:00 | 992.5165 | 1217.9696 | 9573.3333 | 10000 | 9798.7865 | 0 | 0
2019-04-01 07:00 | 1253.9937 | 3535.867 | 9573.3333 | 10000 | 11855.2067 | 0 | 0
2019-04-01 08:00 | 1187.446 | 938.7646 | 9060 | 10000 | 8811.3186 | 0 | 0
2019-04-01 09:00 | 1084.8074 | 2512.5154 | 6160 | 10000 | 7587.708 | 0 | 0
2019-04-01 10:00 | 1120.8507 | 4026.7238 | 7873.3333 | 10000 | 10779.2065 | 0 | 0
2019-04-01 11:00 | 1104.0757 | 6546.5912 | 9573.3333 | 10000 | 15015.8488 | 0 | 0
2019-04-01 12:00 | 1069.4951 | 8214.2039 | 9873.3333 | 10000 | 17018.0422 | 0 | 0
2019-04-01 13:00 | 1033.6441 | 7491.2587 | 9873.3333 | 10000 | 16330.948 | 0 | 0
2019-04-01 14:00 | 1015.4021 | 6317.8205 | 9573.3333 | 10000 | 14875.7518 | 0 | 0
2019-04-01 15:00 | 1045.2219 | 4576.3376 | 9060 | 10000 | 12591.1157 | 0 | 0
2019-04-01 16:00 | 1173.3086 | 2456.5035 | 7873.3333 | 10000 | 9156.5283 | 0 | 0
2019-04-01 17:00 | 1434.4963 | 484.5249 | 2773.3333 | 10000 | 1823.3619 | 0 | 0
2019-04-01 18:00 | 1555.0798 | 0 | 2773.3333 | 10000 | 1218.2536 | 0 | 0
2019-04-01 19:00 | 1681.8952 | 0 | 2773.3333 | 10000 | 1091.4381 | 0 | 0
2019-04-01 20:00 | 1954.9647 | 0 | 2773.3333 | 10000 | 818.3686 | 0 | 0
2019-04-01 21:00 | 1983.1151 | 0 | 2773.3333 | 10000 | 790.2182 | 0 | 0
2019-04-01 22:00 | 1634.793 | 0 | 1666.6667 | 10000 | 31.8737 | 0 | 0
2019-04-01 23:00 | 1291.783 | 0 | 873.3333 | 10000 | -418.4497 | -418.4497 | 0
2019-04-02 | 817.9423 | 0 | 873.3333 | 9581.5503 | 55.391 | 55.391 | 0
2019-04-02 01:00 | 760.6067 | 0 | 286.6667 | 9636.9413 | -473.94 | -473.94 | 0
2019-04-02 02:00 | 748.5346 | 0 | 286.6667 | 9163.0013 | -461.8679 | -461.8679 | 0
2019-04-02 03:00 | 748.9497 | 0 | 286.6667 | 8701.1334 | -462.283 | -462.283 | 0
2019-04-02 04:00 | 808.5324 | 0 | 286.6667 | 8238.8504 | -521.8658 | -521.8658 | 0
2019-04-02 05:00 | 988.2949 | 0 | 0 | 7716.9847 | -988.2949 | -988.2949 | 0
2019-04-02 06:00 | 1254.8446 | 1234.4387 | 286.6667 | 6728.6897 | 266.2608 | 266.2608 | 0
2019-04-02 07:00 | 1185.2992 | 3481.8032 | 286.6667 | 6994.9505 | 2583.1707 | 2583.1707 | 0
2019-04-02 08:00 | 1084.9766 | 5506.415 | 1666.6667 | 9578.1213 | 6088.1051 | 421.8787 | 0
2019-04-02 09:00 | 1122.5757 | 6940.0648 | 6160 | 10000 | 11977.4891 | 0 | 0
2019-04-02 10:00 | 1102.7205 | 7852.8175 | 1666.6667 | 10000 | 8416.7637 | 0 | 0
2019-04-02 11:00 | 1066.9015 | 8194.5078 | 873.3333 | 10000 | 8000.9397 | 0 | 0
2019-04-02 12:00 | 1032.2675 | 8022.1435 | 1666.6667 | 10000 | 8656.5427 | 0 | 0
2019-04-02 13:00 | 1014.2118 | 7407.1879 | 873.3333 | 10000 | 7266.3094 | 0 | 0
2019-04-02 14:00 | 1042.3225 | 6307.1508 | 2773.3333 | 10000 | 8038.1617 | 0 | 0
2019-04-02 15:00 | 1169.7847 | 4614.3888 | 0 | 10000 | 3444.6041 | 0 | 0
2019-04-02 16:00 | 1426.2994 | 2471.3902 | 286.6667 | 10000 | 1331.7576 | 0 | 0
2019-04-02 17:00 | 1539.3242 | 502.1532 | 2773.3333 | 10000 | 1736.1623 | 0 | 0
2019-04-02 18:00 | 1667.09 | 0 | 873.3333 | 10000 | -793.7566 | -793.7566 | 0
2019-04-02 19:00 | 1940.7643 | 0 | 873.3333 | 9206.2434 | -1067.431 | -1067.431 | 0
2019-04-02 20:00 | 1968.88 | 0 | 286.6667 | 8138.8124 | -1682.2133 | -1682.2133 | 0
2019-04-02 21:00 | 1619.7482 | 0 | 873.3333 | 6456.5991 | -746.4148 | -746.4148 | 0
2019-04-02 22:00 | 1276.2911 | 0 | 873.3333 | 5710.1843 | -402.9578 | -402.9578 | 0
2019-04-02 23:00 | 934.691 | 0 | 286.6667 | 5307.2265 | -648.0243 | -648.0243 | 0
2019-04-03 | 807.5843 | 0 | 873.3333 | 4659.2022 | 65.749 | 65.749 | 0
2019-04-03 01:00 | 753.3187 | 0 | 286.6667 | 4724.9512 | -466.652 | -466.652 | 0
2019-04-03 02:00 | 745.1627 | 0 | 286.6667 | 4258.2992 | -458.496 | -458.496 | 0
2019-04-03 03:00 | 743.1673 | 0 | 0 | 3799.8032 | -743.1673 | -743.1673 | 0
2019-04-03 04:00 | 805.4168 | 0 | 0 | 3056.6359 | -805.4168 | -805.4168 | 0
2019-04-03 05:00 | 975.8791 | 0 | 873.3333 | 2251.2191 | -102.5458 | -102.5458 | 0
2019-04-03 06:00 | 1247.8247 | 1245.3718 | 0 | 2148.6733 | -2.4529 | -2.4529 | 0
2019-04-03 07:00 | 1158.9708 | 3422.1907 | 0 | 2146.2204 | 2263.2199 | 2263.2199 | 0
2019-04-03 08:00 | 1044.3242 | 5444.3231 | 286.6667 | 4409.4404 | 4686.6656 | 4686.6656 | 0
2019-04-03 09:00 | 1076.4912 | 6889.4924 | 873.3333 | 9096.106 | 6686.3346 | 903.894 | 0
2019-04-03 10:00 | 1071.1016 | 7819.3353 | 286.6667 | 10000 | 7034.9003 | 0 | 0
2019-04-03 11:00 | 1045.3782 | 8168.2533 | 2773.3333 | 10000 | 9896.2085 | 0 | 0
2019-04-03 12:00 | 1018.0939 | 8037.8824 | 1666.6667 | 10000 | 8686.4552 | 0 | 0
2019-04-03 13:00 | 1012.3689 | 7395.2038 | 1666.6667 | 10000 | 8049.5015 | 0 | 0
2019-04-03 14:00 | 1040.9131 | 6251.2551 | 2773.3333 | 10000 | 7983.6754 | 0 | 0
2019-04-03 15:00 | 1182.0515 | 4564.0705 | 1666.6667 | 10000 | 5048.6858 | 0 | 0
2019-04-03 16:00 | 1408.0216 | 2467.6723 | 1666.6667 | 10000 | 2726.3174 | 0 | 0
2019-04-03 17:00 | 1536.5842 | 517.8013 | 873.3333 | 10000 | -145.4496 | -145.4496 | 0
2019-04-03 18:00 | 1665.4138 | 0 | 873.3333 | 9854.5504 | -792.0805 | -792.0805 | 0
2019-04-03 19:00 | 1936.7999 | 0 | 286.6667 | 9062.47 | -1650.1332 | -1650.1332 | 0
2019-04-03 20:00 | 1959.6827 | 0 | 873.3333 | 7412.3368 | -1086.3493 | -1086.3493 | 0
2019-04-03 21:00 | 1612.0873 | 0 | 286.6667 | 6325.9874 | -1325.4207 | -1325.4207 | 0
2019-04-03 22:00 | 1272.2883 | 0 | 286.6667 | 5000.5667 | -985.6216 | -985.6216 | 0
2019-04-03 23:00 | 937.249 | 0 | 286.6667 | 4014.9451 | -650.5823 | -650.5823 | 0
2019-04-04 | 825.3243 | 0 | 873.3333 | 3364.3628 | 48.0091 | 48.0091 | 0
2019-04-04 01:00 | 771.9385 | 0 | 286.6667 | 3412.3718 | -485.2719 | -485.2719 | 0
2019-04-04 02:00 | 760.7634 | 0 | 0 | 2927.0999 | -760.7634 | -760.7634 | 0
2019-04-04 03:00 | 744.8126 | 0 | 0 | 2166.3366 | -744.8126 | -744.8126 | 0
2019-04-04 04:00 | 798.544 | 0 | 1666.6667 | 1421.524 | 868.1227 | 868.1227 | 0
2019-04-04 05:00 | 961.7831 | 0 | 7873.3333 | 2289.6467 | 6911.5503 | 6911.5503 | 0
2019-04-04 06:00 | 1208.2911 | 983.3869 | 9060 | 9201.1969 | 8835.0957 | 798.8031 | 0
2019-04-04 07:00 | 1125.5978 | 2588.5338 | 9573.3333 | 10000 | 11036.2694 | 0 | 0
2019-04-04 08:00 | 1002.0371 | 4980.351 | 9573.3333 | 10000 | 13551.6472 | 0 | 0
2019-04-04 09:00 | 1022.3031 | 6345.953 | 9873.3333 | 10000 | 15196.9832 | 0 | 0
2019-04-04 10:00 | 1018.9577 | 7463.2263 | 9573.3333 | 10000 | 16017.6019 | 0 | 0
2019-04-04 11:00 | 993.0764 | 6960.1243 | 9060 | 10000 | 15027.0479 | 0 | 0
2019-04-04 12:00 | 963.059 | 7784.2799 | 6160 | 10000 | 12981.2208 | 0 | 0
2019-04-04 13:00 | 957.3778 | 7265.1491 | 6160 | 10000 | 12467.7713 | 0 | 0
2019-04-04 14:00 | 988.012 | 6168.025 | 9060 | 10000 | 14240.013 | 0 | 0
2019-04-04 15:00 | 1114.3019 | 4542.5414 | 9060 | 10000 | 12488.2395 | 0 | 0
2019-04-04 16:00 | 1362.8962 | 2491.4278 | 6160 | 10000 | 7288.5317 | 0 | 0
2019-04-04 17:00 | 1485.6928 | 536.9258 | 9060 | 10000 | 8111.233 | 0 | 0
2019-04-04 18:00 | 1619.088 | 0 | 9060 | 10000 | 7440.912 | 0 | 0
2019-04-04 19:00 | 1890.7825 | 0 | 7873.3333 | 10000 | 5982.5508 | 0 | 0
2019-04-04 20:00 | 1921.6122 | 0 | 4266.6667 | 10000 | 2345.0544 | 0 | 0
2019-04-04 21:00 | 1583.8991 | 0 | 873.3333 | 10000 | -710.5657 | -710.5657 | 0
2019-04-04 22:00 | 1256.2565 | 0 | 1666.6667 | 9289.4343 | 410.4102 | 410.4102 | 0
2019-04-04 23:00 | 924.5783 | 0 | 1666.6667 | 9699.8444 | 742.0883 | 300.1556 | 0
2019-04-05 | 800.1032 | 0 | 873.3333 | 10000 | 73.2302 | 0 | 0
2019-04-05 01:00 | 743.1153 | 0 | 873.3333 | 10000 | 130.2181 | 0 | 0
2019-04-05 02:00 | 734.1314 | 0 | 873.3333 | 10000 | 139.2019 | 0 | 0
2019-04-05 03:00 | 731.7537 | 0 | 1666.6667 | 10000 | 934.913 | 0 | 0
2019-04-05 04:00 | 796.3801 | 0 | 1666.6667 | 10000 | 870.2866 | 0 | 0
2019-04-05 05:00 | 970.2044 | 0 | 1666.6667 | 10000 | 696.4622 | 0 | 0
2019-04-05 06:00 | 1226.1059 | 1365.5169 | 286.6667 | 10000 | 426.0777 | 0 | 0
2019-04-05 07:00 | 1133.5786 | 3589.7675 | 286.6667 | 10000 | 2742.8557 | 0 | 0
2019-04-05 08:00 | 1001.8945 | 5553.5754 | 0 | 10000 | 4551.6809 | 0 | 0
2019-04-05 09:00 | 1001.9919 | 5914.4431 | 286.6667 | 10000 | 5199.1179 | 0 | 0
2019-04-05 10:00 | 986.7214 | 7905.7888 | 286.6667 | 10000 | 7205.7341 | 0 | 0
2019-04-05 11:00 | 952.0746 | 6451.5506 | 286.6667 | 10000 | 5786.1426 | 0 | 0
2019-04-05 12:00 | 912.1892 | 4294.6957 | 873.3333 | 10000 | 4255.8398 | 0 | 0
2019-04-05 13:00 | 901.9189 | 6344.903 | 873.3333 | 10000 | 6316.3175 | 0 | 0
2019-04-05 14:00 | 929.289 | 1018.4676 | 873.3333 | 10000 | 962.512 | 0 | 0
2019-04-05 15:00 | 1058.9106 | 4660.7855 | 873.3333 | 10000 | 4475.2082 | 0 | 0
2019-04-05 16:00 | 1299.3801 | 36.7609 | 873.3333 | 10000 | -389.2859 | -389.2859 | 0
2019-04-05 17:00 | 1436.2447 | 0 | 286.6667 | 9610.7141 | -1149.5781 | -1149.5781 | 0
2019-04-05 18:00 | 1573.4119 | 0 | 0 | 8461.1361 | -1573.4119 | -1573.4119 | 0
2019-04-05 19:00 | 1851.4075 | 0 | 286.6667 | 6887.7241 | -1564.7408 | -1564.7408 | 0
2019-04-05 20:00 | 1885.2434 | 0 | 873.3333 | 5322.9833 | -1011.91 | -1011.91 | 0
2019-04-05 21:00 | 1551.0321 | 0 | 0 | 4311.0733 | -1551.0321 | -1551.0321 | 0
2019-04-05 22:00 | 1227.8414 | 0 | 0 | 2760.0413 | -1227.8414 | -1227.8414 | 0
2019-04-05 23:00 | 910.2527 | 0 | 0 | 1532.1998 | -910.2527 | -910.2527 | 0
2019-04-06 | 794.6347 | 0 | 873.3333 | 621.9471 | 78.6986 | 78.6986 | 0
2019-04-06 01:00 | 740.2601 | 0 | 873.3333 | 700.6458 | 133.0733 | 133.0733 | 0
2019-04-06 02:00 | 729.0493 | 0 | 1666.6667 | 833.719 | 937.6173 | 937.6173 | 0
2019-04-06 03:00 | 726.6772 | 0 | 873.3333 | 1771.3364 | 146.6561 | 146.6561 | 0
2019-04-06 04:00 | 784.4286 | 0 | 873.3333 | 1917.9925 | 88.9047 | 88.9047 | 0
2019-04-06 05:00 | 957.1512 | 38.8999 | 1666.6667 | 2006.8972 | 748.4154 | 748.4154 | 0
2019-04-06 06:00 | 1209.769 | 1328.1465 | 2773.3333 | 2755.3126 | 2891.7108 | 2891.7108 | 0
2019-04-06 07:00 | 1126.183 | 3535.4657 | 2773.3333 | 5647.0234 | 5182.616 | 4352.9766 | 0
2019-04-06 08:00 | 1001.7224 | 2059.4223 | 2773.3333 | 10000 | 3831.0333 | 0 | 0
2019-04-06 09:00 | 1018.031 | 453.4117 | 2773.3333 | 10000 | 2208.714 | 0 | 0
2019-04-06 10:00 | 997.4338 | 297.9144 | 4266.6667 | 10000 | 3567.1472 | 0 | 0
2019-04-06 11:00 | 966.5857 | 336.8327 | 4266.6667 | 10000 | 3636.9137 | 0 | 0
2019-04-06 12:00 | 930.7265 | 5089.5883 | 4266.6667 | 10000 | 8425.5285 | 0 | 0
2019-04-06 13:00 | 912.6396 | 561.5289 | 4266.6667 | 10000 | 3915.556 | 0 | 0
2019-04-06 14:00 | 945.6298 | 4510.2206 | 6160 | 10000 | 9724.5909 | 0 | 0
2019-04-06 15:00 | 1075.3315 | 1375.1021 | 4266.6667 | 10000 | 4566.4374 | 0 | 0
2019-04-06 16:00 | 1322.2624 | 1311.0816 | 6160 | 10000 | 6148.8192 | 0 | 0
2019-04-06 17:00 | 1449.4075 | 332.3868 | 6160 | 10000 | 5042.9793 | 0 | 0
2019-04-06 18:00 | 1581.1397 | 0 | 9060 | 10000 | 7478.8603 | 0 | 0
2019-04-06 19:00 | 1864.1126 | 0 | 9573.3333 | 10000 | 7709.2208 | 0 | 0
2019-04-06 20:00 | 1898.1071 | 0 | 286.6667 | 10000 | -1611.4404 | -1611.4404 | 0
2019-04-06 21:00 | 1563.2618 | 0 | 0 | 8388.5596 | -1563.2618 | -1563.2618 | 0
2019-04-06 22:00 | 1240.2402 | 0 | 4266.6667 | 6825.2978 | 3026.4264 | 3026.4264 | 0
2019-04-06 23:00 | 914.0772 | 0 | 6160 | 9851.7242 | 5245.9228 | 148.2758 | 0
2019-04-07 | 792.0929 | 0 | 2773.3333 | 10000 | 1981.2404 | 0 | 0
2019-04-07 01:00 | 740.4777 | 0 | 2773.3333 | 10000 | 2032.8556 | 0 | 0
2019-04-07 02:00 | 735.912 | 0 | 873.3333 | 10000 | 137.4213 | 0 | 0
2019-04-07 03:00 | 737.4341 | 0 | 873.3333 | 10000 | 135.8993 | 0 | 0
2019-04-07 04:00 | 817.6408 | 0 | 873.3333 | 10000 | 55.6925 | 0 | 0
2019-04-07 05:00 | 1010.3899 | 52.2548 | 2773.3333 | 10000 | 1815.1983 | 0 | 0
2019-04-07 06:00 | 1259.6429 | 1061.3453 | 2773.3333 | 10000 | 2575.0358 | 0 | 0
2019-04-07 07:00 | 1183.3011 | 3148.6494 | 4266.6667 | 10000 | 6232.015 | 0 | 0
2019-04-07 08:00 | 1067.6539 | 4316.295 | 7873.3333 | 10000 | 11121.9745 | 0 | 0
2019-04-07 09:00 | 1089.4345 | 5946.512 | 9060 | 10000 | 13917.0775 | 0 | 0
2019-04-07 10:00 | 1067.4814 | 6105.2764 | 9573.3333 | 10000 | 14611.1284 | 0 | 0
2019-04-07 11:00 | 1023.3109 | 7921.9992 | 6160 | 10000 | 13058.6883 | 0 | 0
2019-04-07 12:00 | 983.945 | 7682.7004 | 7873.3333 | 10000 | 14572.0886 | 0 | 0
2019-04-07 13:00 | 963.0057 | 7073.3591 | 9060 | 10000 | 15170.3534 | 0 | 0
2019-04-07 14:00 | 988.7534 | 5992.7167 | 7873.3333 | 10000 | 12877.2966 | 0 | 0
2019-04-07 15:00 | 1112.536 | 4329.8121 | 6160 | 10000 | 9377.2761 | 0 | 0
2019-04-07 16:00 | 1360.2258 | 2277.2691 | 6160 | 10000 | 7077.0433 | 0 | 0
2019-04-07 17:00 | 1474.3376 | 494.1952 | 2773.3333 | 10000 | 1793.191 | 0 | 0
2019-04-07 18:00 | 1606.4193 | 0 | 6160 | 10000 | 4553.5807 | 0 | 0
2019-04-07 19:00 | 1885.9704 | 0 | 4266.6667 | 10000 | 2380.6963 | 0 | 0
2019-04-07 20:00 | 1928.8433 | 0 | 4266.6667 | 10000 | 2337.8234 | 0 | 0
2019-04-07 21:00 | 1592.8366 | 0 | 6160 | 10000 | 4567.1634 | 0 | 0
2019-04-07 22:00 | 1272.3276 | 0 | 7873.3333 | 10000 | 6601.0057 | 0 | 0
2019-04-07 23:00 | 943.7851 | 0 | 4266.6667 | 10000 | 3322.8816 | 0 | 0
2019-04-08 | 834.0547 | 0 | 6160 | 10000 | 5325.9453 | 0 | 0
2019-04-08 01:00 | 775.7316 | 0 | 6160 | 10000 | 5384.2684 | 0 | 0
2019-04-08 02:00 | 764.7069 | 0 | 4266.6667 | 10000 | 3501.9597 | 0 | 0
2019-04-08 03:00 | 773.9559 | 0 | 4266.6667 | 10000 | 3492.7108 | 0 | 0
2019-04-08 04:00 | 839.2492 | 0 | 4266.6667 | 10000 | 3427.4175 | 0 | 0
2019-04-08 05:00 | 1019.2589 | 42.5845 | 6160 | 10000 | 5183.3256 | 0 | 0
2019-04-08 06:00 | 1286.3884 | 1350.7923 | 9060 | 10000 | 9124.4039 | 0 | 0
2019-04-08 07:00 | 1207.8025 | 3361.3545 | 9060 | 10000 | 11213.5521 | 0 | 0
2019-04-08 08:00 | 1095.8079 | 5273.9563 | 4266.6667 | 10000 | 8444.8151 | 0 | 0
2019-04-08 09:00 | 1114.6338 | 5747.447 | 7873.3333 | 10000 | 12506.1466 | 0 | 0
2019-04-08 10:00 | 1096.4232 | 7727.3318 | 9060 | 10000 | 15690.9087 | 0 | 0
2019-04-08 11:00 | 1048.4762 | 8055.7638 | 7873.3333 | 10000 | 14880.6209 | 0 | 0
2019-04-08 12:00 | 1011.7174 | 6943.9277 | 9060 | 10000 | 14992.2103 | 0 | 0
2019-04-08 13:00 | 996.8745 | 4076.3992 | 9573.3333 | 10000 | 12652.8581 | 0 | 0
2019-04-08 14:00 | 1019.5918 | 3158.9235 | 7873.3333 | 10000 | 10012.665 | 0 | 0
2019-04-08 15:00 | 1146.5235 | 1500.2026 | 6160 | 10000 | 6513.6791 | 0 | 0
2019-04-08 16:00 | 1396.8449 | 2494.5765 | 4266.6667 | 10000 | 5364.3983 | 0 | 0
2019-04-08 17:00 | 1517.0332 | 626.3107 | 2773.3333 | 10000 | 1882.6108 | 0 | 0
2019-04-08 18:00 | 1647.4027 | 0 | 873.3333 | 10000 | -774.0694 | -774.0694 | 0
2019-04-08 19:00 | 1928.1722 | 0 | 873.3333 | 9225.9306 | -1054.8389 | -1054.8389 | 0
2019-04-08 20:00 | 1958.3297 | 0 | 286.6667 | 8171.0917 | -1671.6631 | -1671.6631 | 0
2019-04-08 21:00 | 1617.7598 | 0 | 873.3333 | 6499.4287 | -744.4264 | -744.4264 | 0
2019-04-08 22:00 | 1278.7875 | 0 | 873.3333 | 5755.0022 | -405.4542 | -405.4542 | 0
2019-04-08 23:00 | 942.1852 | 0 | 873.3333 | 5349.548 | -68.8518 | -68.8518 | 0
2019-04-09 | 819.0579 | 0 | 0 | 5280.6962 | -819.0579 | -819.0579 | 0
2019-04-09 01:00 | 763.0827 | 0 | 873.3333 | 4461.6383 | 110.2507 | 110.2507 | 0
2019-04-09 02:00 | 751.7073 | 0 | 1666.6667 | 4571.889 | 914.9594 | 914.9594 | 0
2019-04-09 03:00 | 756.4582 | 0 | 873.3333 | 5486.8484 | 116.8751 | 116.8751 | 0
2019-04-09 04:00 | 818.3034 | 0 | 1666.6667 | 5603.7235 | 848.3633 | 848.3633 | 0
2019-04-09 05:00 | 998.4162 | 0 | 873.3333 | 6452.0867 | -125.0829 | -125.0829 | 0
2019-04-09 06:00 | 1260.9407 | 150.8593 | 873.3333 | 6327.0039 | -236.748 | -236.748 | 0
2019-04-09 07:00 | 1182.2474 | 189.4602 | 1666.6667 | 6090.2558 | 673.8794 | 673.8794 | 0
2019-04-09 08:00 | 1055.564 | 530.9182 | 2773.3333 | 6764.1353 | 2248.6875 | 2248.6875 | 0
2019-04-09 09:00 | 1059.2499 | 1481.967 | 2773.3333 | 9012.8228 | 3196.0505 | 987.1772 | 0
2019-04-09 10:00 | 1034.4841 | 822.8399 | 1666.6667 | 10000 | 1455.0225 | 0 | 0
2019-04-09 11:00 | 987.4489 | 947.4045 | 873.3333 | 10000 | 833.2889 | 0 | 0
2019-04-09 12:00 | 941.5076 | 878.7656 | 873.3333 | 10000 | 810.5914 | 0 | 0
2019-04-09 13:00 | 916.6237 | 533.4447 | 873.3333 | 10000 | 490.1544 | 0 | 0
2019-04-09 14:00 | 936.7577 | 897.9924 | 0 | 10000 | -38.7652 | -38.7652 | 0
2019-04-09 15:00 | 1065.802 | 798.1851 | 286.6667 | 9961.2348 | 19.0497 | 19.0497 | 0
2019-04-09 16:00 | 1303.6804 | 419.9604 | 286.6667 | 9980.2845 | -597.0533 | -597.0533 | 0
2019-04-09 17:00 | 1442.0863 | 1.932 | 286.6667 | 9383.2312 | -1153.4876 | -1153.4876 | 0
2019-04-09 18:00 | 1584.9204 | 0 | 0 | 8229.7435 | -1584.9204 | -1584.9204 | 0
2019-04-09 19:00 | 1868.482 | 0 | 0 | 6644.8231 | -1868.482 | -1868.482 | 0
2019-04-09 20:00 | 1909.207 | 0 | 2773.3333 | 4776.3411 | 864.1263 | 864.1263 | 0
2019-04-09 21:00 | 1566.8168 | 0 | 873.3333 | 5640.4674 | -693.4835 | -693.4835 | 0
2019-04-09 22:00 | 1227.4809 | 0 | 1666.6667 | 4946.984 | 439.1858 | 439.1858 | 0
2019-04-09 23:00 | 892.9352 | 0 | 1666.6667 | 5386.1697 | 773.7315 | 773.7315 | 0
2019-04-10 | 764.4979 | 0 | 2773.3333 | 6159.9012 | 2008.8354 | 2008.8354 | 0
2019-04-10 01:00 | 710.5843 | 0 | 873.3333 | 8168.7366 | 162.749 | 162.749 | 0
2019-04-10 02:00 | 702.0005 | 0 | 873.3333 | 8331.4857 | 171.3328 | 171.3328 | 0
2019-04-10 03:00 | 706.6633 | 0 | 286.6667 | 8502.8185 | -419.9967 | -419.9967 | 0
2019-04-10 04:00 | 765.1309 | 0 | 0 | 8082.8218 | -765.1309 | -765.1309 | 0
2019-04-10 05:00 | 945.5335 | 85.3081 | 0 | 7317.6909 | -860.2254 | -860.2254 | 0
2019-04-10 06:00 | 1189.1087 | 1626.8809 | 286.6667 | 6457.4655 | 724.4389 | 724.4389 | 0
2019-04-10 07:00 | 1103.4831 | 4124.3864 | 873.3333 | 7181.9044 | 3894.2367 | 2818.0956 | 0
2019-04-10 08:00 | 979.2929 | 3186.075 | 2773.3333 | 10000 | 4980.1154 | 0 | 0
2019-04-10 09:00 | 997.4369 | 7874.0833 | 6160 | 10000 | 13036.6465 | 0 | 0
2019-04-10 10:00 | 982.1153 | 3995.6589 | 4266.6667 | 10000 | 7280.2102 | 0 | 0
2019-04-10 11:00 | 945.1184 | 8982.8616 | 4266.6667 | 10000 | 12304.4099 | 0 | 0
2019-04-10 12:00 | 916.017 | 8664.583 | 6160 | 10000 | 13908.566 | 0 | 0
2019-04-10 13:00 | 895.612 | 7960.8531 | 9060 | 10000 | 16125.2412 | 0 | 0
2019-04-10 14:00 | 921.4031 | 6694.9642 | 6160 | 10000 | 11933.5611 | 0 | 0
2019-04-10 15:00 | 1049.3355 | 4940.2068 | 6160 | 10000 | 10050.8713 | 0 | 0
2019-04-10 16:00 | 1281.6363 | 2744.1013 | 4266.6667 | 10000 | 5729.1316 | 0 | 0
2019-04-10 17:00 | 1416.6551 | 631.9112 | 4266.6667 | 10000 | 3481.9228 | 0 | 0
2019-04-10 18:00 | 1543.5692 | 0 | 873.3333 | 10000 | -670.2359 | -670.2359 | 0
2019-04-10 19:00 | 1817.5354 | 0 | 873.3333 | 9329.7641 | -944.2021 | -944.2021 | 0
2019-04-10 20:00 | 1845.4249 | 0 | 873.3333 | 8385.562 | -972.0915 | -972.0915 | 0
2019-04-10 21:00 | 1515.4076 | 0 | 873.3333 | 7413.4705 | -642.0743 | -642.0743 | 0
2019-04-10 22:00 | 1192.3466 | 0 | 1666.6667 | 6771.3962 | 474.32 | 474.32 | 0
2019-04-10 23:00 | 860.3137 | 0 | 4266.6667 | 7245.7162 | 3406.3529 | 2754.2838 | 0
2019-04-11 | 736.4357 | 0 | 873.3333 | 10000 | 136.8976 | 0 | 0
2019-04-11 01:00 | 679.6358 | 0 | 873.3333 | 10000 | 193.6975 | 0 | 0
2019-04-11 02:00 | 673.7221 | 0 | 286.6667 | 10000 | -387.0555 | -387.0555 | 0
2019-04-11 03:00 | 672.7001 | 0 | 286.6667 | 9612.9445 | -386.0334 | -386.0334 | 0
2019-04-11 04:00 | 729.1384 | 0 | 873.3333 | 9226.9111 | 144.195 | 144.195 | 0
2019-04-11 05:00 | 906.5879 | 54.9286 | 2773.3333 | 9371.1061 | 1921.674 | 628.8939 | 0
2019-04-11 06:00 | 1163.7858 | 12.2256 | 2773.3333 | 10000 | 1621.7732 | 0 | 0
2019-04-11 07:00 | 1074.9982 | 933.9575 | 1666.6667 | 10000 | 1525.626 | 0 | 0
2019-04-11 08:00 | 950.6752 | 2743.1318 | 286.6667 | 10000 | 2079.1233 | 0 | 0
2019-04-11 09:00 | 963.4274 | 4734.305 | 873.3333 | 10000 | 4644.211 | 0 | 0
2019-04-11 10:00 | 958.3458 | 7719.9178 | 873.3333 | 10000 | 7634.9053 | 0 | 0
2019-04-11 11:00 | 938.6817 | 8241.5532 | 286.6667 | 10000 | 7589.5381 | 0 | 0
2019-04-11 12:00 | 911.863 | 8293.8173 | 873.3333 | 10000 | 8255.2876 | 0 | 0
2019-04-11 13:00 | 899.4267 | 7614.5859 | 1666.6667 | 10000 | 8381.8258 | 0 | 0
2019-04-11 14:00 | 930.5672 | 6530.4498 | 2773.3333 | 10000 | 8373.2159 | 0 | 0
2019-04-11 15:00 | 1060.7543 | 4833.3097 | 4266.6667 | 10000 | 8039.2221 | 0 | 0
2019-04-11 16:00 | 1313.6449 | 2697.5619 | 4266.6667 | 10000 | 5650.5837 | 0 | 0
2019-04-11 17:00 | 1443.8379 | 654.4547 | 2773.3333 | 10000 | 1983.9501 | 0 | 0
2019-04-11 18:00 | 1584.5072 | 0 | 2773.3333 | 10000 | 1188.8262 | 0 | 0
2019-04-11 19:00 | 1865.3619 | 0 | 1666.6667 | 10000 | -198.6952 | -198.6952 | 0
2019-04-11 20:00 | 1909.6381 | 0 | 1666.6667 | 9801.3048 | -242.9714 | -242.9714 | 0
2019-04-11 21:00 | 1575.3565 | 0 | 2773.3333 | 9558.3333 | 1197.9768 | 441.6667 | 0
2019-04-11 22:00 | 1251.3686 | 0 | 873.3333 | 10000 | -378.0353 | -378.0353 | 0
2019-04-11 23:00 | 931.1812 | 0 | 873.3333 | 9621.9647 | -57.8479 | -57.8479 | 0
2019-04-12 | 809.628 | 0 | 873.3333 | 9564.1169 | 63.7053 | 63.7053 | 0
2019-04-12 01:00 | 756.7098 | 0 | 286.6667 | 9627.8222 | -470.0431 | -470.0431 | 0
2019-04-12 02:00 | 749.0357 | 0 | 0 | 9157.7791 | -749.0357 | -749.0357 | 0
2019-04-12 03:00 | 756.3121 | 0 | 0 | 8408.7434 | -756.3121 | -756.3121 | 0
2019-04-12 04:00 | 822.1442 | 0 | 0 | 7652.4313 | -822.1442 | -822.1442 | 0
2019-04-12 05:00 | 995.124 | 138.5899 | 0 | 6830.2871 | -856.534 | -856.534 | 0
2019-04-12 06:00 | 1248.4378 | 1640.567 | 0 | 5973.753 | 392.1292 | 392.1292 | 0
2019-04-12 07:00 | 1158.7559 | 3987.6284 | 286.6667 | 6365.8823 | 3115.5392 | 3115.5392 | 0
2019-04-12 08:00 | 1032.5357 | 5985.3498 | 286.6667 | 9481.4215 | 5239.4808 | 518.5785 | 0
2019-04-12 09:00 | 1041.697 | 7376.5991 | 1666.6667 | 10000 | 8001.5687 | 0 | 0
2019-04-12 10:00 | 1027.0721 | 8296.9636 | 873.3333 | 10000 | 8143.2249 | 0 | 0
2019-04-12 11:00 | 986.6359 | 6817.1022 | 1666.6667 | 10000 | 7497.133 | 0 | 0
2019-04-12 12:00 | 953.0026 | 6449.3035 | 286.6667 | 10000 | 5782.9675 | 0 | 0
2019-04-12 13:00 | 930.2908 | 6281.0309 | 0 | 10000 | 5350.7401 | 0 | 0
2019-04-12 14:00 | 960.0916 | 3736.0061 | 0 | 10000 | 2775.9145 | 0 | 0
2019-04-12 15:00 | 1094.388 | 3968.5281 | 286.6667 | 10000 | 3160.8068 | 0 | 0
2019-04-12 16:00 | 1347.347 | 2738.9297 | 286.6667 | 10000 | 1678.2494 | 0 | 0
2019-04-12 17:00 | 1477.8523 | 108.6382 | 0 | 10000 | -1369.2141 | -1369.2141 | 0
2019-04-12 18:00 | 1612.9812 | 0 | 2773.3333 | 8630.7859 | 1160.3521 | 1160.3521 | 0
2019-04-12 19:00 | 1894.5635 | 0 | 2773.3333 | 9791.1381 | 878.7698 | 208.8619 | 0
2019-04-12 20:00 | 1934.3799 | 0 | 873.3333 | 10000 | -1061.0466 | -1061.0466 | 0
2019-04-12 21:00 | 1600.9903 | 0 | 2773.3333 | 8938.9534 | 1172.343 | 1061.0466 | 0
2019-04-12 22:00 | 1282.0915 | 0 | 1666.6667 | 10000 | 384.5752 | 0 | 0
2019-04-12 23:00 | 951.3503 | 0 | 4266.6667 | 10000 | 3315.3163 | 0 | 0
2019-04-13 | 833.8936 | 0 | 4266.6667 | 10000 | 3432.7731 | 0 | 0
2019-04-13 01:00 | 782.676 | 0 | 2773.3333 | 10000 | 1990.6573 | 0 | 0
2019-04-13 02:00 | 775.9778 | 0 | 286.6667 | 10000 | -489.3112 | -489.3112 | 0
2019-04-13 03:00 | 775.0705 | 0 | 286.6667 | 9510.6888 | -488.4038 | -488.4038 | 0
2019-04-13 04:00 | 840.8717 | 0 | 286.6667 | 9022.285 | -554.205 | -554.205 | 0
2019-04-13 05:00 | 1025.9018 | 160.1202 | 4266.6667 | 8468.08 | 3400.8851 | 1531.92 | 0
2019-04-13 06:00 | 1260.5475 | 1704.2218 | 4266.6667 | 10000 | 4710.3409 | 0 | 0
2019-04-13 07:00 | 1168.2697 | 3009.0911 | 2773.3333 | 10000 | 4614.1548 | 0 | 0
2019-04-13 08:00 | 1034.5384 | 4186.2254 | 1666.6667 | 10000 | 4818.3537 | 0 | 0
2019-04-13 09:00 | 1050.2107 | 5959.3517 | 1666.6667 | 10000 | 6575.8077 | 0 | 0
2019-04-13 10:00 | 1024.3371 | 6905.3705 | 1666.6667 | 10000 | 7547.7001 | 0 | 0
2019-04-13 11:00 | 981.9918 | 7192.882 | 4266.6667 | 10000 | 10477.5569 | 0 | 0
2019-04-13 12:00 | 942.8117 | 7596.1766 | 1666.6667 | 10000 | 8320.0316 | 0 | 0
2019-04-13 13:00 | 933.4642 | 7760.2287 | 1666.6667 | 10000 | 8493.4312 | 0 | 0
2019-04-13 14:00 | 966.9363 | 6559.8277 | 6160 | 10000 | 11752.8914 | 0 | 0
2019-04-13 15:00 | 1096.9981 | 4860.9407 | 4266.6667 | 10000 | 8030.6093 | 0 | 0
2019-04-13 16:00 | 1353.2592 | 2750.3124 | 4266.6667 | 10000 | 5663.7199 | 0 | 0
2019-04-13 17:00 | 1466.6127 | 691.8664 | 4266.6667 | 10000 | 3491.9204 | 0 | 0
2019-04-13 18:00 | 1601.5848 | 0 | 2773.3333 | 10000 | 1171.7485 | 0 | 0
2019-04-13 19:00 | 1885.3531 | 0 | 873.3333 | 10000 | -1012.0198 | -1012.0198 | 0
2019-04-13 20:00 | 1921.7951 | 0 | 0 | 8987.9802 | -1921.7951 | -1921.7951 | 0
2019-04-13 21:00 | 1588.3958 | 0 | 0 | 7066.1851 | -1588.3958 | -1588.3958 | 0
2019-04-13 22:00 | 1269.6056 | 0 | 0 | 5477.7893 | -1269.6056 | -1269.6056 | 0
2019-04-13 23:00 | 941.3457 | 0 | 0 | 4208.1837 | -941.3457 | -941.3457 | 0
2019-04-14 | 821.877 | 0 | 0 | 3266.838 | -821.877 | -821.877 | 0
2019-04-14 01:00 | 767.8275 | 0 | 286.6667 | 2444.961 | -481.1608 | -481.1608 | 0
2019-04-14 02:00 | 759.8149 | 0 | 873.3333 | 1963.8002 | 113.5185 | 113.5185 | 0
2019-04-14 03:00 | 761.8287 | 0 | 286.6667 | 2077.3187 | -475.162 | -475.162 | 0
2019-04-14 04:00 | 823.2722 | 0 | 286.6667 | 1602.1567 | -536.6056 | -536.6056 | 0
2019-04-14 05:00 | 1009.1574 | 176.7837 | 873.3333 | 1065.5511 | 40.9597 | 40.9597 | 0
2019-04-14 06:00 | 1244.56 | 1705.1499 | 286.6667 | 1106.5108 | 747.2565 | 747.2565 | 0
2019-04-14 07:00 | 1149.2439 | 4046.1899 | 0 | 1853.7673 | 2896.946 | 2896.946 | 0
2019-04-14 08:00 | 1009.7182 | 6001.3428 | 0 | 4750.7132 | 4991.6246 | 4991.6246 | 0
2019-04-14 09:00 | 1009.6798 | 7432.8444 | 286.6667 | 9742.3379 | 6709.8314 | 257.6621 | 0
2019-04-14 10:00 | 991.9522 | 8284.1687 | 286.6667 | 10000 | 7578.8832 | 0 | 0
2019-04-14 11:00 | 950.8626 | 8621.9467 | 4266.6667 | 10000 | 11937.7508 | 0 | 0
2019-04-14 12:00 | 911.5227 | 8422.0354 | 4266.6667 | 10000 | 11777.1794 | 0 | 0
2019-04-14 13:00 | 893.7813 | 7769.2194 | 4266.6667 | 10000 | 11142.1048 | 0 | 0
2019-04-14 14:00 | 922.0185 | 6581.3844 | 4266.6667 | 10000 | 9926.0326 | 0 | 0
2019-04-14 15:00 | 1050.2246 | 4892.9441 | 2773.3333 | 10000 | 6616.0528 | 0 | 0
2019-04-14 16:00 | 1307.0474 | 2737.6233 | 1666.6667 | 10000 | 3097.2425 | 0 | 0
2019-04-14 17:00 | 1443.7381 | 675.1144 | 873.3333 | 10000 | 104.7096 | 0 | 0
2019-04-14 18:00 | 1581.4508 | 0 | 286.6667 | 10000 | -1294.7841 | -1294.7841 | 0
2019-04-14 19:00 | 1862.6611 | 0 | 286.6667 | 8705.2159 | -1575.9944 | -1575.9944 | 0
2019-04-14 20:00 | 1903.5798 | 0 | 286.6667 | 7129.2214 | -1616.9131 | -1616.9131 | 0
2019-04-14 21:00 | 1569.0317 | 0 | 873.3333 | 5512.3083 | -695.6983 | -695.6983 | 0
2019-04-14 22:00 | 1240.2537 | 0 | 286.6667 | 4816.61 | -953.587 | -953.587 | 0
2019-04-14 23:00 | 913.1577 | 0 | 286.6667 | 3863.023 | -626.491 | -626.491 | 0
2019-04-15 | 795.8853 | 0 | 286.6667 | 3236.5319 | -509.2186 | -509.2186 | 0
2019-04-15 01:00 | 733.6462 | 0 | 286.6667 | 2727.3133 | -446.9795 | -446.9795 | 0
2019-04-15 02:00 | 720.0367 | 0 | 873.3333 | 2280.3338 | 153.2967 | 153.2967 | 0
2019-04-15 03:00 | 719.9036 | 0 | 0 | 2433.6304 | -719.9036 | -719.9036 | 0
2019-04-15 04:00 | 779.5673 | 0 | 0 | 1713.7268 | -779.5673 | -779.5673 | 0
2019-04-15 05:00 | 971.3786 | 178.1292 | 286.6667 | 934.1595 | -506.5827 | -506.5827 | 0
2019-04-15 06:00 | 1226.6504 | 1742.5168 | 286.6667 | 427.5768 | 802.5331 | 802.5331 | 0
2019-04-15 07:00 | 1160.7083 | 4050.0021 | 286.6667 | 1230.1099 | 3175.9605 | 3175.9605 | 0
2019-04-15 08:00 | 1064.1427 | 6036.6444 | 286.6667 | 4406.0703 | 5259.1683 | 5259.1683 | 0
2019-04-15 09:00 | 1087.1635 | 7423.7985 | 4266.6667 | 9665.2387 | 10603.3017 | 334.7613 | 0
2019-04-15 10:00 | 1074.2933 | 8283.9951 | 2773.3333 | 10000 | 9983.0351 | 0 | 0
2019-04-15 11:00 | 1036.8422 | 8605.3695 | 6160 | 10000 | 13728.5273 | 0 | 0
2019-04-15 12:00 | 998.2136 | 8411.0632 | 6160 | 10000 | 13572.8496 | 0 | 0
2019-04-15 13:00 | 978.4553 | 7766.2041 | 9060 | 10000 | 15847.7488 | 0 | 0
2019-04-15 14:00 | 1002.5083 | 6606.9075 | 9060 | 10000 | 14664.3993 | 0 | 0
2019-04-15 15:00 | 1125.6542 | 4922.2288 | 9873.3333 | 10000 | 13669.908 | 0 | 0
2019-04-15 16:00 | 1344.5669 | 2803.2032 | 10000 | 10000 | 11458.6363 | 0 | 0
2019-04-15 17:00 | 1478.5001 | 668.6537 | 6160 | 10000 | 5350.1536 | 0 | 0
2019-04-15 18:00 | 1607.5555 | 0 | 9873.3333 | 10000 | 8265.7778 | 0 | 0
2019-04-15 19:00 | 1883.441 | 0 | 9573.3333 | 10000 | 7689.8923 | 0 | 0
2019-04-15 20:00 | 1910.1299 | 0 | 7873.3333 | 10000 | 5963.2034 | 0 | 0
2019-04-15 21:00 | 1563.0444 | 0 | 9573.3333 | 10000 | 8010.2889 | 0 | 0
2019-04-15 22:00 | 1223.1345 | 0 | 9060 | 10000 | 7836.8655 | 0 | 0
2019-04-15 23:00 | 880.1493 | 0 | 7873.3333 | 10000 | 6993.1841 | 0 | 0
2019-04-16 | 757.7527 | 0 | 9573.3333 | 10000 | 8815.5806 | 0 | 0
2019-04-16 01:00 | 697.0939 | 0 | 7873.3333 | 10000 | 7176.2395 | 0 | 0
2019-04-16 02:00 | 688.2865 | 0 | 6160 | 10000 | 5471.7135 | 0 | 0
2019-04-16 03:00 | 691.7659 | 0 | 4266.6667 | 10000 | 3574.9008 | 0 | 0
2019-04-16 04:00 | 752.9448 | 0 | 4266.6667 | 10000 | 3513.7218 | 0 | 0
2019-04-16 05:00 | 933.6278 | 0 | 4266.6667 | 10000 | 3333.0389 | 0 | 0
2019-04-16 06:00 | 1200.256 | 96.5402 | 2773.3333 | 10000 | 1669.6175 | 0 | 0
2019-04-16 07:00 | 1118.4552 | 188.347 | 2773.3333 | 10000 | 1843.2252 | 0 | 0
2019-04-16 08:00 | 1004.9288 | 756.9265 | 2773.3333 | 10000 | 2525.331 | 0 | 0
2019-04-16 09:00 | 1016.1555 | 2567.4302 | 6160 | 10000 | 7711.2747 | 0 | 0
2019-04-16 10:00 | 1006.9111 | 2837.9171 | 6160 | 10000 | 7991.006 | 0 | 0
2019-04-16 11:00 | 965.7216 | 765.831 | 9573.3333 | 10000 | 9373.4427 | 0 | 0
2019-04-16 12:00 | 921.9766 | 1227.2432 | 7873.3333 | 10000 | 8178.6 | 0 | 0
2019-04-16 13:00 | 894.5771 | 602.1917 | 9060 | 10000 | 8767.6146 | 0 | 0
2019-04-16 14:00 | 915.5801 | 1459.2338 | 9060 | 10000 | 9603.6537 | 0 | 0
2019-04-16 15:00 | 1039.9992 | 1314.7341 | 9060 | 10000 | 9334.7348 | 0 | 0
2019-04-16 16:00 | 1273.2215 | 205.183 | 9060 | 10000 | 7991.9615 | 0 | 0
2019-04-16 17:00 | 1407.4859 | 248.0791 | 7873.3333 | 10000 | 6713.9266 | 0 | 0
2019-04-16 18:00 | 1544.4015 | 0 | 7873.3333 | 10000 | 6328.9319 | 0 | 0
2019-04-16 19:00 | 1825.6326 | 0 | 7873.3333 | 10000 | 6047.7008 | 0 | 0
2019-04-16 20:00 | 1864.7767 | 0 | 6160 | 10000 | 4295.2233 | 0 | 0
2019-04-16 21:00 | 1530.418 | 0 | 2773.3333 | 10000 | 1242.9153 | 0 | 0
2019-04-16 22:00 | 1205.2202 | 0 | 2773.3333 | 10000 | 1568.1131 | 0 | 0
2019-04-16 23:00 | 870.7968 | 0 | 2773.3333 | 10000 | 1902.5365 | 0 | 0
2019-04-17 | 748.7628 | 0 | 2773.3333 | 10000 | 2024.5705 | 0 | 0
2019-04-17 01:00 | 701.9743 | 0 | 2773.3333 | 10000 | 2071.359 | 0 | 0
2019-04-17 02:00 | 696.6507 | 0 | 2773.3333 | 10000 | 2076.6827 | 0 | 0
2019-04-17 03:00 | 704.0856 | 0 | 1666.6667 | 10000 | 962.5811 | 0 | 0
2019-04-17 04:00 | 766.2425 | 0 | 1666.6667 | 10000 | 900.4242 | 0 | 0
2019-04-17 05:00 | 942.4286 | 237.2749 | 873.3333 | 10000 | 168.1796 | 0 | 0
2019-04-17 06:00 | 1194.3633 | 75.087 | 2773.3333 | 10000 | 1654.057 | 0 | 0
2019-04-17 07:00 | 1108.1393 | 1228.7129 | 4266.6667 | 10000 | 4387.2403 | 0 | 0
2019-04-17 08:00 | 991.9319 | 855.3826 | 4266.6667 | 10000 | 4130.1174 | 0 | 0
2019-04-17 09:00 | 1005.3445 | 1017.4912 | 4266.6667 | 10000 | 4278.8134 | 0 | 0
2019-04-17 10:00 | 1028.7208 | 1112.1167 | 7873.3333 | 10000 | 7956.7293 | 0 | 0
2019-04-17 11:00 | 986.8374 | 1343.1091 | 2773.3333 | 10000 | 3129.6051 | 0 | 0
2019-04-17 12:00 | 952.5444 | 858.4428 | 9060 | 10000 | 8965.8984 | 0 | 0
2019-04-17 13:00 | 934.7398 | 2029.4602 | 6160 | 10000 | 7254.7204 | 0 | 0
2019-04-17 14:00 | 953.9809 | 990.25 | 2773.3333 | 10000 | 2809.6025 | 0 | 0
2019-04-17 15:00 | 1092.8452 | 1327.6014 | 4266.6667 | 10000 | 4501.4228 | 0 | 0
2019-04-17 16:00 | 1352.8312 | 365.4458 | 1666.6667 | 10000 | 679.2813 | 0 | 0
2019-04-17 17:00 | 1478.2983 | 156.9416 | 873.3333 | 10000 | -448.0233 | -448.0233 | 0
2019-04-17 18:00 | 1606.0577 | 0 | 4266.6667 | 9551.9767 | 2660.6089 | 448.0233 | 0
2019-04-17 19:00 | 1881.4953 | 0 | 4266.6667 | 10000 | 2385.1714 | 0 | 0
2019-04-17 20:00 | 1914.3646 | 0 | 873.3333 | 10000 | -1041.0313 | -1041.0313 | 0
2019-04-17 21:00 | 1582.8259 | 0 | 6160 | 8958.9687 | 4577.1741 | 1041.0313 | 0
2019-04-17 22:00 | 1256.782 | 0 | 6160 | 10000 | 4903.218 | 0 | 0
2019-04-17 23:00 | 929.5465 | 0 | 4266.6667 | 10000 | 3337.1202 | 0 | 0
2019-04-18 | 812.6619 | 0 | 1666.6667 | 10000 | 854.0047 | 0 | 0
2019-04-18 01:00 | 763.5673 | 0 | 1666.6667 | 10000 | 903.0994 | 0 | 0
2019-04-18 02:00 | 759.6452 | 0 | 2773.3333 | 10000 | 2013.6882 | 0 | 0
2019-04-18 03:00 | 760.4993 | 0 | 1666.6667 | 10000 | 906.1674 | 0 | 0
2019-04-18 04:00 | 822.0143 | 0 | 1666.6667 | 10000 | 844.6524 | 0 | 0
2019-04-18 05:00 | 993.8145 | 106.8982 | 2773.3333 | 10000 | 1886.4171 | 0 | 0
2019-04-18 06:00 | 1239.0904 | 726.2468 | 873.3333 | 10000 | 360.4898 | 0 | 0
2019-04-18 07:00 | 1151.4188 | 2062.4342 | 873.3333 | 10000 | 1784.3487 | 0 | 0
2019-04-18 08:00 | 1016.9159 | 1804.5662 | 2773.3333 | 10000 | 3560.9836 | 0 | 0
2019-04-18 09:00 | 1027.2778 | 2324.7664 | 6160 | 10000 | 7457.4886 | 0 | 0
2019-04-18 10:00 | 1007.1661 | 3033.3504 | 6160 | 10000 | 8186.1843 | 0 | 0
2019-04-18 11:00 | 972.6723 | 5854.4809 | 6160 | 10000 | 11041.8086 | 0 | 0
2019-04-18 12:00 | 944.2007 | 6284.0738 | 6160 | 10000 | 11499.8731 | 0 | 0
2019-04-18 13:00 | 935.4504 | 5791.9451 | 6160 | 10000 | 11016.4947 | 0 | 0
2019-04-18 14:00 | 969.0001 | 2454.7877 | 4266.6667 | 10000 | 5752.4542 | 0 | 0
2019-04-18 15:00 | 1105.5095 | 4489.3516 | 4266.6667 | 10000 | 7650.5088 | 0 | 0
2019-04-18 16:00 | 1352.8701 | 2813.4071 | 4266.6667 | 10000 | 5727.2037 | 0 | 0
2019-04-18 17:00 | 1481.0507 | 139.7859 | 4266.6667 | 10000 | 2925.4019 | 0 | 0
2019-04-18 18:00 | 1618.1648 | 0 | 4266.6667 | 10000 | 2648.5019 | 0 | 0
2019-04-18 19:00 | 1896.2558 | 0 | 1666.6667 | 10000 | -229.5891 | -229.5891 | 0
2019-04-18 20:00 | 1925.9464 | 0 | 873.3333 | 9770.4109 | -1052.6131 | -1052.6131 | 0
2019-04-18 21:00 | 1587.2364 | 0 | 286.6667 | 8717.7978 | -1300.5698 | -1300.5698 | 0
2019-04-18 22:00 | 1264.3227 | 0 | 286.6667 | 7417.2281 | -977.6561 | -977.6561 | 0
2019-04-18 23:00 | 936.6313 | 0 | 873.3333 | 6439.572 | -63.2979 | -63.2979 | 0
2019-04-19 | 820.5758 | 0 | 1666.6667 | 6376.2741 | 846.0909 | 846.0909 | 0
2019-04-19 01:00 | 768.7767 | 0 | 873.3333 | 7222.3649 | 104.5566 | 104.5566 | 0
2019-04-19 02:00 | 759.8151 | 0 | 873.3333 | 7326.9216 | 113.5183 | 113.5183 | 0
2019-04-19 03:00 | 758.7395 | 0 | 873.3333 | 7440.4398 | 114.5939 | 114.5939 | 0
2019-04-19 04:00 | 816.9484 | 0 | 286.6667 | 7555.0337 | -530.2817 | -530.2817 | 0
2019-04-19 05:00 | 1004.3698 | 225.7243 | 0 | 7024.752 | -778.6455 | -778.6455 | 0
2019-04-19 06:00 | 1238.2621 | 1920.7334 | 286.6667 | 6246.1065 | 969.138 | 969.138 | 0
2019-04-19 07:00 | 1132.8648 | 4274.6581 | 286.6667 | 7215.2446 | 3428.46 | 2784.7554 | 0
2019-04-19 08:00 | 1000.8839 | 6212.0608 | 873.3333 | 10000 | 6084.5102 | 0 | 0
2019-04-19 09:00 | 1013.8217 | 7561.4961 | 1666.6667 | 10000 | 8214.341 | 0 | 0
2019-04-19 10:00 | 994.615 | 5556.3572 | 2773.3333 | 10000 | 7335.0756 | 0 | 0
2019-04-19 11:00 | 952.2838 | 4754.5818 | 4266.6667 | 10000 | 8068.9648 | 0 | 0
2019-04-19 12:00 | 917.662 | 7190.4187 | 6160 | 10000 | 12432.7567 | 0 | 0
2019-04-19 13:00 | 911.8212 | 3759.9158 | 7873.3333 | 10000 | 10721.4279 | 0 | 0
2019-04-19 14:00 | 938.2634 | 4397.0975 | 9060 | 10000 | 12518.8341 | 0 | 0
2019-04-19 15:00 | 1050.2299 | 4866.4343 | 6160 | 10000 | 9976.2044 | 0 | 0
2019-04-19 16:00 | 1299.4937 | 1376.3407 | 4266.6667 | 10000 | 4343.5137 | 0 | 0
2019-04-19 17:00 | 1431.2007 | 746.1579 | 4266.6667 | 10000 | 3581.6239 | 0 | 0
2019-04-19 18:00 | 1576.9432 | 0 | 4266.6667 | 10000 | 2689.7234 | 0 | 0
2019-04-19 19:00 | 1854.3666 | 0 | 2773.3333 | 10000 | 918.9667 | 0 | 0
2019-04-19 20:00 | 1892.6798 | 0 | 2773.3333 | 10000 | 880.6535 | 0 | 0
2019-04-19 21:00 | 1557.8892 | 0 | 2773.3333 | 10000 | 1215.4441 | 0 | 0
2019-04-19 22:00 | 1239.922 | 0 | 2773.3333 | 10000 | 1533.4113 | 0 | 0
2019-04-19 23:00 | 911.5861 | 0 | 873.3333 | 10000 | -38.2528 | -38.2528 | 0
2019-04-20 | 794.4146 | 0 | 2773.3333 | 9961.7472 | 1978.9187 | 38.2528 | 0
2019-04-20 01:00 | 738.4772 | 0 | 1666.6667 | 10000 | 928.1894 | 0 | 0
2019-04-20 02:00 | 732.2863 | 0 | 286.6667 | 10000 | -445.6197 | -445.6197 | 0
2019-04-20 03:00 | 729.0211 | 0 | 286.6667 | 9554.3803 | -442.3544 | -442.3544 | 0
2019-04-20 04:00 | 786.5484 | 0 | 0 | 9112.0259 | -786.5484 | -786.5484 | 0
2019-04-20 05:00 | 962.7349 | 243.8034 | 0 | 8325.4775 | -718.9314 | -718.9314 | 0
2019-04-20 06:00 | 1208.6253 | 1864.1442 | 0 | 7606.5461 | 655.5189 | 655.5189 | 0
2019-04-20 07:00 | 1118.8924 | 4085.214 | 0 | 8262.065 | 2966.3216 | 1737.935 | 0
2019-04-20 08:00 | 993.8221 | 5938.2159 | 0 | 10000 | 4944.3938 | 0 | 0
2019-04-20 09:00 | 993.6349 | 6208.045 | 286.6667 | 10000 | 5501.0768 | 0 | 0
2019-04-20 10:00 | 973.8258 | 8135.3047 | 0 | 10000 | 7161.4789 | 0 | 0
2019-04-20 11:00 | 940.0865 | 6214.8012 | 873.3333 | 10000 | 6148.0481 | 0 | 0
2019-04-20 12:00 | 902.4077 | 6070.2543 | 1666.6667 | 10000 | 6834.5132 | 0 | 0
2019-04-20 13:00 | 883.4617 | 5896.8837 | 1666.6667 | 10000 | 6680.0888 | 0 | 0
2019-04-20 14:00 | 911.6273 | 3556.475 | 4266.6667 | 10000 | 6911.5144 | 0 | 0
2019-04-20 15:00 | 1040.5953 | 2343.9633 | 2773.3333 | 10000 | 4076.7014 | 0 | 0
2019-04-20 16:00 | 1281.5682 | 1535.3236 | 1666.6667 | 10000 | 1920.4221 | 0 | 0
2019-04-20 17:00 | 1417.5555 | 611.624 | 4266.6667 | 10000 | 3460.7353 | 0 | 0
2019-04-20 18:00 | 1553.239 | 0 | 1666.6667 | 10000 | 113.4277 | 0 | 0
2019-04-20 19:00 | 1832.9499 | 0 | 873.3333 | 10000 | -959.6165 | -959.6165 | 0
2019-04-20 20:00 | 1869.0827 | 0 | 2773.3333 | 9040.3835 | 904.2506 | 904.2506 | 0
2019-04-20 21:00 | 1530.5912 | 0 | 4266.6667 | 9944.6341 | 2736.0755 | 55.3659 | 0
2019-04-20 22:00 | 1202.9046 | 0 | 2773.3333 | 10000 | 1570.4287 | 0 | 0
2019-04-20 23:00 | 870.3787 | 0 | 873.3333 | 10000 | 2.9546 | 0 | 0
2019-04-21 | 744.9629 | 0 | 2773.3333 | 10000 | 2028.3704 | 0 | 0
2019-04-21 01:00 | 687.008 | 0 | 2773.3333 | 10000 | 2086.3253 | 0 | 0
2019-04-21 02:00 | 676.7984 | 0 | 4266.6667 | 10000 | 3589.8683 | 0 | 0
2019-04-21 03:00 | 674.9283 | 0 | 4266.6667 | 10000 | 3591.7383 | 0 | 0
2019-04-21 04:00 | 732.9978 | 0 | 2773.3333 | 10000 | 2040.3355 | 0 | 0
2019-04-21 05:00 | 906.376 | 256.7076 | 2773.3333 | 10000 | 2123.665 | 0 | 0
2019-04-21 06:00 | 1172.5024 | 1819.6266 | 4266.6667 | 10000 | 4913.7909 | 0 | 0
2019-04-21 07:00 | 1085.0399 | 2867.433 | 4266.6667 | 10000 | 6049.0597 | 0 | 0
2019-04-21 08:00 | 970.5592 | 5266.2272 | 4266.6667 | 10000 | 8562.3346 | 0 | 0
2019-04-21 09:00 | 988.8517 | 6539.3474 | 6160 | 10000 | 11710.4956 | 0 | 0
2019-04-21 10:00 | 984.1325 | 6832.0005 | 6160 | 10000 | 12007.868 | 0 | 0
2019-04-21 11:00 | 957.323 | 5777.0192 | 4266.6667 | 10000 | 9086.3629 | 0 | 0
2019-04-21 12:00 | 926.1734 | 5132.1763 | 6160 | 10000 | 10366.0029 | 0 | 0
2019-04-21 13:00 | 911.8556 | 5632.6149 | 6160 | 10000 | 10880.7593 | 0 | 0
2019-04-21 14:00 | 935.3232 | 4995.9922 | 6160 | 10000 | 10220.6689 | 0 | 0
2019-04-21 15:00 | 1066.0841 | 3571.4043 | 4266.6667 | 10000 | 6771.9869 | 0 | 0
2019-04-21 16:00 | 1311.7469 | 1280.0201 | 4266.6667 | 10000 | 4234.9399 | 0 | 0
2019-04-21 17:00 | 1436.2447 | 625.6483 | 2773.3333 | 10000 | 1962.7369 | 0 | 0
2019-04-21 18:00 | 1564.4857 | 0 | 2773.3333 | 10000 | 1208.8476 | 0 | 0
2019-04-21 19:00 | 1839.4948 | 0 | 873.3333 | 10000 | -966.1615 | -966.1615 | 0
2019-04-21 20:00 | 1872.2698 | 0 | 873.3333 | 9033.8385 | -998.9365 | -998.9365 | 0
2019-04-21 21:00 | 1531.2526 | 0 | 873.3333 | 8034.902 | -657.9193 | -657.9193 | 0
2019-04-21 22:00 | 1203.1826 | 0 | 1666.6667 | 7376.9827 | 463.4841 | 463.4841 | 0
2019-04-21 23:00 | 876.5545 | 0 | 873.3333 | 7840.4668 | -3.2212 | -3.2212 | 0
2019-04-22 | 758.8381 | 0 | 1666.6667 | 7837.2456 | 907.8286 | 907.8286 | 0
2019-04-22 01:00 | 698.5011 | 0 | 1666.6667 | 8745.0741 | 968.1655 | 968.1655 | 0
2019-04-22 02:00 | 688.2262 | 0 | 1666.6667 | 9713.2397 | 978.4404 | 286.7603 | 0
2019-04-22 03:00 | 690.1338 | 0 | 1666.6667 | 10000 | 976.5329 | 0 | 0
2019-04-22 04:00 | 753.5372 | 0 | 1666.6667 | 10000 | 913.1294 | 0 | 0
2019-04-22 05:00 | 932.1081 | 289.4332 | 1666.6667 | 10000 | 1023.9917 | 0 | 0
2019-04-22 06:00 | 1194.023 | 1769.0553 | 873.3333 | 10000 | 1448.3657 | 0 | 0
2019-04-22 07:00 | 1120.5355 | 3701.9604 | 873.3333 | 10000 | 3454.7582 | 0 | 0
2019-04-22 08:00 | 1012.5354 | 5431.7317 | 0 | 10000 | 4419.1963 | 0 | 0
2019-04-22 09:00 | 1025.8226 | 6786.1293 | 2773.3333 | 10000 | 8533.64 | 0 | 0
2019-04-22 10:00 | 1015.3384 | 7837.5547 | 1666.6667 | 10000 | 8488.883 | 0 | 0
2019-04-22 11:00 | 985.5417 | 5801.2797 | 873.3333 | 10000 | 5689.0713 | 0 | 0
2019-04-22 12:00 | 945.7853 | 5903.4433 | 873.3333 | 10000 | 5830.9914 | 0 | 0
2019-04-22 13:00 | 924.741 | 267.245 | 873.3333 | 10000 | 215.8374 | 0 | 0
2019-04-22 14:00 | 950.077 | 2320.3458 | 1666.6667 | 10000 | 3036.9354 | 0 | 0
2019-04-22 15:00 | 1083.5927 | 170.4702 | 873.3333 | 10000 | -39.7891 | -39.7891 | 0
2019-04-22 16:00 | 1329.6989 | 1874.1492 | 873.3333 | 9960.2109 | 1417.7836 | 39.7891 | 0
2019-04-22 17:00 | 1456.7781 | 769.4558 | 873.3333 | 10000 | 186.011 | 0 | 0
2019-04-22 18:00 | 1586.6245 | 0 | 873.3333 | 10000 | -713.2912 | -713.2912 | 0
2019-04-22 19:00 | 1870.4108 | 0 | 0 | 9286.7088 | -1870.4108 | -1870.4108 | 0
2019-04-22 20:00 | 1901.2706 | 0 | 0 | 7416.298 | -1901.2706 | -1901.2706 | 0
2019-04-22 21:00 | 1555.8128 | 0 | 0 | 5515.0274 | -1555.8128 | -1555.8128 | 0
2019-04-22 22:00 | 1215.5965 | 0 | 0 | 3959.2146 | -1215.5965 | -1215.5965 | 0
2019-04-22 23:00 | 878.6409 | 0 | 0 | 2743.6181 | -878.6409 | -878.6409 | 0
2019-04-23 | 755.6165 | 0 | 0 | 1864.9772 | -755.6165 | -755.6165 | 0
2019-04-23 01:00 | 699.3738 | 0 | 0 | 1109.3606 | -699.3738 | -699.3738 | 0
2019-04-23 02:00 | 684.6277 | 0 | 873.3333 | 409.9868 | 188.7057 | 188.7057 | 0
2019-04-23 03:00 | 685.356 | 0 | 873.3333 | 598.6925 | 187.9774 | 187.9774 | 0
2019-04-23 04:00 | 743.9138 | 0 | 1666.6667 | 786.6699 | 922.7528 | 922.7528 | 0
2019-04-23 05:00 | 924.5821 | 93.1718 | 873.3333 | 1709.4227 | 41.9231 | 41.9231 | 0
2019-04-23 06:00 | 1182.7012 | 1083.584 | 1666.6667 | 1751.3458 | 1567.5496 | 1567.5496 | 0
2019-04-23 07:00 | 1111.123 | 2035.094 | 873.3333 | 3318.8953 | 1797.3044 | 1797.3044 | 0
2019-04-23 08:00 | 993.8458 | 3884.7299 | 286.6667 | 5116.1997 | 3177.5508 | 3177.5508 | 0
2019-04-23 09:00 | 1008.4643 | 5346.5006 | 873.3333 | 8293.7506 | 5211.3697 | 1706.2494 | 0
2019-04-23 10:00 | 996.7851 | 3944.0998 | 873.3333 | 10000 | 3820.648 | 0 | 0
2019-04-23 11:00 | 964.3498 | 5136.0334 | 1666.6667 | 10000 | 5838.3502 | 0 | 0
2019-04-23 12:00 | 937.8735 | 6337.8984 | 2773.3333 | 10000 | 8173.3582 | 0 | 0
2019-04-23 13:00 | 916.7383 | 3082.483 | 4266.6667 | 10000 | 6432.4114 | 0 | 0
2019-04-23 14:00 | 945.1973 | 4110.9222 | 2773.3333 | 10000 | 5939.0582 | 0 | 0
2019-04-23 15:00 | 1075.0724 | 439.4782 | 7873.3333 | 10000 | 7237.7392 | 0 | 0
2019-04-23 16:00 | 1328.0735 | 2873.168 | 7873.3333 | 10000 | 9418.4279 | 0 | 0
2019-04-23 17:00 | 1457.5774 | 798.4899 | 9060 | 10000 | 8400.9124 | 0 | 0
2019-04-23 18:00 | 1593.933 | 0 | 4266.6667 | 10000 | 2672.7337 | 0 | 0
2019-04-23 19:00 | 1874.6921 | 0 | 2773.3333 | 10000 | 898.6412 | 0 | 0
2019-04-23 20:00 | 1910.3795 | 0 | 1666.6667 | 10000 | -243.7128 | -243.7128 | 0
2019-04-23 21:00 | 1568.2532 | 0 | 1666.6667 | 9756.2872 | 98.4134 | 98.4134 | 0
2019-04-23 22:00 | 1227.8989 | 0 | 873.3333 | 9854.7006 | -354.5655 | -354.5655 | 0
2019-04-23 23:00 | 890.9819 | 0 | 873.3333 | 9500.1351 | -17.6486 | -17.6486 | 0
2019-04-24 | 765.3343 | 0 | 286.6667 | 9482.4865 | -478.6677 | -478.6677 | 0
2019-04-24 01:00 | 710.2082 | 0 | 286.6667 | 9003.8188 | -423.5415 | -423.5415 | 0
2019-04-24 02:00 | 702.9322 | 0 | 286.6667 | 8580.2773 | -416.2655 | -416.2655 | 0
2019-04-24 03:00 | 703.1349 | 0 | 873.3333 | 8164.0118 | 170.1984 | 170.1984 | 0
2019-04-24 04:00 | 769.949 | 0 | 1666.6667 | 8334.2103 | 896.7177 | 896.7177 | 0
2019-04-24 05:00 | 948.6389 | 316.8687 | 1666.6667 | 9230.928 | 1034.8965 | 769.072 | 0
2019-04-24 06:00 | 1188.2932 | 2045.6246 | 0 | 10000 | 857.3314 | 0 | 0
2019-04-24 07:00 | 1097.1221 | 4329.0542 | 0 | 10000 | 3231.9322 | 0 | 0
2019-04-24 08:00 | 971.8489 | 6204.2143 | 0 | 10000 | 5232.3654 | 0 | 0
2019-04-24 09:00 | 987.9323 | 7533.65 | 873.3333 | 10000 | 7419.0511 | 0 | 0
2019-04-24 10:00 | 980.0717 | 8288.3927 | 286.6667 | 10000 | 7594.9877 | 0 | 0
2019-04-24 11:00 | 948.5498 | 8577.6211 | 286.6667 | 10000 | 7915.738 | 0 | 0
2019-04-24 12:00 | 917.9484 | 8355.9816 | 873.3333 | 10000 | 8311.3665 | 0 | 0
2019-04-24 13:00 | 900.1956 | 7671.1267 | 873.3333 | 10000 | 7644.2644 | 0 | 0
2019-04-24 14:00 | 934.6526 | 6567.3613 | 2773.3333 | 10000 | 8406.0421 | 0 | 0
2019-04-24 15:00 | 1062.2125 | 4879.8019 | 4266.6667 | 10000 | 8084.2561 | 0 | 0
2019-04-24 16:00 | 1311.7337 | 2580.1423 | 1666.6667 | 10000 | 2935.0753 | 0 | 0
2019-04-24 17:00 | 1433.73 | 801.4511 | 1666.6667 | 10000 | 1034.3878 | 0 | 0
2019-04-24 18:00 | 1564.4344 | 0 | 873.3333 | 10000 | -691.1011 | -691.1011 | 0
2019-04-24 19:00 | 1842.0882 | 0 | 873.3333 | 9308.8989 | -968.7549 | -968.7549 | 0
2019-04-24 20:00 | 1878.3057 | 0 | 0 | 8340.1441 | -1878.3057 | -1878.3057 | 0
2019-04-24 21:00 | 1544.2719 | 0 | 0 | 6461.8384 | -1544.2719 | -1544.2719 | 0
2019-04-24 22:00 | 1219.4356 | 0 | 0 | 4917.5665 | -1219.4356 | -1219.4356 | 0
2019-04-24 23:00 | 889.7536 | 0 | 286.6667 | 3698.1309 | -603.0869 | -603.0869 | 0
2019-04-25 | 768.8868 | 0 | 873.3333 | 3095.044 | 104.4465 | 104.4465 | 0
2019-04-25 01:00 | 715.0323 | 0 | 2773.3333 | 3199.4905 | 2058.301 | 2058.301 | 0
2019-04-25 02:00 | 706.061 | 0 | 873.3333 | 5257.7916 | 167.2724 | 167.2724 | 0
2019-04-25 03:00 | 706.2807 | 0 | 1666.6667 | 5425.0639 | 960.386 | 960.386 | 0
2019-04-25 04:00 | 766.9119 | 0 | 1666.6667 | 6385.4499 | 899.7548 | 899.7548 | 0
2019-04-25 05:00 | 948.5713 | 193.1126 | 1666.6667 | 7285.2046 | 911.208 | 911.208 | 0
2019-04-25 06:00 | 1190.5578 | 340.7611 | 4266.6667 | 8196.4126 | 3416.87 | 1803.5874 | 0
2019-04-25 07:00 | 1107.5944 | 2414.2582 | 4266.6667 | 10000 | 5573.3305 | 0 | 0
2019-04-25 08:00 | 987.3194 | 4579.8393 | 6160 | 10000 | 9752.5199 | 0 | 0
2019-04-25 09:00 | 1005.14 | 5928.0832 | 7873.3333 | 10000 | 12796.2766 | 0 | 0
2019-04-25 10:00 | 1001.9265 | 6965.9065 | 9060 | 10000 | 15023.98 | 0 | 0
2019-04-25 11:00 | 977.5268 | 6750.914 | 7873.3333 | 10000 | 13646.7206 | 0 | 0
2019-04-25 12:00 | 951.9901 | 6121.8329 | 9060 | 10000 | 14229.8429 | 0 | 0
2019-04-25 13:00 | 942.7661 | 6387.8187 | 7873.3333 | 10000 | 13318.386 | 0 | 0
2019-04-25 14:00 | 975.9502 | 4884.0109 | 7873.3333 | 10000 | 11781.394 | 0 | 0
2019-04-25 15:00 | 1104.3823 | 2963.6604 | 7873.3333 | 10000 | 9732.6114 | 0 | 0
2019-04-25 16:00 | 1328.4801 | 492.4909 | 9060 | 10000 | 8224.0109 | 0 | 0
2019-04-25 17:00 | 1464.6844 | 604.9863 | 7873.3333 | 10000 | 7013.6352 | 0 | 0
2019-04-25 18:00 | 1593.817 | 0 | 6160 | 10000 | 4566.183 | 0 | 0
2019-04-25 19:00 | 1865.9311 | 0 | 4266.6667 | 10000 | 2400.7355 | 0 | 0
2019-04-25 20:00 | 1893.7019 | 0 | 4266.6667 | 10000 | 2372.9648 | 0 | 0
2019-04-25 21:00 | 1550.6459 | 0 | 2773.3333 | 10000 | 1222.6875 | 0 | 0
2019-04-25 22:00 | 1222.3861 | 0 | 2773.3333 | 10000 | 1550.9472 | 0 | 0
2019-04-25 23:00 | 889.9069 | 0 | 873.3333 | 10000 | -16.5735 | -16.5735 | 0
2019-04-26 | 766.0194 | 0 | 1666.6667 | 9983.4265 | 900.6472 | 16.5735 | 0
2019-04-26 01:00 | 707.6166 | 0 | 1666.6667 | 10000 | 959.0501 | 0 | 0
2019-04-26 02:00 | 697.0749 | 0 | 2773.3333 | 10000 | 2076.2585 | 0 | 0
2019-04-26 03:00 | 693.4843 | 0 | 7873.3333 | 10000 | 7179.8491 | 0 | 0
2019-04-26 04:00 | 751.9198 | 0 | 4266.6667 | 10000 | 3514.7469 | 0 | 0
2019-04-26 05:00 | 923.5106 | 291.6791 | 2773.3333 | 10000 | 2141.5018 | 0 | 0
2019-04-26 06:00 | 1174.4447 | 1113.346 | 873.3333 | 10000 | 812.2347 | 0 | 0
2019-04-26 07:00 | 1093.3013 | 703.2307 | 873.3333 | 10000 | 483.2628 | 0 | 0
2019-04-26 08:00 | 973.5119 | 3086.6345 | 1666.6667 | 10000 | 3779.7893 | 0 | 0
2019-04-26 09:00 | 987.1037 | 4381.2366 | 1666.6667 | 10000 | 5060.7996 | 0 | 0
2019-04-26 10:00 | 970.8502 | 6871.5777 | 873.3333 | 10000 | 6774.0609 | 0 | 0
2019-04-26 11:00 | 930.7374 | 6709.7026 | 873.3333 | 10000 | 6652.2985 | 0 | 0
2019-04-26 12:00 | 901.7049 | 7090.3837 | 1666.6667 | 10000 | 7855.3454 | 0 | 0
2019-04-26 13:00 | 885.1571 | 3785.363 | 286.6667 | 10000 | 3186.8726 | 0 | 0
2019-04-26 14:00 | 913.8418 | 2591.8953 | 0 | 10000 | 1678.0535 | 0 | 0
2019-04-26 15:00 | 1043.6872 | 819.3957 | 286.6667 | 10000 | 62.3752 | 0 | 0
2019-04-26 16:00 | 1285.1309 | 1905.2648 | 286.6667 | 10000 | 906.8006 | 0 | 0
2019-04-26 17:00 | 1404.4036 | 562.6881 | 286.6667 | 10000 | -555.0488 | -555.0488 | 0
2019-04-26 18:00 | 1537.3233 | 0 | 873.3333 | 9444.9512 | -663.99 | -663.99 | 0
2019-04-26 19:00 | 1805.0295 | 0 | 286.6667 | 8780.9612 | -1518.3629 | -1518.3629 | 0
2019-04-26 20:00 | 1839.3252 | 0 | 286.6667 | 7262.5984 | -1552.6585 | -1552.6585 | 0
2019-04-26 21:00 | 1503.8555 | 0 | 0 | 5709.9398 | -1503.8555 | -1503.8555 | 0
2019-04-26 22:00 | 1182.1257 | 0 | 0 | 4206.0844 | -1182.1257 | -1182.1257 | 0
2019-04-26 23:00 | 855.6089 | 0 | 0 | 3023.9587 | -855.6089 | -855.6089 | 0
2019-04-27 | 736.604 | 0 | 0 | 2168.3498 | -736.604 | -736.604 | 0
2019-04-27 01:00 | 683.2732 | 0 | 0 | 1431.7458 | -683.2732 | -683.2732 | 0
2019-04-27 02:00 | 676.8462 | 0 | 0 | 748.4726 | -676.8462 | -676.8462 | 0
2019-04-27 03:00 | 674.9869 | 0 | 0 | 71.6264 | -674.9869 | -71.6264 | -603.3605
2019-04-27 04:00 | 733.5733 | 0 | 0 | 0 | -733.5733 | 0 | -1336.9338
2019-04-27 05:00 | 909.6745 | 83.0369 | 0 | 0 | -826.6376 | 0 | -2163.5714
2019-04-27 06:00 | 1145.7663 | 214.061 | 0 | 0 | -931.7053 | 0 | -3095.2767
2019-04-27 07:00 | 1047.482 | 943.8751 | 0 | 0 | -103.6068 | 0 | -3198.8836
2019-04-27 08:00 | 907.2285 | 1060.4736 | 0 | 0 | 153.2452 | 153.2452 | -3045.6384
2019-04-27 09:00 | 871.4652 | 1331.3343 | 0 | 153.2452 | 459.8691 | 459.8691 | -2432.5241
2019-04-27 10:00 | 868.3749 | 1292.3688 | 0 | 613.1143 | 423.994 | 423.994 | -1395.4158
2019-04-27 11:00 | 847.758 | 935.027 | 873.3333 | 1037.1083 | 960.6024 | 960.6024 | 0
2019-04-27 12:00 | 823.7088 | 1228.2023 | 873.3333 | 1997.7107 | 1277.8268 | 1277.8268 | 0
2019-04-27 13:00 | 815.9545 | 1243.8515 | 873.3333 | 3275.5375 | 1301.2304 | 1301.2304 | 0
2019-04-27 14:00 | 846.3013 | 990.6709 | 873.3333 | 4576.7679 | 1017.703 | 1017.703 | 0
2019-04-27 15:00 | 975.826 | 161.713 | 2773.3333 | 5594.4709 | 1959.2203 | 1959.2203 | 0
2019-04-27 16:00 | 1203.1223 | 1170.4665 | 1666.6667 | 7553.6912 | 1634.0109 | 1634.0109 | 0
2019-04-27 17:00 | 1344.2348 | 62.4312 | 286.6667 | 9187.7021 | -995.1369 | -995.1369 | 0
2019-04-27 18:00 | 1473.8274 | 0 | 286.6667 | 8192.5652 | -1187.1607 | -1187.1607 | 0
2019-04-27 19:00 | 1747.839 | 0 | 286.6667 | 7005.4045 | -1461.1724 | -1461.1724 | 0
2019-04-27 20:00 | 1775.0343 | 0 | 0 | 5544.2321 | -1775.0343 | -1775.0343 | 0
2019-04-27 21:00 | 1426.6169 | 0 | 0 | 3769.1978 | -1426.6169 | -1426.6169 | 0
2019-04-27 22:00 | 1088.0352 | 0 | 0 | 2342.581 | -1088.0352 | -1088.0352 | 0
2019-04-27 23:00 | 745.1074 | 0 | 286.6667 | 1254.5458 | -458.4408 | -458.4408 | 0
2019-04-28 | 614.5462 | 0 | 0 | 796.105 | -614.5462 | -614.5462 | 0
2019-04-28 01:00 | 552.5338 | 0 | 0 | 181.5589 | -552.5338 | -181.5589 | -370.9749
2019-04-28 02:00 | 539.0912 | 0 | 0 | 0 | -539.0912 | 0 | -910.0661
2019-04-28 03:00 | 536.3645 | 0 | 0 | 0 | -536.3645 | 0 | -1446.4306
2019-04-28 04:00 | 602.1987 | 0 | 0 | 0 | -602.1987 | 0 | -2048.6293
2019-04-28 05:00 | 774.4467 | 353.97 | 0 | 0 | -420.4767 | 0 | -2469.106
2019-04-28 06:00 | 1036.8877 | 2218.174 | 0 | 0 | 1181.2863 | 1181.2863 | -1287.8197
2019-04-28 07:00 | 957.804 | 1127.4462 | 0 | 1181.2863 | 169.6422 | 169.6422 | 0
2019-04-28 08:00 | 844.563 | 749.6976 | 286.6667 | 1350.9285 | 191.8013 | 191.8013 | 0
2019-04-28 09:00 | 847.4639 | 1717.6699 | 286.6667 | 1542.7298 | 1156.8727 | 1156.8727 | 0
2019-04-28 10:00 | 864.418 | 1791.7931 | 286.6667 | 2699.6025 | 1214.0419 | 1214.0419 | 0
2019-04-28 11:00 | 847.758 | 6759.5206 | 873.3333 | 3913.6444 | 6785.096 | 6086.3556 | 0
2019-04-28 12:00 | 823.7088 | 5673.5445 | 286.6667 | 10000 | 5136.5024 | 0 | 0
2019-04-28 13:00 | 815.9545 | 4713.8741 | 286.6667 | 10000 | 4184.5864 | 0 | 0
2019-04-28 14:00 | 846.3013 | 2210.4046 | 286.6667 | 10000 | 1650.7701 | 0 | 0
2019-04-28 15:00 | 975.826 | 3237.6847 | 873.3333 | 10000 | 3135.192 | 0 | 0
2019-04-28 16:00 | 1223.3895 | 1728.0728 | 1666.6667 | 10000 | 2171.35 | 0 | 0
2019-04-28 17:00 | 1369.8071 | 511.3015 | 2773.3333 | 10000 | 1914.8278 | 0 | 0
2019-04-28 18:00 | 1514.8718 | 0 | 286.6667 | 10000 | -1228.2051 | -1228.2051 | 0
2019-04-28 19:00 | 1809.5423 | 0 | 286.6667 | 8771.7949 | -1522.8757 | -1522.8757 | 0
2019-04-28 20:00 | 1849.7633 | 0 | 873.3333 | 7248.9192 | -976.43 | -976.43 | 0
2019-04-28 21:00 | 1523.9465 | 0 | 0 | 6272.4892 | -1523.9465 | -1523.9465 | 0
2019-04-28 22:00 | 1206.338 | 0 | 286.6667 | 4748.5428 | -919.6713 | -919.6713 | 0
2019-04-28 23:00 | 881.288 | 0 | 873.3333 | 3828.8715 | -7.9547 | -7.9547 | 0
2019-04-29 | 764.6577 | 0 | 286.6667 | 3820.9168 | -477.991 | -477.991 | 0
2019-04-29 01:00 | 712.668 | 0 | 286.6667 | 3342.9258 | -426.0013 | -426.0013 | 0
2019-04-29 02:00 | 703.9409 | 0 | 0 | 2916.9244 | -703.9409 | -703.9409 | 0
2019-04-29 03:00 | 711.0344 | 0 | 286.6667 | 2212.9836 | -424.3677 | -424.3677 | 0
2019-04-29 04:00 | 772.6618 | 0 | 286.6667 | 1788.6158 | -485.9951 | -485.9951 | 0
2019-04-29 05:00 | 967.7251 | 394.8467 | 286.6667 | 1302.6207 | -286.2117 | -286.2117 | 0
2019-04-29 06:00 | 1239.3266 | 2219.6184 | 0 | 1016.409 | 980.2918 | 980.2918 | 0
2019-04-29 07:00 | 1163.9249 | 4479.2695 | 0 | 1996.7009 | 3315.3446 | 3315.3446 | 0
2019-04-29 08:00 | 1061.645 | 6349.227 | 286.6667 | 5312.0455 | 5574.2487 | 4687.9545 | 0
2019-04-29 09:00 | 1094.6673 | 7642.7609 | 2773.3333 | 10000 | 9321.4269 | 0 | 0
2019-04-29 10:00 | 1088.9868 | 7658.4261 | 4266.6667 | 10000 | 10836.1061 | 0 | 0
2019-04-29 11:00 | 1062.8188 | 9083.9178 | 4266.6667 | 10000 | 12287.7657 | 0 | 0
2019-04-29 12:00 | 1026.9885 | 8973.5443 | 6160 | 10000 | 14106.5558 | 0 | 0
2019-04-29 13:00 | 1010.9955 | 8343.5547 | 7873.3333 | 10000 | 15205.8926 | 0 | 0
2019-04-29 14:00 | 1038.9717 | 7131.1787 | 9060 | 10000 | 15152.207 | 0 | 0
2019-04-29 15:00 | 1165.8015 | 5411.8528 | 6160 | 10000 | 10406.0513 | 0 | 0
2019-04-29 16:00 | 1413.8773 | 3074.6676 | 9060 | 10000 | 10720.7903 | 0 | 0
2019-04-29 17:00 | 1529.927 | 901.0963 | 6160 | 10000 | 5531.1693 | 0 | 0
2019-04-29 18:00 | 1656.7376 | 22.4756 | 4266.6667 | 10000 | 2632.4047 | 0 | 0
2019-04-29 19:00 | 1927.0907 | 0 | 6160 | 10000 | 4232.9093 | 0 | 0
2019-04-29 20:00 | 1955.5349 | 0 | 2773.3333 | 10000 | 817.7984 | 0 | 0
2019-04-29 21:00 | 1604.7215 | 0 | 4266.6667 | 10000 | 2661.9451 | 0 | 0
2019-04-29 22:00 | 1259.9048 | 0 | 2773.3333 | 10000 | 1513.4285 | 0 | 0
2019-04-29 23:00 | 917.6447 | 0 | 2773.3333 | 10000 | 1855.6886 | 0 | 0
2019-04-30 | 789.9062 | 0 | 2773.3333 | 10000 | 1983.4271 | 0 | 0
2019-04-30 01:00 | 732.5754 | 0 | 4266.6667 | 10000 | 3534.0913 | 0 | 0
2019-04-30 02:00 | 723.6601 | 0 | 2773.3333 | 10000 | 2049.6732 | 0 | 0
2019-04-30 03:00 | 717.9109 | 0 | 2773.3333 | 10000 | 2055.4224 | 0 | 0
2019-04-30 04:00 | 777.8724 | 0 | 1666.6667 | 10000 | 888.7942 | 0 | 0
2019-04-30 05:00 | 966.4157 | 402.9174 | 2773.3333 | 10000 | 2209.8351 | 0 | 0
2019-04-30 06:00 | 1225.7409 | 2249.2746 | 873.3333 | 10000 | 1896.8671 | 0 | 0
2019-04-30 07:00 | 1154.4378 | 4512.8219 | 1666.6667 | 10000 | 5025.0508 | 0 | 0
2019-04-30 08:00 | 1055.1071 | 4870.8698 | 6160 | 10000 | 9975.7628 | 0 | 0
2019-04-30 09:00 | 1076.255 | 6905.5522 | 4266.6667 | 10000 | 10095.9639 | 0 | 0
2019-04-30 10:00 | 1070.1364 | 7648.4142 | 4266.6667 | 10000 | 10844.9445 | 0 | 0
2019-04-30 11:00 | 1035.4377 | 7736.9378 | 2773.3333 | 10000 | 9474.8334 | 0 | 0
2019-04-30 12:00 | 998.4029 | 8393.1347 | 2773.3333 | 10000 | 10168.0651 | 0 | 0
2019-04-30 13:00 | 982.2519 | 7040.0412 | 2773.3333 | 10000 | 8831.1227 | 0 | 0
2019-04-30 14:00 | 1007.7148 | 4475.2584 | 873.3333 | 10000 | 4340.8769 | 0 | 0
2019-04-30 15:00 | 1130.9068 | 4925.573 | 873.3333 | 10000 | 4667.9996 | 0 | 0
2019-04-30 16:00 | 1377.281 | 2856.6701 | 873.3333 | 10000 | 2352.7225 | 0 | 0
2019-04-30 17:00 | 1495.8592 | 871.0284 | 873.3333 | 10000 | 248.5025 | 0 | 0
2019-04-30 18:00 | 1626.1109 | 40.2925 | 0 | 10000 | -1585.8184 | -1585.8184 | 0
2019-04-30 19:00 | 1900.2785 | 0 | 286.6667 | 8414.1816 | -1613.6118 | -1613.6118 | 0
2019-04-30 20:00 | 1932.2671 | 0 | 286.6667 | 6800.5698 | -1645.6004 | -1645.6004 | 0
2019-04-30 21:00 | 1588.0282 | 0 | 286.6667 | 5154.9694 | -1301.3615 | -1301.3615 | 0
2019-04-30 22:00 | 1249.9527 | 0 | 286.6667 | 3853.6079 | -963.286 | -963.286 | 0
2019-04-30 23:00 | 913.0816 | 0 | 286.6667 | 2890.3219 | -626.4149 | -626.4149 | 0
2019-05-01 | 785.6385 | 0 | 1666.6667 | 2263.907 | 881.0282 | 881.0282 | 0
2019-05-01 01:00 | 735.4434 | 0 | 1666.6667 | 3144.9352 | 931.2232 | 931.2232 | 0
2019-05-01 02:00 | 731.1585 | 0 | 873.3333 | 4076.1584 | 142.1748 | 142.1748 | 0
2019-05-01 03:00 | 736.8025 | 0 | 286.6667 | 4218.3332 | -450.1359 | -450.1359 | 0
2019-05-01 04:00 | 800.0309 | 0 | 286.6667 | 3768.1974 | -513.3643 | -513.3643 | 0
2019-05-01 05:00 | 952.2016 | 464.5586 | 0 | 3254.8331 | -487.643 | -487.643 | 0
2019-05-01 06:00 | 1153.5373 | 2281.9392 | 0 | 2767.1901 | 1128.402 | 1128.402 | 0
2019-05-01 07:00 | 1060.9901 | 4475.532 | 286.6667 | 3895.5921 | 3701.2086 | 3701.2086 | 0
2019-05-01 08:00 | 972.2357 | 6328.2959 | 873.3333 | 7596.8008 | 6229.3936 | 2403.1992 | 0
2019-05-01 09:00 | 993.3196 | 7652.3358 | 1666.6667 | 10000 | 8325.6828 | 0 | 0
2019-05-01 10:00 | 976.5085 | 8451.3017 | 1666.6667 | 10000 | 9141.4598 | 0 | 0
2019-05-01 11:00 | 939.0585 | 8681.22 | 873.3333 | 10000 | 8615.4949 | 0 | 0
2019-05-01 12:00 | 899.3522 | 6210.1518 | 873.3333 | 10000 | 6184.1329 | 0 | 0
2019-05-01 13:00 | 880.2498 | 5678.1767 | 873.3333 | 10000 | 5671.2603 | 0 | 0
2019-05-01 14:00 | 913.6965 | 6654.5095 | 286.6667 | 10000 | 6027.4797 | 0 | 0
2019-05-01 15:00 | 1036.3432 | 4944.3848 | 873.3333 | 10000 | 4781.3749 | 0 | 0
2019-05-01 16:00 | 1275.6933 | 2920.9781 | 873.3333 | 10000 | 2518.6182 | 0 | 0
2019-05-01 17:00 | 1380.5793 | 979.4757 | 873.3333 | 10000 | 472.2297 | 0 | 0
2019-05-01 18:00 | 1459.8557 | 41.3425 | 873.3333 | 10000 | -545.1798 | -545.1798 | 0
2019-05-01 19:00 | 1699.0642 | 0 | 873.3333 | 9454.8202 | -825.7308 | -825.7308 | 0
2019-05-01 20:00 | 1853.0032 | 0 | 873.3333 | 8629.0893 | -979.6699 | -979.6699 | 0
2019-05-01 21:00 | 1553.9772 | 0 | 873.3333 | 7649.4195 | -680.6438 | -680.6438 | 0
2019-05-01 22:00 | 1242.9218 | 0 | 286.6667 | 6968.7756 | -956.2551 | -956.2551 | 0
2019-05-01 23:00 | 911.8556 | 0 | 2773.3333 | 6012.5205 | 1861.4778 | 1861.4778 | 0
2019-05-02 | 789.4635 | 0 | 1666.6667 | 7873.9983 | 877.2032 | 877.2032 | 0
2019-05-02 01:00 | 739.7923 | 0 | 873.3333 | 8751.2015 | 133.541 | 133.541 | 0
2019-05-02 02:00 | 728.2151 | 0 | 286.6667 | 8884.7425 | -441.5485 | -441.5485 | 0
2019-05-02 03:00 | 731.9882 | 0 | 2773.3333 | 8443.194 | 2041.3451 | 1556.806 | 0
2019-05-02 04:00 | 791.3667 | 0 | 1666.6667 | 10000 | 875.2999 | 0 | 0
2019-05-02 05:00 | 951.5265 | 0 | 2773.3333 | 10000 | 1821.8068 | 0 | 0
2019-05-02 06:00 | 1142.838 | 223.0977 | 0 | 10000 | -919.7403 | -919.7403 | 0
2019-05-02 07:00 | 1056.8212 | 536.0725 | 0 | 9080.2597 | -520.7487 | -520.7487 | 0
2019-05-02 08:00 | 964.9838 | 1129.8509 | 0 | 8559.511 | 164.8671 | 164.8671 | 0
2019-05-02 09:00 | 977.799 | 1462.3664 | 0 | 8724.3781 | 484.5674 | 484.5674 | 0
2019-05-02 10:00 | 961.4683 | 1025.2273 | 0 | 9208.9455 | 63.759 | 63.759 | 0
2019-05-02 11:00 | 923.5756 | 1321.5512 | 0 | 9272.7045 | 397.9756 | 397.9756 | 0
2019-05-02 12:00 | 882.4962 | 722.9923 | 873.3333 | 9670.6801 | 713.8294 | 329.3199 | 0
2019-05-02 13:00 | 852.3901 | 951.909 | 0 | 10000 | 99.5189 | 0 | 0
2019-05-02 14:00 | 870.6201 | 1652.4338 | 0 | 10000 | 781.8137 | 0 | 0
2019-05-02 15:00 | 992.7437 | 1675.6201 | 286.6667 | 10000 | 969.5431 | 0 | 0
2019-05-02 16:00 | 1212.4351 | 1104.4991 | 0 | 10000 | -107.936 | -107.936 | 0
2019-05-02 17:00 | 1311.7426 | 1.6779 | 0 | 9892.064 | -1310.0647 | -1310.0647 | 0
2019-05-02 18:00 | 1393.7441 | 0 | 0 | 8581.9993 | -1393.7441 | -1393.7441 | 0
2019-05-02 19:00 | 1638.3356 | 0 | 0 | 7188.2552 | -1638.3356 | -1638.3356 | 0
2019-05-02 20:00 | 1797.3185 | 0 | 9573.3333 | 5549.9196 | 7776.0149 | 4450.0804 | 0
2019-05-02 21:00 | 1503.656 | 0 | 9060 | 10000 | 7556.344 | 0 | 0
2019-05-02 22:00 | 1188.4426 | 0 | 6160 | 10000 | 4971.5574 | 0 | 0
2019-05-02 23:00 | 864.0112 | 0 | 873.3333 | 10000 | 9.3221 | 0 | 0
2019-05-03 | 744.1279 | 0 | 873.3333 | 10000 | 129.2055 | 0 | 0
2019-05-03 01:00 | 693.5906 | 0 | 286.6667 | 10000 | -406.924 | -406.924 | 0
2019-05-03 02:00 | 685.7685 | 0 | 286.6667 | 9593.076 | -399.1018 | -399.1018 | 0
2019-05-03 03:00 | 689.8232 | 0 | 873.3333 | 9193.9742 | 183.5101 | 183.5101 | 0
2019-05-03 04:00 | 746.6804 | 0 | 873.3333 | 9377.4844 | 126.6529 | 126.6529 | 0
2019-05-03 05:00 | 898.9754 | 0 | 2773.3333 | 9504.1373 | 1874.3579 | 495.8627 | 0
2019-05-03 06:00 | 1105.5222 | 42.665 | 6160 | 10000 | 5097.1428 | 0 | 0
2019-05-03 07:00 | 1023.5925 | 594.4948 | 7873.3333 | 10000 | 7444.2356 | 0 | 0
2019-05-03 08:00 | 935.9142 | 423.8543 | 9060 | 10000 | 8547.9401 | 0 | 0
2019-05-03 09:00 | 951.0835 | 393.0067 | 6160 | 10000 | 5601.9232 | 0 | 0
2019-05-03 10:00 | 939.0521 | 670.7409 | 4266.6667 | 10000 | 3998.3555 | 0 | 0
2019-05-03 11:00 | 904.2028 | 472.2394 | 2773.3333 | 10000 | 2341.37 | 0 | 0
2019-05-03 12:00 | 864.3625 | 1237.6841 | 6160 | 10000 | 6533.3215 | 0 | 0
2019-05-03 13:00 | 846.8867 | 827.1133 | 6160 | 10000 | 6140.2266 | 0 | 0
2019-05-03 14:00 | 873.4019 | 744.6078 | 6160 | 10000 | 6031.2058 | 0 | 0
2019-05-03 15:00 | 1007.5363 | 271.8876 | 7873.3333 | 10000 | 7137.6847 | 0 | 0
2019-05-03 16:00 | 1242.116 | 133.3287 | 7873.3333 | 10000 | 6764.546 | 0 | 0
2019-05-03 17:00 | 1336.3412 | 153.5169 | 6160 | 10000 | 4977.1758 | 0 | 0
2019-05-03 18:00 | 1410.6563 | 0 | 4266.6667 | 10000 | 2856.0104 | 0 | 0
2019-05-03 19:00 | 1656.5358 | 0 | 4266.6667 | 10000 | 2610.1308 | 0 | 0
2019-05-03 20:00 | 1815.9459 | 0 | 1666.6667 | 10000 | -149.2792 | -149.2792 | 0
2019-05-03 21:00 | 1516.2402 | 0 | 873.3333 | 9850.7208 | -642.9069 | -642.9069 | 0
2019-05-03 22:00 | 1196.7419 | 0 | 1666.6667 | 9207.8138 | 469.9248 | 469.9248 | 0
2019-05-03 23:00 | 864.7925 | 0 | 873.3333 | 9677.7386 | 8.5408 | 8.5408 | 0
2019-05-04 | 745.0156 | 0 | 873.3333 | 9686.2795 | 128.3177 | 128.3177 | 0
2019-05-04 01:00 | 695.5782 | 0 | 873.3333 | 9814.5972 | 177.7552 | 177.7552 | 0
2019-05-04 02:00 | 696.4565 | 0 | 873.3333 | 9992.3523 | 176.8768 | 7.6477 | 0
2019-05-04 03:00 | 700.7704 | 0 | 1666.6667 | 10000 | 965.8962 | 0 | 0
2019-05-04 04:00 | 759.8714 | 0 | 873.3333 | 10000 | 113.4619 | 0 | 0
2019-05-04 05:00 | 926.8576 | 314.5871 | 286.6667 | 10000 | -325.6039 | -325.6039 | 0
2019-05-04 06:00 | 1121.6505 | 203.6627 | 286.6667 | 9674.3961 | -631.3211 | -631.3211 | 0
2019-05-04 07:00 | 1025.7709 | 374.639 | 286.6667 | 9043.075 | -364.4653 | -364.4653 | 0
2019-05-04 08:00 | 939.1018 | 725.0704 | 286.6667 | 8678.6097 | 72.6352 | 72.6352 | 0
2019-05-04 09:00 | 954.8424 | 1966.6449 | 873.3333 | 8751.2449 | 1885.1359 | 1248.7551 | 0
2019-05-04 10:00 | 944.3991 | 931.3643 | 873.3333 | 10000 | 860.2986 | 0 | 0
2019-05-04 11:00 | 914.936 | 1335.3881 | 2773.3333 | 10000 | 3193.7854 | 0 | 0
2019-05-04 12:00 | 882.5535 | 1624.981 | 4266.6667 | 10000 | 5009.0942 | 0 | 0
2019-05-04 13:00 | 862.431 | 1858.837 | 4266.6667 | 10000 | 5263.0727 | 0 | 0
2019-05-04 14:00 | 885.9762 | 1636.0544 | 6160 | 10000 | 6910.0782 | 0 | 0
2019-05-04 15:00 | 1012.1227 | 1627.6088 | 9060 | 10000 | 9675.4861 | 0 | 0
2019-05-04 16:00 | 1242.8191 | 831.7064 | 9060 | 10000 | 8648.8873 | 0 | 0
2019-05-04 17:00 | 1337.0225 | 884.2994 | 6160 | 10000 | 5707.2769 | 0 | 0
2019-05-04 18:00 | 1411.5738 | 62.0896 | 2773.3333 | 10000 | 1423.8492 | 0 | 0
2019-05-04 19:00 | 1652.5941 | 0 | 1666.6667 | 10000 | 14.0725 | 0 | 0
2019-05-04 20:00 | 1806.5436 | 0 | 873.3333 | 10000 | -933.2102 | -933.2102 | 0
2019-05-04 21:00 | 1504.4574 | 0 | 873.3333 | 9066.7898 | -631.124 | -631.124 | 0
2019-05-04 22:00 | 1185.633 | 0 | 286.6667 | 8435.6657 | -898.9663 | -898.9663 | 0
2019-05-04 23:00 | 857.3594 | 0 | 873.3333 | 7536.6995 | 15.9739 | 15.9739 | 0
2019-05-05 | 735.5719 | 0 | 873.3333 | 7552.6733 | 137.7615 | 137.7615 | 0
2019-05-05 01:00 | 682.8616 | 0 | 286.6667 | 7690.4348 | -396.195 | -396.195 | 0
2019-05-05 02:00 | 674.8612 | 0 | 873.3333 | 7294.2399 | 198.4721 | 198.4721 | 0
2019-05-05 03:00 | 677.8412 | 0 | 873.3333 | 7492.712 | 195.4922 | 195.4922 | 0
2019-05-05 04:00 | 739.7781 | 0 | 286.6667 | 7688.2042 | -453.1115 | -453.1115 | 0
2019-05-05 05:00 | 891.927 | 469.9383 | 873.3333 | 7235.0927 | 451.3447 | 451.3447 | 0
2019-05-05 06:00 | 1117.0456 | 1886.4508 | 286.6667 | 7686.4374 | 1056.0719 | 1056.0719 | 0
2019-05-05 07:00 | 1039.693 | 4489.9162 | 0 | 8742.5092 | 3450.2233 | 1257.4908 | 0
2019-05-05 08:00 | 969.2856 | 6217.9304 | 2773.3333 | 10000 | 8021.9781 | 0 | 0
2019-05-05 09:00 | 1004.7548 | 7460.9459 | 2773.3333 | 10000 | 9229.5244 | 0 | 0
2019-05-05 10:00 | 1024.7574 | 8226.4997 | 4266.6667 | 10000 | 11468.409 | 0 | 0
2019-05-05 11:00 | 985.2284 | 8498.546 | 7873.3333 | 10000 | 15386.651 | 0 | 0
2019-05-05 12:00 | 955.1765 | 8286.5757 | 6160 | 10000 | 13491.3992 | 0 | 0
2019-05-05 13:00 | 936.879 | 7590.7049 | 6160 | 10000 | 12813.826 | 0 | 0
2019-05-05 14:00 | 961.8192 | 6493.0587 | 6160 | 10000 | 11691.2395 | 0 | 0
2019-05-05 15:00 | 1087.18 | 4913.1312 | 2773.3333 | 10000 | 6599.2846 | 0 | 0
2019-05-05 16:00 | 1321.2467 | 2933.5246 | 2773.3333 | 10000 | 4385.6113 | 0 | 0
2019-05-05 17:00 | 1403.5609 | 968.7565 | 7873.3333 | 10000 | 7438.529 | 0 | 0
2019-05-05 18:00 | 1469.7454 | 68.5814 | 6160 | 10000 | 4758.836 | 0 | 0
2019-05-05 19:00 | 1702.4387 | 0 | 2773.3333 | 10000 | 1070.8947 | 0 | 0
2019-05-05 20:00 | 1850.491 | 0 | 873.3333 | 10000 | -977.1577 | -977.1577 | 0
2019-05-05 21:00 | 1544.269 | 0 | 0 | 9022.8423 | -1544.269 | -1544.269 | 0
2019-05-05 22:00 | 1219.9652 | 0 | 0 | 7478.5733 | -1219.9652 | -1219.9652 | 0
2019-05-05 23:00 | 886.0045 | 0 | 0 | 6258.6081 | -886.0045 | -886.0045 | 0
2019-05-06 | 764.0611 | 0 | 0 | 5372.6036 | -764.0611 | -764.0611 | 0
2019-05-06 01:00 | 706.9194 | 0 | 0 | 4608.5425 | -706.9194 | -706.9194 | 0
2019-05-06 02:00 | 694.5533 | 0 | 0 | 3901.6231 | -694.5533 | -694.5533 | 0
2019-05-06 03:00 | 695.5111 | 0 | 286.6667 | 3207.0698 | -408.8444 | -408.8444 | 0
2019-05-06 04:00 | 754.1329 | 0 | 286.6667 | 2798.2254 | -467.4662 | -467.4662 | 0
2019-05-06 05:00 | 919.1565 | 552.3427 | 873.3333 | 2330.7592 | 506.5195 | 506.5195 | 0
2019-05-06 06:00 | 1123.9886 | 2257.8214 | 2773.3333 | 2837.2787 | 3907.1662 | 3907.1662 | 0
2019-05-06 07:00 | 1042.4665 | 4370.1495 | 4266.6667 | 6744.4449 | 7594.3497 | 3255.5551 | 0
2019-05-06 08:00 | 964.6223 | 6113.2792 | 0 | 10000 | 5148.657 | 0 | 0
2019-05-06 09:00 | 981.9912 | 6577.5273 | 0 | 10000 | 5595.5362 | 0 | 0
2019-05-06 10:00 | 973.387 | 8088.2478 | 286.6667 | 10000 | 7401.5275 | 0 | 0
2019-05-06 11:00 | 934.4796 | 8305.3173 | 4266.6667 | 10000 | 11637.5043 | 0 | 0
2019-05-06 12:00 | 892.761 | 7221.6964 | 2773.3333 | 10000 | 9102.2688 | 0 | 0
2019-05-06 13:00 | 867.635 | 7455.8157 | 4266.6667 | 10000 | 10854.8474 | 0 | 0
2019-05-06 14:00 | 890.1469 | 6328.0556 | 7873.3333 | 10000 | 13311.242 | 0 | 0
2019-05-06 15:00 | 1015.17 | 4741.6179 | 4266.6667 | 10000 | 7993.1146 | 0 | 0
2019-05-06 16:00 | 1237.5129 | 1324.1077 | 4266.6667 | 10000 | 4353.2614 | 0 | 0
2019-05-06 17:00 | 1339.3461 | 1010.2589 | 873.3333 | 10000 | 544.2462 | 0 | 0
2019-05-06 18:00 | 1414.835 | 92.1989 | 2773.3333 | 10000 | 1450.6973 | 0 | 0
2019-05-06 19:00 | 1659.5599 | 0 | 1666.6667 | 10000 | 7.1067 | 0 | 0
2019-05-06 20:00 | 1820.4852 | 0 | 873.3333 | 10000 | -947.1519 | -947.1519 | 0
2019-05-06 21:00 | 1513.2969 | 0 | 1666.6667 | 9052.8481 | 153.3697 | 153.3697 | 0
2019-05-06 22:00 | 1180.5042 | 0 | 2773.3333 | 9206.2178 | 1592.8292 | 793.7822 | 0
2019-05-06 23:00 | 842.5191 | 0 | 2773.3333 | 10000 | 1930.8142 | 0 | 0
2019-05-07 | 714.1359 | 0 | 1666.6667 | 10000 | 952.5308 | 0 | 0
2019-05-07 01:00 | 658.444 | 0 | 1666.6667 | 10000 | 1008.2227 | 0 | 0
2019-05-07 02:00 | 648.2723 | 0 | 873.3333 | 10000 | 225.061 | 0 | 0
2019-05-07 03:00 | 650.9706 | 0 | 873.3333 | 10000 | 222.3627 | 0 | 0
2019-05-07 04:00 | 710.3781 | 0 | 1666.6667 | 10000 | 956.2885 | 0 | 0
2019-05-07 05:00 | 873.2318 | 507.9044 | 4266.6667 | 10000 | 3901.3393 | 0 | 0
2019-05-07 06:00 | 1085.3552 | 2309.0919 | 4266.6667 | 10000 | 5490.4034 | 0 | 0
2019-05-07 07:00 | 1008.6788 | 4409.7325 | 4266.6667 | 10000 | 7667.7203 | 0 | 0
2019-05-07 08:00 | 937.6029 | 6181.4489 | 6160 | 10000 | 11403.846 | 0 | 0
2019-05-07 09:00 | 951.5523 | 7477.8003 | 6160 | 10000 | 12686.248 | 0 | 0
2019-05-07 10:00 | 954.0698 | 8181.1207 | 6160 | 10000 | 13387.0509 | 0 | 0
2019-05-07 11:00 | 925.8698 | 8399.6092 | 9060 | 10000 | 16533.7394 | 0 | 0
2019-05-07 12:00 | 887.3647 | 8223.382 | 6160 | 10000 | 13496.0173 | 0 | 0
2019-05-07 13:00 | 864.2239 | 7473.8143 | 9060 | 10000 | 15669.5905 | 0 | 0
2019-05-07 14:00 | 883.5061 | 5450.5469 | 9060 | 10000 | 13627.0408 | 0 | 0
2019-05-07 15:00 | 1006.2554 | 4754.867 | 9060 | 10000 | 12808.6116 | 0 | 0
2019-05-07 16:00 | 1226.6609 | 2872.5747 | 9060 | 10000 | 10705.9138 | 0 | 0
2019-05-07 17:00 | 1329.3443 | 896.7976 | 9060 | 10000 | 8627.4533 | 0 | 0
2019-05-07 18:00 | 1406.2199 | 107.6009 | 6160 | 10000 | 4861.381 | 0 | 0
2019-05-07 19:00 | 1651.058 | 0 | 4266.6667 | 10000 | 2615.6087 | 0 | 0
2019-05-07 20:00 | 1808.4082 | 0 | 1666.6667 | 10000 | -141.7415 | -141.7415 | 0
2019-05-07 21:00 | 1500.5145 | 0 | 873.3333 | 9858.2585 | -627.1812 | -627.1812 | 0
2019-05-07 22:00 | 1168.1774 | 0 | 286.6667 | 9231.0773 | -881.5107 | -881.5107 | 0
2019-05-07 23:00 | 830.5674 | 0 | 1666.6667 | 8349.5665 | 836.0993 | 836.0993 | 0
2019-05-08 | 702.6296 | 0 | 4266.6667 | 9185.6658 | 3564.0371 | 814.3342 | 0
2019-05-08 01:00 | 649.0888 | 0 | 4266.6667 | 10000 | 3617.5779 | 0 | 0
2019-05-08 02:00 | 644.6295 | 0 | 6160 | 10000 | 5515.3705 | 0 | 0
2019-05-08 03:00 | 646.9191 | 0 | 4266.6667 | 10000 | 3619.7475 | 0 | 0
2019-05-08 04:00 | 709.075 | 0 | 4266.6667 | 10000 | 3557.5917 | 0 | 0
2019-05-08 05:00 | 867.3513 | 316.4351 | 2773.3333 | 10000 | 2222.4172 | 0 | 0
2019-05-08 06:00 | 1062.9565 | 626.735 | 4266.6667 | 10000 | 3830.4452 | 0 | 0
2019-05-08 07:00 | 972.4081 | 884.7916 | 2773.3333 | 10000 | 2685.7168 | 0 | 0
2019-05-08 08:00 | 885.1025 | 1245.749 | 4266.6667 | 10000 | 4627.3132 | 0 | 0
2019-05-08 09:00 | 887.4523 | 3203.2088 | 2773.3333 | 10000 | 5089.0899 | 0 | 0
2019-05-08 10:00 | 884.8246 | 5840.1278 | 2773.3333 | 10000 | 7728.6365 | 0 | 0
2019-05-08 11:00 | 856.9668 | 4668.6596 | 4266.6667 | 10000 | 8078.3595 | 0 | 0
2019-05-08 12:00 | 821.6524 | 4621.7821 | 2773.3333 | 10000 | 6573.4631 | 0 | 0
2019-05-08 13:00 | 803.2029 | 6110.487 | 2773.3333 | 10000 | 8080.6174 | 0 | 0
2019-05-08 14:00 | 830.9965 | 5654.5787 | 4266.6667 | 10000 | 9090.2489 | 0 | 0
2019-05-08 15:00 | 960.1297 | 4571.4156 | 4266.6667 | 10000 | 7877.9526 | 0 | 0
2019-05-08 16:00 | 1174.0058 | 2081.8933 | 2773.3333 | 10000 | 3681.2208 | 0 | 0
2019-05-08 17:00 | 1283.8737 | 378.9031 | 2773.3333 | 10000 | 1868.3627 | 0 | 0
2019-05-08 18:00 | 1363.1181 | 0.03565 | 1666.6667 | 10000 | 303.5843 | 0 | 0
2019-05-08 19:00 | 1607.9502 | 0 | 873.3333 | 10000 | -734.6168 | -734.6168 | 0
2019-05-08 20:00 | 1766.0519 | 0 | 1666.6667 | 9265.3832 | -99.3852 | -99.3852 | 0
2019-05-08 21:00 | 1468.6435 | 0 | 2773.3333 | 9165.998 | 1304.6898 | 834.002 | 0
2019-05-08 22:00 | 1150.3964 | 0 | 1666.6667 | 10000 | 516.2703 | 0 | 0
2019-05-08 23:00 | 817.8852 | 0 | 0 | 10000 | -817.8852 | -817.8852 | 0
2019-05-09 | 692.5325 | 0 | 286.6667 | 9182.1148 | -405.8659 | -405.8659 | 0
2019-05-09 01:00 | 641.5741 | 0 | 286.6667 | 8776.249 | -354.9074 | -354.9074 | 0
2019-05-09 02:00 | 634.8879 | 0 | 286.6667 | 8421.3416 | -348.2212 | -348.2212 | 0
2019-05-09 03:00 | 636.4368 | 0 | 286.6667 | 8073.1204 | -349.7702 | -349.7702 | 0
2019-05-09 04:00 | 696.6089 | 0 | 0 | 7723.3502 | -696.6089 | -696.6089 | 0
2019-05-09 05:00 | 847.4133 | 408.5455 | 286.6667 | 7026.7412 | -152.2011 | -152.2011 | 0
2019-05-09 06:00 | 1056.879 | 1432.2077 | 286.6667 | 6874.5401 | 661.9954 | 661.9954 | 0
2019-05-09 07:00 | 977.8028 | 1874.2688 | 286.6667 | 7536.5355 | 1183.1327 | 1183.1327 | 0
2019-05-09 08:00 | 905.9035 | 2028.3493 | 286.6667 | 8719.6682 | 1409.1124 | 1280.3318 | 0
2019-05-09 09:00 | 924.7239 | 2995.8293 | 2773.3333 | 10000 | 4844.4388 | 0 | 0
2019-05-09 10:00 | 934.4119 | 4185.2318 | 4266.6667 | 10000 | 7517.4866 | 0 | 0
2019-05-09 11:00 | 901.815 | 2878.8951 | 873.3333 | 10000 | 2850.4134 | 0 | 0
2019-05-09 12:00 | 868.0897 | 2483.6619 | 2773.3333 | 10000 | 4388.9055 | 0 | 0
2019-05-09 13:00 | 851.5901 | 2006.9409 | 1666.6667 | 10000 | 2822.0174 | 0 | 0
2019-05-09 14:00 | 878.2889 | 1235.5289 | 873.3333 | 10000 | 1230.5734 | 0 | 0
2019-05-09 15:00 | 1003.8695 | 1076.1907 | 286.6667 | 10000 | 358.9878 | 0 | 0
2019-05-09 16:00 | 1222.9451 | 683.5462 | 286.6667 | 10000 | -252.7322 | -252.7322 | 0
2019-05-09 17:00 | 1321.906 | 864.3538 | 286.6667 | 9747.2678 | -170.8855 | -170.8855 | 0
2019-05-09 18:00 | 1396.7277 | 102.4408 | 0 | 9576.3823 | -1294.2869 | -1294.2869 | 0
2019-05-09 19:00 | 1632.2182 | 0 | 0 | 8282.0954 | -1632.2182 | -1632.2182 | 0
2019-05-09 20:00 | 1784.1334 | 0 | 0 | 6649.8772 | -1784.1334 | -1784.1334 | 0
2019-05-09 21:00 | 1478.6092 | 0 | 0 | 4865.7438 | -1478.6092 | -1478.6092 | 0
2019-05-09 22:00 | 1153.8272 | 0 | 0 | 3387.1346 | -1153.8272 | -1153.8272 | 0
2019-05-09 23:00 | 820.6982 | 0 | 0 | 2233.3074 | -820.6982 | -820.6982 | 0
2019-05-10 | 693.8056 | 0 | 0 | 1412.6092 | -693.8056 | -693.8056 | 0
2019-05-10 01:00 | 638.4652 | 0 | 286.6667 | 718.8036 | -351.7985 | -351.7985 | 0
2019-05-10 02:00 | 631.8515 | 0 | 286.6667 | 367.0051 | -345.1848 | -345.1848 | 0
2019-05-10 03:00 | 634.6574 | 0 | 873.3333 | 21.8203 | 238.6759 | 238.6759 | 0
2019-05-10 04:00 | 692.8019 | 0 | 873.3333 | 260.4962 | 180.5315 | 180.5315 | 0
2019-05-10 05:00 | 847.5559 | 314.9183 | 873.3333 | 441.0277 | 340.6957 | 340.6957 | 0
2019-05-10 06:00 | 1046.3589 | 491.311 | 873.3333 | 781.7234 | 318.2855 | 318.2855 | 0
2019-05-10 07:00 | 957.2482 | 2502.4057 | 286.6667 | 1100.0089 | 1831.8242 | 1831.8242 | 0
2019-05-10 08:00 | 873.7958 | 2360.6636 | 0 | 2931.8331 | 1486.8679 | 1486.8679 | 0
2019-05-10 09:00 | 879.0858 | 4071.5796 | 873.3333 | 4418.701 | 4065.8271 | 4065.8271 | 0
2019-05-10 10:00 | 879.8813 | 5441.0663 | 873.3333 | 8484.5281 | 5434.5183 | 1515.4719 | 0
2019-05-10 11:00 | 855.0093 | 7281.0859 | 873.3333 | 10000 | 7299.4099 | 0 | 0
2019-05-10 12:00 | 818.5285 | 6734.009 | 1666.6667 | 10000 | 7582.1472 | 0 | 0
2019-05-10 13:00 | 802.0839 | 6335.0464 | 1666.6667 | 10000 | 7199.6291 | 0 | 0
2019-05-10 14:00 | 830.9965 | 5530.0406 | 2773.3333 | 10000 | 7472.3775 | 0 | 0
2019-05-10 15:00 | 960.1297 | 3802.3715 | 873.3333 | 10000 | 3715.5751 | 0 | 0
2019-05-10 16:00 | 1174.0058 | 2537.9994 | 873.3333 | 10000 | 2237.3269 | 0 | 0
2019-05-10 17:00 | 1282.078 | 920.0771 | 286.6667 | 10000 | -75.3343 | -75.3343 | 0
2019-05-10 18:00 | 1352.8778 | 120.7247 | 0 | 9924.6657 | -1232.1531 | -1232.1531 | 0
2019-05-10 19:00 | 1592.1039 | 0 | 286.6667 | 8692.5125 | -1305.4373 | -1305.4373 | 0
2019-05-10 20:00 | 1749.8139 | 0 | 873.3333 | 7387.0753 | -876.4806 | -876.4806 | 0
2019-05-10 21:00 | 1452.8994 | 0 | 873.3333 | 6510.5947 | -579.5661 | -579.5661 | 0
2019-05-10 22:00 | 1137.4148 | 0 | 286.6667 | 5931.0286 | -850.7482 | -850.7482 | 0
2019-05-10 23:00 | 808.1705 | 0 | 0 | 5080.2804 | -808.1705 | -808.1705 | 0
2019-05-11 | 690.4856 | 0 | 286.6667 | 4272.1099 | -403.8189 | -403.8189 | 0
2019-05-11 01:00 | 638.125 | 0 | 286.6667 | 3868.291 | -351.4583 | -351.4583 | 0
2019-05-11 02:00 | 633.2435 | 0 | 0 | 3516.8327 | -633.2435 | -633.2435 | 0
2019-05-11 03:00 | 638.4623 | 0 | 873.3333 | 2883.5892 | 234.871 | 234.871 | 0
2019-05-11 04:00 | 699.7881 | 0 | 286.6667 | 3118.4602 | -413.1215 | -413.1215 | 0
2019-05-11 05:00 | 856.5398 | 613.4157 | 1666.6667 | 2705.3387 | 1423.5426 | 1423.5426 | 0
2019-05-11 06:00 | 1057.7475 | 2419.3447 | 873.3333 | 4128.8813 | 2234.9306 | 2234.9306 | 0
2019-05-11 07:00 | 969.9108 | 4610.718 | 873.3333 | 6363.8119 | 4514.1405 | 3636.1881 | 0
2019-05-11 08:00 | 888.2278 | 6407.6539 | 2773.3333 | 10000 | 8292.7595 | 0 | 0
2019-05-11 09:00 | 895.1463 | 7671.6822 | 2773.3333 | 10000 | 9549.8692 | 0 | 0
2019-05-11 10:00 | 896.5985 | 8468.309 | 4266.6667 | 10000 | 11838.3772 | 0 | 0
2019-05-11 11:00 | 869.1967 | 8738.5544 | 4266.6667 | 10000 | 12136.0244 | 0 | 0
2019-05-11 12:00 | 833.8749 | 8567.8128 | 2773.3333 | 10000 | 10507.2712 | 0 | 0
2019-05-11 13:00 | 812.4669 | 7939.3597 | 2773.3333 | 10000 | 9900.226 | 0 | 0
2019-05-11 14:00 | 836.5322 | 6838.7855 | 4266.6667 | 10000 | 10268.9199 | 0 | 0
2019-05-11 15:00 | 965.6494 | 4542.8254 | 1666.6667 | 10000 | 5243.8427 | 0 | 0
2019-05-11 16:00 | 1181.9977 | 2666.7246 | 873.3333 | 10000 | 2358.0603 | 0 | 0
2019-05-11 17:00 | 1283.6001 | 981.4203 | 286.6667 | 10000 | -15.5131 | -15.5131 | 0
2019-05-11 18:00 | 1360.1972 | 157.619 | 0 | 9984.4869 | -1202.5782 | -1202.5782 | 0
2019-05-11 19:00 | 1603.5274 | 0 | 286.6667 | 8781.9088 | -1316.8608 | -1316.8608 | 0
2019-05-11 20:00 | 1761.5327 | 0 | 873.3333 | 7465.048 | -888.1994 | -888.1994 | 0
2019-05-11 21:00 | 1464.7083 | 0 | 286.6667 | 6576.8486 | -1178.0417 | -1178.0417 | 0
2019-05-11 22:00 | 1150.2071 | 0 | 286.6667 | 5398.807 | -863.5405 | -863.5405 | 0
2019-05-11 23:00 | 823.469 | 0 | 286.6667 | 4535.2665 | -536.8023 | -536.8023 | 0
2019-05-12 | 704.1674 | 0 | 0 | 3998.4642 | -704.1674 | -704.1674 | 0
2019-05-12 01:00 | 655.6768 | 0 | 0 | 3294.2968 | -655.6768 | -655.6768 | 0
2019-05-12 02:00 | 650.1581 | 0 | 0 | 2638.62 | -650.1581 | -650.1581 | 0
2019-05-12 03:00 | 655.5004 | 0 | 286.6667 | 1988.4619 | -368.8337 | -368.8337 | 0
2019-05-12 04:00 | 715.9752 | 0 | 286.6667 | 1619.6282 | -429.3085 | -429.3085 | 0
2019-05-12 05:00 | 871.5271 | 563.7691 | 286.6667 | 1190.3197 | -21.0913 | -21.0913 | 0
2019-05-12 06:00 | 1063.0554 | 1506.9968 | 286.6667 | 1169.2284 | 730.6081 | 730.6081 | 0
2019-05-12 07:00 | 974.0956 | 1951.9433 | 1666.6667 | 1899.8365 | 2644.5144 | 2644.5144 | 0
2019-05-12 08:00 | 889.1531 | 2757.984 | 873.3333 | 4544.3509 | 2742.1642 | 2742.1642 | 0
2019-05-12 09:00 | 882.9613 | 3770.9926 | 1666.6667 | 7286.5151 | 4554.698 | 2713.4849 | 0
2019-05-12 10:00 | 882.5042 | 4839.8509 | 1666.6667 | 10000 | 5624.0134 | 0 | 0
2019-05-12 11:00 | 856.8515 | 5221.4692 | 873.3333 | 10000 | 5237.951 | 0 | 0
2019-05-12 12:00 | 817.799 | 5762.6661 | 1666.6667 | 10000 | 6611.5337 | 0 | 0
2019-05-12 13:00 | 800.5394 | 5180.7994 | 1666.6667 | 10000 | 6046.9267 | 0 | 0
2019-05-12 14:00 | 830.9965 | 5902.7476 | 2773.3333 | 10000 | 7845.0844 | 0 | 0
2019-05-12 15:00 | 960.1297 | 3161.5087 | 873.3333 | 10000 | 3074.7123 | 0 | 0
2019-05-12 16:00 | 1174.0058 | 1938.7884 | 873.3333 | 10000 | 1638.116 | 0 | 0
2019-05-12 17:00 | 1282.078 | 966.3358 | 286.6667 | 10000 | -29.0756 | -29.0756 | 0
2019-05-12 18:00 | 1352.8778 | 158.9139 | 0 | 9970.9244 | -1193.9639 | -1193.9639 | 0
2019-05-12 19:00 | 1588.2639 | 0 | 0 | 8776.9605 | -1588.2639 | -1588.2639 | 0
2019-05-12 20:00 | 1736.5987 | 0 | 0 | 7188.6966 | -1736.5987 | -1736.5987 | 0
2019-05-12 21:00 | 1434.4497 | 0 | 286.6667 | 5452.0979 | -1147.783 | -1147.783 | 0
2019-05-12 22:00 | 1122.884 | 0 | 0 | 4304.3148 | -1122.884 | -1122.884 | 0
2019-05-12 23:00 | 798.3683 | 0 | 0 | 3181.4308 | -798.3683 | -798.3683 | 0
2019-05-13 | 685.598 | 0 | 0 | 2383.0625 | -685.598 | -685.598 | 0
2019-05-13 01:00 | 634.3628 | 0 | 0 | 1697.4645 | -634.3628 | -634.3628 | 0
2019-05-13 02:00 | 628.0716 | 0 | 0 | 1063.1017 | -628.0716 | -628.0716 | 0
2019-05-13 03:00 | 635.9019 | 0 | 0 | 435.0301 | -635.9019 | -435.0301 | -200.8718
2019-05-13 04:00 | 700.7459 | 0 | 286.6667 | 0 | -414.0792 | 0 | -614.951
2019-05-13 05:00 | 860.4121 | 590.4675 | 873.3333 | 0 | 603.3887 | 603.3887 | -11.5623
2019-05-13 06:00 | 1080.0958 | 2466.6856 | 873.3333 | 603.3887 | 2259.9231 | 2259.9231 | 0
2019-05-13 07:00 | 1013.6293 | 4593.6566 | 286.6667 | 2863.3118 | 3866.6939 | 3866.6939 | 0
2019-05-13 08:00 | 947.8215 | 5478.4884 | 286.6667 | 6730.0057 | 4817.3337 | 3269.9943 | 0
2019-05-13 09:00 | 966.8576 | 6710.7318 | 873.3333 | 10000 | 6617.2076 | 0 | 0
2019-05-13 10:00 | 965.1536 | 8358.2736 | 2773.3333 | 10000 | 10166.4533 | 0 | 0
2019-05-13 11:00 | 931.4862 | 8586.5532 | 4266.6667 | 10000 | 11921.7337 | 0 | 0
2019-05-13 12:00 | 895.4162 | 7546.8014 | 6160 | 10000 | 12811.3852 | 0 | 0
2019-05-13 13:00 | 871.164 | 7662.9997 | 7873.3333 | 10000 | 14665.169 | 0 | 0
2019-05-13 14:00 | 886.6109 | 5736.2391 | 6160 | 10000 | 11009.6282 | 0 | 0
2019-05-13 15:00 | 1007.7672 | 3996.0349 | 4266.6667 | 10000 | 7254.9344 | 0 | 0
2019-05-13 16:00 | 1216.8199 | 3088.5044 | 2773.3333 | 10000 | 4645.0179 | 0 | 0
2019-05-13 17:00 | 1322.822 | 1096.947 | 4266.6667 | 10000 | 4040.7917 | 0 | 0
2019-05-13 18:00 | 1399.7026 | 143.8362 | 2773.3333 | 10000 | 1517.467 | 0 | 0
2019-05-13 19:00 | 1640.4894 | 0 | 4266.6667 | 10000 | 2626.1773 | 0 | 0
2019-05-13 20:00 | 1803.1878 | 0 | 2773.3333 | 10000 | 970.1456 | 0 | 0
2019-05-13 21:00 | 1497.9409 | 0 | 4266.6667 | 10000 | 2768.7258 | 0 | 0
2019-05-13 22:00 | 1164.7258 | 0 | 4266.6667 | 10000 | 3101.9408 | 0 | 0
2019-05-13 23:00 | 829.16 | 0 | 4266.6667 | 10000 | 3437.5066 | 0 | 0
2019-05-14 | 704.5919 | 0 | 4266.6667 | 10000 | 3562.0747 | 0 | 0
2019-05-14 01:00 | 650.4714 | 0 | 2773.3333 | 10000 | 2122.8619 | 0 | 0
2019-05-14 02:00 | 641.616 | 0 | 9060 | 10000 | 8418.384 | 0 | 0
2019-05-14 03:00 | 645.7857 | 0 | 9060 | 10000 | 8414.2143 | 0 | 0
2019-05-14 04:00 | 707.0775 | 0 | 7873.3333 | 10000 | 7166.2559 | 0 | 0
2019-05-14 05:00 | 863.1941 | 628.5452 | 9060 | 10000 | 8825.351 | 0 | 0
2019-05-14 06:00 | 1084.3055 | 2427.0819 | 9060 | 10000 | 10402.7764 | 0 | 0
2019-05-14 07:00 | 1016.8857 | 4535.5666 | 9060 | 10000 | 12578.681 | 0 | 0
2019-05-14 08:00 | 955.7392 | 6246.4285 | 9573.3333 | 10000 | 14864.0227 | 0 | 0
2019-05-14 09:00 | 973.533 | 7489.2554 | 9060 | 10000 | 15575.7224 | 0 | 0
2019-05-14 10:00 | 977.2747 | 8218.7211 | 9060 | 10000 | 16301.4464 | 0 | 0
2019-05-14 11:00 | 947.9819 | 8528.7887 | 7873.3333 | 10000 | 15454.1402 | 0 | 0
2019-05-14 12:00 | 912.4339 | 8370.6039 | 4266.6667 | 10000 | 11724.8367 | 0 | 0
2019-05-14 13:00 | 898.1323 | 7680.1428 | 6160 | 10000 | 12942.0104 | 0 | 0
2019-05-14 14:00 | 926.042 | 6647.2415 | 6160 | 10000 | 11881.1995 | 0 | 0
2019-05-14 15:00 | 1058.1347 | 5093.3971 | 6160 | 10000 | 10195.2624 | 0 | 0
2019-05-14 16:00 | 1290.4438 | 3099.695 | 6160 | 10000 | 7969.2512 | 0 | 0
2019-05-14 17:00 | 1388.6107 | 1004.4065 | 4266.6667 | 10000 | 3882.4625 | 0 | 0
2019-05-14 18:00 | 1467.0562 | 152.0875 | 4266.6667 | 10000 | 2951.698 | 0 | 0
2019-05-14 19:00 | 1706.9443 | 0 | 4266.6667 | 10000 | 2559.7223 | 0 | 0
2019-05-14 20:00 | 1861.1757 | 0 | 6160 | 10000 | 4298.8243 | 0 | 0
2019-05-14 21:00 | 1552.3336 | 0 | 2773.3333 | 10000 | 1220.9997 | 0 | 0
2019-05-14 22:00 | 1217.4096 | 0 | 2773.3333 | 10000 | 1555.9237 | 0 | 0
2019-05-14 23:00 | 874.4829 | 0 | 1666.6667 | 10000 | 792.1838 | 0 | 0
2019-05-15 | 742.626 | 0 | 2773.3333 | 10000 | 2030.7073 | 0 | 0
2019-05-15 01:00 | 688.635 | 0 | 2773.3333 | 10000 | 2084.6983 | 0 | 0
2019-05-15 02:00 | 684.6068 | 0 | 4266.6667 | 10000 | 3582.0599 | 0 | 0
2019-05-15 03:00 | 685.1793 | 0 | 4266.6667 | 10000 | 3581.4874 | 0 | 0
2019-05-15 04:00 | 740.2686 | 0 | 4266.6667 | 10000 | 3526.3981 | 0 | 0
2019-05-15 05:00 | 887.6069 | 389.8902 | 6160 | 10000 | 5662.2834 | 0 | 0
2019-05-15 06:00 | 1106.9696 | 805.3507 | 7873.3333 | 10000 | 7571.7145 | 0 | 0
2019-05-15 07:00 | 1020.4475 | 1280.3249 | 7873.3333 | 10000 | 8133.2108 | 0 | 0
2019-05-15 08:00 | 952.9437 | 2254.2139 | 4266.6667 | 10000 | 5567.9369 | 0 | 0
2019-05-15 09:00 | 975.237 | 4101.2726 | 1666.6667 | 10000 | 4792.7023 | 0 | 0
2019-05-15 10:00 | 975.5226 | 828.6946 | 1666.6667 | 10000 | 1519.8386 | 0 | 0
2019-05-15 11:00 | 955.7456 | 3257.8545 | 4266.6667 | 10000 | 6568.7756 | 0 | 0
2019-05-15 12:00 | 928.6532 | 3204.406 | 7873.3333 | 10000 | 10149.0862 | 0 | 0
2019-05-15 13:00 | 914.3203 | 2914.6244 | 2773.3333 | 10000 | 4773.6374 | 0 | 0
2019-05-15 14:00 | 939.8602 | 3518.732 | 4266.6667 | 10000 | 6845.5385 | 0 | 0
2019-05-15 15:00 | 1066.0059 | 2409.7698 | 7873.3333 | 10000 | 9217.0973 | 0 | 0
2019-05-15 16:00 | 1293.7363 | 2332.0689 | 9060 | 10000 | 10098.3326 | 0 | 0
2019-05-15 17:00 | 1385.3473 | 917.5562 | 4266.6667 | 10000 | 3798.8756 | 0 | 0
2019-05-15 18:00 | 1453.0686 | 155.4524 | 1666.6667 | 10000 | 369.0504 | 0 | 0
2019-05-15 19:00 | 1684.6892 | 0 | 873.3333 | 10000 | -811.3559 | -811.3559 | 0
2019-05-15 20:00 | 1834.1141 | 0 | 286.6667 | 9188.6441 | -1547.4474 | -1547.4474 | 0
2019-05-15 21:00 | 1529.0278 | 0 | 873.3333 | 7641.1967 | -655.6944 | -655.6944 | 0
2019-05-15 22:00 | 1204.2945 | 0 | 873.3333 | 6985.5023 | -330.9611 | -330.9611 | 0
2019-05-15 23:00 | 864.6126 | 0 | 873.3333 | 6654.5411 | 8.7208 | 8.7208 | 0
2019-05-16 | 737.9054 | 0 | 873.3333 | 6663.2619 | 135.4279 | 135.4279 | 0
2019-05-16 01:00 | 684.0029 | 0 | 873.3333 | 6798.6898 | 189.3304 | 189.3304 | 0
2019-05-16 02:00 | 672.3993 | 0 | 2773.3333 | 6988.0202 | 2100.934 | 2100.934 | 0
2019-05-16 03:00 | 670.7753 | 0 | 4266.6667 | 9088.9541 | 3595.8913 | 911.0459 | 0
2019-05-16 04:00 | 724.8991 | 0 | 4266.6667 | 10000 | 3541.7676 | 0 | 0
2019-05-16 05:00 | 873.8263 | 434.5597 | 2773.3333 | 10000 | 2334.0667 | 0 | 0
2019-05-16 06:00 | 1092.4797 | 1136.6956 | 4266.6667 | 10000 | 4310.8826 | 0 | 0
2019-05-16 07:00 | 1010.3077 | 2472.2723 | 4266.6667 | 10000 | 5728.6312 | 0 | 0
2019-05-16 08:00 | 940.6001 | 2811.6292 | 4266.6667 | 10000 | 6137.6958 | 0 | 0
2019-05-16 09:00 | 967.2184 | 4611.5678 | 2773.3333 | 10000 | 6417.6827 | 0 | 0
2019-05-16 10:00 | 962.5205 | 4811.2032 | 2773.3333 | 10000 | 6622.0161 | 0 | 0
2019-05-16 11:00 | 941.2539 | 3162.9911 | 1666.6667 | 10000 | 3888.4038 | 0 | 0
2019-05-16 12:00 | 913.8682 | 2215.4531 | 873.3333 | 10000 | 2174.9183 | 0 | 0
2019-05-16 13:00 | 916.4512 | 1998.1054 | 1666.6667 | 10000 | 2748.3209 | 0 | 0
2019-05-16 14:00 | 947.0662 | 1509.7154 | 6160 | 10000 | 6722.6492 | 0 | 0
2019-05-16 15:00 | 1074.4653 | 775.5209 | 873.3333 | 10000 | 574.389 | 0 | 0
2019-05-16 16:00 | 1293.4201 | 176.3916 | 2773.3333 | 10000 | 1656.3049 | 0 | 0
2019-05-16 17:00 | 1384.517 | 169.4191 | 2773.3333 | 10000 | 1558.2355 | 0 | 0
2019-05-16 18:00 | 1451.5431 | 0 | 873.3333 | 10000 | -578.2097 | -578.2097 | 0
2019-05-16 19:00 | 1681.2563 | 0 | 873.3333 | 9421.7903 | -807.923 | -807.923 | 0
2019-05-16 20:00 | 1823.3156 | 0 | 286.6667 | 8613.8673 | -1536.649 | -1536.649 | 0
2019-05-16 21:00 | 1515.254 | 0 | 873.3333 | 7077.2183 | -641.9206 | -641.9206 | 0
2019-05-16 22:00 | 1185.8885 | 0 | 286.6667 | 6435.2977 | -899.2218 | -899.2218 | 0
2019-05-16 23:00 | 849.5576 | 0 | 0 | 5536.0759 | -849.5576 | -849.5576 | 0
2019-05-17 | 720.158 | 0 | 286.6667 | 4686.5182 | -433.4914 | -433.4914 | 0
2019-05-17 01:00 | 662.4273 | 0 | 0 | 4253.0269 | -662.4273 | -662.4273 | 0
2019-05-17 02:00 | 650.6829 | 0 | 0 | 3590.5996 | -650.6829 | -650.6829 | 0
2019-05-17 03:00 | 649.4862 | 0 | 0 | 2939.9167 | -649.4862 | -649.4862 | 0
2019-05-17 04:00 | 707.5117 | 0 | 0 | 2290.4304 | -707.5117 | -707.5117 | 0
2019-05-17 05:00 | 857.2125 | 0 | 286.6667 | 1582.9188 | -570.5458 | -570.5458 | 0
2019-05-17 06:00 | 1066.7037 | 735.1812 | 286.6667 | 1012.373 | -44.8558 | -44.8558 | 0
2019-05-17 07:00 | 989.7387 | 2325.2678 | 286.6667 | 967.5172 | 1622.1958 | 1622.1958 | 0
2019-05-17 08:00 | 919.1415 | 2557.5505 | 286.6667 | 2589.713 | 1925.0757 | 1925.0757 | 0
2019-05-17 09:00 | 936.8356 | 2314.9546 | 286.6667 | 4514.7887 | 1664.7857 | 1664.7857 | 0
2019-05-17 10:00 | 928.8779 | 7367.2887 | 873.3333 | 6179.5744 | 7311.7441 | 3820.4256 | 0
2019-05-17 11:00 | 894.7814 | 8553.4251 | 4266.6667 | 10000 | 11925.3104 | 0 | 0
2019-05-17 12:00 | 863.62 | 6339.5889 | 873.3333 | 10000 | 6349.3023 | 0 | 0
2019-05-17 13:00 | 843.4728 | 7771.9863 | 1666.6667 | 10000 | 8595.1802 | 0 | 0
2019-05-17 14:00 | 869.0045 | 6632.5296 | 6160 | 10000 | 11923.525 | 0 | 0
2019-05-17 15:00 | 994.9872 | 5043.7033 | 1666.6667 | 10000 | 5715.3828 | 0 | 0
2019-05-17 16:00 | 1225.6038 | 3049.7471 | 1666.6667 | 10000 | 3490.8099 | 0 | 0
2019-05-17 17:00 | 1325.647 | 1109.9697 | 6160 | 10000 | 5944.3227 | 0 | 0
2019-05-17 18:00 | 1402.8316 | 173.5143 | 6160 | 10000 | 4930.6827 | 0 | 0
2019-05-17 19:00 | 1643.0532 | 0 | 6160 | 10000 | 4516.9468 | 0 | 0
2019-05-17 20:00 | 1799.5167 | 0 | 2773.3333 | 10000 | 973.8166 | 0 | 0
2019-05-17 21:00 | 1502.559 | 0 | 2773.3333 | 10000 | 1270.7743 | 0 | 0
2019-05-17 22:00 | 1182.8506 | 0 | 1666.6667 | 10000 | 483.8161 | 0 | 0
2019-05-17 23:00 | 850.6995 | 0 | 4266.6667 | 10000 | 3415.9672 | 0 | 0
2019-05-18 | 726.4939 | 0 | 6160 | 10000 | 5433.5061 | 0 | 0
2019-05-18 01:00 | 670.6698 | 0 | 4266.6667 | 10000 | 3595.9969 | 0 | 0
2019-05-18 02:00 | 662.7234 | 0 | 4266.6667 | 10000 | 3603.9432 | 0 | 0
2019-05-18 03:00 | 663.5943 | 0 | 873.3333 | 10000 | 209.739 | 0 | 0
2019-05-18 04:00 | 721.6552 | 0 | 1666.6667 | 10000 | 945.0115 | 0 | 0
2019-05-18 05:00 | 872.2143 | 631.7399 | 873.3333 | 10000 | 632.8589 | 0 | 0
2019-05-18 06:00 | 1080.6537 | 2494.3189 | 1666.6667 | 10000 | 3080.3319 | 0 | 0
2019-05-18 07:00 | 1000.8994 | 4610.9687 | 873.3333 | 10000 | 4483.4026 | 0 | 0
2019-05-18 08:00 | 925.3408 | 6318.1598 | 2773.3333 | 10000 | 8166.1524 | 0 | 0
2019-05-18 09:00 | 943.4144 | 7536.3836 | 2773.3333 | 10000 | 9366.3024 | 0 | 0
2019-05-18 10:00 | 936.0809 | 8251.9411 | 2773.3333 | 10000 | 10089.1936 | 0 | 0
2019-05-18 11:00 | 904.6416 | 8427.3656 | 4266.6667 | 10000 | 11789.3906 | 0 | 0
2019-05-18 12:00 | 879.5226 | 4885.415 | 4266.6667 | 10000 | 8272.5592 | 0 | 0
2019-05-18 13:00 | 869.1524 | 2901.3028 | 2773.3333 | 10000 | 4805.4837 | 0 | 0
2019-05-18 14:00 | 894.8536 | 2502.0159 | 2773.3333 | 10000 | 4380.4957 | 0 | 0
2019-05-18 15:00 | 1021.6303 | 1817.6992 | 6160 | 10000 | 6956.0689 | 0 | 0
2019-05-18 16:00 | 1251.6773 | 269.192 | 2773.3333 | 10000 | 1790.848 | 0 | 0
2019-05-18 17:00 | 1340.4634 | 985.2107 | 4266.6667 | 10000 | 3911.414 | 0 | 0
2019-05-18 18:00 | 1410.7625 | 194.0234 | 9060 | 10000 | 7843.2609 | 0 | 0
2019-05-18 19:00 | 1644.5328 | 0 | 9060 | 10000 | 7415.4672 | 0 | 0
2019-05-18 20:00 | 1793.634 | 0 | 9060 | 10000 | 7266.366 | 0 | 0
2019-05-18 21:00 | 1488.8241 | 0 | 7873.3333 | 10000 | 6384.5092 | 0 | 0
2019-05-18 22:00 | 1165.237 | 0 | 7873.3333 | 10000 | 6708.0963 | 0 | 0
2019-05-18 23:00 | 826.8196 | 0 | 2773.3333 | 10000 | 1946.5138 | 0 | 0
2019-05-19 | 701.7447 | 0 | 4266.6667 | 10000 | 3564.922 | 0 | 0
2019-05-19 01:00 | 650.1066 | 0 | 6160 | 10000 | 5509.8934 | 0 | 0
2019-05-19 02:00 | 640.8411 | 0 | 4266.6667 | 10000 | 3625.8256 | 0 | 0
2019-05-19 03:00 | 640.7436 | 0 | 2773.3333 | 10000 | 2132.5898 | 0 | 0
2019-05-19 04:00 | 699.8892 | 15.3767 | 2773.3333 | 10000 | 2088.8208 | 0 | 0
2019-05-19 05:00 | 859.8252 | 672.6603 | 1666.6667 | 10000 | 1479.5017 | 0 | 0
2019-05-19 06:00 | 1058.2104 | 2539.875 | 873.3333 | 10000 | 2354.998 | 0 | 0
2019-05-19 07:00 | 966.4962 | 4749.0745 | 1666.6667 | 10000 | 5449.245 | 0 | 0
2019-05-19 08:00 | 879.8033 | 6514.9386 | 6160 | 10000 | 11795.1353 | 0 | 0
2019-05-19 09:00 | 877.4494 | 6542.5064 | 6160 | 10000 | 11825.057 | 0 | 0
2019-05-19 10:00 | 875.2091 | 5153.4628 | 6160 | 10000 | 10438.2537 | 0 | 0
2019-05-19 11:00 | 848.6769 | 4858.1807 | 6160 | 10000 | 10169.5039 | 0 | 0
2019-05-19 12:00 | 817.8206 | 6325.1886 | 9060 | 10000 | 14567.368 | 0 | 0
2019-05-19 13:00 | 800.5394 | 4096.9152 | 9060 | 10000 | 12356.3758 | 0 | 0
2019-05-19 14:00 | 830.9965 | 4494.9475 | 4266.6667 | 10000 | 7930.6176 | 0 | 0
2019-05-19 15:00 | 960.1297 | 1421.1424 | 9060 | 10000 | 9521.0127 | 0 | 0
2019-05-19 16:00 | 1174.0058 | 2733.6546 | 7873.3333 | 10000 | 9432.9822 | 0 | 0
2019-05-19 17:00 | 1282.078 | 1092.5552 | 4266.6667 | 10000 | 4077.1438 | 0 | 0
2019-05-19 18:00 | 1352.8778 | 169.0477 | 9060 | 10000 | 7876.1699 | 0 | 0
2019-05-19 19:00 | 1588.2639 | 0 | 2773.3333 | 10000 | 1185.0694 | 0 | 0
2019-05-19 20:00 | 1736.5987 | 0 | 4266.6667 | 10000 | 2530.0679 | 0 | 0
2019-05-19 21:00 | 1430.0299 | 0 | 1666.6667 | 10000 | 236.6368 | 0 | 0
2019-05-19 22:00 | 1112.4899 | 0 | 1666.6667 | 10000 | 554.1768 | 0 | 0
2019-05-19 23:00 | 784.1044 | 0 | 873.3333 | 10000 | 89.2289 | 0 | 0
2019-05-20 | 669.1406 | 0 | 286.6667 | 10000 | -382.4739 | -382.4739 | 0
2019-05-20 01:00 | 617.7073 | 0 | 286.6667 | 9617.5261 | -331.0406 | -331.0406 | 0
2019-05-20 02:00 | 611.3879 | 0 | 0 | 9286.4854 | -611.3879 | -611.3879 | 0
2019-05-20 03:00 | 617.4015 | 0 | 873.3333 | 8675.0975 | 255.9318 | 255.9318 | 0
2019-05-20 04:00 | 679.0572 | 23.5336 | 873.3333 | 8931.0293 | 217.8098 | 217.8098 | 0
2019-05-20 05:00 | 838.1855 | 648.8519 | 1666.6667 | 9148.8391 | 1477.333 | 851.1609 | 0
2019-05-20 06:00 | 1045.0073 | 2066.32 | 4266.6667 | 10000 | 5287.9794 | 0 | 0
2019-05-20 07:00 | 965.1863 | 3939.5297 | 4266.6667 | 10000 | 7241.0101 | 0 | 0
2019-05-20 08:00 | 890.6172 | 6391.0813 | 4266.6667 | 10000 | 9767.1308 | 0 | 0
2019-05-20 09:00 | 888.4956 | 7580.8184 | 4266.6667 | 10000 | 10958.9895 | 0 | 0
2019-05-20 10:00 | 907.2331 | 8269.4832 | 4266.6667 | 10000 | 11628.9168 | 0 | 0
2019-05-20 11:00 | 885.4087 | 7332.3954 | 2773.3333 | 10000 | 9220.32 | 0 | 0
2019-05-20 12:00 | 856.6399 | 7322.7101 | 2773.3333 | 10000 | 9239.4035 | 0 | 0
2019-05-20 13:00 | 843.9611 | 2881.9966 | 2773.3333 | 10000 | 4811.3689 | 0 | 0
2019-05-20 14:00 | 872.1246 | 2071.9964 | 1666.6667 | 10000 | 2866.5384 | 0 | 0
2019-05-20 15:00 | 999.9915 | 1707.405 | 873.3333 | 10000 | 1580.7469 | 0 | 0
2019-05-20 16:00 | 1213.2394 | 1546.6488 | 873.3333 | 10000 | 1206.7427 | 0 | 0
2019-05-20 17:00 | 1320.1557 | 863.7627 | 1666.6667 | 10000 | 1210.2737 | 0 | 0
2019-05-20 18:00 | 1390.8827 | 159.7672 | 286.6667 | 10000 | -944.4488 | -944.4488 | 0
2019-05-20 19:00 | 1626.9465 | 0 | 286.6667 | 9055.5512 | -1340.2798 | -1340.2798 | 0
2019-05-20 20:00 | 1776.1153 | 0 | 873.3333 | 7715.2714 | -902.7819 | -902.7819 | 0
2019-05-20 21:00 | 1455.8321 | 0 | 286.6667 | 6812.4894 | -1169.1655 | -1169.1655 | 0
2019-05-20 22:00 | 1108.494 | 0 | 286.6667 | 5643.324 | -821.8274 | -821.8274 | 0
2019-05-20 23:00 | 753.62 | 0 | 873.3333 | 4821.4966 | 119.7133 | 119.7133 | 0
2019-05-21 | 616.6278 | 0 | 873.3333 | 4941.2099 | 256.7055 | 256.7055 | 0
2019-05-21 01:00 | 554.7377 | 0 | 873.3333 | 5197.9154 | 318.5956 | 318.5956 | 0
2019-05-21 02:00 | 548.5423 | 0 | 286.6667 | 5516.511 | -261.8757 | -261.8757 | 0
2019-05-21 03:00 | 558.0081 | 0 | 0 | 5254.6353 | -558.0081 | -558.0081 | 0
2019-05-21 04:00 | 622.9212 | 31.9895 | 0 | 4696.6272 | -590.9316 | -590.9316 | 0
2019-05-21 05:00 | 785.3873 | 731.5472 | 0 | 4105.6956 | -53.8401 | -53.8401 | 0
2019-05-21 06:00 | 1016.1773 | 2451.1985 | 873.3333 | 4051.8555 | 2308.3545 | 2308.3545 | 0
2019-05-21 07:00 | 949.6873 | 4485.4945 | 1666.6667 | 6360.2101 | 5202.4738 | 3639.7899 | 0
2019-05-21 08:00 | 887.5639 | 6185.9765 | 1666.6667 | 10000 | 6965.0792 | 0 | 0
2019-05-21 09:00 | 898.6209 | 6014.2596 | 873.3333 | 10000 | 5988.972 | 0 | 0
2019-05-21 10:00 | 907.2331 | 8237.1521 | 873.3333 | 10000 | 8203.2523 | 0 | 0
2019-05-21 11:00 | 885.4087 | 8441.8751 | 1666.6667 | 10000 | 9223.1331 | 0 | 0
2019-05-21 12:00 | 856.6399 | 8286.9954 | 2773.3333 | 10000 | 10203.6889 | 0 | 0
2019-05-21 13:00 | 843.9611 | 5146.4179 | 2773.3333 | 10000 | 7075.7902 | 0 | 0
2019-05-21 14:00 | 872.1246 | 6645.129 | 4266.6667 | 10000 | 10039.671 | 0 | 0
2019-05-21 15:00 | 999.9915 | 5047.4811 | 2773.3333 | 10000 | 6820.823 | 0 | 0
2019-05-21 16:00 | 1213.2394 | 2020.113 | 2773.3333 | 10000 | 3580.2069 | 0 | 0
2019-05-21 17:00 | 1320.1557 | 394.7478 | 2773.3333 | 10000 | 1847.9255 | 0 | 0
2019-05-21 18:00 | 1390.8827 | 40.0648 | 1666.6667 | 10000 | 315.8488 | 0 | 0
2019-05-21 19:00 | 1626.9465 | 0 | 873.3333 | 10000 | -753.6131 | -753.6131 | 0
2019-05-21 20:00 | 1776.1153 | 0 | 286.6667 | 9246.3869 | -1489.4486 | -1489.4486 | 0
2019-05-21 21:00 | 1455.8321 | 0 | 1666.6667 | 7756.9383 | 210.8345 | 210.8345 | 0
2019-05-21 22:00 | 1120.7391 | 0 | 873.3333 | 7967.7728 | -247.4058 | -247.4058 | 0
2019-05-21 23:00 | 785.6773 | 0 | 873.3333 | 7720.367 | 87.656 | 87.656 | 0
2019-05-22 | 662.6805 | 0 | 286.6667 | 7808.023 | -376.0139 | -376.0139 | 0
2019-05-22 01:00 | 614.4852 | 0 | 873.3333 | 7432.0091 | 258.8481 | 258.8481 | 0
2019-05-22 02:00 | 612.6358 | 0 | 0 | 7690.8573 | -612.6358 | -612.6358 | 0
2019-05-22 03:00 | 616.8026 | 0 | 286.6667 | 7078.2214 | -330.1359 | -330.1359 | 0
2019-05-22 04:00 | 677.0118 | 0 | 286.6667 | 6748.0855 | -390.3451 | -390.3451 | 0
2019-05-22 05:00 | 834.3248 | 674.3485 | 286.6667 | 6357.7404 | 126.6904 | 126.6904 | 0
2019-05-22 06:00 | 1034.4284 | 1713.7047 | 873.3333 | 6484.4308 | 1552.6097 | 1552.6097 | 0
2019-05-22 07:00 | 943.4332 | 3120.847 | 286.6667 | 8037.0405 | 2464.0804 | 1962.9595 | 0
2019-05-22 08:00 | 860.538 | 3034.1979 | 873.3333 | 10000 | 3046.9933 | 0 | 0
2019-05-22 09:00 | 861.4457 | 4204.1481 | 286.6667 | 10000 | 3629.3691 | 0 | 0
2019-05-22 10:00 | 863.7511 | 5110.5954 | 286.6667 | 10000 | 4533.5109 | 0 | 0
2019-05-22 11:00 | 832.3486 | 6155.3957 | 286.6667 | 10000 | 5609.7138 | 0 | 0
2019-05-22 12:00 | 808.2658 | 3965.6381 | 873.3333 | 10000 | 4030.7057 | 0 | 0
2019-05-22 13:00 | 800.5394 | 5022.2535 | 286.6667 | 10000 | 4508.3808 | 0 | 0
2019-05-22 14:00 | 830.9965 | 1132.566 | 873.3333 | 10000 | 1174.9028 | 0 | 0
2019-05-22 15:00 | 960.1297 | 2889.6027 | 1666.6667 | 10000 | 3596.1397 | 0 | 0
2019-05-22 16:00 | 1174.0058 | 1582.3747 | 1666.6667 | 10000 | 2075.0356 | 0 | 0
2019-05-22 17:00 | 1282.078 | 987.0197 | 873.3333 | 10000 | 578.275 | 0 | 0
2019-05-22 18:00 | 1352.8778 | 222.4284 | 286.6667 | 10000 | -843.7828 | -843.7828 | 0
2019-05-22 19:00 | 1588.2639 | 0 | 0 | 9156.2172 | -1588.2639 | -1588.2639 | 0
2019-05-22 20:00 | 1736.5987 | 0 | 0 | 7567.9533 | -1736.5987 | -1736.5987 | 0
2019-05-22 21:00 | 1424.4323 | 0 | 0 | 5831.3546 | -1424.4323 | -1424.4323 | 0
2019-05-22 22:00 | 1091.2534 | 0 | 286.6667 | 4406.9223 | -804.5868 | -804.5868 | 0
2019-05-22 23:00 | 746.3246 | 0 | 0 | 3602.3356 | -746.3246 | -746.3246 | 0
2019-05-23 | 624.3857 | 0 | 0 | 2856.011 | -624.3857 | -624.3857 | 0
2019-05-23 01:00 | 583.7465 | 0 | 0 | 2231.6252 | -583.7465 | -583.7465 | 0
2019-05-23 02:00 | 584.1067 | 0 | 0 | 1647.8787 | -584.1067 | -584.1067 | 0
2019-05-23 03:00 | 593.6991 | 0 | 0 | 1063.7721 | -593.6991 | -593.6991 | 0
2019-05-23 04:00 | 659.2638 | 39.7164 | 0 | 470.0729 | -619.5474 | -470.0729 | -149.4745
2019-05-23 05:00 | 815.6532 | 615.7514 | 0 | 0 | -199.9018 | 0 | -349.3762
2019-05-23 06:00 | 1016.2637 | 2505.39 | 286.6667 | 0 | 1775.793 | 1775.793 | 0
2019-05-23 07:00 | 925.4024 | 4593.177 | 286.6667 | 1775.793 | 3954.4413 | 3954.4413 | 0
2019-05-23 08:00 | 843.5154 | 6293.9615 | 873.3333 | 5730.2343 | 6323.7794 | 4269.7657 | 0
2019-05-23 09:00 | 838.4702 | 7530.1758 | 286.6667 | 10000 | 6978.3723 | 0 | 0
2019-05-23 10:00 | 848.981 | 8261.8127 | 286.6667 | 10000 | 7699.4984 | 0 | 0
2019-05-23 11:00 | 832.3486 | 8514.0871 | 873.3333 | 10000 | 8555.0719 | 0 | 0
2019-05-23 12:00 | 808.2658 | 4670.8273 | 286.6667 | 10000 | 4149.2282 | 0 | 0
2019-05-23 13:00 | 800.5394 | 7829.0102 | 286.6667 | 10000 | 7315.1375 | 0 | 0
2019-05-23 14:00 | 830.9965 | 2418.1418 | 873.3333 | 10000 | 2460.4786 | 0 | 0
2019-05-23 15:00 | 960.1297 | 4619.2797 | 286.6667 | 10000 | 3945.8167 | 0 | 0
2019-05-23 16:00 | 1174.0058 | 1966.1768 | 286.6667 | 10000 | 1078.8377 | 0 | 0
2019-05-23 17:00 | 1282.078 | 934.1611 | 0 | 10000 | -347.9169 | -347.9169 | 0
2019-05-23 18:00 | 1352.8778 | 220.6263 | 0 | 9652.0831 | -1132.2515 | -1132.2515 | 0
2019-05-23 19:00 | 1588.2639 | 0 | 0 | 8519.8316 | -1588.2639 | -1588.2639 | 0
2019-05-23 20:00 | 1736.5987 | 0 | 0 | 6931.5677 | -1736.5987 | -1736.5987 | 0
2019-05-23 21:00 | 1424.4323 | 0 | 286.6667 | 5194.9689 | -1137.7656 | -1137.7656 | 0
2019-05-23 22:00 | 1091.2534 | 0 | 0 | 4057.2033 | -1091.2534 | -1091.2534 | 0
2019-05-23 23:00 | 746.3246 | 0 | 0 | 2965.9499 | -746.3246 | -746.3246 | 0
2019-05-24 | 612.2474 | 0 | 0 | 2219.6253 | -612.2474 | -612.2474 | 0
2019-05-24 01:00 | 566.044 | 0 | 0 | 1607.3779 | -566.044 | -566.044 | 0
2019-05-24 02:00 | 570.0109 | 0 | 0 | 1041.3339 | -570.0109 | -570.0109 | 0
2019-05-24 03:00 | 581.6772 | 0 | 0 | 471.323 | -581.6772 | -471.323 | -110.3542
2019-05-24 04:00 | 649.0819 | 32.9383 | 0 | 0 | -616.1436 | 0 | -726.4978
2019-05-24 05:00 | 807.7214 | 653.7888 | 0 | 0 | -153.9326 | 0 | -880.4304
2019-05-24 06:00 | 1012.0077 | 2083.907 | 0 | 0 | 1071.8993 | 1071.8993 | 0
2019-05-24 07:00 | 932.3416 | 3686.5147 | 0 | 1071.8993 | 2754.1731 | 2754.1731 | 0
2019-05-24 08:00 | 851.2958 | 6254.0611 | 0 | 3826.0724 | 5402.7653 | 5402.7653 | 0
2019-05-24 09:00 | 847.9525 | 5712.3398 | 0 | 9228.8377 | 4864.3873 | 771.1623 | 0
2019-05-24 10:00 | 855.8018 | 2685.1361 | 0 | 10000 | 1829.3344 | 0 | 0
2019-05-24 11:00 | 832.3486 | 5325.8949 | 286.6667 | 10000 | 4780.213 | 0 | 0
2019-05-24 12:00 | 808.2658 | 5076.0333 | 0 | 10000 | 4267.7675 | 0 | 0
2019-05-24 13:00 | 800.5394 | 6871.6962 | 0 | 10000 | 6071.1568 | 0 | 0
2019-05-24 14:00 | 830.9965 | 4826.9295 | 286.6667 | 10000 | 4282.5996 | 0 | 0
2019-05-24 15:00 | 960.1297 | 1660.7426 | 873.3333 | 10000 | 1573.9462 | 0 | 0
2019-05-24 16:00 | 1174.0058 | 2319.7409 | 873.3333 | 10000 | 2019.0684 | 0 | 0
2019-05-24 17:00 | 1282.078 | 1200.6253 | 873.3333 | 10000 | 791.8806 | 0 | 0
2019-05-24 18:00 | 1352.8778 | 212.735 | 286.6667 | 10000 | -853.4761 | -853.4761 | 0
2019-05-24 19:00 | 1588.2639 | 0 | 286.6667 | 9146.5239 | -1301.5973 | -1301.5973 | 0
2019-05-24 20:00 | 1740.1709 | 0 | 0 | 7844.9266 | -1740.1709 | -1740.1709 | 0
2019-05-24 21:00 | 1442.7163 | 0 | 0 | 6104.7558 | -1442.7163 | -1442.7163 | 0
2019-05-24 22:00 | 1125.3634 | 0 | 0 | 4662.0395 | -1125.3634 | -1125.3634 | 0
2019-05-24 23:00 | 797.9027 | 0 | 0 | 3536.6761 | -797.9027 | -797.9027 | 0
2019-05-25 | 674.9949 | 0 | 0 | 2738.7733 | -674.9949 | -674.9949 | 0
2019-05-25 01:00 | 625.4151 | 0 | 0 | 2063.7785 | -625.4151 | -625.4151 | 0
2019-05-25 02:00 | 618.5378 | 0 | 286.6667 | 1438.3633 | -331.8711 | -331.8711 | 0
2019-05-25 03:00 | 620.205 | 0 | 873.3333 | 1106.4922 | 253.1283 | 253.1283 | 0
2019-05-25 04:00 | 679.5895 | 47.0074 | 873.3333 | 1359.6206 | 240.7512 | 240.7512 | 0
2019-05-25 05:00 | 832.1843 | 660.3507 | 2773.3333 | 1600.3718 | 2601.4998 | 2601.4998 | 0
2019-05-25 06:00 | 1051.8865 | 2512.1094 | 4266.6667 | 4201.8715 | 5726.8896 | 5726.8896 | 0
2019-05-25 07:00 | 971.1856 | 4634.1665 | 4266.6667 | 9928.7611 | 7929.6475 | 71.2389 | 0
2019-05-25 08:00 | 904.3189 | 6332.4681 | 4266.6667 | 10000 | 9694.8158 | 0 | 0
2019-05-25 09:00 | 927.5649 | 7519.7982 | 7873.3333 | 10000 | 14465.5666 | 0 | 0
2019-05-25 10:00 | 930.4011 | 8229.9635 | 7873.3333 | 10000 | 15172.8957 | 0 | 0
2019-05-25 11:00 | 907.326 | 8477.5159 | 7873.3333 | 10000 | 15443.5233 | 0 | 0
2019-05-25 12:00 | 878.5027 | 8293.4469 | 7873.3333 | 10000 | 15288.2775 | 0 | 0
2019-05-25 13:00 | 869.6487 | 7675.7796 | 7873.3333 | 10000 | 14679.4643 | 0 | 0
2019-05-25 14:00 | 896.7336 | 6594.7003 | 7873.3333 | 10000 | 13571.3001 | 0 | 0
2019-05-25 15:00 | 1022.8904 | 5085.2287 | 6160 | 10000 | 10222.3383 | 0 | 0
2019-05-25 16:00 | 1245.782 | 3210.3457 | 6160 | 10000 | 8124.5637 | 0 | 0
2019-05-25 17:00 | 1338.5917 | 1184.0527 | 4266.6667 | 10000 | 4112.1277 | 0 | 0
2019-05-25 18:00 | 1405.9503 | 190.509 | 6160 | 10000 | 4944.5587 | 0 | 0
2019-05-25 19:00 | 1638.2902 | 0 | 6160 | 10000 | 4521.7098 | 0 | 0
2019-05-25 20:00 | 1786.2663 | 0 | 6160 | 10000 | 4373.7337 | 0 | 0
2019-05-25 21:00 | 1479.5189 | 0 | 4266.6667 | 10000 | 2787.1478 | 0 | 0
2019-05-25 22:00 | 1154.1875 | 0 | 4266.6667 | 10000 | 3112.4792 | 0 | 0
2019-05-25 23:00 | 816.9412 | 0 | 4266.6667 | 10000 | 3449.7255 | 0 | 0
2019-05-26 | 673.508 | 0 | 1666.6667 | 10000 | 993.1587 | 0 | 0
2019-05-26 01:00 | 623.8209 | 0 | 286.6667 | 10000 | -337.1543 | -337.1543 | 0
2019-05-26 02:00 | 620.2176 | 0 | 7873.3333 | 9662.8457 | 7253.1157 | 337.1543 | 0
2019-05-26 03:00 | 613.1945 | 0 | 2773.3333 | 10000 | 2160.1388 | 0 | 0
2019-05-26 04:00 | 665.1167 | 46.5497 | 1666.6667 | 10000 | 1048.0997 | 0 | 0
2019-05-26 05:00 | 782.9753 | 626.2946 | 1666.6667 | 10000 | 1509.986 | 0 | 0
2019-05-26 06:00 | 945.3313 | 2062.5204 | 2773.3333 | 10000 | 3890.5225 | 0 | 0
2019-05-26 07:00 | 795.7722 | 3971.448 | 1666.6667 | 10000 | 4842.3424 | 0 | 0
2019-05-26 08:00 | 653.4611 | 6209.9931 | 2773.3333 | 10000 | 8329.8653 | 0 | 0
2019-05-26 09:00 | 631.8849 | 7289.0484 | 1666.6667 | 10000 | 8323.8302 | 0 | 0
2019-05-26 10:00 | 632.3872 | 8017.5574 | 2773.3333 | 10000 | 10158.5035 | 0 | 0
2019-05-26 11:00 | 636.009 | 8277.5217 | 2773.3333 | 10000 | 10414.846 | 0 | 0
2019-05-26 12:00 | 625.0384 | 8098.1056 | 1666.6667 | 10000 | 9139.7339 | 0 | 0
2019-05-26 13:00 | 638.3419 | 7496.0657 | 4266.6667 | 10000 | 11124.3904 | 0 | 0
2019-05-26 14:00 | 676.9832 | 6469.9368 | 1666.6667 | 10000 | 7459.6202 | 0 | 0
2019-05-26 15:00 | 812.2638 | 4463.1063 | 873.3333 | 10000 | 4524.1758 | 0 | 0
2019-05-26 16:00 | 1039.3866 | 1533.4951 | 873.3333 | 10000 | 1367.4418 | 0 | 0
2019-05-26 17:00 | 1136.7793 | 1200.5574 | 873.3333 | 10000 | 937.1115 | 0 | 0
2019-05-26 18:00 | 1208.0734 | 241.761 | 286.6667 | 10000 | -679.6457 | -679.6457 | 0
2019-05-26 19:00 | 1448.5633 | 0 | 286.6667 | 9320.3543 | -1161.8967 | -1161.8967 | 0
2019-05-26 20:00 | 1603.6752 | 0 | 0 | 8158.4576 | -1603.6752 | -1603.6752 | 0
2019-05-26 21:00 | 1340.995 | 0 | 0 | 6554.7825 | -1340.995 | -1340.995 | 0
2019-05-26 22:00 | 1084.497 | 0 | 0 | 5213.7874 | -1084.497 | -1084.497 | 0
2019-05-26 23:00 | 799.9891 | 0 | 0 | 4129.2904 | -799.9891 | -799.9891 | 0
2019-05-27 | 688.8872 | 0 | 286.6667 | 3329.3013 | -402.2205 | -402.2205 | 0
2019-05-27 01:00 | 639.3724 | 0 | 286.6667 | 2927.0808 | -352.7057 | -352.7057 | 0
2019-05-27 02:00 | 636.1253 | 0 | 286.6667 | 2574.3751 | -349.4586 | -349.4586 | 0
2019-05-27 03:00 | 629.1012 | 0 | 286.6667 | 2224.9164 | -342.4346 | -342.4346 | 0
2019-05-27 04:00 | 679.3106 | 0 | 0 | 1882.4819 | -679.3106 | -679.3106 | 0
2019-05-27 05:00 | 796.0559 | 409.538 | 0 | 1203.1713 | -386.5179 | -386.5179 | 0
2019-05-27 06:00 | 950.7136 | 683.077 | 286.6667 | 816.6534 | 19.0301 | 19.0301 | 0
2019-05-27 07:00 | 808.3853 | 2680.8167 | 286.6667 | 835.6835 | 2159.0981 | 2159.0981 | 0
2019-05-27 08:00 | 669.6122 | 2228.4424 | 286.6667 | 2994.7815 | 1845.4968 | 1845.4968 | 0
2019-05-27 09:00 | 666.8314 | 7067.678 | 286.6667 | 4840.2784 | 6687.5133 | 5159.7216 | 0
2019-05-27 10:00 | 654.25 | 7567.7141 | 2773.3333 | 10000 | 9686.7974 | 0 | 0
2019-05-27 11:00 | 649.6315 | 7807.7329 | 2773.3333 | 10000 | 9931.4348 | 0 | 0
2019-05-27 12:00 | 635.5227 | 7601.9623 | 1666.6667 | 10000 | 8633.1062 | 0 | 0
2019-05-27 13:00 | 641.1367 | 6322.7287 | 1666.6667 | 10000 | 7348.2587 | 0 | 0
2019-05-27 14:00 | 674.468 | 2371.8451 | 1666.6667 | 10000 | 3364.0438 | 0 | 0
2019-05-27 15:00 | 807.1945 | 3636.216 | 2773.3333 | 10000 | 5602.3548 | 0 | 0
2019-05-27 16:00 | 1032.439 | 403.9306 | 2773.3333 | 10000 | 2144.8249 | 0 | 0
2019-05-27 17:00 | 1128.6259 | 122.6464 | 2773.3333 | 10000 | 1767.3538 | 0 | 0
2019-05-27 18:00 | 1199.7301 | 251.4337 | 873.3333 | 10000 | -74.9631 | -74.9631 | 0
2019-05-27 19:00 | 1440.4647 | 0 | 873.3333 | 9925.0369 | -567.1314 | -567.1314 | 0
2019-05-27 20:00 | 1594.4511 | 0 | 873.3333 | 9357.9055 | -721.1178 | -721.1178 | 0
2019-05-27 21:00 | 1333.2029 | 0 | 286.6667 | 8636.7877 | -1046.5363 | -1046.5363 | 0
2019-05-27 22:00 | 1078.4921 | 0 | 286.6667 | 7590.2515 | -791.8254 | -791.8254 | 0
2019-05-27 23:00 | 793.6948 | 0 | 286.6667 | 6798.426 | -507.0281 | -507.0281 | 0
2019-05-28 | 681.9822 | 0 | 286.6667 | 6291.398 | -395.3156 | -395.3156 | 0
2019-05-28 01:00 | 633.9121 | 0 | 873.3333 | 5896.0824 | 239.4212 | 239.4212 | 0
2019-05-28 02:00 | 631.5011 | 0 | 873.3333 | 6135.5036 | 241.8322 | 241.8322 | 0
2019-05-28 03:00 | 625.8343 | 0 | 286.6667 | 6377.3359 | -339.1676 | -339.1676 | 0
2019-05-28 04:00 | 675.8407 | 132.0016 | 0 | 6038.1682 | -543.8391 | -543.8391 | 0
2019-05-28 05:00 | 798.7235 | 701.669 | 0 | 5494.3291 | -97.0544 | -97.0544 | 0
2019-05-28 06:00 | 941.8414 | 2649.2895 | 0 | 5397.2747 | 1707.4481 | 1707.4481 | 0
2019-05-28 07:00 | 785.4443 | 4804.6896 | 0 | 7104.7228 | 4019.2454 | 2895.2772 | 0
2019-05-28 08:00 | 635.5168 | 6547.3203 | 286.6667 | 10000 | 6198.4701 | 0 | 0
2019-05-28 09:00 | 608.1718 | 7753.7554 | 286.6667 | 10000 | 7432.2502 | 0 | 0
2019-05-28 10:00 | 600.7712 | 8463.9091 | 873.3333 | 10000 | 8736.4713 | 0 | 0
2019-05-28 11:00 | 592.9337 | 8711.3017 | 4266.6667 | 10000 | 12385.0348 | 0 | 0
2019-05-28 12:00 | 583.1818 | 8502.7757 | 4266.6667 | 10000 | 12186.2606 | 0 | 0
2019-05-28 13:00 | 599.207 | 7863.8759 | 2773.3333 | 10000 | 10038.0023 | 0 | 0
2019-05-28 14:00 | 640.2477 | 6783.9351 | 0 | 10000 | 6143.6874 | 0 | 0
2019-05-28 15:00 | 774.7319 | 5240.2222 | 0 | 10000 | 4465.4904 | 0 | 0
2019-05-28 16:00 | 989.203 | 3320.2213 | 0 | 10000 | 2331.0183 | 0 | 0
2019-05-28 17:00 | 1095.4789 | 1253.0388 | 0 | 10000 | 157.56 | 0 | 0
2019-05-28 18:00 | 1162.1693 | 218.3171 | 873.3333 | 10000 | -70.5188 | -70.5188 | 0
2019-05-28 19:00 | 1398.324 | 0 | 873.3333 | 9929.4812 | -524.9907 | -524.9907 | 0
2019-05-28 20:00 | 1547.3607 | 0 | 873.3333 | 9404.4905 | -674.0273 | -674.0273 | 0
2019-05-28 21:00 | 1275.6455 | 0 | 873.3333 | 8730.4631 | -402.3122 | -402.3122 | 0
2019-05-28 22:00 | 1008.3802 | 0 | 873.3333 | 8328.151 | -135.0468 | -135.0468 | 0
2019-05-28 23:00 | 713.6009 | 0 | 286.6667 | 8193.1041 | -426.9343 | -426.9343 | 0
2019-05-29 | 623.3883 | 0 | 873.3333 | 7766.1699 | 249.945 | 249.945 | 0
2019-05-29 01:00 | 574.2723 | 0 | 286.6667 | 8016.1149 | -287.6056 | -287.6056 | 0
2019-05-29 02:00 | 571.0326 | 0 | 0 | 7728.5093 | -571.0326 | -571.0326 | 0
2019-05-29 03:00 | 576.5231 | 0 | 2773.3333 | 7157.4767 | 2196.8102 | 2196.8102 | 0
2019-05-29 04:00 | 637.5113 | 64.7197 | 1666.6667 | 9354.2869 | 1093.8751 | 645.7131 | 0
2019-05-29 05:00 | 791.2714 | 682.379 | 873.3333 | 10000 | 764.4409 | 0 | 0
2019-05-29 06:00 | 999.331 | 2562.76 | 1666.6667 | 10000 | 3230.0957 | 0 | 0
2019-05-29 07:00 | 913.3834 | 4618.9566 | 1666.6667 | 10000 | 5372.2398 | 0 | 0
2019-05-29 08:00 | 835.1167 | 6283.2941 | 2773.3333 | 10000 | 8221.5107 | 0 | 0
2019-05-29 09:00 | 834.6759 | 7461.6278 | 2773.3333 | 10000 | 9400.2852 | 0 | 0
2019-05-29 10:00 | 848.981 | 8155.601 | 2773.3333 | 10000 | 10079.9534 | 0 | 0
2019-05-29 11:00 | 832.3486 | 8391.8893 | 2773.3333 | 10000 | 10332.874 | 0 | 0
2019-05-29 12:00 | 808.2658 | 8192.5666 | 1666.6667 | 10000 | 9050.9675 | 0 | 0
2019-05-29 13:00 | 800.5394 | 7592.5196 | 1666.6667 | 10000 | 8458.6469 | 0 | 0
2019-05-29 14:00 | 830.9965 | 6521.9409 | 873.3333 | 10000 | 6564.2778 | 0 | 0
2019-05-29 15:00 | 960.1297 | 5057.593 | 286.6667 | 10000 | 4384.13 | 0 | 0
2019-05-29 16:00 | 1174.0058 | 3194.2457 | 286.6667 | 10000 | 2306.9066 | 0 | 0
2019-05-29 17:00 | 1282.078 | 1234.2329 | 1666.6667 | 10000 | 1618.8215 | 0 | 0
2019-05-29 18:00 | 1352.8778 | 213.0916 | 1666.6667 | 10000 | 526.8804 | 0 | 0
2019-05-29 19:00 | 1588.2639 | 0 | 873.3333 | 10000 | -714.9306 | -714.9306 | 0
2019-05-29 20:00 | 1736.5987 | 0 | 286.6667 | 9285.0694 | -1449.9321 | -1449.9321 | 0
2019-05-29 21:00 | 1424.4323 | 0 | 0 | 7835.1374 | -1424.4323 | -1424.4323 | 0
2019-05-29 22:00 | 1091.2534 | 0 | 0 | 6410.7051 | -1091.2534 | -1091.2534 | 0
2019-05-29 23:00 | 746.3246 | 0 | 286.6667 | 5319.4516 | -459.6579 | -459.6579 | 0
2019-05-30 | 612.2474 | 0 | 0 | 4859.7937 | -612.2474 | -612.2474 | 0
2019-05-30 01:00 | 551.2375 | 0 | 0 | 4247.5463 | -551.2375 | -551.2375 | 0
2019-05-30 02:00 | 544.7922 | 0 | 0 | 3696.3089 | -544.7922 | -544.7922 | 0
2019-05-30 03:00 | 557.0311 | 0 | 0 | 3151.5167 | -557.0311 | -557.0311 | 0
2019-05-30 04:00 | 621.9505 | 62.8601 | 0 | 2594.4856 | -559.0904 | -559.0904 | 0
2019-05-30 05:00 | 781.4013 | 710.723 | 0 | 2035.3952 | -70.6783 | -70.6783 | 0
2019-05-30 06:00 | 990.7104 | 2483.1501 | 0 | 1964.717 | 1492.4397 | 1492.4397 | 0
2019-05-30 07:00 | 908.3835 | 4521.9012 | 0 | 3457.1567 | 3613.5177 | 3613.5177 | 0
2019-05-30 08:00 | 830.9829 | 6166.8865 | 286.6667 | 7070.6744 | 5622.5703 | 2929.3256 | 0
2019-05-30 09:00 | 836.5877 | 7321.1162 | 286.6667 | 10000 | 6771.1951 | 0 | 0
2019-05-30 10:00 | 848.981 | 7974.5278 | 286.6667 | 10000 | 7412.2134 | 0 | 0
2019-05-30 11:00 | 832.3486 | 7286.9095 | 873.3333 | 10000 | 7327.8942 | 0 | 0
2019-05-30 12:00 | 808.2658 | 7141.3735 | 286.6667 | 10000 | 6619.7743 | 0 | 0
2019-05-30 13:00 | 800.5394 | 7489.3117 | 286.6667 | 10000 | 6975.439 | 0 | 0
2019-05-30 14:00 | 830.9965 | 6123.091 | 286.6667 | 10000 | 5578.7612 | 0 | 0
2019-05-30 15:00 | 960.1297 | 4326.6668 | 2773.3333 | 10000 | 6139.8705 | 0 | 0
2019-05-30 16:00 | 1174.0058 | 3014.8182 | 1666.6667 | 10000 | 3507.479 | 0 | 0
2019-05-30 17:00 | 1282.078 | 1133.8528 | 286.6667 | 10000 | 138.4415 | 0 | 0
2019-05-30 18:00 | 1352.8778 | 212.482 | 0 | 10000 | -1140.3958 | -1140.3958 | 0
2019-05-30 19:00 | 1588.2639 | 0 | 0 | 8859.6042 | -1588.2639 | -1588.2639 | 0
2019-05-30 20:00 | 1736.5987 | 0 | 2773.3333 | 7271.3403 | 1036.7346 | 1036.7346 | 0
2019-05-30 21:00 | 1424.4323 | 0 | 1666.6667 | 8308.0749 | 242.2344 | 242.2344 | 0
2019-05-30 22:00 | 1091.2534 | 0 | 1666.6667 | 8550.3093 | 575.4132 | 575.4132 | 0
2019-05-30 23:00 | 746.3246 | 0 | 873.3333 | 9125.7225 | 127.0088 | 127.0088 | 0
2019-05-31 | 612.2474 | 0 | 286.6667 | 9252.7313 | -325.5807 | -325.5807 | 0
2019-05-31 01:00 | 559.2168 | 0 | 873.3333 | 8927.1506 | 314.1165 | 314.1165 | 0
2019-05-31 02:00 | 560.7286 | 0 | 286.6667 | 9241.2671 | -274.0619 | -274.0619 | 0
2019-05-31 03:00 | 573.9266 | 0 | 873.3333 | 8967.2052 | 299.4067 | 299.4067 | 0
2019-05-31 04:00 | 640.3698 | 79.9928 | 286.6667 | 9266.6119 | -273.7103 | -273.7103 | 0
2019-05-31 05:00 | 797.8825 | 667.9464 | 873.3333 | 8992.9016 | 743.3973 | 743.3973 | 0
2019-05-31 06:00 | 1011.8932 | 2219.331 | 0 | 9736.2989 | 1207.4378 | 263.7011 | 0
2019-05-31 07:00 | 936.519 | 4148.027 | 0 | 10000 | 3211.508 | 0 | 0
2019-05-31 08:00 | 867.1148 | 4521.7425 | 0 | 10000 | 3654.6277 | 0 | 0
2019-05-31 09:00 | 885.8333 | 4869.9567 | 0 | 10000 | 3984.1234 | 0 | 0
2019-05-31 10:00 | 889.3175 | 6479.8291 | 0 | 10000 | 5590.5116 | 0 | 0
2019-05-31 11:00 | 866.2802 | 5645.7778 | 286.6667 | 10000 | 5066.1643 | 0 | 0
2019-05-31 12:00 | 837.5974 | 2610.1285 | 286.6667 | 10000 | 2059.1978 | 0 | 0
2019-05-31 13:00 | 821.0463 | 1766.5127 | 286.6667 | 10000 | 1232.133 | 0 | 0
2019-05-31 14:00 | 851.9126 | 1632.0788 | 873.3333 | 10000 | 1653.4996 | 0 | 0
2019-05-31 15:00 | 980.0936 | 2528.1784 | 1666.6667 | 10000 | 3214.7515 | 0 | 0
2019-05-31 16:00 | 1205.4043 | 2529.8436 | 1666.6667 | 10000 | 2991.1059 | 0 | 0
2019-05-31 17:00 | 1306.0335 | 760.3478 | 286.6667 | 10000 | -259.019 | -259.019 | 0
2019-05-31 18:00 | 1380.3547 | 296.7287 | 873.3333 | 9740.981 | -210.2926 | -210.2926 | 0
2019-05-31 19:00 | 1618.1362 | 0 | 873.3333 | 9530.6883 | -744.8029 | -744.8029 | 0
2019-05-31 20:00 | 1769.9371 | 0 | 873.3333 | 8785.8855 | -896.6037 | -896.6037 | 0
2019-05-31 21:00 | 1465.2121 | 0 | 2773.3333 | 7889.2817 | 1308.1212 | 1308.1212 | 0
2019-05-31 22:00 | 1140.6274 | 0 | 873.3333 | 9197.4029 | -267.294 | -267.294 | 0
2019-05-31 23:00 | 804.8492 | 0 | 0 | 8930.1089 | -804.8492 | -804.8492 | 0
2019-06-01 | 629.1481 | 0 | 0 | 8125.2597 | -629.1481 | -629.1481 | 0
2019-06-01 01:00 | 569.7781 | 0 | 286.6667 | 7496.1116 | -283.1114 | -283.1114 | 0
2019-06-01 02:00 | 556.909 | 0 | 0 | 7213.0002 | -556.909 | -556.909 | 0
2019-06-01 03:00 | 553.4816 | 0 | 0 | 6656.0912 | -553.4816 | -553.4816 | 0
2019-06-01 04:00 | 602.8992 | 11.5908 | 0 | 6102.6096 | -591.3083 | -591.3083 | 0
2019-06-01 05:00 | 734.5217 | 31.6491 | 0 | 5511.3012 | -702.8725 | -702.8725 | 0
2019-06-01 06:00 | 920.6065 | 111.8984 | 286.6667 | 4808.4287 | -522.0413 | -522.0413 | 0
2019-06-01 07:00 | 844.0427 | 968.5196 | 0 | 4286.3874 | 124.4769 | 124.4769 | 0
2019-06-01 08:00 | 782.7415 | 1873.3477 | 873.3333 | 4410.8643 | 1963.9395 | 1963.9395 | 0
2019-06-01 09:00 | 783.1187 | 3188.7867 | 2773.3333 | 6374.8038 | 5179.0014 | 3625.1962 | 0
2019-06-01 10:00 | 794.1786 | 4958.0398 | 1666.6667 | 10000 | 5830.5279 | 0 | 0
2019-06-01 11:00 | 777.2173 | 6745.9196 | 2773.3333 | 10000 | 8742.0356 | 0 | 0
2019-06-01 12:00 | 753.3045 | 3110.4245 | 6160 | 10000 | 8517.12 | 0 | 0
2019-06-01 13:00 | 743.4332 | 2591.9068 | 4266.6667 | 10000 | 6115.1403 | 0 | 0
2019-06-01 14:00 | 773.8357 | 1250.8147 | 4266.6667 | 10000 | 4743.6457 | 0 | 0
2019-06-01 15:00 | 883.8759 | 1188.2409 | 286.6667 | 10000 | 591.0318 | 0 | 0
2019-06-01 16:00 | 1075.218 | 287.0515 | 873.3333 | 10000 | 85.1668 | 0 | 0
2019-06-01 17:00 | 1164.1397 | 814.9693 | 873.3333 | 10000 | 524.163 | 0 | 0
2019-06-01 18:00 | 1207.4263 | 247.2948 | 873.3333 | 10000 | -86.7981 | -86.7981 | 0
2019-06-01 19:00 | 1408.7309 | 0 | 873.3333 | 9913.2019 | -535.3975 | -535.3975 | 0
2019-06-01 20:00 | 1601.6645 | 0 | 873.3333 | 9377.8044 | -728.3312 | -728.3312 | 0
2019-06-01 21:00 | 1353.1276 | 0 | 873.3333 | 8649.4732 | -479.7942 | -479.7942 | 0
2019-06-01 22:00 | 1028.6956 | 0 | 873.3333 | 8169.679 | -155.3623 | -155.3623 | 0
2019-06-01 23:00 | 695.2705 | 0 | 4266.6667 | 8014.3167 | 3571.3961 | 1985.6833 | 0
2019-06-02 | 566.513 | 0 | 4266.6667 | 10000 | 3700.1536 | 0 | 0
2019-06-02 01:00 | 505.0422 | 0 | 4266.6667 | 10000 | 3761.6245 | 0 | 0
2019-06-02 02:00 | 492.2011 | 0 | 286.6667 | 10000 | -205.5344 | -205.5344 | 0
2019-06-02 03:00 | 490.5838 | 0 | 286.6667 | 9794.4656 | -203.9171 | -203.9171 | 0
2019-06-02 04:00 | 543.5541 | 0 | 873.3333 | 9590.5485 | 329.7792 | 329.7792 | 0
2019-06-02 05:00 | 692.8615 | 81.167 | 873.3333 | 9920.3277 | 261.6388 | 79.6723 | 0
2019-06-02 06:00 | 889.9695 | 1209.4079 | 873.3333 | 10000 | 1192.7717 | 0 | 0
2019-06-02 07:00 | 831.2163 | 1244.9705 | 1666.6667 | 10000 | 2080.4208 | 0 | 0
2019-06-02 08:00 | 783.2161 | 1349.1869 | 7873.3333 | 10000 | 8439.3042 | 0 | 0
2019-06-02 09:00 | 789.6634 | 5333.4585 | 4266.6667 | 10000 | 8810.4618 | 0 | 0
2019-06-02 10:00 | 794.1786 | 7791.5467 | 7873.3333 | 10000 | 14870.7014 | 0 | 0
2019-06-02 11:00 | 777.2173 | 8004.5244 | 2773.3333 | 10000 | 10000.6405 | 0 | 0
2019-06-02 12:00 | 753.3045 | 2860.3133 | 6160 | 10000 | 8267.0088 | 0 | 0
2019-06-02 13:00 | 743.4332 | 875.5778 | 6160 | 10000 | 6292.1446 | 0 | 0
2019-06-02 14:00 | 773.8357 | 2724.6812 | 6160 | 10000 | 8110.8455 | 0 | 0
2019-06-02 15:00 | 883.8759 | 4493.8239 | 4266.6667 | 10000 | 7876.6148 | 0 | 0
2019-06-02 16:00 | 1075.218 | 16.1138 | 4266.6667 | 10000 | 3207.5624 | 0 | 0
2019-06-02 17:00 | 1164.1397 | 220.9817 | 4266.6667 | 10000 | 3323.5087 | 0 | 0
2019-06-02 18:00 | 1207.4263 | 305.9322 | 2773.3333 | 10000 | 1871.8392 | 0 | 0
2019-06-02 19:00 | 1408.7309 | 0 | 1666.6667 | 10000 | 257.9358 | 0 | 0
2019-06-02 20:00 | 1601.6645 | 0 | 4266.6667 | 10000 | 2665.0022 | 0 | 0
2019-06-02 21:00 | 1353.3314 | 0 | 873.3333 | 10000 | -479.998 | -479.998 | 0
2019-06-02 22:00 | 1043.9097 | 0 | 286.6667 | 9520.002 | -757.243 | -757.243 | 0
2019-06-02 23:00 | 730.8475 | 0 | 286.6667 | 8762.7589 | -444.1809 | -444.1809 | 0
2019-06-03 | 622.6978 | 0 | 286.6667 | 8318.5781 | -336.0311 | -336.0311 | 0
2019-06-03 01:00 | 573.5503 | 0 | 286.6667 | 7982.5469 | -286.8837 | -286.8837 | 0
2019-06-03 02:00 | 572.7845 | 0 | 286.6667 | 7695.6633 | -286.1179 | -286.1179 | 0
2019-06-03 03:00 | 579.6768 | 0 | 286.6667 | 7409.5454 | -293.0102 | -293.0102 | 0
2019-06-03 04:00 | 640.2816 | 0 | 286.6667 | 7116.5352 | -353.6149 | -353.6149 | 0
2019-06-03 05:00 | 790.3543 | 337.7297 | 286.6667 | 6762.9203 | -165.9579 | -165.9579 | 0
2019-06-03 06:00 | 983.1641 | 188.0284 | 873.3333 | 6596.9624 | 78.1977 | 78.1977 | 0
2019-06-03 07:00 | 918.8342 | 2761.9182 | 873.3333 | 6675.1601 | 2716.4173 | 2716.4173 | 0
2019-06-03 08:00 | 873.6916 | 6213.5247 | 2773.3333 | 9391.5774 | 8113.1664 | 608.4226 | 0
2019-06-03 09:00 | 891.4903 | 7335.0841 | 2773.3333 | 10000 | 9216.9271 | 0 | 0
2019-06-03 10:00 | 887.7021 | 8048.3049 | 2773.3333 | 10000 | 9933.9361 | 0 | 0
2019-06-03 11:00 | 851.5353 | 8288.533 | 873.3333 | 10000 | 8310.3311 | 0 | 0
2019-06-03 12:00 | 812.2069 | 8128.392 | 4266.6667 | 10000 | 11582.8518 | 0 | 0
2019-06-03 13:00 | 786.8548 | 7496.0737 | 2773.3333 | 10000 | 9482.5523 | 0 | 0
2019-06-03 14:00 | 814.9638 | 577.7496 | 873.3333 | 10000 | 636.1192 | 0 | 0
2019-06-03 15:00 | 923.7376 | 708.6277 | 2773.3333 | 10000 | 2558.2234 | 0 | 0
2019-06-03 16:00 | 1114.4517 | 3255.6983 | 2773.3333 | 10000 | 4914.58 | 0 | 0
2019-06-03 17:00 | 1202.2173 | 1208.282 | 286.6667 | 10000 | 292.7313 | 0 | 0
2019-06-03 18:00 | 1245.4312 | 299.5761 | 286.6667 | 10000 | -659.1884 | -659.1884 | 0
2019-06-03 19:00 | 1447.4134 | 0 | 286.6667 | 9340.8116 | -1160.7467 | -1160.7467 | 0
2019-06-03 20:00 | 1641.181 | 0 | 286.6667 | 8180.0649 | -1354.5144 | -1354.5144 | 0
2019-06-03 21:00 | 1384.5274 | 0 | 1666.6667 | 6825.5505 | 282.1392 | 282.1392 | 0
2019-06-03 22:00 | 1056.5495 | 0 | 1666.6667 | 7107.6898 | 610.1172 | 610.1172 | 0
2019-06-03 23:00 | 737.8193 | 0 | 1666.6667 | 7717.807 | 928.8473 | 928.8473 | 0
2019-06-04 | 622.4742 | 0 | 286.6667 | 8646.6543 | -335.8076 | -335.8076 | 0
2019-06-04 01:00 | 578.2376 | 0 | 286.6667 | 8310.8467 | -291.5709 | -291.5709 | 0
2019-06-04 02:00 | 575.7286 | 0 | 286.6667 | 8019.2758 | -289.0619 | -289.0619 | 0
2019-06-04 03:00 | 582.8932 | 0 | 873.3333 | 7730.2139 | 290.4402 | 290.4402 | 0
2019-06-04 04:00 | 643.1879 | 80.0986 | 873.3333 | 8020.6541 | 310.2441 | 310.2441 | 0
2019-06-04 05:00 | 789.4569 | 714.3708 | 873.3333 | 8330.8982 | 798.2473 | 798.2473 | 0
2019-06-04 06:00 | 981.5888 | 2563.5489 | 286.6667 | 9129.1454 | 1868.6268 | 870.8546 | 0
2019-06-04 07:00 | 917.8533 | 4599.1524 | 286.6667 | 10000 | 3967.9658 | 0 | 0
2019-06-04 08:00 | 870.108 | 6269.4297 | 0 | 10000 | 5399.3217 | 0 | 0
2019-06-04 09:00 | 892.9019 | 7471.3637 | 1666.6667 | 10000 | 8245.1284 | 0 | 0
2019-06-04 10:00 | 888.523 | 8227.0494 | 873.3333 | 10000 | 8211.8597 | 0 | 0
2019-06-04 11:00 | 856.2288 | 8473.1402 | 873.3333 | 10000 | 8490.2447 | 0 | 0
2019-06-04 12:00 | 820.0807 | 8275.0251 | 2773.3333 | 10000 | 10228.2777 | 0 | 0
2019-06-04 13:00 | 799.0714 | 7685.8099 | 2773.3333 | 10000 | 9660.0719 | 0 | 0
2019-06-04 14:00 | 822.4013 | 6648.4421 | 873.3333 | 10000 | 6699.3741 | 0 | 0
2019-06-04 15:00 | 926.7591 | 5184.5312 | 2773.3333 | 10000 | 7031.1055 | 0 | 0
2019-06-04 16:00 | 1118.6657 | 3313.1937 | 1666.6667 | 10000 | 3861.1947 | 0 | 0
2019-06-04 17:00 | 1202.2173 | 1234.0995 | 873.3333 | 10000 | 905.2155 | 0 | 0
2019-06-04 18:00 | 1245.4312 | 229.2146 | 286.6667 | 10000 | -729.55 | -729.55 | 0
2019-06-04 19:00 | 1447.4134 | 0 | 873.3333 | 9270.45 | -574.0801 | -574.0801 | 0
2019-06-04 20:00 | 1642.9537 | 0 | 2773.3333 | 8696.37 | 1130.3796 | 1130.3796 | 0
2019-06-04 21:00 | 1394.8486 | 0 | 873.3333 | 9826.7496 | -521.5153 | -521.5153 | 0
2019-06-04 22:00 | 1068.7828 | 0 | 873.3333 | 9305.2343 | -195.4495 | -195.4495 | 0
2019-06-04 23:00 | 738.6839 | 0 | 873.3333 | 9109.7848 | 134.6494 | 134.6494 | 0
2019-06-05 | 611.5889 | 0 | 286.6667 | 9244.4342 | -324.9222 | -324.9222 | 0
2019-06-05 01:00 | 557.336 | 0 | 286.6667 | 8919.512 | -270.6693 | -270.6693 | 0
2019-06-05 02:00 | 551.8507 | 0 | 873.3333 | 8648.8427 | 321.4826 | 321.4826 | 0
2019-06-05 03:00 | 553.3762 | 0 | 1666.6667 | 8970.3253 | 1113.2905 | 1029.6747 | 0
2019-06-05 04:00 | 605.4506 | 31.2535 | 873.3333 | 10000 | 299.1363 | 0 | 0
2019-06-05 05:00 | 742.5465 | 581.4952 | 2773.3333 | 10000 | 2612.282 | 0 | 0
2019-06-05 06:00 | 928.5739 | 1355.8212 | 2773.3333 | 10000 | 3200.5807 | 0 | 0
2019-06-05 07:00 | 863.5587 | 4070.111 | 6160 | 10000 | 9366.5523 | 0 | 0
2019-06-05 08:00 | 813.8419 | 5367.05 | 6160 | 10000 | 10713.2081 | 0 | 0
2019-06-05 09:00 | 830.3077 | 6113.3333 | 6160 | 10000 | 11443.0256 | 0 | 0
2019-06-05 10:00 | 834.9696 | 7080.6512 | 6160 | 10000 | 12405.6816 | 0 | 0
2019-06-05 11:00 | 811.0773 | 8489.515 | 6160 | 10000 | 13838.4378 | 0 | 0
2019-06-05 12:00 | 778.2063 | 8347.8178 | 6160 | 10000 | 13729.6115 | 0 | 0
2019-06-05 13:00 | 763.5149 | 7733.0887 | 4266.6667 | 10000 | 11236.2405 | 0 | 0
2019-06-05 14:00 | 787.9375 | 6745.4653 | 4266.6667 | 10000 | 10224.1945 | 0 | 0
2019-06-05 15:00 | 887.1851 | 3953.7472 | 4266.6667 | 10000 | 7333.2287 | 0 | 0
2019-06-05 16:00 | 1075.218 | 3360.4736 | 6160 | 10000 | 8445.2556 | 0 | 0
2019-06-05 17:00 | 1164.1397 | 633.2222 | 6160 | 10000 | 5629.0825 | 0 | 0
2019-06-05 18:00 | 1207.4263 | 139.1788 | 6160 | 10000 | 5091.7524 | 0 | 0
2019-06-05 19:00 | 1408.7309 | 0 | 6160 | 10000 | 4751.2691 | 0 | 0
2019-06-05 20:00 | 1601.6645 | 0 | 6160 | 10000 | 4558.3355 | 0 | 0
2019-06-05 21:00 | 1353.1276 | 0 | 9573.3333 | 10000 | 8220.2058 | 0 | 0
2019-06-05 22:00 | 1028.6956 | 0 | 9060 | 10000 | 8031.3044 | 0 | 0
2019-06-05 23:00 | 696.0602 | 0 | 9060 | 10000 | 8363.9398 | 0 | 0
2019-06-06 | 573.897 | 0 | 9873.3333 | 10000 | 9299.4364 | 0 | 0
2019-06-06 01:00 | 521.0096 | 0 | 9060 | 10000 | 8538.9904 | 0 | 0
2019-06-06 02:00 | 514.8366 | 0 | 9873.3333 | 10000 | 9358.4967 | 0 | 0
2019-06-06 03:00 | 516.8417 | 0 | 9573.3333 | 10000 | 9056.4917 | 0 | 0
2019-06-06 04:00 | 571.8962 | 0 | 9573.3333 | 10000 | 9001.4372 | 0 | 0
2019-06-06 05:00 | 708.7778 | 731.1228 | 7873.3333 | 10000 | 7895.6784 | 0 | 0
2019-06-06 06:00 | 899.3881 | 948.658 | 9573.3333 | 10000 | 9622.6032 | 0 | 0
2019-06-06 07:00 | 837.2709 | 1612.7991 | 9573.3333 | 10000 | 10348.8615 | 0 | 0
2019-06-06 08:00 | 790.3846 | 1875.4533 | 9060 | 10000 | 10145.0688 | 0 | 0
2019-06-06 09:00 | 812.6055 | 1693.9696 | 6160 | 10000 | 7041.364 | 0 | 0
2019-06-06 10:00 | 832.3069 | 3464.5624 | 6160 | 10000 | 8792.2555 | 0 | 0
2019-06-06 11:00 | 816.1061 | 3311.2375 | 4266.6667 | 10000 | 6761.7981 | 0 | 0
2019-06-06 12:00 | 794.98 | 2159.8645 | 9060 | 10000 | 10424.8844 | 0 | 0
2019-06-06 13:00 | 788.8397 | 406.0765 | 7873.3333 | 10000 | 7490.5701 | 0 | 0
2019-06-06 14:00 | 822.4869 | 1434.9171 | 9060 | 10000 | 9672.4302 | 0 | 0
2019-06-06 15:00 | 932.9716 | 917.1307 | 7873.3333 | 10000 | 7857.4924 | 0 | 0
2019-06-06 16:00 | 1140.7132 | 635.8499 | 4266.6667 | 10000 | 3761.8034 | 0 | 0
2019-06-06 17:00 | 1214.0748 | 227.8897 | 1666.6667 | 10000 | 680.4816 | 0 | 0
2019-06-06 18:00 | 1256.5469 | 230.2208 | 873.3333 | 10000 | -152.9928 | -152.9928 | 0
2019-06-06 19:00 | 1459.864 | 0 | 0 | 9847.0072 | -1459.864 | -1459.864 | 0
2019-06-06 20:00 | 1652.7175 | 0 | 286.6667 | 8387.1433 | -1366.0509 | -1366.0509 | 0
2019-06-06 21:00 | 1410.1576 | 0 | 0 | 7021.0924 | -1410.1576 | -1410.1576 | 0
2019-06-06 22:00 | 1095.7145 | 0 | 0 | 5610.9348 | -1095.7145 | -1095.7145 | 0
2019-06-06 23:00 | 772.2595 | 0 | 286.6667 | 4515.2203 | -485.5929 | -485.5929 | 0
2019-06-07 | 649.5664 | 0 | 0 | 4029.6275 | -649.5664 | -649.5664 | 0
2019-06-07 01:00 | 592.4138 | 0 | 286.6667 | 3380.061 | -305.7471 | -305.7471 | 0
2019-06-07 02:00 | 583.153 | 0 | 286.6667 | 3074.3139 | -296.4863 | -296.4863 | 0
2019-06-07 03:00 | 585.5231 | 0 | 286.6667 | 2777.8276 | -298.8564 | -298.8564 | 0
2019-06-07 04:00 | 636.9161 | 103.6794 | 286.6667 | 2478.9711 | -246.5701 | -246.5701 | 0
2019-06-07 05:00 | 777.4899 | 605.1932 | 286.6667 | 2232.4011 | 114.3701 | 114.3701 | 0
2019-06-07 06:00 | 959.6393 | 473.0916 | 873.3333 | 2346.7711 | 386.7856 | 386.7856 | 0
2019-06-07 07:00 | 897.5557 | 1469.7816 | 873.3333 | 2733.5568 | 1445.5593 | 1445.5593 | 0
2019-06-07 08:00 | 852.1644 | 1963.6031 | 873.3333 | 4179.1161 | 1984.772 | 1984.772 | 0
2019-06-07 09:00 | 869.5477 | 4116.9137 | 873.3333 | 6163.8881 | 4120.6994 | 3836.1119 | 0
2019-06-07 10:00 | 885.8018 | 6191.8576 | 873.3333 | 10000 | 6179.3892 | 0 | 0
2019-06-07 11:00 | 869.3575 | 6027.2075 | 873.3333 | 10000 | 6031.1834 | 0 | 0
2019-06-07 12:00 | 843.3109 | 7385.3517 | 2773.3333 | 10000 | 9315.3741 | 0 | 0
2019-06-07 13:00 | 829.2556 | 7336.6849 | 1666.6667 | 10000 | 8174.0959 | 0 | 0
2019-06-07 14:00 | 855.0335 | 6303.6445 | 873.3333 | 10000 | 6321.9443 | 0 | 0
2019-06-07 15:00 | 953.3609 | 4894.5702 | 286.6667 | 10000 | 4227.8759 | 0 | 0
2019-06-07 16:00 | 1152.8433 | 2709.8818 | 286.6667 | 10000 | 1843.7053 | 0 | 0
2019-06-07 17:00 | 1218.6341 | 1424.3371 | 0 | 10000 | 205.703 | 0 | 0
2019-06-07 18:00 | 1257.353 | 348.7364 | 286.6667 | 10000 | -621.95 | -621.95 | 0
2019-06-07 19:00 | 1459.0548 | 0 | 0 | 9378.05 | -1459.0548 | -1459.0548 | 0
2019-06-07 20:00 | 1655.7444 | 0 | 0 | 7918.9952 | -1655.7444 | -1655.7444 | 0
2019-06-07 21:00 | 1415.8662 | 0 | 0 | 6263.2508 | -1415.8662 | -1415.8662 | 0
2019-06-07 22:00 | 1105.2274 | 0 | 0 | 4847.3846 | -1105.2274 | -1105.2274 | 0
2019-06-07 23:00 | 788.8707 | 0 | 0 | 3742.1572 | -788.8707 | -788.8707 | 0
2019-06-08 | 670.1596 | 0 | 0 | 2953.2865 | -670.1596 | -670.1596 | 0
2019-06-08 01:00 | 618.2302 | 0 | 0 | 2283.1269 | -618.2302 | -618.2302 | 0
2019-06-08 02:00 | 610.9698 | 0 | 0 | 1664.8967 | -610.9698 | -610.9698 | 0
2019-06-08 03:00 | 613.2226 | 0 | 0 | 1053.9269 | -613.2226 | -613.2226 | 0
2019-06-08 04:00 | 666.7627 | 57.0676 | 0 | 440.7043 | -609.6951 | -440.7043 | -168.9907
2019-06-08 05:00 | 805.4943 | 713.6336 | 0 | 0 | -91.8606 | 0 | -260.8514
2019-06-08 06:00 | 976.3136 | 1970.2582 | 0 | 0 | 993.9446 | 993.9446 | 0
2019-06-08 07:00 | 897.457 | 3906.7915 | 0 | 993.9446 | 3009.3345 | 3009.3345 | 0
2019-06-08 08:00 | 833.9245 | 5356.7391 | 0 | 4003.2792 | 4522.8146 | 4522.8146 | 0
2019-06-08 09:00 | 854.0126 | 5894.5343 | 0 | 8526.0938 | 5040.5217 | 1473.9062 | 0
2019-06-08 10:00 | 838.1134 | 6753.2784 | 286.6667 | 10000 | 6201.8317 | 0 | 0
2019-06-08 11:00 | 809.1785 | 7573.0869 | 2773.3333 | 10000 | 9537.2418 | 0 | 0
2019-06-08 12:00 | 775.2379 | 7401.6323 | 873.3333 | 10000 | 7499.7277 | 0 | 0
2019-06-08 13:00 | 753.8352 | 4254.594 | 2773.3333 | 10000 | 6274.0922 | 0 | 0
2019-06-08 14:00 | 779.1948 | 3254.8691 | 1666.6667 | 10000 | 4142.341 | 0 | 0
2019-06-08 15:00 | 885.8759 | 4685.5094 | 1666.6667 | 10000 | 5466.3002 | 0 | 0
2019-06-08 16:00 | 1084.3939 | 2534.1078 | 873.3333 | 10000 | 2323.0473 | 0 | 0
2019-06-08 17:00 | 1164.1397 | 1255.5309 | 286.6667 | 10000 | 378.0579 | 0 | 0
2019-06-08 18:00 | 1207.4263 | 326.0951 | 873.3333 | 10000 | -7.9978 | -7.9978 | 0
2019-06-08 19:00 | 1412.2591 | 0 | 873.3333 | 9992.0022 | -538.9257 | -538.9257 | 0
2019-06-08 20:00 | 1614.232 | 0 | 873.3333 | 9453.0764 | -740.8987 | -740.8987 | 0
2019-06-08 21:00 | 1378.1296 | 0 | 873.3333 | 8712.1777 | -504.7963 | -504.7963 | 0
2019-06-08 22:00 | 1070.1591 | 0 | 0 | 8207.3815 | -1070.1591 | -1070.1591 | 0
2019-06-08 23:00 | 751.9951 | 0 | 0 | 7137.2224 | -751.9951 | -751.9951 | 0
2019-06-09 | 635.254 | 0 | 0 | 6385.2272 | -635.254 | -635.254 | 0
2019-06-09 01:00 | 584.438 | 0 | 0 | 5749.9733 | -584.438 | -584.438 | 0
2019-06-09 02:00 | 577.5638 | 0 | 0 | 5165.5353 | -577.5638 | -577.5638 | 0
2019-06-09 03:00 | 581.1082 | 0 | 0 | 4587.9715 | -581.1082 | -581.1082 | 0
2019-06-09 04:00 | 634.7498 | 80.5195 | 0 | 4006.8634 | -554.2302 | -554.2302 | 0
2019-06-09 05:00 | 774.5911 | 776.2316 | 873.3333 | 3452.6332 | 874.9738 | 874.9738 | 0
2019-06-09 06:00 | 955.622 | 2331.8492 | 873.3333 | 4327.607 | 2249.5606 | 2249.5606 | 0
2019-06-09 07:00 | 881.489 | 4089.4311 | 873.3333 | 6577.1676 | 4081.2754 | 3422.8324 | 0
2019-06-09 08:00 | 828.0687 | 5582.8475 | 0 | 10000 | 4754.7788 | 0 | 0
2019-06-09 09:00 | 839.0484 | 6711.952 | 286.6667 | 10000 | 6159.5702 | 0 | 0
2019-06-09 10:00 | 825.325 | 7325.0296 | 286.6667 | 10000 | 6786.3713 | 0 | 0
2019-06-09 11:00 | 797.26 | 6433.5278 | 286.6667 | 10000 | 5922.9345 | 0 | 0
2019-06-09 12:00 | 754.91 | 6057.4306 | 9060 | 10000 | 14362.5206 | 0 | 0
2019-06-09 13:00 | 743.4332 | 5937.5845 | 9060 | 10000 | 14254.1514 | 0 | 0
2019-06-09 14:00 | 773.8357 | 5475.9274 | 2773.3333 | 10000 | 7475.425 | 0 | 0
2019-06-09 15:00 | 883.8759 | 3906.6213 | 2773.3333 | 10000 | 5796.0788 | 0 | 0
2019-06-09 16:00 | 1075.218 | 2521.5429 | 1666.6667 | 10000 | 3112.9915 | 0 | 0
2019-06-09 17:00 | 1164.1397 | 1208.1118 | 873.3333 | 10000 | 917.3054 | 0 | 0
2019-06-09 18:00 | 1207.4263 | 303.2722 | 873.3333 | 10000 | -30.8207 | -30.8207 | 0
2019-06-09 19:00 | 1408.7309 | 0 | 873.3333 | 9969.1793 | -535.3975 | -535.3975 | 0
2019-06-09 20:00 | 1601.6645 | 0 | 873.3333 | 9433.7818 | -728.3312 | -728.3312 | 0
2019-06-09 21:00 | 1353.1276 | 0 | 1666.6667 | 8705.4506 | 313.5391 | 313.5391 | 0
2019-06-09 22:00 | 1028.6956 | 0 | 1666.6667 | 9018.9897 | 637.9711 | 637.9711 | 0
2019-06-09 23:00 | 695.2705 | 0 | 1666.6667 | 9656.9607 | 971.3961 | 343.0393 | 0
2019-06-10 | 570.8934 | 0 | 873.3333 | 10000 | 302.4399 | 0 | 0
2019-06-10 01:00 | 507.9402 | 0 | 873.3333 | 10000 | 365.3932 | 0 | 0
2019-06-10 02:00 | 493.7164 | 0 | 873.3333 | 10000 | 379.6169 | 0 | 0
2019-06-10 03:00 | 495.8293 | 0 | 286.6667 | 10000 | -209.1626 | -209.1626 | 0
2019-06-10 04:00 | 559.6374 | 0 | 0 | 9790.8374 | -559.6374 | -559.6374 | 0
2019-06-10 05:00 | 709.4815 | 0 | 0 | 9231.2 | -709.4815 | -709.4815 | 0
2019-06-10 06:00 | 913.5716 | 529.8556 | 0 | 8521.7185 | -383.716 | -383.716 | 0
2019-06-10 07:00 | 859.4778 | 1438.6212 | 0 | 8138.0025 | 579.1435 | 579.1435 | 0
2019-06-10 08:00 | 819.3575 | 2159.8449 | 0 | 8717.146 | 1340.4874 | 1282.854 | 0
2019-06-10 09:00 | 839.6008 | 3354.4442 | 286.6667 | 10000 | 2801.51 | 0 | 0
2019-06-10 10:00 | 852.4307 | 2746.5554 | 873.3333 | 10000 | 2767.458 | 0 | 0
2019-06-10 11:00 | 830.2774 | 1738.6781 | 2773.3333 | 10000 | 3681.734 | 0 | 0
2019-06-10 12:00 | 801.6786 | 1936.0526 | 2773.3333 | 10000 | 3907.7073 | 0 | 0
2019-06-10 13:00 | 786.8548 | 4036.4229 | 2773.3333 | 10000 | 6022.9015 | 0 | 0
2019-06-10 14:00 | 814.9638 | 4965.6046 | 6160 | 10000 | 10310.6407 | 0 | 0
2019-06-10 15:00 | 923.7376 | 4999.3593 | 2773.3333 | 10000 | 6848.9551 | 0 | 0
2019-06-10 16:00 | 1114.4517 | 3224.0974 | 2773.3333 | 10000 | 4882.9791 | 0 | 0
2019-06-10 17:00 | 1202.2173 | 892.3437 | 2773.3333 | 10000 | 2463.4597 | 0 | 0
2019-06-10 18:00 | 1245.4312 | 323.4076 | 4266.6667 | 10000 | 3344.6431 | 0 | 0
2019-06-10 19:00 | 1447.4134 | 0 | 2773.3333 | 10000 | 1325.9199 | 0 | 0
2019-06-10 20:00 | 1641.181 | 0 | 4266.6667 | 10000 | 2625.4856 | 0 | 0
2019-06-10 21:00 | 1384.5274 | 0 | 4266.6667 | 10000 | 2882.1392 | 0 | 0
2019-06-10 22:00 | 1045.9362 | 0 | 4266.6667 | 10000 | 3220.7305 | 0 | 0
2019-06-10 23:00 | 702.566 | 0 | 4266.6667 | 10000 | 3564.1007 | 0 | 0
2019-06-11 | 573.8168 | 0 | 2773.3333 | 10000 | 2199.5165 | 0 | 0
2019-06-11 01:00 | 524.6023 | 0 | 2773.3333 | 10000 | 2248.7311 | 0 | 0
2019-06-11 02:00 | 523.0248 | 0 | 2773.3333 | 10000 | 2250.3085 | 0 | 0
2019-06-11 03:00 | 532.6081 | 0 | 1666.6667 | 10000 | 1134.0586 | 0 | 0
2019-06-11 04:00 | 592.0819 | 132.0533 | 873.3333 | 10000 | 413.3048 | 0 | 0
2019-06-11 05:00 | 741.4412 | 713.4692 | 873.3333 | 10000 | 845.3614 | 0 | 0
2019-06-11 06:00 | 939.7893 | 2586.8629 | 1666.6667 | 10000 | 3313.7403 | 0 | 0
2019-06-11 07:00 | 879.5008 | 4650.4148 | 873.3333 | 10000 | 4644.2474 | 0 | 0
2019-06-11 08:00 | 831.8106 | 6328.3936 | 2773.3333 | 10000 | 8269.9164 | 0 | 0
2019-06-11 09:00 | 839.2523 | 6175.5184 | 7873.3333 | 10000 | 13209.5994 | 0 | 0
2019-06-11 10:00 | 852.4307 | 7371.2849 | 4266.6667 | 10000 | 10785.5209 | 0 | 0
2019-06-11 11:00 | 830.2774 | 8547.3049 | 4266.6667 | 10000 | 11983.6941 | 0 | 0
2019-06-11 12:00 | 801.6786 | 7475.33 | 6160 | 10000 | 12833.6514 | 0 | 0
2019-06-11 13:00 | 786.8548 | 7796.6723 | 7873.3333 | 10000 | 14883.1508 | 0 | 0
2019-06-11 14:00 | 814.9638 | 6791.3215 | 7873.3333 | 10000 | 13849.6911 | 0 | 0
2019-06-11 15:00 | 923.7376 | 5322.7922 | 9573.3333 | 10000 | 13972.388 | 0 | 0
2019-06-11 16:00 | 1114.4517 | 3440.7597 | 9060 | 10000 | 11386.3081 | 0 | 0
2019-06-11 17:00 | 1202.2173 | 1396.6577 | 6160 | 10000 | 6354.4404 | 0 | 0
2019-06-11 18:00 | 1245.4312 | 211.0537 | 4266.6667 | 10000 | 3232.2892 | 0 | 0
2019-06-11 19:00 | 1447.4134 | 0 | 4266.6667 | 10000 | 2819.2533 | 0 | 0
2019-06-11 20:00 | 1641.181 | 0 | 2773.3333 | 10000 | 1132.1523 | 0 | 0
2019-06-11 21:00 | 1384.5274 | 0 | 4266.6667 | 10000 | 2882.1392 | 0 | 0
2019-06-11 22:00 | 1048.2941 | 0 | 2773.3333 | 10000 | 1725.0392 | 0 | 0
2019-06-11 23:00 | 721.8668 | 0 | 286.6667 | 10000 | -435.2001 | -435.2001 | 0
2019-06-12 | 602.3914 | 0 | 1666.6667 | 9564.7999 | 1064.2753 | 435.2001 | 0
2019-06-12 01:00 | 554.8937 | 0 | 873.3333 | 10000 | 318.4396 | 0 | 0
2019-06-12 02:00 | 552.0994 | 0 | 286.6667 | 10000 | -265.4327 | -265.4327 | 0
2019-06-12 03:00 | 557.8469 | 0 | 286.6667 | 9734.5673 | -271.1802 | -271.1802 | 0
2019-06-12 04:00 | 614.179 | 76.1277 | 0 | 9463.3871 | -538.0513 | -538.0513 | 0
2019-06-12 05:00 | 750.785 | 650.8413 | 873.3333 | 8925.3358 | 773.3897 | 773.3897 | 0
2019-06-12 06:00 | 943.0522 | 2551.4624 | 873.3333 | 9698.7254 | 2481.7436 | 301.2746 | 0
2019-06-12 07:00 | 881.4425 | 4600.6244 | 286.6667 | 10000 | 4005.8486 | 0 | 0
2019-06-12 08:00 | 835.6454 | 6267.3953 | 286.6667 | 10000 | 5718.4166 | 0 | 0
2019-06-12 09:00 | 868.1829 | 7495.4746 | 286.6667 | 10000 | 6913.9584 | 0 | 0
2019-06-12 10:00 | 863.0073 | 8215.6989 | 286.6667 | 10000 | 7639.3583 | 0 | 0
2019-06-12 11:00 | 842.0632 | 8472.2581 | 873.3333 | 10000 | 8503.5283 | 0 | 0
2019-06-12 12:00 | 816.5688 | 8344.1838 | 6160 | 10000 | 13687.615 | 0 | 0
2019-06-12 13:00 | 806.086 | 7722.61 | 6160 | 10000 | 13076.524 | 0 | 0
2019-06-12 14:00 | 840.263 | 6708.5146 | 4266.6667 | 10000 | 10134.9183 | 0 | 0
2019-06-12 15:00 | 948.1677 | 5253.7716 | 4266.6667 | 10000 | 8572.2705 | 0 | 0
2019-06-12 16:00 | 1155.8183 | 3383.7255 | 4266.6667 | 10000 | 6494.5739 | 0 | 0
2019-06-12 17:00 | 1233.2113 | 1372.548 | 2773.3333 | 10000 | 2912.67 | 0 | 0
2019-06-12 18:00 | 1272.4605 | 209.0965 | 286.6667 | 10000 | -776.6973 | -776.6973 | 0
2019-06-12 19:00 | 1473.4681 | 0 | 873.3333 | 9223.3027 | -600.1348 | -600.1348 | 0
2019-06-12 20:00 | 1667.9089 | 0 | 4266.6667 | 8623.1679 | 2598.7577 | 1376.8321 | 0
2019-06-12 21:00 | 1423.5546 | 0 | 2773.3333 | 10000 | 1349.7787 | 0 | 0
2019-06-12 22:00 | 1107.983 | 0 | 1666.6667 | 10000 | 558.6837 | 0 | 0
2019-06-12 23:00 | 784.3064 | 0 | 1666.6667 | 10000 | 882.3603 | 0 | 0
2019-06-13 | 660.5832 | 0 | 873.3333 | 10000 | 212.7501 | 0 | 0
2019-06-13 01:00 | 604.5606 | 0 | 286.6667 | 10000 | -317.894 | -317.894 | 0
2019-06-13 02:00 | 593.2908 | 0 | 286.6667 | 9682.106 | -306.6242 | -306.6242 | 0
2019-06-13 03:00 | 594.103 | 0 | 873.3333 | 9375.4819 | 279.2304 | 279.2304 | 0
2019-06-13 04:00 | 644.9565 | 157.9893 | 873.3333 | 9654.7123 | 386.3662 | 345.2877 | 0
2019-06-13 05:00 | 778.1957 | 599.1442 | 1666.6667 | 10000 | 1487.6152 | 0 | 0
2019-06-13 06:00 | 964.7408 | 2316.0034 | 4266.6667 | 10000 | 5617.9292 | 0 | 0
2019-06-13 07:00 | 899.5547 | 4534.1176 | 2773.3333 | 10000 | 6407.8962 | 0 | 0
2019-06-13 08:00 | 847.7916 | 6137.5166 | 2773.3333 | 10000 | 8063.0584 | 0 | 0
2019-06-13 09:00 | 875.6046 | 7267.8539 | 286.6667 | 10000 | 6678.916 | 0 | 0
2019-06-13 10:00 | 864.3134 | 7970.2463 | 1666.6667 | 10000 | 8772.5997 | 0 | 0
2019-06-13 11:00 | 835.2614 | 8220.9314 | 2773.3333 | 10000 | 10159.0033 | 0 | 0
2019-06-13 12:00 | 802.3468 | 6853.54 | 1666.6667 | 10000 | 7717.8598 | 0 | 0
2019-06-13 13:00 | 777.5996 | 6797.7914 | 873.3333 | 10000 | 6893.5252 | 0 | 0
2019-06-13 14:00 | 796.9365 | 5515.5507 | 2773.3333 | 10000 | 7491.9475 | 0 | 0
2019-06-13 15:00 | 900.299 | 5242.1635 | 6160 | 10000 | 10501.8645 | 0 | 0
2019-06-13 16:00 | 1102.6062 | 3406.0608 | 6160 | 10000 | 8463.4546 | 0 | 0
2019-06-13 17:00 | 1175.8022 | 1336.9681 | 873.3333 | 10000 | 1034.4993 | 0 | 0
2019-06-13 18:00 | 1217.4146 | 246.1299 | 0 | 10000 | -971.2847 | -971.2847 | 0
2019-06-13 19:00 | 1416.8392 | 0 | 0 | 9028.7153 | -1416.8392 | -1416.8392 | 0
2019-06-13 20:00 | 1612.5434 | 0 | 1666.6667 | 7611.8762 | 54.1233 | 54.1233 | 0
2019-06-13 21:00 | 1372.337 | 0 | 9060 | 7665.9994 | 7687.663 | 2334.0006 | 0
2019-06-13 22:00 | 1060.9422 | 0 | 4266.6667 | 10000 | 3205.7245 | 0 | 0
2019-06-13 23:00 | 741.9808 | 0 | 0 | 10000 | -741.9808 | -741.9808 | 0
2019-06-14 | 625.6052 | 0 | 873.3333 | 9258.0192 | 247.7281 | 247.7281 | 0
2019-06-14 01:00 | 571.966 | 0 | 0 | 9505.7473 | -571.966 | -571.966 | 0
2019-06-14 02:00 | 566.2459 | 0 | 0 | 8933.7814 | -566.2459 | -566.2459 | 0
2019-06-14 03:00 | 569.0766 | 0 | 873.3333 | 8367.5354 | 304.2567 | 304.2567 | 0
2019-06-14 04:00 | 623.5722 | 137.7366 | 873.3333 | 8671.7921 | 387.4978 | 387.4978 | 0
2019-06-14 05:00 | 766.1033 | 724.9657 | 873.3333 | 9059.29 | 832.1958 | 832.1958 | 0
2019-06-14 06:00 | 948.0947 | 1208.1808 | 286.6667 | 9891.4858 | 546.7527 | 108.5142 | 0
2019-06-14 07:00 | 875.9314 | 2023.847 | 286.6667 | 10000 | 1434.5823 | 0 | 0
2019-06-14 08:00 | 824.0109 | 1609.4825 | 2773.3333 | 10000 | 3558.8049 | 0 | 0
2019-06-14 09:00 | 841.9366 | 4725.3293 | 2773.3333 | 10000 | 6656.726 | 0 | 0
2019-06-14 10:00 | 855.0258 | 3909.4652 | 1666.6667 | 10000 | 4721.1061 | 0 | 0
2019-06-14 11:00 | 821.1017 | 2292.8424 | 2773.3333 | 10000 | 4245.0741 | 0 | 0
2019-06-14 12:00 | 796.4823 | 1025.5677 | 4266.6667 | 10000 | 4495.752 | 0 | 0
2019-06-14 13:00 | 786.2594 | 1507.0474 | 4266.6667 | 10000 | 4987.4547 | 0 | 0
2019-06-14 14:00 | 816.6811 | 1652.8731 | 2773.3333 | 10000 | 3609.5254 | 0 | 0
2019-06-14 15:00 | 927.8512 | 3463.1341 | 4266.6667 | 10000 | 6801.9496 | 0 | 0
2019-06-14 16:00 | 1135.2526 | 1669.9944 | 2773.3333 | 10000 | 3308.075 | 0 | 0
2019-06-14 17:00 | 1210.257 | 1105.265 | 1666.6667 | 10000 | 1561.6747 | 0 | 0
2019-06-14 18:00 | 1254.6725 | 360.4261 | 1666.6667 | 10000 | 772.4202 | 0 | 0
2019-06-14 19:00 | 1459.5854 | 0 | 873.3333 | 10000 | -586.2521 | -586.2521 | 0
2019-06-14 20:00 | 1651.5668 | 0 | 286.6667 | 9413.7479 | -1364.9001 | -1364.9001 | 0
2019-06-14 21:00 | 1409.4955 | 0 | 873.3333 | 8048.8478 | -536.1622 | -536.1622 | 0
2019-06-14 22:00 | 1093.7772 | 0 | 873.3333 | 7512.6857 | -220.4438 | -220.4438 | 0
2019-06-14 23:00 | 769.7329 | 0 | 286.6667 | 7292.2418 | -483.0663 | -483.0663 | 0
2019-06-15 | 648.7883 | 0 | 286.6667 | 6809.1756 | -362.1217 | -362.1217 | 0
2019-06-15 01:00 | 593.928 | 0 | 286.6667 | 6447.0539 | -307.2613 | -307.2613 | 0
2019-06-15 02:00 | 584.5543 | 0 | 286.6667 | 6139.7926 | -297.8877 | -297.8877 | 0
2019-06-15 03:00 | 587.1095 | 0 | 0 | 5841.9049 | -587.1095 | -587.1095 | 0
2019-06-15 04:00 | 642.3624 | 0 | 0 | 5254.7954 | -642.3624 | -642.3624 | 0
2019-06-15 05:00 | 775.6177 | 607.1402 | 0 | 4612.433 | -168.4775 | -168.4775 | 0
2019-06-15 06:00 | 976.4984 | 1595.9332 | 0 | 4443.9556 | 619.4348 | 619.4348 | 0
2019-06-15 07:00 | 910.0741 | 4172.2632 | 0 | 5063.3904 | 3262.1892 | 3262.1892 | 0
2019-06-15 08:00 | 861.2881 | 5769.1889 | 0 | 8325.5796 | 4907.9008 | 1674.4204 | 0
2019-06-15 09:00 | 893.0037 | 2373.47 | 2773.3333 | 10000 | 4253.7997 | 0 | 0
2019-06-15 10:00 | 887.259 | 7726.1933 | 4266.6667 | 10000 | 11105.601 | 0 | 0
2019-06-15 11:00 | 863.6481 | 7878.3188 | 4266.6667 | 10000 | 11281.3374 | 0 | 0
2019-06-15 12:00 | 835.269 | 6669.0374 | 6160 | 10000 | 11993.7685 | 0 | 0
2019-06-15 13:00 | 821.9769 | 6184.079 | 4266.6667 | 10000 | 9628.7688 | 0 | 0
2019-06-15 14:00 | 854.4654 | 5345.4438 | 4266.6667 | 10000 | 8757.645 | 0 | 0
2019-06-15 15:00 | 959.7158 | 4883.4635 | 4266.6667 | 10000 | 8190.4143 | 0 | 0
2019-06-15 16:00 | 1161.7068 | 3155.0503 | 4266.6667 | 10000 | 6260.0101 | 0 | 0
2019-06-15 17:00 | 1235.2665 | 1330.3004 | 7873.3333 | 10000 | 7968.3672 | 0 | 0
2019-06-15 18:00 | 1274.2594 | 254.219 | 4266.6667 | 10000 | 3246.6263 | 0 | 0
2019-06-15 19:00 | 1479.334 | 0 | 4266.6667 | 10000 | 2787.3327 | 0 | 0
2019-06-15 20:00 | 1672.1566 | 0 | 2773.3333 | 10000 | 1101.1768 | 0 | 0
2019-06-15 21:00 | 1428.8078 | 0 | 2773.3333 | 10000 | 1344.5256 | 0 | 0
2019-06-15 22:00 | 1111.1877 | 0 | 2773.3333 | 10000 | 1662.1456 | 0 | 0
2019-06-15 23:00 | 787.5444 | 0 | 4266.6667 | 10000 | 3479.1222 | 0 | 0
2019-06-16 | 665.3756 | 0 | 873.3333 | 10000 | 207.9577 | 0 | 0
2019-06-16 01:00 | 609.2132 | 0 | 873.3333 | 10000 | 264.1201 | 0 | 0
2019-06-16 02:00 | 599.354 | 0 | 873.3333 | 10000 | 273.9794 | 0 | 0
2019-06-16 03:00 | 597.2397 | 0 | 873.3333 | 10000 | 276.0937 | 0 | 0
2019-06-16 04:00 | 648.3739 | 83.843 | 873.3333 | 10000 | 308.8024 | 0 | 0
2019-06-16 05:00 | 790.9383 | 696.655 | 1666.6667 | 10000 | 1572.3834 | 0 | 0
2019-06-16 06:00 | 969.0389 | 2171.1218 | 873.3333 | 10000 | 2075.4162 | 0 | 0
2019-06-16 07:00 | 903.8336 | 3838.9864 | 1666.6667 | 10000 | 4601.8195 | 0 | 0
2019-06-16 08:00 | 855.5143 | 5299.783 | 2773.3333 | 10000 | 7217.6021 | 0 | 0
2019-06-16 09:00 | 889.5455 | 6222.7638 | 2773.3333 | 10000 | 8106.5517 | 0 | 0
2019-06-16 10:00 | 880.5447 | 7746.3954 | 2773.3333 | 10000 | 9639.184 | 0 | 0
2019-06-16 11:00 | 856.6722 | 7966.533 | 1666.6667 | 10000 | 8776.5275 | 0 | 0
2019-06-16 12:00 | 821.78 | 7821.7112 | 873.3333 | 10000 | 7873.2645 | 0 | 0
2019-06-16 13:00 | 799.2508 | 7261.7233 | 1666.6667 | 10000 | 8129.1392 | 0 | 0
2019-06-16 14:00 | 823.2949 | 6328.849 | 2773.3333 | 10000 | 8278.8875 | 0 | 0
2019-06-16 15:00 | 924.7556 | 4945.8728 | 2773.3333 | 10000 | 6794.4506 | 0 | 0
2019-06-16 16:00 | 1128.6169 | 3190.1713 | 2773.3333 | 10000 | 4834.8877 | 0 | 0
2019-06-16 17:00 | 1201.1448 | 1365.6641 | 873.3333 | 10000 | 1037.8527 | 0 | 0
2019-06-16 18:00 | 1242.7965 | 266.2227 | 873.3333 | 10000 | -103.2404 | -103.2404 | 0
2019-06-16 19:00 | 1444.8726 | 0 | 873.3333 | 9896.7596 | -571.5393 | -571.5393 | 0
2019-06-16 20:00 | 1638.3709 | 0 | 286.6667 | 9325.2203 | -1351.7042 | -1351.7042 | 0
2019-06-16 21:00 | 1396.7975 | 0 | 0 | 7973.5161 | -1396.7975 | -1396.7975 | 0
2019-06-16 22:00 | 1081.89 | 0 | 0 | 6576.7186 | -1081.89 | -1081.89 | 0
2019-06-16 23:00 | 760.1088 | 0 | 0 | 5494.8285 | -760.1088 | -760.1088 | 0
2019-06-17 | 642.6319 | 0 | 0 | 4734.7197 | -642.6319 | -642.6319 | 0
2019-06-17 01:00 | 584.8543 | 0 | 0 | 4092.0878 | -584.8543 | -584.8543 | 0
2019-06-17 02:00 | 573.5865 | 0 | 0 | 3507.2334 | -573.5865 | -573.5865 | 0
2019-06-17 03:00 | 574.833 | 0 | 0 | 2933.647 | -574.833 | -574.833 | 0
2019-06-17 04:00 | 628.0205 | 38.5227 | 0 | 2358.814 | -589.4978 | -589.4978 | 0
2019-06-17 05:00 | 774.1574 | 278.7174 | 0 | 1769.3163 | -495.4399 | -495.4399 | 0
2019-06-17 06:00 | 965.6159 | 896.6791 | 0 | 1273.8763 | -68.9367 | -68.9367 | 0
2019-06-17 07:00 | 899.9576 | 3108.6535 | 0 | 1204.9396 | 2208.6959 | 2208.6959 | 0
2019-06-17 08:00 | 847.6983 | 1978.782 | 0 | 3413.6355 | 1131.0837 | 1131.0837 | 0
2019-06-17 09:00 | 856.1747 | 1168.8588 | 0 | 4544.7193 | 312.6842 | 312.6842 | 0
2019-06-17 10:00 | 855.6335 | 6002.2422 | 0 | 4857.4035 | 5146.6086 | 5142.5965 | 0
2019-06-17 11:00 | 830.2774 | 4605.1462 | 0 | 10000 | 3774.8688 | 0 | 0
2019-06-17 12:00 | 801.6786 | 4528.7552 | 0 | 10000 | 3727.0766 | 0 | 0
2019-06-17 13:00 | 786.8548 | 5374.9194 | 286.6667 | 10000 | 4874.7313 | 0 | 0
2019-06-17 14:00 | 814.9638 | 2765.3797 | 0 | 10000 | 1950.4159 | 0 | 0
2019-06-17 15:00 | 923.7376 | 975.0689 | 286.6667 | 10000 | 337.9979 | 0 | 0
2019-06-17 16:00 | 1114.4517 | 783.2604 | 286.6667 | 10000 | -44.5246 | -44.5246 | 0
2019-06-17 17:00 | 1202.2173 | 1143.6359 | 286.6667 | 9955.4754 | 228.0852 | 44.5246 | 0
2019-06-17 18:00 | 1245.4312 | 299.8625 | 286.6667 | 10000 | -658.902 | -658.902 | 0
2019-06-17 19:00 | 1447.4134 | 0 | 0 | 9341.098 | -1447.4134 | -1447.4134 | 0
2019-06-17 20:00 | 1641.181 | 0 | 0 | 7893.6846 | -1641.181 | -1641.181 | 0
2019-06-17 21:00 | 1384.5274 | 0 | 0 | 6252.5035 | -1384.5274 | -1384.5274 | 0
2019-06-17 22:00 | 1045.9362 | 0 | 0 | 4867.9761 | -1045.9362 | -1045.9362 | 0
2019-06-17 23:00 | 702.566 | 0 | 286.6667 | 3822.0399 | -415.8993 | -415.8993 | 0
2019-06-18 | 570.8934 | 0 | 286.6667 | 3406.1406 | -284.2268 | -284.2268 | 0
2019-06-18 01:00 | 516.3642 | 0 | 0 | 3121.9138 | -516.3642 | -516.3642 | 0
2019-06-18 02:00 | 514.1968 | 0 | 873.3333 | 2605.5496 | 359.1366 | 359.1366 | 0
2019-06-18 03:00 | 527.5854 | 0 | 0 | 2964.6861 | -527.5854 | -527.5854 | 0
2019-06-18 04:00 | 588.0963 | 29.3641 | 286.6667 | 2437.1007 | -272.0656 | -272.0656 | 0
2019-06-18 05:00 | 734.3899 | 537.3007 | 873.3333 | 2165.0351 | 676.2442 | 676.2442 | 0
2019-06-18 06:00 | 932.5226 | 493.7962 | 873.3333 | 2841.2793 | 434.607 | 434.607 | 0
2019-06-18 07:00 | 872.9009 | 1091.8813 | 873.3333 | 3275.8863 | 1092.3138 | 1092.3138 | 0
2019-06-18 08:00 | 828.4503 | 938.7461 | 2773.3333 | 4368.2001 | 2883.6292 | 2883.6292 | 0
2019-06-18 09:00 | 842.0983 | 1254.5867 | 873.3333 | 7251.8293 | 1285.8217 | 1285.8217 | 0
2019-06-18 10:00 | 852.4307 | 1730.5878 | 873.3333 | 8537.651 | 1751.4905 | 1462.349 | 0
2019-06-18 11:00 | 830.2774 | 2673.7143 | 4266.6667 | 10000 | 6110.1036 | 0 | 0
2019-06-18 12:00 | 801.6786 | 2433.9175 | 7873.3333 | 10000 | 9505.5722 | 0 | 0
2019-06-18 13:00 | 786.8548 | 2530.8935 | 7873.3333 | 10000 | 9617.3721 | 0 | 0
2019-06-18 14:00 | 814.9638 | 972.3675 | 7873.3333 | 10000 | 8030.7371 | 0 | 0
2019-06-18 15:00 | 923.7376 | 1368.9726 | 9060 | 10000 | 9505.235 | 0 | 0
2019-06-18 16:00 | 1114.4517 | 1403.1023 | 6160 | 10000 | 6448.6507 | 0 | 0
2019-06-18 17:00 | 1202.2173 | 1482.9549 | 6160 | 10000 | 6440.7376 | 0 | 0
2019-06-18 18:00 | 1245.4312 | 370.5116 | 4266.6667 | 10000 | 3391.7471 | 0 | 0
2019-06-18 19:00 | 1447.4134 | 0 | 4266.6667 | 10000 | 2819.2533 | 0 | 0
2019-06-18 20:00 | 1641.181 | 0 | 4266.6667 | 10000 | 2625.4856 | 0 | 0
2019-06-18 21:00 | 1384.5274 | 0 | 6160 | 10000 | 4775.4726 | 0 | 0
2019-06-18 22:00 | 1045.9362 | 0 | 4266.6667 | 10000 | 3220.7305 | 0 | 0
2019-06-18 23:00 | 702.566 | 0 | 2773.3333 | 10000 | 2070.7673 | 0 | 0
2019-06-19 | 566.513 | 0 | 2773.3333 | 10000 | 2206.8203 | 0 | 0
2019-06-19 01:00 | 505.0422 | 0 | 2773.3333 | 10000 | 2268.2911 | 0 | 0
2019-06-19 02:00 | 501.0453 | 0 | 6160 | 10000 | 5658.9547 | 0 | 0
2019-06-19 03:00 | 510.4109 | 0 | 2773.3333 | 10000 | 2262.9224 | 0 | 0
2019-06-19 04:00 | 569.7438 | 10.0038 | 2773.3333 | 10000 | 2213.5934 | 0 | 0
2019-06-19 05:00 | 713.9004 | 471.669 | 2773.3333 | 10000 | 2531.102 | 0 | 0
2019-06-19 06:00 | 901.4246 | 1192.6052 | 1666.6667 | 10000 | 1957.8473 | 0 | 0
2019-06-19 07:00 | 833.535 | 2217.1678 | 1666.6667 | 10000 | 3050.2994 | 0 | 0
2019-06-19 08:00 | 786.3766 | 3224.0538 | 2773.3333 | 10000 | 5211.0105 | 0 | 0
2019-06-19 09:00 | 810.6067 | 6865.5403 | 2773.3333 | 10000 | 8828.2668 | 0 | 0
2019-06-19 10:00 | 815.1024 | 5503.5918 | 2773.3333 | 10000 | 7461.8227 | 0 | 0
2019-06-19 11:00 | 792.3518 | 4403.6617 | 7873.3333 | 10000 | 11484.6432 | 0 | 0
2019-06-19 12:00 | 759.7668 | 3771.7527 | 4266.6667 | 10000 | 7278.6526 | 0 | 0
2019-06-19 13:00 | 743.4332 | 7278.2661 | 7873.3333 | 10000 | 14408.1662 | 0 | 0
2019-06-19 14:00 | 773.8357 | 3817.2766 | 9573.3333 | 10000 | 12616.7743 | 0 | 0
2019-06-19 15:00 | 883.8759 | 4963.0113 | 9060 | 10000 | 13139.1354 | 0 | 0
2019-06-19 16:00 | 1075.218 | 3225.2129 | 7873.3333 | 10000 | 10023.3283 | 0 | 0
2019-06-19 17:00 | 1164.1397 | 1396.7037 | 9573.3333 | 10000 | 9805.8974 | 0 | 0
2019-06-19 18:00 | 1207.4263 | 255.1689 | 2773.3333 | 10000 | 1821.0759 | 0 | 0
2019-06-19 19:00 | 1408.7309 | 0 | 4266.6667 | 10000 | 2857.9358 | 0 | 0
2019-06-19 20:00 | 1601.6645 | 0 | 4266.6667 | 10000 | 2665.0022 | 0 | 0
2019-06-19 21:00 | 1353.1276 | 0 | 4266.6667 | 10000 | 2913.5391 | 0 | 0
2019-06-19 22:00 | 1031.0658 | 0 | 4266.6667 | 10000 | 3235.6009 | 0 | 0
2019-06-19 23:00 | 713.3043 | 0 | 2773.3333 | 10000 | 2060.029 | 0 | 0
2019-06-20 | 600.214 | 0 | 1666.6667 | 10000 | 1066.4526 | 0 | 0
2019-06-20 01:00 | 550.4549 | 0 | 2773.3333 | 10000 | 2222.8784 | 0 | 0
2019-06-20 02:00 | 547.892 | 0 | 4266.6667 | 10000 | 3718.7747 | 0 | 0
2019-06-20 03:00 | 554.4051 | 0 | 2773.3333 | 10000 | 2218.9283 | 0 | 0
2019-06-20 04:00 | 607.2431 | 75.2548 | 873.3333 | 10000 | 341.3451 | 0 | 0
2019-06-20 05:00 | 746.0887 | 624.4224 | 286.6667 | 10000 | 165.0003 | 0 | 0
2019-06-20 06:00 | 924.7067 | 2533.0613 | 286.6667 | 10000 | 1895.0213 | 0 | 0
2019-06-20 07:00 | 850.5793 | 4620.332 | 1666.6667 | 10000 | 5436.4194 | 0 | 0
2019-06-20 08:00 | 790.8137 | 6311.8693 | 4266.6667 | 10000 | 9787.7223 | 0 | 0
2019-06-20 09:00 | 802.1423 | 7508.5927 | 6160 | 10000 | 12866.4504 | 0 | 0
2019-06-20 10:00 | 798.3697 | 8237.7962 | 7873.3333 | 10000 | 15312.7598 | 0 | 0
2019-06-20 11:00 | 777.2173 | 8506.7696 | 6160 | 10000 | 13889.5524 | 0 | 0
2019-06-20 12:00 | 753.3045 | 8326.7325 | 9060 | 10000 | 16633.428 | 0 | 0
2019-06-20 13:00 | 743.4332 | 7761.2936 | 9060 | 10000 | 16077.8605 | 0 | 0
2019-06-20 14:00 | 773.8357 | 6749.6317 | 9060 | 10000 | 15035.7961 | 0 | 0
2019-06-20 15:00 | 883.8759 | 5296.9149 | 6160 | 10000 | 10573.0391 | 0 | 0
2019-06-20 16:00 | 1075.218 | 3469.2958 | 7873.3333 | 10000 | 10267.4112 | 0 | 0
2019-06-20 17:00 | 1164.1397 | 1446.3814 | 6160 | 10000 | 6442.2418 | 0 | 0
2019-06-20 18:00 | 1207.4263 | 214.4336 | 873.3333 | 10000 | -119.6594 | -119.6594 | 0
2019-06-20 19:00 | 1408.7309 | 0 | 873.3333 | 9880.3406 | -535.3975 | -535.3975 | 0
2019-06-20 20:00 | 1601.6645 | 0 | 1666.6667 | 9344.9431 | 65.0022 | 65.0022 | 0
2019-06-20 21:00 | 1353.1276 | 0 | 286.6667 | 9409.9453 | -1066.4609 | -1066.4609 | 0
2019-06-20 22:00 | 1028.6956 | 0 | 286.6667 | 8343.4844 | -742.0289 | -742.0289 | 0
2019-06-20 23:00 | 695.2705 | 0 | 873.3333 | 7601.4554 | 178.0628 | 178.0628 | 0
2019-06-21 | 566.513 | 0 | 873.3333 | 7779.5182 | 306.8203 | 306.8203 | 0
2019-06-21 01:00 | 510.9249 | 0 | 873.3333 | 8086.3385 | 362.4084 | 362.4084 | 0
2019-06-21 02:00 | 512.4047 | 0 | 1666.6667 | 8448.7469 | 1154.262 | 1154.262 | 0
2019-06-21 03:00 | 522.1498 | 0 | 1666.6667 | 9603.0089 | 1144.5169 | 396.9911 | 0
2019-06-21 04:00 | 581.4871 | 75.3054 | 873.3333 | 10000 | 367.1517 | 0 | 0
2019-06-21 05:00 | 721.1996 | 613.065 | 873.3333 | 10000 | 765.1987 | 0 | 0
2019-06-21 06:00 | 904.1019 | 2464.5431 | 873.3333 | 10000 | 2433.7746 | 0 | 0
2019-06-21 07:00 | 828.0709 | 4480.0964 | 873.3333 | 10000 | 4525.3588 | 0 | 0
2019-06-21 08:00 | 766.867 | 6099.7736 | 2773.3333 | 10000 | 8106.24 | 0 | 0
2019-06-21 09:00 | 782.7454 | 7276.9826 | 4266.6667 | 10000 | 10760.9039 | 0 | 0
2019-06-21 10:00 | 794.1786 | 8002.6349 | 6160 | 10000 | 13368.4564 | 0 | 0
2019-06-21 11:00 | 777.2173 | 8268.385 | 6160 | 10000 | 13651.1677 | 0 | 0
2019-06-21 12:00 | 753.3045 | 7208.2253 | 2773.3333 | 10000 | 9228.2541 | 0 | 0
2019-06-21 13:00 | 743.4332 | 6743.738 | 4266.6667 | 10000 | 10266.9715 | 0 | 0
2019-06-21 14:00 | 773.8357 | 6613.7685 | 2773.3333 | 10000 | 8613.2661 | 0 | 0
2019-06-21 15:00 | 883.8759 | 4348.8112 | 4266.6667 | 10000 | 7731.6021 | 0 | 0
2019-06-21 16:00 | 1177.7798 | 3438.6196 | 873.3333 | 10000 | 3134.1731 | 0 | 0
2019-06-21 17:00 | 1288.1232 | 1427.8342 | 6160 | 10000 | 6299.7111 | 0 | 0
2019-06-21 18:00 | 1308.7576 | 248.0274 | 2773.3333 | 10000 | 1712.6032 | 0 | 0
2019-06-21 19:00 | 1408.7309 | 0 | 2773.3333 | 10000 | 1364.6025 | 0 | 0
2019-06-21 20:00 | 1601.6645 | 0 | 873.3333 | 10000 | -728.3312 | -728.3312 | 0
2019-06-21 21:00 | 1353.1276 | 0 | 873.3333 | 9271.6688 | -479.7942 | -479.7942 | 0
2019-06-21 22:00 | 1028.6956 | 0 | 873.3333 | 8791.8746 | -155.3623 | -155.3623 | 0
2019-06-21 23:00 | 695.2705 | 0 | 873.3333 | 8636.5123 | 178.0628 | 178.0628 | 0
2019-06-22 | 566.513 | 0 | 873.3333 | 8814.5751 | 306.8203 | 306.8203 | 0
2019-06-22 01:00 | 505.0422 | 0 | 873.3333 | 9121.3954 | 368.2911 | 368.2911 | 0
2019-06-22 02:00 | 492.2011 | 0 | 873.3333 | 9489.6866 | 381.1323 | 381.1323 | 0
2019-06-22 03:00 | 490.5838 | 0 | 286.6667 | 9870.8188 | -203.9171 | -203.9171 | 0
2019-06-22 04:00 | 543.5541 | 98.3469 | 286.6667 | 9666.9017 | -158.5406 | -158.5406 | 0
2019-06-22 05:00 | 683.4632 | 710.5206 | 0 | 9508.3612 | 27.0574 | 27.0574 | 0
2019-06-22 06:00 | 877.4393 | 1444.2804 | 286.6667 | 9535.4185 | 853.5077 | 464.5815 | 0
2019-06-22 07:00 | 814.3266 | 2278.4053 | 286.6667 | 10000 | 1750.7454 | 0 | 0
2019-06-22 08:00 | 766.867 | 4931.3852 | 0 | 10000 | 4164.5182 | 0 | 0
2019-06-22 09:00 | 782.7454 | 5231.0326 | 286.6667 | 10000 | 4734.9539 | 0 | 0
2019-06-22 10:00 | 794.1786 | 3588.5336 | 286.6667 | 10000 | 3081.0217 | 0 | 0
2019-06-22 11:00 | 777.2173 | 4027.0148 | 873.3333 | 10000 | 4123.1309 | 0 | 0
2019-06-22 12:00 | 753.3045 | 2882.7303 | 2773.3333 | 10000 | 4902.7591 | 0 | 0
2019-06-22 13:00 | 743.4332 | 3693.1065 | 873.3333 | 10000 | 3823.0067 | 0 | 0
2019-06-22 14:00 | 773.8357 | 3035.7976 | 0 | 10000 | 2261.9619 | 0 | 0
2019-06-22 15:00 | 883.8759 | 2353.7717 | 873.3333 | 10000 | 2343.2292 | 0 | 0
2019-06-22 16:00 | 1075.218 | 869.8381 | 873.3333 | 10000 | 667.9535 | 0 | 0
2019-06-22 17:00 | 1164.1397 | 869.638 | 873.3333 | 10000 | 578.8317 | 0 | 0
2019-06-22 18:00 | 1207.4263 | 392.6376 | 873.3333 | 10000 | 58.5446 | 0 | 0
2019-06-22 19:00 | 1408.7309 | 0 | 286.6667 | 10000 | -1122.0642 | -1122.0642 | 0
2019-06-22 20:00 | 1601.6645 | 0 | 873.3333 | 8877.9358 | -728.3312 | -728.3312 | 0
2019-06-22 21:00 | 1353.1276 | 0 | 286.6667 | 8149.6047 | -1066.4609 | -1066.4609 | 0
2019-06-22 22:00 | 1028.6956 | 0 | 286.6667 | 7083.1438 | -742.0289 | -742.0289 | 0
2019-06-22 23:00 | 695.2705 | 0 | 873.3333 | 6341.1148 | 178.0628 | 178.0628 | 0
2019-06-23 | 566.513 | 0 | 2773.3333 | 6519.1776 | 2206.8203 | 2206.8203 | 0
2019-06-23 01:00 | 505.0422 | 0 | 873.3333 | 8725.9979 | 368.2911 | 368.2911 | 0
2019-06-23 02:00 | 498.6164 | 0 | 0 | 9094.289 | -498.6164 | -498.6164 | 0
2019-06-23 03:00 | 507.2348 | 0 | 0 | 8595.6727 | -507.2348 | -507.2348 | 0
2019-06-23 04:00 | 566.328 | 105.831 | 0 | 8088.4379 | -460.497 | -460.497 | 0
2019-06-23 05:00 | 706.2804 | 600.7853 | 873.3333 | 7627.941 | 767.8383 | 767.8383 | 0
2019-06-23 06:00 | 901.191 | 2125.5956 | 286.6667 | 8395.7792 | 1511.0713 | 1511.0713 | 0
2019-06-23 07:00 | 840.0908 | 4181.0975 | 286.6667 | 9906.8505 | 3627.6734 | 93.1495 | 0
2019-06-23 08:00 | 790.0632 | 6041.4893 | 286.6667 | 10000 | 5538.0928 | 0 | 0
2019-06-23 09:00 | 802.3922 | 7231.1586 | 873.3333 | 10000 | 7302.0998 | 0 | 0
2019-06-23 10:00 | 799.4288 | 7949.1898 | 873.3333 | 10000 | 8023.0944 | 0 | 0
2019-06-23 11:00 | 777.2173 | 8215.5655 | 6160 | 10000 | 13598.3482 | 0 | 0
2019-06-23 12:00 | 753.3045 | 8085.7949 | 7873.3333 | 10000 | 15205.8237 | 0 | 0
2019-06-23 13:00 | 743.4332 | 7492.7399 | 6160 | 10000 | 12909.3067 | 0 | 0
2019-06-23 14:00 | 773.8357 | 6522.9276 | 9060 | 10000 | 14809.092 | 0 | 0
2019-06-23 15:00 | 883.8759 | 5128.5273 | 6160 | 10000 | 10404.6515 | 0 | 0
2019-06-23 16:00 | 1075.218 | 3327.2248 | 4266.6667 | 10000 | 6518.6735 | 0 | 0
2019-06-23 17:00 | 1164.1397 | 1411.9999 | 7873.3333 | 10000 | 8121.1935 | 0 | 0
2019-06-23 18:00 | 1207.4263 | 243.187 | 4266.6667 | 10000 | 3302.4274 | 0 | 0
2019-06-23 19:00 | 1408.7309 | 0 | 6160 | 10000 | 4751.2691 | 0 | 0
2019-06-23 20:00 | 1601.6645 | 0 | 1666.6667 | 10000 | 65.0022 | 0 | 0
2019-06-23 21:00 | 1353.1276 | 0 | 873.3333 | 10000 | -479.7942 | -479.7942 | 0
2019-06-23 22:00 | 1028.6956 | 0 | 873.3333 | 9520.2058 | -155.3623 | -155.3623 | 0
2019-06-23 23:00 | 695.2705 | 0 | 1666.6667 | 9364.8435 | 971.3961 | 635.1565 | 0
2019-06-24 | 570.8934 | 0 | 1666.6667 | 10000 | 1095.7732 | 0 | 0
2019-06-24 01:00 | 507.9402 | 0 | 1666.6667 | 10000 | 1158.7265 | 0 | 0
2019-06-24 02:00 | 493.7164 | 0 | 1666.6667 | 10000 | 1172.9503 | 0 | 0
2019-06-24 03:00 | 493.5482 | 0 | 1666.6667 | 10000 | 1173.1185 | 0 | 0
2019-06-24 04:00 | 548.1006 | 64.5495 | 2773.3333 | 10000 | 2289.7822 | 0 | 0
2019-06-24 05:00 | 695.2554 | 604.5021 | 2773.3333 | 10000 | 2682.58 | 0 | 0
2019-06-24 06:00 | 900.9242 | 2364.837 | 286.6667 | 10000 | 1750.5794 | 0 | 0
2019-06-24 07:00 | 850.3256 | 4314.5815 | 873.3333 | 10000 | 4337.5893 | 0 | 0
2019-06-24 08:00 | 816.8425 | 5888.092 | 873.3333 | 10000 | 5944.5828 | 0 | 0
2019-06-24 09:00 | 839.2523 | 6988.6408 | 0 | 10000 | 6149.3885 | 0 | 0
2019-06-24 10:00 | 852.4307 | 7650.7027 | 873.3333 | 10000 | 7671.6054 | 0 | 0
2019-06-24 11:00 | 830.2774 | 7961.0578 | 873.3333 | 10000 | 8004.1137 | 0 | 0
2019-06-24 12:00 | 801.6786 | 7838.1205 | 2773.3333 | 10000 | 9809.7753 | 0 | 0
2019-06-24 13:00 | 835.0518 | 7223.357 | 2773.3333 | 10000 | 9161.6386 | 0 | 0
2019-06-24 14:00 | 1051.1838 | 6294.7262 | 6160 | 10000 | 11403.5424 | 0 | 0
2019-06-24 15:00 | 1273.8353 | 4943.0036 | 9060 | 10000 | 12729.1683 | 0 | 0
2019-06-24 16:00 | 1637.0698 | 3206.9084 | 7873.3333 | 10000 | 9443.1719 | 0 | 0
2019-06-24 17:00 | 1667.3182 | 1470.4026 | 6160 | 10000 | 5963.0844 | 0 | 0
2019-06-24 18:00 | 1657.4048 | 364.964 | 4266.6667 | 10000 | 2974.2259 | 0 | 0
2019-06-24 19:00 | 1764.0299 | 0 | 2773.3333 | 10000 | 1009.3035 | 0 | 0
2019-06-24 20:00 | 1884.0924 | 0 | 4266.6667 | 10000 | 2382.5743 | 0 | 0
2019-06-24 21:00 | 1507.7917 | 0 | 2773.3333 | 10000 | 1265.5416 | 0 | 0
2019-06-24 22:00 | 1045.9362 | 0 | 2773.3333 | 10000 | 1727.3971 | 0 | 0
2019-06-24 23:00 | 702.566 | 0 | 1666.6667 | 10000 | 964.1007 | 0 | 0
2019-06-25 | 570.8934 | 0 | 1666.6667 | 10000 | 1095.7732 | 0 | 0
2019-06-25 01:00 | 507.9402 | 0 | 873.3333 | 10000 | 365.3932 | 0 | 0
2019-06-25 02:00 | 493.7164 | 0 | 873.3333 | 10000 | 379.6169 | 0 | 0
2019-06-25 03:00 | 493.5482 | 0 | 873.3333 | 10000 | 379.7851 | 0 | 0
2019-06-25 04:00 | 548.1006 | 56.4397 | 873.3333 | 10000 | 381.6724 | 0 | 0
2019-06-25 05:00 | 695.2554 | 803.559 | 1666.6667 | 10000 | 1774.9703 | 0 | 0
2019-06-25 06:00 | 900.9242 | 1793.5043 | 873.3333 | 10000 | 1765.9135 | 0 | 0
2019-06-25 07:00 | 850.3256 | 2003.7255 | 873.3333 | 10000 | 2026.7333 | 0 | 0
2019-06-25 08:00 | 816.8425 | 1781.3569 | 1666.6667 | 10000 | 2631.1811 | 0 | 0
2019-06-25 09:00 | 839.2523 | 4445.5343 | 2773.3333 | 10000 | 6379.6153 | 0 | 0
2019-06-25 10:00 | 852.4307 | 6183.2625 | 1666.6667 | 10000 | 6997.4985 | 0 | 0
2019-06-25 11:00 | 830.2774 | 5671.4504 | 286.6667 | 10000 | 5127.8396 | 0 | 0
2019-06-25 12:00 | 801.6786 | 5418.1525 | 873.3333 | 10000 | 5489.8073 | 0 | 0
2019-06-25 13:00 | 786.8548 | 5224.8847 | 873.3333 | 10000 | 5311.3632 | 0 | 0
2019-06-25 14:00 | 814.9638 | 3366.9424 | 286.6667 | 10000 | 2838.6453 | 0 | 0
2019-06-25 15:00 | 999.141 | 2988.8339 | 6160 | 10000 | 8149.6929 | 0 | 0
2019-06-25 16:00 | 1339.4564 | 1574.0659 | 2773.3333 | 10000 | 3007.9429 | 0 | 0
2019-06-25 17:00 | 1442.576 | 1038.1671 | 4266.6667 | 10000 | 3862.2578 | 0 | 0
2019-06-25 18:00 | 1453.3453 | 313.061 | 6160 | 10000 | 5019.7158 | 0 | 0
2019-06-25 19:00 | 1591.3616 | 0 | 4266.6667 | 10000 | 2675.305 | 0 | 0
2019-06-25 20:00 | 1743.1628 | 0 | 873.3333 | 10000 | -869.8294 | -869.8294 | 0
2019-06-25 21:00 | 1388.653 | 0 | 6160 | 9130.1706 | 4771.347 | 869.8294 | 0
2019-06-25 22:00 | 1045.9362 | 0 | 873.3333 | 10000 | -172.6029 | -172.6029 | 0
2019-06-25 23:00 | 702.566 | 0 | 286.6667 | 9827.3971 | -415.8993 | -415.8993 | 0
2019-06-26 | 566.513 | 0 | 873.3333 | 9411.4978 | 306.8203 | 306.8203 | 0
2019-06-26 01:00 | 505.0422 | 0 | 873.3333 | 9718.3181 | 368.2911 | 281.6819 | 0
2019-06-26 02:00 | 492.2011 | 0 | 873.3333 | 10000 | 381.1323 | 0 | 0
2019-06-26 03:00 | 490.5838 | 0 | 873.3333 | 10000 | 382.7496 | 0 | 0
2019-06-26 04:00 | 543.5541 | 28.8098 | 873.3333 | 10000 | 358.589 | 0 | 0
2019-06-26 05:00 | 683.4632 | 317.1194 | 873.3333 | 10000 | 506.9895 | 0 | 0
2019-06-26 06:00 | 877.4393 | 588.9575 | 286.6667 | 10000 | -1.8151 | -1.8151 | 0
2019-06-26 07:00 | 814.3266 | 2474.1893 | 1666.6667 | 9998.1849 | 3326.5294 | 1.8151 | 0
2019-06-26 08:00 | 766.867 | 1357.6946 | 4266.6667 | 10000 | 4857.4943 | 0 | 0
2019-06-26 09:00 | 782.7454 | 1561.9691 | 873.3333 | 10000 | 1652.557 | 0 | 0
2019-06-26 10:00 | 794.1786 | 1515.892 | 1666.6667 | 10000 | 2388.3801 | 0 | 0
2019-06-26 11:00 | 777.2173 | 1945.4837 | 4266.6667 | 10000 | 5434.9332 | 0 | 0
2019-06-26 12:00 | 926.5071 | 3587.2996 | 4266.6667 | 10000 | 6927.4592 | 0 | 0
2019-06-26 13:00 | 1184.399 | 4631.4329 | 4266.6667 | 10000 | 7713.7006 | 0 | 0
2019-06-26 14:00 | 1317.1221 | 5427.8263 | 2773.3333 | 10000 | 6884.0375 | 0 | 0
2019-06-26 15:00 | 1572.0805 | 4216.5705 | 873.3333 | 10000 | 3517.8233 | 0 | 0
2019-06-26 16:00 | 1910.2275 | 837.2241 | 873.3333 | 10000 | -199.67 | -199.67 | 0
2019-06-26 17:00 | 1949.5045 | 1116.8075 | 4266.6667 | 9800.33 | 3433.9697 | 199.67 | 0
2019-06-26 18:00 | 1869.0111 | 304.8408 | 1666.6667 | 10000 | 102.4964 | 0 | 0
2019-06-26 19:00 | 1976.4749 | 0 | 2773.3333 | 10000 | 796.8584 | 0 | 0
2019-06-26 20:00 | 2104.6063 | 0 | 0 | 10000 | -2104.6063 | -2104.6063 | 0
2019-06-26 21:00 | 1712.925 | 0 | 873.3333 | 7895.3937 | -839.5916 | -839.5916 | 0
2019-06-26 22:00 | 1219.1412 | 0 | 286.6667 | 7055.802 | -932.4745 | -932.4745 | 0
2019-06-26 23:00 | 776.758 | 0 | 0 | 6123.3275 | -776.758 | -776.758 | 0
2019-06-27 | 566.513 | 0 | 0 | 5346.5695 | -566.513 | -566.513 | 0
2019-06-27 01:00 | 505.0422 | 0 | 0 | 4780.0565 | -505.0422 | -505.0422 | 0
2019-06-27 02:00 | 492.2011 | 0 | 0 | 4275.0143 | -492.2011 | -492.2011 | 0
2019-06-27 03:00 | 490.5838 | 0 | 0 | 3782.8132 | -490.5838 | -490.5838 | 0
2019-06-27 04:00 | 543.5541 | 57.6345 | 0 | 3292.2295 | -485.9195 | -485.9195 | 0
2019-06-27 05:00 | 683.4632 | 578.5351 | 0 | 2806.3099 | -104.9281 | -104.9281 | 0
2019-06-27 06:00 | 877.4393 | 2404.3866 | 0 | 2701.3818 | 1526.9473 | 1526.9473 | 0
2019-06-27 07:00 | 814.3266 | 4400.6153 | 0 | 4228.3291 | 3586.2887 | 3586.2887 | 0
2019-06-27 08:00 | 766.867 | 6086.5164 | 0 | 7814.6178 | 5319.6495 | 2185.3822 | 0
2019-06-27 09:00 | 935.1585 | 7290.1467 | 873.3333 | 10000 | 7228.3216 | 0 | 0
2019-06-27 10:00 | 1059.3599 | 7993.3545 | 286.6667 | 10000 | 7220.6612 | 0 | 0
2019-06-27 11:00 | 1130.3201 | 8260.0521 | 286.6667 | 10000 | 7416.3987 | 0 | 0
2019-06-27 12:00 | 1251.6912 | 8116.0905 | 286.6667 | 10000 | 7151.0659 | 0 | 0
2019-06-27 13:00 | 1421.5882 | 7491.1897 | 1666.6667 | 10000 | 7736.2681 | 0 | 0
2019-06-27 14:00 | 1564.3027 | 6544.2164 | 9873.3333 | 10000 | 14853.2471 | 0 | 0
2019-06-27 15:00 | 1737.3256 | 5145.7544 | 9060 | 10000 | 12468.4288 | 0 | 0
2019-06-27 16:00 | 2078.2785 | 3369.0434 | 6160 | 10000 | 7450.7649 | 0 | 0
2019-06-27 17:00 | 1744.922 | 1486.5958 | 4266.6667 | 10000 | 4008.3405 | 0 | 0
2019-06-27 18:00 | 1686.1812 | 285.3667 | 1666.6667 | 10000 | 265.8522 | 0 | 0
2019-06-27 19:00 | 1751.4068 | 0 | 4266.6667 | 10000 | 2515.2599 | 0 | 0
2019-06-27 20:00 | 1865.9205 | 0 | 0 | 10000 | -1865.9205 | -1865.9205 | 0
2019-06-27 21:00 | 1502.6833 | 0 | 0 | 8134.0795 | -1502.6833 | -1502.6833 | 0
2019-06-27 22:00 | 1062.9847 | 0 | 0 | 6631.3962 | -1062.9847 | -1062.9847 | 0
2019-06-27 23:00 | 695.2705 | 0 | 286.6667 | 5568.4115 | -408.6039 | -408.6039 | 0
2019-06-28 | 566.513 | 0 | 1666.6667 | 5159.8077 | 1100.1536 | 1100.1536 | 0
2019-06-28 01:00 | 505.0422 | 0 | 873.3333 | 6259.9613 | 368.2911 | 368.2911 | 0
2019-06-28 02:00 | 492.2011 | 0 | 0 | 6628.2524 | -492.2011 | -492.2011 | 0
2019-06-28 03:00 | 490.5838 | 0 | 873.3333 | 6136.0514 | 382.7496 | 382.7496 | 0
2019-06-28 04:00 | 543.5541 | 119.6092 | 873.3333 | 6518.8009 | 449.3884 | 449.3884 | 0
2019-06-28 05:00 | 683.4632 | 616.7243 | 1666.6667 | 6968.1894 | 1599.9277 | 1599.9277 | 0
2019-06-28 06:00 | 877.4393 | 1682.7766 | 2773.3333 | 8568.1171 | 3578.6706 | 1431.8829 | 0
2019-06-28 07:00 | 814.3266 | 3970.375 | 2773.3333 | 10000 | 5929.3817 | 0 | 0
2019-06-28 08:00 | 766.867 | 5658.8659 | 1666.6667 | 10000 | 6558.6657 | 0 | 0
2019-06-28 09:00 | 782.7454 | 5549.3411 | 2773.3333 | 10000 | 7539.929 | 0 | 0
2019-06-28 10:00 | 794.1786 | 7191.8826 | 2773.3333 | 10000 | 9171.0374 | 0 | 0
2019-06-28 11:00 | 777.2173 | 6613.167 | 873.3333 | 10000 | 6709.2831 | 0 | 0
2019-06-28 12:00 | 759.5451 | 7110.3614 | 4266.6667 | 10000 | 10617.483 | 0 | 0
2019-06-28 13:00 | 919.9514 | 5661.7662 | 2773.3333 | 10000 | 7515.1482 | 0 | 0
2019-06-28 14:00 | 973.471 | 3379.7868 | 4266.6667 | 10000 | 6672.9825 | 0 | 0
2019-06-28 15:00 | 1157.1914 | 3271.2198 | 873.3333 | 10000 | 2987.3617 | 0 | 0
2019-06-28 16:00 | 1363.8481 | 819.7913 | 1666.6667 | 10000 | 1122.6099 | 0 | 0
2019-06-28 17:00 | 1476.845 | 84.8815 | 2773.3333 | 10000 | 1381.3698 | 0 | 0
2019-06-28 18:00 | 1411.7338 | 356.8438 | 1666.6667 | 10000 | 611.7768 | 0 | 0
2019-06-28 19:00 | 1554.3735 | 0 | 873.3333 | 10000 | -681.0401 | -681.0401 | 0
2019-06-28 20:00 | 1730.3931 | 0 | 286.6667 | 9318.9599 | -1443.7265 | -1443.7265 | 0
2019-06-28 21:00 | 1389.0228 | 0 | 286.6667 | 7875.2334 | -1102.3562 | -1102.3562 | 0
2019-06-28 22:00 | 1028.6956 | 0 | 286.6667 | 6772.8772 | -742.0289 | -742.0289 | 0
2019-06-28 23:00 | 695.2705 | 0 | 1666.6667 | 6030.8483 | 971.3961 | 971.3961 | 0
2019-06-29 | 566.513 | 0 | 1666.6667 | 7002.2444 | 1100.1536 | 1100.1536 | 0
2019-06-29 01:00 | 505.0422 | 0 | 873.3333 | 8102.398 | 368.2911 | 368.2911 | 0
2019-06-29 02:00 | 492.2011 | 0 | 286.6667 | 8470.6892 | -205.5344 | -205.5344 | 0
2019-06-29 03:00 | 490.5838 | 0 | 0 | 8265.1548 | -490.5838 | -490.5838 | 0
2019-06-29 04:00 | 543.5541 | 0 | 286.6667 | 7774.571 | -256.8874 | -256.8874 | 0
2019-06-29 05:00 | 683.4632 | 68.8229 | 2773.3333 | 7517.6836 | 2158.693 | 2158.693 | 0
2019-06-29 06:00 | 877.4393 | 1669.823 | 873.3333 | 9676.3766 | 1665.717 | 323.6234 | 0
2019-06-29 07:00 | 814.3266 | 1131.278 | 1666.6667 | 10000 | 1983.6181 | 0 | 0
2019-06-29 08:00 | 766.867 | 2062.6124 | 1666.6667 | 10000 | 2962.4121 | 0 | 0
2019-06-29 09:00 | 782.7454 | 1624.9086 | 2773.3333 | 10000 | 3615.4965 | 0 | 0
2019-06-29 10:00 | 794.1786 | 4493.4444 | 2773.3333 | 10000 | 6472.5992 | 0 | 0
2019-06-29 11:00 | 777.2173 | 8176.3931 | 1666.6667 | 10000 | 9065.8425 | 0 | 0
2019-06-29 12:00 | 753.3045 | 6874.8518 | 2773.3333 | 10000 | 8894.8806 | 0 | 0
2019-06-29 13:00 | 743.4332 | 7419.0134 | 2773.3333 | 10000 | 9448.9135 | 0 | 0
2019-06-29 14:00 | 773.8357 | 6463.0092 | 2773.3333 | 10000 | 8462.5068 | 0 | 0
2019-06-29 15:00 | 889.2154 | 5080.363 | 2773.3333 | 10000 | 6964.481 | 0 | 0
2019-06-29 16:00 | 1075.218 | 3324.4717 | 2773.3333 | 10000 | 5022.5871 | 0 | 0
2019-06-29 17:00 | 1234.7109 | 1439.5608 | 2773.3333 | 10000 | 2978.1832 | 0 | 0
2019-06-29 18:00 | 1258.2269 | 273.3998 | 6160 | 10000 | 5175.1729 | 0 | 0
2019-06-29 19:00 | 1408.7309 | 0 | 4266.6667 | 10000 | 2857.9358 | 0 | 0
2019-06-29 20:00 | 1601.6645 | 0 | 2773.3333 | 10000 | 1171.6688 | 0 | 0
2019-06-29 21:00 | 1353.1276 | 0 | 4266.6667 | 10000 | 2913.5391 | 0 | 0
2019-06-29 22:00 | 1028.6956 | 0 | 2773.3333 | 10000 | 1744.6377 | 0 | 0
2019-06-29 23:00 | 695.2705 | 0 | 2773.3333 | 10000 | 2078.0628 | 0 | 0
2019-06-30 | 566.513 | 0 | 4266.6667 | 10000 | 3700.1536 | 0 | 0
2019-06-30 01:00 | 505.0422 | 0 | 4266.6667 | 10000 | 3761.6245 | 0 | 0
2019-06-30 02:00 | 492.2011 | 0 | 4266.6667 | 10000 | 3774.4656 | 0 | 0
2019-06-30 03:00 | 490.5838 | 0 | 2773.3333 | 10000 | 2282.7496 | 0 | 0
2019-06-30 04:00 | 543.5541 | 48.3195 | 2773.3333 | 10000 | 2278.0988 | 0 | 0
2019-06-30 05:00 | 683.4632 | 714.1833 | 4266.6667 | 10000 | 4297.3868 | 0 | 0
2019-06-30 06:00 | 877.4393 | 2268.5141 | 6160 | 10000 | 7551.0748 | 0 | 0
2019-06-30 07:00 | 814.3266 | 4177.0472 | 6160 | 10000 | 9522.7206 | 0 | 0
2019-06-30 08:00 | 766.867 | 5838.2694 | 4266.6667 | 10000 | 9338.0691 | 0 | 0
2019-06-30 09:00 | 782.7454 | 7060.2456 | 1666.6667 | 10000 | 7944.1669 | 0 | 0
2019-06-30 10:00 | 794.1786 | 7778.4079 | 1666.6667 | 10000 | 8650.896 | 0 | 0
2019-06-30 11:00 | 777.2173 | 8109.9127 | 2773.3333 | 10000 | 10106.0288 | 0 | 0
2019-06-30 12:00 | 753.3045 | 7968.7226 | 1666.6667 | 10000 | 8882.0847 | 0 | 0
2019-06-30 13:00 | 743.4332 | 7409.7283 | 1666.6667 | 10000 | 8332.9618 | 0 | 0
2019-06-30 14:00 | 773.8357 | 4120.8709 | 2773.3333 | 10000 | 6120.3685 | 0 | 0
2019-06-30 15:00 | 920.017 | 5109.5029 | 4266.6667 | 10000 | 8456.1525 | 0 | 0
2019-06-30 16:00 | 1350.3611 | 3250.0196 | 4266.6667 | 10000 | 6166.3251 | 0 | 0
2019-06-30 17:00 | 1433.2304 | 1502.4175 | 1666.6667 | 10000 | 1735.8538 | 0 | 0
2019-06-30 18:00 | 1444.9061 | 370.0044 | 1666.6667 | 10000 | 591.765 | 0 | 0
2019-06-30 19:00 | 1595.1697 | 0 | 873.3333 | 10000 | -721.8364 | -721.8364 | 0
2019-06-30 20:00 | 1733.4065 | 0 | 873.3333 | 9278.1636 | -860.0732 | -860.0732 | 0
2019-06-30 21:00 | 1363.1592 | 0 | 2773.3333 | 8418.0904 | 1410.1741 | 1410.1741 | 0
2019-06-30 22:00 | 1028.6956 | 0 | 1666.6667 | 9828.2645 | 637.9711 | 171.7355 | 0
2019-06-30 23:00 | 695.2705 | 0 | 873.3333 | 10000 | 178.0628 | 0 | 0
2019-07-01 | 572.1553 | 0 | 2773.3333 | 10000 | 2201.178 | 0 | 0
2019-07-01 01:00 | 508.2675 | 0 | 2773.3333 | 10000 | 2265.0658 | 0 | 0
2019-07-01 02:00 | 494.0641 | 0 | 873.3333 | 10000 | 379.2692 | 0 | 0
2019-07-01 03:00 | 493.9859 | 0 | 286.6667 | 10000 | -207.3192 | -207.3192 | 0
2019-07-01 04:00 | 548.5066 | 75.5239 | 286.6667 | 9792.6808 | -186.316 | -186.316 | 0
2019-07-01 05:00 | 700.7588 | 623.4897 | 286.6667 | 9606.3648 | 209.3976 | 209.3976 | 0
2019-07-01 06:00 | 917.0629 | 1834.426 | 1666.6667 | 9815.7624 | 2584.0297 | 184.2376 | 0
2019-07-01 07:00 | 869.5445 | 3548.6102 | 1666.6667 | 10000 | 4345.7323 | 0 | 0
2019-07-01 08:00 | 828.3843 | 4502.7065 | 873.3333 | 10000 | 4547.6556 | 0 | 0
2019-07-01 09:00 | 849.1746 | 5470.5224 | 1666.6667 | 10000 | 6288.0145 | 0 | 0
2019-07-01 10:00 | 857.8334 | 6447.8947 | 1666.6667 | 10000 | 7256.728 | 0 | 0
2019-07-01 11:00 | 835.4142 | 6479.0252 | 2773.3333 | 10000 | 8416.9444 | 0 | 0
2019-07-01 12:00 | 806.6603 | 6047.2738 | 6160 | 10000 | 11400.6136 | 0 | 0
2019-07-01 13:00 | 791.7355 | 5542.0455 | 7873.3333 | 10000 | 12623.6433 | 0 | 0
2019-07-01 14:00 | 815.4321 | 4321.7437 | 6160 | 10000 | 9666.3116 | 0 | 0
2019-07-01 15:00 | 928.8291 | 4181.9554 | 9573.3333 | 10000 | 12826.4597 | 0 | 0
2019-07-01 16:00 | 1115.5493 | 2798.2662 | 7873.3333 | 10000 | 9556.0502 | 0 | 0
2019-07-01 17:00 | 1203.8816 | 1086.1991 | 7873.3333 | 10000 | 7755.6509 | 0 | 0
2019-07-01 18:00 | 1244.6359 | 335.1065 | 4266.6667 | 10000 | 3357.1374 | 0 | 0
2019-07-01 19:00 | 1450.7645 | 0 | 2773.3333 | 10000 | 1322.5689 | 0 | 0
2019-07-01 20:00 | 1644.5115 | 0 | 2773.3333 | 10000 | 1128.8219 | 0 | 0
2019-07-01 21:00 | 1385.7285 | 0 | 1666.6667 | 10000 | 280.9382 | 0 | 0
2019-07-01 22:00 | 1043.6238 | 0 | 1666.6667 | 10000 | 623.0429 | 0 | 0
2019-07-01 23:00 | 709.0123 | 0 | 1666.6667 | 10000 | 957.6544 | 0 | 0
2019-07-02 | 587.5487 | 0 | 1666.6667 | 10000 | 1079.118 | 0 | 0
2019-07-02 01:00 | 528.9771 | 0 | 1666.6667 | 10000 | 1137.6895 | 0 | 0
2019-07-02 02:00 | 521.41 | 0 | 873.3333 | 10000 | 351.9233 | 0 | 0
2019-07-02 03:00 | 525.7078 | 0 | 873.3333 | 10000 | 347.6255 | 0 | 0
2019-07-02 04:00 | 579.8905 | 27.1664 | 286.6667 | 10000 | -266.0574 | -266.0574 | 0
2019-07-02 05:00 | 728.0147 | 625.6954 | 286.6667 | 9733.9426 | 184.3475 | 184.3475 | 0
2019-07-02 06:00 | 941.0499 | 1441.4192 | 1666.6667 | 9918.2901 | 2167.0359 | 81.7099 | 0
2019-07-02 07:00 | 890.4976 | 3820.8175 | 2773.3333 | 10000 | 5703.6533 | 0 | 0
2019-07-02 08:00 | 844.443 | 5335.3146 | 1666.6667 | 10000 | 6157.5383 | 0 | 0
2019-07-02 09:00 | 862.3001 | 6457.8043 | 2773.3333 | 10000 | 8368.8375 | 0 | 0
2019-07-02 10:00 | 867.3143 | 7178.4909 | 2773.3333 | 10000 | 9084.5099 | 0 | 0
2019-07-02 11:00 | 836.2708 | 7460.3927 | 4266.6667 | 10000 | 10890.7885 | 0 | 0
2019-07-02 12:00 | 806.6603 | 7390.6958 | 1666.6667 | 10000 | 8250.7022 | 0 | 0
2019-07-02 13:00 | 791.7355 | 6872.2976 | 1666.6667 | 10000 | 7747.2288 | 0 | 0
2019-07-02 14:00 | 815.4321 | 6000.4332 | 1666.6667 | 10000 | 6851.6678 | 0 | 0
2019-07-02 15:00 | 928.8291 | 3962.7378 | 6160 | 10000 | 9193.9087 | 0 | 0
2019-07-02 16:00 | 1115.5493 | 2666.2221 | 7873.3333 | 10000 | 9424.0061 | 0 | 0
2019-07-02 17:00 | 1203.8816 | 538.3771 | 2773.3333 | 10000 | 2107.8288 | 0 | 0
2019-07-02 18:00 | 1244.6359 | 210.9203 | 873.3333 | 10000 | -160.3822 | -160.3822 | 0
2019-07-02 19:00 | 1450.7645 | 0 | 286.6667 | 9839.6178 | -1164.0978 | -1164.0978 | 0
2019-07-02 20:00 | 1644.5115 | 0 | 0 | 8675.52 | -1644.5115 | -1644.5115 | 0
2019-07-02 21:00 | 1385.7285 | 0 | 1666.6667 | 7031.0085 | 280.9382 | 280.9382 | 0
2019-07-02 22:00 | 1043.6238 | 0 | 873.3333 | 7311.9467 | -170.2905 | -170.2905 | 0
2019-07-02 23:00 | 715.2743 | 0 | 0 | 7141.6562 | -715.2743 | -715.2743 | 0
2019-07-03 | 588.0897 | 0 | 2773.3333 | 6426.3819 | 2185.2437 | 2185.2437 | 0
2019-07-03 01:00 | 533.2152 | 0 | 1666.6667 | 8611.6256 | 1133.4514 | 1133.4514 | 0
2019-07-03 02:00 | 526.2947 | 0 | 2773.3333 | 9745.077 | 2247.0386 | 254.923 | 0
2019-07-03 03:00 | 527.2445 | 0 | 873.3333 | 10000 | 346.0889 | 0 | 0
2019-07-03 04:00 | 579.9514 | 0 | 873.3333 | 10000 | 293.382 | 0 | 0
2019-07-03 05:00 | 724.9789 | 630.1874 | 2773.3333 | 10000 | 2678.5418 | 0 | 0
2019-07-03 06:00 | 919.7694 | 1967.0738 | 2773.3333 | 10000 | 3820.6378 | 0 | 0
2019-07-03 07:00 | 855.0617 | 3548.2249 | 2773.3333 | 10000 | 5466.4966 | 0 | 0
2019-07-03 08:00 | 792.5254 | 4910.9761 | 873.3333 | 10000 | 4991.784 | 0 | 0
2019-07-03 09:00 | 797.4112 | 1714.5315 | 1666.6667 | 10000 | 2583.7871 | 0 | 0
2019-07-03 10:00 | 800.3072 | 5067.2243 | 2773.3333 | 10000 | 7040.2504 | 0 | 0
2019-07-03 11:00 | 782.354 | 7499.1707 | 2773.3333 | 10000 | 9490.15 | 0 | 0
2019-07-03 12:00 | 758.2862 | 7370.2787 | 6160 | 10000 | 12771.9925 | 0 | 0
2019-07-03 13:00 | 748.3139 | 6845.5176 | 6160 | 10000 | 12257.2037 | 0 | 0
2019-07-03 14:00 | 774.304 | 5949.1064 | 4266.6667 | 10000 | 9441.4691 | 0 | 0
2019-07-03 15:00 | 888.9674 | 4661.3732 | 2773.3333 | 10000 | 6545.7392 | 0 | 0
2019-07-03 16:00 | 1076.3157 | 3107.921 | 6160 | 10000 | 8191.6053 | 0 | 0
2019-07-03 17:00 | 1165.804 | 1384.7702 | 4266.6667 | 10000 | 4485.6329 | 0 | 0
2019-07-03 18:00 | 1206.631 | 312.9185 | 873.3333 | 10000 | -20.3792 | -20.3792 | 0
2019-07-03 19:00 | 1412.0819 | 0 | 1666.6667 | 9979.6208 | 254.5847 | 20.3792 | 0
2019-07-03 20:00 | 1604.9949 | 0 | 873.3333 | 10000 | -731.6616 | -731.6616 | 0
2019-07-03 21:00 | 1354.3286 | 0 | 873.3333 | 9268.3384 | -480.9953 | -480.9953 | 0
2019-07-03 22:00 | 1026.3832 | 0 | 286.6667 | 8787.3431 | -739.7165 | -739.7165 | 0
2019-07-03 23:00 | 698.1455 | 0 | 1666.6667 | 8047.6266 | 968.5212 | 968.5212 | 0
2019-07-04 | 567.7749 | 0 | 873.3333 | 9016.1478 | 305.5585 | 305.5585 | 0
2019-07-04 01:00 | 505.3696 | 0 | 286.6667 | 9321.7062 | -218.7029 | -218.7029 | 0
2019-07-04 02:00 | 492.5488 | 0 | 0 | 9103.0033 | -492.5488 | -492.5488 | 0
2019-07-04 03:00 | 491.0215 | 0 | 286.6667 | 8610.4545 | -204.3548 | -204.3548 | 0
2019-07-04 04:00 | 543.9601 | 45.7481 | 286.6667 | 8406.0997 | -211.5452 | -211.5452 | 0
2019-07-04 05:00 | 688.9666 | 607.0643 | 0 | 8194.5545 | -81.9023 | -81.9023 | 0
2019-07-04 06:00 | 893.578 | 647.2959 | 286.6667 | 8112.6522 | 40.3846 | 40.3846 | 0
2019-07-04 07:00 | 829.785 | 2250.8708 | 286.6667 | 8153.0368 | 1707.7525 | 1707.7525 | 0
2019-07-04 08:00 | 772.2009 | 1942.9928 | 873.3333 | 9860.7893 | 2044.1253 | 139.2107 | 0
2019-07-04 09:00 | 783.2561 | 3421.4984 | 0 | 10000 | 2638.2423 | 0 | 0
2019-07-04 10:00 | 799.2201 | 2575.5285 | 0 | 10000 | 1776.3084 | 0 | 0
2019-07-04 11:00 | 782.354 | 1679.5439 | 873.3333 | 10000 | 1770.5232 | 0 | 0
2019-07-04 12:00 | 758.2862 | 1327.6968 | 0 | 10000 | 569.4107 | 0 | 0
2019-07-04 13:00 | 748.3139 | 1485.8655 | 873.3333 | 10000 | 1610.885 | 0 | 0
2019-07-04 14:00 | 774.304 | 698.2524 | 286.6667 | 10000 | 210.6151 | 0 | 0
2019-07-04 15:00 | 888.9674 | 515.9716 | 286.6667 | 10000 | -86.329 | -86.329 | 0
2019-07-04 16:00 | 1076.3157 | 359.6188 | 286.6667 | 9913.671 | -430.0302 | -430.0302 | 0
2019-07-04 17:00 | 1165.804 | 435.3406 | 0 | 9483.6407 | -730.4634 | -730.4634 | 0
2019-07-04 18:00 | 1206.631 | 0 | 0 | 8753.1773 | -1206.631 | -1206.631 | 0
2019-07-04 19:00 | 1412.0819 | 0 | 0 | 7546.5463 | -1412.0819 | -1412.0819 | 0
2019-07-04 20:00 | 1604.9949 | 0 | 0 | 6134.4644 | -1604.9949 | -1604.9949 | 0
2019-07-04 21:00 | 1354.3286 | 0 | 0 | 4529.4695 | -1354.3286 | -1354.3286 | 0
2019-07-04 22:00 | 1026.3832 | 0 | 0 | 3175.1408 | -1026.3832 | -1026.3832 | 0
2019-07-04 23:00 | 698.1455 | 0 | 0 | 2148.7576 | -698.1455 | -698.1455 | 0
2019-07-05 | 567.7749 | 0 | 0 | 1450.6121 | -567.7749 | -567.7749 | 0
2019-07-05 01:00 | 505.3696 | 0 | 0 | 882.8373 | -505.3696 | -505.3696 | 0
2019-07-05 02:00 | 492.5488 | 0 | 286.6667 | 377.4677 | -205.8821 | -205.8821 | 0
2019-07-05 03:00 | 491.0215 | 0 | 0 | 171.5856 | -491.0215 | -171.5856 | -319.4359
2019-07-05 04:00 | 543.9601 | 9.9992 | 0 | 0 | -533.9608 | 0 | -853.3967
2019-07-05 05:00 | 688.9666 | 629.4939 | 0 | 0 | -59.4727 | 0 | -912.8694
2019-07-05 06:00 | 893.578 | 1853.11 | 0 | 0 | 959.532 | 959.532 | 0
2019-07-05 07:00 | 829.785 | 4297.5293 | 0 | 959.532 | 3467.7443 | 3467.7443 | 0
2019-07-05 08:00 | 772.2009 | 6008.8213 | 286.6667 | 4427.2763 | 5523.287 | 5523.287 | 0
2019-07-05 09:00 | 783.2561 | 7258.2998 | 286.6667 | 9950.5634 | 6761.7103 | 49.4366 | 0
2019-07-05 10:00 | 799.2201 | 8049.6929 | 286.6667 | 10000 | 7537.1396 | 0 | 0
2019-07-05 11:00 | 782.354 | 8327.0568 | 286.6667 | 10000 | 7831.3695 | 0 | 0
2019-07-05 12:00 | 758.2862 | 8221.3443 | 2773.3333 | 10000 | 10236.3914 | 0 | 0
2019-07-05 13:00 | 748.3139 | 6803.0768 | 2773.3333 | 10000 | 8828.0963 | 0 | 0
2019-07-05 14:00 | 774.304 | 6155.6591 | 4266.6667 | 10000 | 9648.0218 | 0 | 0
2019-07-05 15:00 | 888.9674 | 5201.1498 | 4266.6667 | 10000 | 8578.8492 | 0 | 0
2019-07-05 16:00 | 1076.3157 | 3402.643 | 4266.6667 | 10000 | 6592.994 | 0 | 0
2019-07-05 17:00 | 1165.804 | 1425.6285 | 1666.6667 | 10000 | 1926.4912 | 0 | 0
2019-07-05 18:00 | 1206.631 | 235.1003 | 873.3333 | 10000 | -98.1974 | -98.1974 | 0
2019-07-05 19:00 | 1412.0819 | 0 | 286.6667 | 9901.8026 | -1125.4153 | -1125.4153 | 0
2019-07-05 20:00 | 1604.9949 | 0 | 286.6667 | 8776.3873 | -1318.3282 | -1318.3282 | 0
2019-07-05 21:00 | 1354.3286 | 0 | 873.3333 | 7458.0591 | -480.9953 | -480.9953 | 0
2019-07-05 22:00 | 1026.3832 | 0 | 873.3333 | 6977.0638 | -153.0499 | -153.0499 | 0
2019-07-05 23:00 | 698.1455 | 0 | 873.3333 | 6824.0139 | 175.1879 | 175.1879 | 0
2019-07-06 | 567.7749 | 0 | 286.6667 | 6999.2018 | -281.1082 | -281.1082 | 0
2019-07-06 01:00 | 505.3696 | 0 | 286.6667 | 6718.0936 | -218.7029 | -218.7029 | 0
2019-07-06 02:00 | 492.5488 | 0 | 0 | 6499.3906 | -492.5488 | -492.5488 | 0
2019-07-06 03:00 | 491.0215 | 0 | 0 | 6006.8418 | -491.0215 | -491.0215 | 0
2019-07-06 04:00 | 543.9601 | 30.6728 | 0 | 5515.8204 | -513.2873 | -513.2873 | 0
2019-07-06 05:00 | 688.9666 | 499.614 | 286.6667 | 5002.5331 | 97.3141 | 97.3141 | 0
2019-07-06 06:00 | 893.578 | 1876.2836 | 286.6667 | 5099.8473 | 1269.3724 | 1269.3724 | 0
2019-07-06 07:00 | 829.785 | 4115.0013 | 286.6667 | 6369.2196 | 3571.883 | 3571.883 | 0
2019-07-06 08:00 | 772.2009 | 5346.2545 | 873.3333 | 9941.1026 | 5447.387 | 58.8974 | 0
2019-07-06 09:00 | 783.2561 | 7054.4231 | 286.6667 | 10000 | 6557.8337 | 0 | 0
2019-07-06 10:00 | 799.2201 | 7784.2661 | 873.3333 | 10000 | 7858.3793 | 0 | 0
2019-07-06 11:00 | 782.354 | 8074.0603 | 286.6667 | 10000 | 7578.3729 | 0 | 0
2019-07-06 12:00 | 811.6943 | 7979.0507 | 2773.3333 | 10000 | 9940.6898 | 0 | 0
2019-07-06 13:00 | 1002.2936 | 7423.2281 | 1666.6667 | 10000 | 8087.6012 | 0 | 0
2019-07-06 14:00 | 1335.2567 | 6514.1623 | 2773.3333 | 10000 | 7952.239 | 0 | 0
2019-07-06 15:00 | 1512.7565 | 5143.0564 | 2773.3333 | 10000 | 6403.6333 | 0 | 0
2019-07-06 16:00 | 1888.292 | 3365.5831 | 2773.3333 | 10000 | 4250.6245 | 0 | 0
2019-07-06 17:00 | 1936.6721 | 1435.6945 | 2773.3333 | 10000 | 2272.3557 | 0 | 0
2019-07-06 18:00 | 2006.6401 | 263.0613 | 1666.6667 | 10000 | -76.9121 | -76.9121 | 0
2019-07-06 19:00 | 2147.2208 | 0 | 1666.6667 | 9923.0879 | -480.5541 | -480.5541 | 0
2019-07-06 20:00 | 2248.5233 | 0 | 2773.3333 | 9442.5338 | 524.81 | 524.81 | 0
2019-07-06 21:00 | 1859.7278 | 0 | 873.3333 | 9967.3438 | -986.3945 | -986.3945 | 0
2019-07-06 22:00 | 1376.2629 | 0 | 873.3333 | 8980.9493 | -502.9296 | -502.9296 | 0
2019-07-06 23:00 | 876.9368 | 0 | 1666.6667 | 8478.0198 | 789.7298 | 789.7298 | 0
2019-07-07 | 649.937 | 0 | 873.3333 | 9267.7496 | 223.3964 | 223.3964 | 0
2019-07-07 01:00 | 505.3696 | 0 | 286.6667 | 9491.146 | -218.7029 | -218.7029 | 0
2019-07-07 02:00 | 492.5488 | 0 | 0 | 9272.4431 | -492.5488 | -492.5488 | 0
2019-07-07 03:00 | 491.0215 | 0 | 0 | 8779.8942 | -491.0215 | -491.0215 | 0
2019-07-07 04:00 | 543.9601 | 0 | 0 | 8288.8728 | -543.9601 | -543.9601 | 0
2019-07-07 05:00 | 688.9666 | 417.3074 | 0 | 7744.9127 | -271.6592 | -271.6592 | 0
2019-07-07 06:00 | 893.578 | 916.9985 | 286.6667 | 7473.2536 | 310.0872 | 310.0872 | 0
2019-07-07 07:00 | 836.7924 | 1406.1763 | 0 | 7783.3408 | 569.3839 | 569.3839 | 0
2019-07-07 08:00 | 931.278 | 4763.8106 | 0 | 8352.7246 | 3832.5326 | 1647.2754 | 0
2019-07-07 09:00 | 1327.6084 | 6643.4108 | 0 | 10000 | 5315.8025 | 0 | 0
2019-07-07 10:00 | 1364.9614 | 7435.5435 | 0 | 10000 | 6070.5821 | 0 | 0
2019-07-07 11:00 | 1565.3876 | 7709.8978 | 873.3333 | 10000 | 7017.8436 | 0 | 0
2019-07-07 12:00 | 1698.8766 | 7562.9221 | 873.3333 | 10000 | 6737.3789 | 0 | 0
2019-07-07 13:00 | 1920.2678 | 7045.3784 | 873.3333 | 10000 | 5998.444 | 0 | 0
2019-07-07 14:00 | 2041.5011 | 6137.3304 | 2773.3333 | 10000 | 6869.1625 | 0 | 0
2019-07-07 15:00 | 2205.1866 | 4786.3149 | 4266.6667 | 10000 | 6847.795 | 0 | 0
2019-07-07 16:00 | 2606.6424 | 3130.6243 | 4266.6667 | 10000 | 4790.6485 | 0 | 0
2019-07-07 17:00 | 2420.7584 | 14.7763 | 2773.3333 | 10000 | 367.3513 | 0 | 0
2019-07-07 18:00 | 2329.9877 | 0 | 873.3333 | 10000 | -1456.6543 | -1456.6543 | 0
2019-07-07 19:00 | 2345.5101 | 0 | 873.3333 | 8543.3457 | -1472.1767 | -1472.1767 | 0
2019-07-07 20:00 | 2453.552 | 0 | 286.6667 | 7071.1689 | -2166.8854 | -2166.8854 | 0
2019-07-07 21:00 | 2009.8975 | 0 | 286.6667 | 4904.2835 | -1723.2308 | -1723.2308 | 0
2019-07-07 22:00 | 1497.4498 | 0 | 286.6667 | 3181.0527 | -1210.7832 | -1210.7832 | 0
2019-07-07 23:00 | 963.5204 | 0 | 0 | 1970.2696 | -963.5204 | -963.5204 | 0
2019-07-08 | 727.8464 | 0 | 0 | 1006.7492 | -727.8464 | -727.8464 | 0
2019-07-08 01:00 | 561.4758 | 0 | 0 | 278.9028 | -561.4758 | -278.9028 | -282.573
2019-07-08 02:00 | 494.0641 | 0 | 0 | 0 | -494.0641 | 0 | -776.6372
2019-07-08 03:00 | 493.9859 | 0 | 0 | 0 | -493.9859 | 0 | -1270.6231
2019-07-08 04:00 | 548.5066 | 8.4697 | 0 | 0 | -540.0368 | 0 | -1810.6599
2019-07-08 05:00 | 700.7588 | 603.9616 | 286.6667 | 0 | 189.8695 | 189.8695 | -1620.7904
2019-07-08 06:00 | 917.0629 | 1910.5398 | 2773.3333 | 189.8695 | 3766.8103 | 3766.8103 | 0
2019-07-08 07:00 | 896.1453 | 3852.2389 | 1666.6667 | 3956.6798 | 4622.7604 | 4622.7604 | 0
2019-07-08 08:00 | 1020.8087 | 5401.4546 | 873.3333 | 8579.4401 | 5253.9792 | 1420.5599 | 0
2019-07-08 09:00 | 1413.5066 | 4148.3582 | 286.6667 | 10000 | 3021.5182 | 0 | 0
2019-07-08 10:00 | 1415.5541 | 6250.1844 | 873.3333 | 10000 | 5707.9637 | 0 | 0
2019-07-08 11:00 | 1646.65 | 6696.0544 | 4266.6667 | 10000 | 9316.0711 | 0 | 0
2019-07-08 12:00 | 1874.7026 | 6759.7759 | 2773.3333 | 10000 | 7658.4067 | 0 | 0
2019-07-08 13:00 | 2104.5644 | 5897.2782 | 4266.6667 | 10000 | 8059.3804 | 0 | 0
2019-07-08 14:00 | 2304.9615 | 5939.175 | 4266.6667 | 10000 | 7900.8802 | 0 | 0
2019-07-08 15:00 | 2487.7845 | 4288.8698 | 286.6667 | 10000 | 2087.752 | 0 | 0
2019-07-08 16:00 | 2873.181 | 2761.4225 | 286.6667 | 10000 | 174.9082 | 0 | 0
2019-07-08 17:00 | 2738.9255 | 1426.6658 | 286.6667 | 10000 | -1025.593 | -1025.593 | 0
2019-07-08 18:00 | 2600.169 | 335.1825 | 286.6667 | 8974.407 | -1978.3199 | -1978.3199 | 0
2019-07-08 19:00 | 2650.7983 | 0 | 286.6667 | 6996.0871 | -2364.1316 | -2364.1316 | 0
2019-07-08 20:00 | 2685.4494 | 0 | 286.6667 | 4631.9555 | -2398.7827 | -2398.7827 | 0
2019-07-08 21:00 | 2216.6761 | 0 | 873.3333 | 2233.1728 | -1343.3428 | -1343.3428 | 0
2019-07-08 22:00 | 1716.7913 | 0 | 873.3333 | 889.83 | -843.458 | -843.458 | 0
2019-07-08 23:00 | 1225.1722 | 0 | 873.3333 | 46.372 | -351.8389 | -46.372 | -305.4669
2019-07-09 | 923.7718 | 0 | 873.3333 | 0 | -50.4385 | 0 | -355.9053
2019-07-09 01:00 | 770.5526 | 0 | 1666.6667 | 0 | 896.114 | 896.114 | 0
2019-07-09 02:00 | 681.173 | 0 | 873.3333 | 896.114 | 192.1604 | 192.1604 | 0
2019-07-09 03:00 | 629.7682 | 0 | 2773.3333 | 1088.2744 | 2143.5651 | 2143.5651 | 0
2019-07-09 04:00 | 659.7512 | 27.1803 | 1666.6667 | 3231.8395 | 1034.0957 | 1034.0957 | 0
2019-07-09 05:00 | 895.3762 | 544.6664 | 2773.3333 | 4265.9352 | 2422.6235 | 2422.6235 | 0
2019-07-09 06:00 | 1157.1511 | 1681.5978 | 2773.3333 | 6688.5588 | 3297.7801 | 3297.7801 | 0
2019-07-09 07:00 | 1128.3715 | 3981.3483 | 2773.3333 | 9986.3389 | 5626.3101 | 13.6611 | 0
2019-07-09 08:00 | 1258.7842 | 5600.3539 | 2773.3333 | 10000 | 7114.9031 | 0 | 0
2019-07-09 09:00 | 1610.0504 | 6754.7918 | 2773.3333 | 10000 | 7918.0748 | 0 | 0
2019-07-09 10:00 | 1657.9409 | 7548.0813 | 2773.3333 | 10000 | 8663.4737 | 0 | 0
2019-07-09 11:00 | 1787.64 | 6599.4602 | 1666.6667 | 10000 | 6478.4868 | 0 | 0
2019-07-09 12:00 | 1996.7889 | 6423.3491 | 1666.6667 | 10000 | 6093.2269 | 0 | 0
2019-07-09 13:00 | 2236.665 | 7219.7633 | 873.3333 | 10000 | 5856.4315 | 0 | 0
2019-07-09 14:00 | 2425.6281 | 6279.5968 | 4266.6667 | 10000 | 8120.6354 | 0 | 0
2019-07-09 15:00 | 2527.7032 | 4929.7199 | 2773.3333 | 10000 | 5175.3501 | 0 | 0
2019-07-09 16:00 | 2922.551 | 3211.2749 | 4266.6667 | 10000 | 4555.3906 | 0 | 0
2019-07-09 17:00 | 2771.9665 | 1236.8215 | 873.3333 | 10000 | -661.8116 | -661.8116 | 0
2019-07-09 18:00 | 2724.3199 | 334.113 | 1666.6667 | 9338.1884 | -723.5403 | -723.5403 | 0
2019-07-09 19:00 | 2760.1127 | 0 | 873.3333 | 8614.6481 | -1886.7794 | -1886.7794 | 0
2019-07-09 20:00 | 2850.3821 | 0 | 873.3333 | 6727.8687 | -1977.0487 | -1977.0487 | 0
2019-07-09 21:00 | 2115.4311 | 0 | 873.3333 | 4750.82 | -1242.0978 | -1242.0978 | 0
2019-07-09 22:00 | 1575.7281 | 0 | 873.3333 | 3508.7222 | -702.3947 | -702.3947 | 0
2019-07-09 23:00 | 1105.3049 | 0 | 1666.6667 | 2806.3275 | 561.3618 | 561.3618 | 0
2019-07-10 | 844.565 | 0 | 2773.3333 | 3367.6893 | 1928.7683 | 1928.7683 | 0
2019-07-10 01:00 | 700.8301 | 0 | 2773.3333 | 5296.4576 | 2072.5032 | 2072.5032 | 0
2019-07-10 02:00 | 627.71 | 0 | 873.3333 | 7368.9608 | 245.6234 | 245.6234 | 0
2019-07-10 03:00 | 534.6493 | 0 | 873.3333 | 7614.5842 | 338.6841 | 338.6841 | 0
2019-07-10 04:00 | 561.7475 | 0 | 286.6667 | 7953.2682 | -275.0809 | -275.0809 | 0
2019-07-10 05:00 | 759.6241 | 576.8308 | 286.6667 | 7678.1874 | 103.8733 | 103.8733 | 0
2019-07-10 06:00 | 1010.8728 | 1905.167 | 286.6667 | 7782.0607 | 1180.9609 | 1180.9609 | 0
2019-07-10 07:00 | 981.9819 | 3588.1116 | 873.3333 | 8963.0216 | 3479.463 | 1036.9784 | 0
2019-07-10 08:00 | 1015.434 | 5475.9561 | 2773.3333 | 10000 | 7233.8554 | 0 | 0
2019-07-10 09:00 | 1218.7949 | 5476.1723 | 4266.6667 | 10000 | 8524.0441 | 0 | 0
2019-07-10 10:00 | 1172.3599 | 6467.5275 | 1666.6667 | 10000 | 6961.8343 | 0 | 0
2019-07-10 11:00 | 1257.0146 | 7389.8563 | 2773.3333 | 10000 | 8906.175 | 0 | 0
2019-07-10 12:00 | 1433.7786 | 5228.1645 | 873.3333 | 10000 | 4667.7193 | 0 | 0
2019-07-10 13:00 | 1563.329 | 4712.3803 | 1666.6667 | 10000 | 4815.718 | 0 | 0
2019-07-10 14:00 | 1713.6407 | 4933.5322 | 9060 | 10000 | 12279.8915 | 0 | 0
2019-07-10 15:00 | 1879.0774 | 5082.8309 | 2773.3333 | 10000 | 5977.0869 | 0 | 0
2019-07-10 16:00 | 2248.0333 | 3294.9558 | 2773.3333 | 10000 | 3820.2559 | 0 | 0
2019-07-10 17:00 | 2206.413 | 1393.325 | 873.3333 | 10000 | 60.2454 | 0 | 0
2019-07-10 18:00 | 2127.2417 | 244.0139 | 7873.3333 | 10000 | 5990.1055 | 0 | 0
2019-07-10 19:00 | 2237.9135 | 0 | 6160 | 10000 | 3922.0865 | 0 | 0
2019-07-10 20:00 | 2340.0452 | 0 | 4266.6667 | 10000 | 1926.6215 | 0 | 0
2019-07-10 21:00 | 1846.7071 | 0 | 873.3333 | 10000 | -973.3738 | -973.3738 | 0
2019-07-10 22:00 | 1355.2875 | 0 | 873.3333 | 9026.6262 | -481.9541 | -481.9541 | 0
2019-07-10 23:00 | 884.5032 | 0 | 7873.3333 | 8544.6721 | 6988.8302 | 1455.3279 | 0
2019-07-11 | 671.2194 | 0 | 2773.3333 | 10000 | 2102.114 | 0 | 0
2019-07-11 01:00 | 512.7106 | 0 | 2773.3333 | 10000 | 2260.6227 | 0 | 0
2019-07-11 02:00 | 492.5488 | 0 | 873.3333 | 10000 | 380.7845 | 0 | 0
2019-07-11 03:00 | 491.0215 | 0 | 286.6667 | 10000 | -204.3548 | -204.3548 | 0
2019-07-11 04:00 | 543.9601 | 18.7278 | 286.6667 | 9795.6452 | -238.5656 | -238.5656 | 0
2019-07-11 05:00 | 688.9666 | 583.6192 | 286.6667 | 9557.0796 | 181.3193 | 181.3193 | 0
2019-07-11 06:00 | 893.578 | 1726.3466 | 286.6667 | 9738.3989 | 1119.4354 | 261.6011 | 0
2019-07-11 07:00 | 877.477 | 4057.3035 | 286.6667 | 10000 | 3466.4932 | 0 | 0
2019-07-11 08:00 | 959.2778 | 5692.4333 | 0 | 10000 | 4733.1555 | 0 | 0
2019-07-11 09:00 | 1289.8598 | 6882.3659 | 0 | 10000 | 5592.5061 | 0 | 0
2019-07-11 10:00 | 1336.0969 | 7640.401 | 0 | 10000 | 6304.3042 | 0 | 0
2019-07-11 11:00 | 1472.8078 | 7967.4265 | 286.6667 | 10000 | 6781.2854 | 0 | 0
2019-07-11 12:00 | 1619.8319 | 7846.5247 | 286.6667 | 10000 | 6513.3595 | 0 | 0
2019-07-11 13:00 | 1750.4766 | 7316.0412 | 286.6667 | 10000 | 5852.2314 | 0 | 0
2019-07-11 14:00 | 1887.5405 | 6380.1851 | 0 | 10000 | 4492.6446 | 0 | 0
2019-07-11 15:00 | 2069.4657 | 4993.2966 | 0 | 10000 | 2923.8308 | 0 | 0
2019-07-11 16:00 | 2390.0915 | 3263.0249 | 286.6667 | 10000 | 1159.6001 | 0 | 0
2019-07-11 17:00 | 2284.9057 | 1441.7619 | 286.6667 | 10000 | -556.4771 | -556.4771 | 0
2019-07-11 18:00 | 2223.493 | 266.762 | 873.3333 | 9443.5229 | -1083.3976 | -1083.3976 | 0
2019-07-11 19:00 | 2296.3134 | 0 | 873.3333 | 8360.1253 | -1422.9801 | -1422.9801 | 0
2019-07-11 20:00 | 2361.4246 | 0 | 286.6667 | 6937.1452 | -2074.7579 | -2074.7579 | 0
2019-07-11 21:00 | 1974.8253 | 0 | 286.6667 | 4862.3873 | -1688.1586 | -1688.1586 | 0
2019-07-11 22:00 | 1472.7273 | 0 | 286.6667 | 3174.2287 | -1186.0606 | -1186.0606 | 0
2019-07-11 23:00 | 984.25 | 0 | 873.3333 | 1988.1681 | -110.9167 | -110.9167 | 0
2019-07-12 | 739.4343 | 0 | 286.6667 | 1877.2514 | -452.7676 | -452.7676 | 0
2019-07-12 01:00 | 589.9114 | 0 | 873.3333 | 1424.4838 | 283.4219 | 283.4219 | 0
2019-07-12 02:00 | 516.9687 | 0 | 0 | 1707.9057 | -516.9687 | -516.9687 | 0
2019-07-12 03:00 | 491.0215 | 0 | 0 | 1190.937 | -491.0215 | -491.0215 | 0
2019-07-12 04:00 | 543.9601 | 0 | 0 | 699.9155 | -543.9601 | -543.9601 | 0
2019-07-12 05:00 | 688.9666 | 482.9689 | 0 | 155.9555 | -205.9976 | -155.9555 | -50.0421
2019-07-12 06:00 | 893.578 | 2115.9287 | 0 | 0 | 1222.3507 | 1222.3507 | 0
2019-07-12 07:00 | 829.785 | 4069.919 | 0 | 1222.3507 | 3240.134 | 3240.134 | 0
2019-07-12 08:00 | 772.2009 | 5680.6297 | 0 | 4462.4847 | 4908.4288 | 4908.4288 | 0
2019-07-12 09:00 | 933.5107 | 6864.8652 | 286.6667 | 9370.9135 | 6218.0212 | 629.0865 | 0
2019-07-12 10:00 | 1022.4619 | 7614.6411 | 286.6667 | 10000 | 6878.8458 | 0 | 0
2019-07-12 11:00 | 1093.1293 | 7935.2794 | 873.3333 | 10000 | 7715.4835 | 0 | 0
2019-07-12 12:00 | 1194.036 | 7793.9456 | 286.6667 | 10000 | 6886.5763 | 0 | 0
2019-07-12 13:00 | 1286.881 | 6365.0407 | 1666.6667 | 10000 | 6744.8264 | 0 | 0
2019-07-12 14:00 | 1433.7068 | 6333.6066 | 4266.6667 | 10000 | 9166.5665 | 0 | 0
2019-07-12 15:00 | 1508.9999 | 4932.6168 | 873.3333 | 10000 | 4296.9502 | 0 | 0
2019-07-12 16:00 | 1915.1001 | 3217.6345 | 286.6667 | 10000 | 1589.2011 | 0 | 0
2019-07-12 17:00 | 1894.8331 | 1399.2924 | 286.6667 | 10000 | -208.8741 | -208.8741 | 0
2019-07-12 18:00 | 1809.0733 | 271.883 | 286.6667 | 9791.1259 | -1250.5236 | -1250.5236 | 0
2019-07-12 19:00 | 1939.1993 | 0 | 0 | 8540.6023 | -1939.1993 | -1939.1993 | 0
2019-07-12 20:00 | 2047.3154 | 0 | 0 | 6601.4031 | -2047.3154 | -2047.3154 | 0
2019-07-12 21:00 | 1705.0732 | 0 | 873.3333 | 4554.0876 | -831.7399 | -831.7399 | 0
2019-07-12 22:00 | 1265.3098 | 0 | 286.6667 | 3722.3478 | -978.6432 | -978.6432 | 0
2019-07-12 23:00 | 822.5747 | 0 | 0 | 2743.7046 | -822.5747 | -822.5747 | 0
2019-07-13 | 627.1211 | 0 | 0 | 1921.1299 | -627.1211 | -627.1211 | 0
2019-07-13 01:00 | 505.3696 | 0 | 286.6667 | 1294.0088 | -218.7029 | -218.7029 | 0
2019-07-13 02:00 | 492.5488 | 0 | 0 | 1075.3059 | -492.5488 | -492.5488 | 0
2019-07-13 03:00 | 491.0215 | 0 | 0 | 582.7571 | -491.0215 | -491.0215 | 0
2019-07-13 04:00 | 543.9601 | 0 | 0 | 91.7356 | -543.9601 | -91.7356 | -452.2244
2019-07-13 05:00 | 688.9666 | 561.7037 | 873.3333 | 0 | 746.0705 | 746.0705 | 0
2019-07-13 06:00 | 893.578 | 2041.9653 | 873.3333 | 746.0705 | 2021.7207 | 2021.7207 | 0
2019-07-13 07:00 | 829.785 | 3769.7609 | 873.3333 | 2767.7911 | 3813.3093 | 3813.3093 | 0
2019-07-13 08:00 | 772.2009 | 5343.9051 | 286.6667 | 6581.1004 | 4858.3708 | 3418.8996 | 0
2019-07-13 09:00 | 932.9879 | 6544.7604 | 1666.6667 | 10000 | 7278.4391 | 0 | 0
2019-07-13 10:00 | 1001.2547 | 7317.289 | 4266.6667 | 10000 | 10582.701 | 0 | 0
2019-07-13 11:00 | 1063.105 | 7638.9704 | 4266.6667 | 10000 | 10842.5321 | 0 | 0
2019-07-13 12:00 | 1039.5831 | 7479.102 | 4266.6667 | 10000 | 10706.1856 | 0 | 0
2019-07-13 13:00 | 1066.596 | 6954.1259 | 4266.6667 | 10000 | 10154.1966 | 0 | 0
2019-07-13 14:00 | 1100.9993 | 6062.4722 | 4266.6667 | 10000 | 9228.1396 | 0 | 0
2019-07-13 15:00 | 1128.9851 | 4769.2168 | 1666.6667 | 10000 | 5306.8984 | 0 | 0
2019-07-13 16:00 | 1293.863 | 1200.1216 | 873.3333 | 10000 | 779.5919 | 0 | 0
2019-07-13 17:00 | 1416.0629 | 1305.8721 | 2773.3333 | 10000 | 2663.1426 | 0 | 0
2019-07-13 18:00 | 1437.5433 | 319.7149 | 873.3333 | 10000 | -244.495 | -244.495 | 0
2019-07-13 19:00 | 1571.2431 | 0 | 1666.6667 | 9755.505 | 95.4236 | 95.4236 | 0
2019-07-13 20:00 | 1724.2959 | 0 | 1666.6667 | 9850.9286 | -57.6292 | -57.6292 | 0
2019-07-13 21:00 | 1407.3335 | 0 | 286.6667 | 9793.2994 | -1120.6668 | -1120.6668 | 0
2019-07-13 22:00 | 1026.3832 | 0 | 286.6667 | 8672.6326 | -739.7165 | -739.7165 | 0
2019-07-13 23:00 | 698.1455 | 0 | 286.6667 | 7932.916 | -411.4788 | -411.4788 | 0
2019-07-14 | 567.7749 | 0 | 286.6667 | 7521.4372 | -281.1082 | -281.1082 | 0
2019-07-14 01:00 | 505.3696 | 0 | 873.3333 | 7240.329 | 367.9638 | 367.9638 | 0
2019-07-14 02:00 | 492.5488 | 0 | 286.6667 | 7608.2928 | -205.8821 | -205.8821 | 0
2019-07-14 03:00 | 491.0215 | 0 | 0 | 7402.4106 | -491.0215 | -491.0215 | 0
2019-07-14 04:00 | 543.9601 | 0 | 0 | 6911.3892 | -543.9601 | -543.9601 | 0
2019-07-14 05:00 | 688.9666 | 330.8469 | 286.6667 | 6367.4291 | -71.453 | -71.453 | 0
2019-07-14 06:00 | 893.578 | 724.761 | 286.6667 | 6295.9762 | 117.8498 | 117.8498 | 0
2019-07-14 07:00 | 829.785 | 2309.0263 | 286.6667 | 6413.8259 | 1765.908 | 1765.908 | 0
2019-07-14 08:00 | 772.2009 | 5325.2211 | 286.6667 | 8179.734 | 4839.6868 | 1820.266 | 0
2019-07-14 09:00 | 783.2561 | 6481.5288 | 286.6667 | 10000 | 5984.9393 | 0 | 0
2019-07-14 10:00 | 799.2201 | 6101.1732 | 286.6667 | 10000 | 5588.6198 | 0 | 0
2019-07-14 11:00 | 782.354 | 6078.4929 | 286.6667 | 10000 | 5582.8055 | 0 | 0
2019-07-14 12:00 | 767.9549 | 3229.982 | 873.3333 | 10000 | 3335.3604 | 0 | 0
2019-07-14 13:00 | 838.8886 | 1973.822 | 286.6667 | 10000 | 1421.6001 | 0 | 0
2019-07-14 14:00 | 897.1283 | 5104.1232 | 286.6667 | 10000 | 4493.6616 | 0 | 0
2019-07-14 15:00 | 1127.1985 | 2690.3525 | 286.6667 | 10000 | 1849.8207 | 0 | 0
2019-07-14 16:00 | 1189.1694 | 205.4601 | 286.6667 | 10000 | -697.0426 | -697.0426 | 0
2019-07-14 17:00 | 1287.9541 | 1234.2432 | 873.3333 | 9302.9574 | 819.6225 | 697.0426 | 0
2019-07-14 18:00 | 1206.631 | 332.8974 | 873.3333 | 10000 | -0.40025 | -0.40025 | 0
2019-07-14 19:00 | 1412.0819 | 0 | 286.6667 | 9999.5997 | -1125.4153 | -1125.4153 | 0
2019-07-14 20:00 | 1604.9949 | 0 | 0 | 8874.1845 | -1604.9949 | -1604.9949 | 0
2019-07-14 21:00 | 1354.3286 | 0 | 0 | 7269.1896 | -1354.3286 | -1354.3286 | 0
2019-07-14 22:00 | 1026.3832 | 0 | 0 | 5914.8609 | -1026.3832 | -1026.3832 | 0
2019-07-14 23:00 | 698.1455 | 0 | 0 | 4888.4777 | -698.1455 | -698.1455 | 0
2019-07-15 | 572.1553 | 0 | 0 | 4190.3322 | -572.1553 | -572.1553 | 0
2019-07-15 01:00 | 508.2675 | 0 | 0 | 3618.177 | -508.2675 | -508.2675 | 0
2019-07-15 02:00 | 494.0641 | 0 | 0 | 3109.9094 | -494.0641 | -494.0641 | 0
2019-07-15 03:00 | 493.9859 | 0 | 0 | 2615.8453 | -493.9859 | -493.9859 | 0
2019-07-15 04:00 | 548.5066 | 0 | 0 | 2121.8594 | -548.5066 | -548.5066 | 0
2019-07-15 05:00 | 700.7588 | 300.733 | 0 | 1573.3528 | -400.0257 | -400.0257 | 0
2019-07-15 06:00 | 917.0629 | 530.3489 | 0 | 1173.3271 | -386.7139 | -386.7139 | 0
2019-07-15 07:00 | 865.784 | 3473.4497 | 0 | 786.6131 | 2607.6657 | 2607.6657 | 0
2019-07-15 08:00 | 822.1765 | 3246.2269 | 0 | 3394.2788 | 2424.0504 | 2424.0504 | 0
2019-07-15 09:00 | 839.763 | 3462.9226 | 0 | 5818.3293 | 2623.1595 | 2623.1595 | 0
2019-07-15 10:00 | 857.4722 | 4577.3369 | 286.6667 | 8441.4888 | 4006.5315 | 1558.5112 | 0
2019-07-15 11:00 | 835.4142 | 6485.6688 | 286.6667 | 10000 | 5936.9213 | 0 | 0
2019-07-15 12:00 | 849.5421 | 4146.9276 | 286.6667 | 10000 | 3584.0522 | 0 | 0
2019-07-15 13:00 | 952.6476 | 1650.7893 | 286.6667 | 10000 | 984.8084 | 0 | 0
2019-07-15 14:00 | 1169.2774 | 2749.9524 | 873.3333 | 10000 | 2454.0084 | 0 | 0
2019-07-15 15:00 | 1380.2093 | 3491.7645 | 1666.6667 | 10000 | 3778.2219 | 0 | 0
2019-07-15 16:00 | 1739.8045 | 709.3947 | 873.3333 | 10000 | -157.0764 | -157.0764 | 0
2019-07-15 17:00 | 1777.9249 | 1426.6049 | 0 | 9842.9236 | -351.32 | -351.32 | 0
2019-07-15 18:00 | 1790.0588 | 328.8575 | 0 | 9491.6036 | -1461.2013 | -1461.2013 | 0
2019-07-15 19:00 | 1915.801 | 0 | 0 | 8030.4023 | -1915.801 | -1915.801 | 0
2019-07-15 20:00 | 2037.2312 | 0 | 286.6667 | 6114.6012 | -1750.5645 | -1750.5645 | 0
2019-07-15 21:00 | 1672.7403 | 0 | 286.6667 | 4364.0367 | -1386.0736 | -1386.0736 | 0
2019-07-15 22:00 | 1208.0309 | 0 | 286.6667 | 2977.9631 | -921.3642 | -921.3642 | 0
2019-07-15 23:00 | 741.3323 | 0 | 286.6667 | 2056.5988 | -454.6657 | -454.6657 | 0
2019-07-16 | 572.1553 | 0 | 0 | 1601.9332 | -572.1553 | -572.1553 | 0
2019-07-16 01:00 | 508.2675 | 0 | 286.6667 | 1029.7779 | -221.6009 | -221.6009 | 0
2019-07-16 02:00 | 494.0641 | 0 | 873.3333 | 808.177 | 379.2692 | 379.2692 | 0
2019-07-16 03:00 | 493.9859 | 0 | 286.6667 | 1187.4462 | -207.3192 | -207.3192 | 0
2019-07-16 04:00 | 548.5066 | 0 | 286.6667 | 980.127 | -261.8399 | -261.8399 | 0
2019-07-16 05:00 | 700.7588 | 500.9273 | 1666.6667 | 718.2871 | 1466.8352 | 1466.8352 | 0
2019-07-16 06:00 | 917.0629 | 813.2639 | 286.6667 | 2185.1223 | 182.8677 | 182.8677 | 0
2019-07-16 07:00 | 865.784 | 528.0363 | 286.6667 | 2367.99 | -51.081 | -51.081 | 0
2019-07-16 08:00 | 822.1765 | 344.8356 | 0 | 2316.909 | -477.3409 | -477.3409 | 0
2019-07-16 09:00 | 842.1462 | 1835.8623 | 873.3333 | 1839.5681 | 1867.0494 | 1867.0494 | 0
2019-07-16 10:00 | 906.0345 | 4534.3741 | 873.3333 | 3706.6175 | 4501.6729 | 4501.6729 | 0
2019-07-16 11:00 | 1032.8644 | 1478.0697 | 2773.3333 | 8208.2904 | 3218.5387 | 1791.7096 | 0
2019-07-16 12:00 | 1129.2571 | 3128.1253 | 1666.6667 | 10000 | 3665.5349 | 0 | 0
2019-07-16 13:00 | 1255.5293 | 2820.6774 | 2773.3333 | 10000 | 4338.4815 | 0 | 0
2019-07-16 14:00 | 1415.3299 | 1600.9564 | 4266.6667 | 10000 | 4452.2932 | 0 | 0
2019-07-16 15:00 | 1669.0501 | 1901.2766 | 2773.3333 | 10000 | 3005.5598 | 0 | 0
2019-07-16 16:00 | 1820.0816 | 957.6268 | 2773.3333 | 10000 | 1910.8786 | 0 | 0
2019-07-16 17:00 | 1838.156 | 1079.7614 | 873.3333 | 10000 | 114.9387 | 0 | 0
2019-07-16 18:00 | 1772.0312 | 306.6199 | 873.3333 | 10000 | -592.0779 | -592.0779 | 0
2019-07-16 19:00 | 1893.1633 | 0 | 873.3333 | 9407.9221 | -1019.8299 | -1019.8299 | 0
2019-07-16 20:00 | 2022.7782 | 0 | 286.6667 | 8388.0922 | -1736.1115 | -1736.1115 | 0
2019-07-16 21:00 | 1649.0333 | 0 | 286.6667 | 6651.9806 | -1362.3666 | -1362.3666 | 0
2019-07-16 22:00 | 1180.2711 | 0 | 286.6667 | 5289.6141 | -893.6044 | -893.6044 | 0
2019-07-16 23:00 | 727.2579 | 0 | 286.6667 | 4396.0096 | -440.5912 | -440.5912 | 0
2019-07-17 | 567.7749 | 0 | 0 | 3955.4184 | -567.7749 | -567.7749 | 0
2019-07-17 01:00 | 505.3696 | 0 | 0 | 3387.6435 | -505.3696 | -505.3696 | 0
2019-07-17 02:00 | 492.5488 | 0 | 0 | 2882.2739 | -492.5488 | -492.5488 | 0
2019-07-17 03:00 | 491.0215 | 0 | 873.3333 | 2389.7251 | 382.3119 | 382.3119 | 0
2019-07-17 04:00 | 543.9601 | 0 | 286.6667 | 2772.037 | -257.2934 | -257.2934 | 0
2019-07-17 05:00 | 688.9666 | 537.4008 | 0 | 2514.7436 | -151.5658 | -151.5658 | 0
2019-07-17 06:00 | 893.578 | 1309.1105 | 0 | 2363.1778 | 415.5326 | 415.5326 | 0
2019-07-17 07:00 | 829.785 | 2938.5467 | 0 | 2778.7104 | 2108.7617 | 2108.7617 | 0
2019-07-17 08:00 | 772.2009 | 5528.7251 | 286.6667 | 4887.4721 | 5043.1908 | 5043.1908 | 0
2019-07-17 09:00 | 794.8595 | 5815.8927 | 286.6667 | 9930.6628 | 5307.6999 | 69.3372 | 0
2019-07-17 10:00 | 828.2979 | 6994.8635 | 873.3333 | 10000 | 7039.899 | 0 | 0
2019-07-17 11:00 | 907.1778 | 6735.2487 | 2773.3333 | 10000 | 8601.4043 | 0 | 0
2019-07-17 12:00 | 960.0864 | 6516.4129 | 1666.6667 | 10000 | 7222.9932 | 0 | 0
2019-07-17 13:00 | 1006.6113 | 5995.1673 | 873.3333 | 10000 | 5861.8894 | 0 | 0
2019-07-17 14:00 | 1313.5896 | 5676.9646 | 1666.6667 | 10000 | 6030.0417 | 0 | 0
2019-07-17 15:00 | 1312.8949 | 4453.36 | 873.3333 | 10000 | 4013.7984 | 0 | 0
2019-07-17 16:00 | 1387.4382 | 2516.6634 | 873.3333 | 10000 | 2002.5586 | 0 | 0
2019-07-17 17:00 | 1579.3598 | 1308.4758 | 2773.3333 | 10000 | 2502.4493 | 0 | 0
2019-07-17 18:00 | 1588.7128 | 237.8418 | 2773.3333 | 10000 | 1422.4623 | 0 | 0
2019-07-17 19:00 | 1769.9222 | 0 | 1666.6667 | 10000 | -103.2556 | -103.2556 | 0
2019-07-17 20:00 | 1848.3895 | 0 | 286.6667 | 9896.7444 | -1561.7229 | -1561.7229 | 0
2019-07-17 21:00 | 1558.452 | 0 | 286.6667 | 8335.0216 | -1271.7853 | -1271.7853 | 0
2019-07-17 22:00 | 1133.1424 | 0 | 286.6667 | 7063.2363 | -846.4757 | -846.4757 | 0
2019-07-17 23:00 | 698.1455 | 0 | 0 | 6216.7605 | -698.1455 | -698.1455 | 0
2019-07-18 | 567.7749 | 0 | 0 | 5518.6151 | -567.7749 | -567.7749 | 0
2019-07-18 01:00 | 505.3696 | 0 | 0 | 4950.8402 | -505.3696 | -505.3696 | 0
2019-07-18 02:00 | 492.5488 | 0 | 286.6667 | 4445.4706 | -205.8821 | -205.8821 | 0
2019-07-18 03:00 | 491.0215 | 0 | 0 | 4239.5885 | -491.0215 | -491.0215 | 0
2019-07-18 04:00 | 543.9601 | 0 | 0 | 3748.567 | -543.9601 | -543.9601 | 0
2019-07-18 05:00 | 688.9666 | 455.8887 | 873.3333 | 3204.607 | 640.2555 | 640.2555 | 0
2019-07-18 06:00 | 893.578 | 2046.4411 | 286.6667 | 3844.8625 | 1439.5298 | 1439.5298 | 0
2019-07-18 07:00 | 829.785 | 4019.6226 | 873.3333 | 5284.3923 | 4063.1709 | 4063.1709 | 0
2019-07-18 08:00 | 772.2009 | 5708.8104 | 286.6667 | 9347.5632 | 5223.2762 | 652.4368 | 0
2019-07-18 09:00 | 783.2561 | 6913.5401 | 0 | 10000 | 6130.284 | 0 | 0
2019-07-18 10:00 | 816.4677 | 7597.2772 | 286.6667 | 10000 | 7067.4762 | 0 | 0
2019-07-18 11:00 | 921.5912 | 6738.9321 | 2773.3333 | 10000 | 8590.6743 | 0 | 0
2019-07-18 12:00 | 1003.2703 | 7811.6349 | 286.6667 | 10000 | 7095.0313 | 0 | 0
2019-07-18 13:00 | 1119.4454 | 7082.6706 | 873.3333 | 10000 | 6836.5585 | 0 | 0
2019-07-18 14:00 | 1173.4746 | 6122.347 | 286.6667 | 10000 | 5235.5391 | 0 | 0
2019-07-18 15:00 | 1330.597 | 4780.3304 | 286.6667 | 10000 | 3736.4 | 0 | 0
2019-07-18 16:00 | 1496.7449 | 3115.5087 | 286.6667 | 10000 | 1905.4304 | 0 | 0
2019-07-18 17:00 | 1596.4385 | 1378.1473 | 286.6667 | 10000 | 68.3755 | 0 | 0
2019-07-18 18:00 | 1587.3489 | 252.0156 | 873.3333 | 10000 | -462 | -462 | 0
2019-07-18 19:00 | 1690.742 | 0 | 0 | 9538 | -1690.742 | -1690.742 | 0
2019-07-18 20:00 | 1814.254 | 0 | 873.3333 | 7847.258 | -940.9206 | -940.9206 | 0
2019-07-18 21:00 | 1441.9747 | 0 | 286.6667 | 6906.3373 | -1155.308 | -1155.308 | 0
2019-07-18 22:00 | 1047.9283 | 0 | 286.6667 | 5751.0293 | -761.2616 | -761.2616 | 0
2019-07-18 23:00 | 698.1455 | 0 | 873.3333 | 4989.7677 | 175.1879 | 175.1879 | 0
2019-07-19 | 567.7749 | 0 | 873.3333 | 5164.9556 | 305.5585 | 305.5585 | 0
2019-07-19 01:00 | 505.3696 | 0 | 0 | 5470.514 | -505.3696 | -505.3696 | 0
2019-07-19 02:00 | 492.5488 | 0 | 0 | 4965.1445 | -492.5488 | -492.5488 | 0
2019-07-19 03:00 | 491.0215 | 0 | 0 | 4472.5957 | -491.0215 | -491.0215 | 0
2019-07-19 04:00 | 543.9601 | 0 | 0 | 3981.5742 | -543.9601 | -543.9601 | 0
2019-07-19 05:00 | 688.9666 | 475.9033 | 286.6667 | 3437.6141 | 73.6034 | 73.6034 | 0
2019-07-19 06:00 | 893.578 | 1905.0774 | 286.6667 | 3511.2176 | 1298.1661 | 1298.1661 | 0
2019-07-19 07:00 | 829.785 | 2670.3805 | 286.6667 | 4809.3836 | 2127.2622 | 2127.2622 | 0
2019-07-19 08:00 | 772.2009 | 4610.8537 | 286.6667 | 6936.6458 | 4125.3194 | 3063.3542 | 0
2019-07-19 09:00 | 783.2561 | 5304.6855 | 873.3333 | 10000 | 5394.7627 | 0 | 0
2019-07-19 10:00 | 799.2201 | 4581.447 | 873.3333 | 10000 | 4655.5603 | 0 | 0
2019-07-19 11:00 | 782.354 | 6064.3697 | 0 | 10000 | 5282.0157 | 0 | 0
2019-07-19 12:00 | 791.1589 | 4504.2383 | 2773.3333 | 10000 | 6486.4128 | 0 | 0
2019-07-19 13:00 | 854.7225 | 5648.6321 | 2773.3333 | 10000 | 7567.243 | 0 | 0
2019-07-19 14:00 | 981.0008 | 2864.8535 | 2773.3333 | 10000 | 4657.186 | 0 | 0
2019-07-19 15:00 | 1170.3502 | 2496.7006 | 873.3333 | 10000 | 2199.6837 | 0 | 0
2019-07-19 16:00 | 1367.4598 | 1526.0523 | 873.3333 | 10000 | 1031.9258 | 0 | 0
2019-07-19 17:00 | 1476.0468 | 850.3594 | 4266.6667 | 10000 | 3640.9793 | 0 | 0
2019-07-19 18:00 | 1463.1332 | 235.7672 | 873.3333 | 10000 | -354.0327 | -354.0327 | 0
2019-07-19 19:00 | 1621.6193 | 0 | 873.3333 | 9645.9673 | -748.286 | -748.286 | 0
2019-07-19 20:00 | 1777.0325 | 0 | 286.6667 | 8897.6813 | -1490.3659 | -1490.3659 | 0
2019-07-19 21:00 | 1448.0633 | 0 | 286.6667 | 7407.3155 | -1161.3966 | -1161.3966 | 0
2019-07-19 22:00 | 1026.3832 | 0 | 286.6667 | 6245.9189 | -739.7165 | -739.7165 | 0
2019-07-19 23:00 | 698.1455 | 0 | 286.6667 | 5506.2023 | -411.4788 | -411.4788 | 0
2019-07-20 | 567.7749 | 0 | 873.3333 | 5094.7235 | 305.5585 | 305.5585 | 0
2019-07-20 01:00 | 505.3696 | 0 | 0 | 5400.282 | -505.3696 | -505.3696 | 0
2019-07-20 02:00 | 492.5488 | 0 | 0 | 4894.9124 | -492.5488 | -492.5488 | 0
2019-07-20 03:00 | 491.0215 | 0 | 0 | 4402.3636 | -491.0215 | -491.0215 | 0
2019-07-20 04:00 | 543.9601 | 0 | 0 | 3911.3422 | -543.9601 | -543.9601 | 0
2019-07-20 05:00 | 688.9666 | 501.3747 | 286.6667 | 3367.3821 | 99.0748 | 99.0748 | 0
2019-07-20 06:00 | 893.578 | 1416.179 | 286.6667 | 3466.4569 | 809.2677 | 809.2677 | 0
2019-07-20 07:00 | 829.785 | 1584.8483 | 286.6667 | 4275.7246 | 1041.73 | 1041.73 | 0
2019-07-20 08:00 | 772.2009 | 1380.8809 | 286.6667 | 5317.4546 | 895.3466 | 895.3466 | 0
2019-07-20 09:00 | 783.2561 | 4285.176 | 286.6667 | 6212.8013 | 3788.5865 | 3787.1987 | 0
2019-07-20 10:00 | 799.2201 | 2995.5924 | 873.3333 | 10000 | 3069.7057 | 0 | 0
2019-07-20 11:00 | 782.354 | 5786.0352 | 873.3333 | 10000 | 5877.0145 | 0 | 0
2019-07-20 12:00 | 758.2862 | 6394.4508 | 1666.6667 | 10000 | 7302.8313 | 0 | 0
2019-07-20 13:00 | 748.3139 | 7307.215 | 873.3333 | 10000 | 7432.2345 | 0 | 0
2019-07-20 14:00 | 774.304 | 5048.1113 | 1666.6667 | 10000 | 5940.474 | 0 | 0
2019-07-20 15:00 | 888.9674 | 4359.2383 | 1666.6667 | 10000 | 5136.9376 | 0 | 0
2019-07-20 16:00 | 1076.3157 | 3213.4013 | 1666.6667 | 10000 | 3803.7523 | 0 | 0
2019-07-20 17:00 | 1202.4409 | 1359.2908 | 873.3333 | 10000 | 1030.1832 | 0 | 0
2019-07-20 18:00 | 1207.0084 | 241.6483 | 0 | 10000 | -965.3601 | -965.3601 | 0
2019-07-20 19:00 | 1412.0819 | 0 | 873.3333 | 9034.6399 | -538.7486 | -538.7486 | 0
2019-07-20 20:00 | 1604.9949 | 0 | 0 | 8495.8913 | -1604.9949 | -1604.9949 | 0
2019-07-20 21:00 | 1354.3286 | 0 | 0 | 6890.8964 | -1354.3286 | -1354.3286 | 0
2019-07-20 22:00 | 1026.3832 | 0 | 0 | 5536.5677 | -1026.3832 | -1026.3832 | 0
2019-07-20 23:00 | 698.1455 | 0 | 0 | 4510.1845 | -698.1455 | -698.1455 | 0
2019-07-21 | 567.7749 | 0 | 0 | 3812.0391 | -567.7749 | -567.7749 | 0
2019-07-21 01:00 | 505.3696 | 0 | 0 | 3244.2642 | -505.3696 | -505.3696 | 0
2019-07-21 02:00 | 492.5488 | 0 | 286.6667 | 2738.8946 | -205.8821 | -205.8821 | 0
2019-07-21 03:00 | 491.0215 | 0 | 286.6667 | 2533.0125 | -204.3548 | -204.3548 | 0
2019-07-21 04:00 | 543.9601 | 0 | 286.6667 | 2328.6577 | -257.2934 | -257.2934 | 0
2019-07-21 05:00 | 688.9666 | 477.4236 | 286.6667 | 2071.3643 | 75.1237 | 75.1237 | 0
2019-07-21 06:00 | 893.578 | 1973.2896 | 286.6667 | 2146.488 | 1366.3783 | 1366.3783 | 0
2019-07-21 07:00 | 829.785 | 3845.6701 | 286.6667 | 3512.8663 | 3302.5518 | 3302.5518 | 0
2019-07-21 08:00 | 772.2009 | 5491.1051 | 873.3333 | 6815.4182 | 5592.2375 | 3184.5818 | 0
2019-07-21 09:00 | 907.5058 | 6722.862 | 2773.3333 | 10000 | 8588.6896 | 0 | 0
2019-07-21 10:00 | 967.0364 | 7507.1816 | 1666.6667 | 10000 | 8206.8119 | 0 | 0
2019-07-21 11:00 | 1087.7394 | 7817.7931 | 1666.6667 | 10000 | 8396.7204 | 0 | 0
2019-07-21 12:00 | 1196.065 | 7733.6672 | 873.3333 | 10000 | 7410.9356 | 0 | 0
2019-07-21 13:00 | 1440.3033 | 7234.8581 | 873.3333 | 10000 | 6667.8881 | 0 | 0
2019-07-21 14:00 | 1682.5393 | 6279.2369 | 1666.6667 | 10000 | 6263.3642 | 0 | 0
2019-07-21 15:00 | 1463.9238 | 4906.0518 | 873.3333 | 10000 | 4315.4613 | 0 | 0
2019-07-21 16:00 | 1652.0758 | 3178.5045 | 1666.6667 | 10000 | 3193.0954 | 0 | 0
2019-07-21 17:00 | 1726.8165 | 1343.2851 | 2773.3333 | 10000 | 2389.802 | 0 | 0
2019-07-21 18:00 | 1748.8472 | 232.6887 | 2773.3333 | 10000 | 1257.1748 | 0 | 0
2019-07-21 19:00 | 1909.7883 | 0 | 2773.3333 | 10000 | 863.545 | 0 | 0
2019-07-21 20:00 | 2053.2332 | 0 | 2773.3333 | 10000 | 720.1001 | 0 | 0
2019-07-21 21:00 | 1698.5243 | 0 | 1666.6667 | 10000 | -31.8576 | -31.8576 | 0
2019-07-21 22:00 | 1248.1427 | 0 | 1666.6667 | 9968.1424 | 418.524 | 31.8576 | 0
2019-07-21 23:00 | 815.5742 | 0 | 2773.3333 | 10000 | 1957.7592 | 0 | 0
2019-07-22 | 586.1975 | 0 | 1666.6667 | 10000 | 1080.4692 | 0 | 0
2019-07-22 01:00 | 508.2675 | 0 | 1666.6667 | 10000 | 1158.3991 | 0 | 0
2019-07-22 02:00 | 494.0641 | 0 | 873.3333 | 10000 | 379.2692 | 0 | 0
2019-07-22 03:00 | 493.9859 | 0 | 873.3333 | 10000 | 379.3474 | 0 | 0
2019-07-22 04:00 | 548.5066 | 0 | 873.3333 | 10000 | 324.8268 | 0 | 0
2019-07-22 05:00 | 700.7588 | 469.3598 | 873.3333 | 10000 | 641.9344 | 0 | 0
2019-07-22 06:00 | 917.0629 | 1882.0934 | 286.6667 | 10000 | 1251.6972 | 0 | 0
2019-07-22 07:00 | 865.784 | 3693.5125 | 286.6667 | 10000 | 3114.3952 | 0 | 0
2019-07-22 08:00 | 822.1765 | 5223.5909 | 0 | 10000 | 4401.4145 | 0 | 0
2019-07-22 09:00 | 839.763 | 6390.2395 | 0 | 10000 | 5550.4765 | 0 | 0
2019-07-22 10:00 | 857.4722 | 7125.4023 | 0 | 10000 | 6267.9301 | 0 | 0
2019-07-22 11:00 | 835.4142 | 7454.6749 | 0 | 10000 | 6619.2607 | 0 | 0
2019-07-22 12:00 | 806.6603 | 7315.3133 | 286.6667 | 10000 | 6795.3197 | 0 | 0
2019-07-22 13:00 | 827.5004 | 6790.221 | 873.3333 | 10000 | 6836.0539 | 0 | 0
2019-07-22 14:00 | 980.9568 | 5862.0353 | 873.3333 | 10000 | 5754.4119 | 0 | 0
2019-07-22 15:00 | 1165.4237 | 1319.0086 | 286.6667 | 10000 | 440.2516 | 0 | 0
2019-07-22 16:00 | 1359.3206 | 2989.3387 | 0 | 10000 | 1630.0181 | 0 | 0
2019-07-22 17:00 | 1514.642 | 1330.3913 | 0 | 10000 | -184.2507 | -184.2507 | 0
2019-07-22 18:00 | 1532.8185 | 260.6187 | 0 | 9815.7493 | -1272.1998 | -1272.1998 | 0
2019-07-22 19:00 | 1712.4245 | 0 | 0 | 8543.5495 | -1712.4245 | -1712.4245 | 0
2019-07-22 20:00 | 1912.6031 | 0 | 0 | 6831.125 | -1912.6031 | -1912.6031 | 0
2019-07-22 21:00 | 1544.6012 | 0 | 0 | 4918.5218 | -1544.6012 | -1544.6012 | 0
2019-07-22 22:00 | 1048.8296 | 0 | 0 | 3373.9206 | -1048.8296 | -1048.8296 | 0
2019-07-22 23:00 | 705.441 | 0 | 0 | 2325.091 | -705.441 | -705.441 | 0
2019-07-23 | 572.1553 | 0 | 0 | 1619.6501 | -572.1553 | -572.1553 | 0
2019-07-23 01:00 | 508.2675 | 0 | 873.3333 | 1047.4948 | 365.0658 | 365.0658 | 0
2019-07-23 02:00 | 494.0641 | 0 | 7873.3333 | 1412.5606 | 7379.2692 | 7379.2692 | 0
2019-07-23 03:00 | 493.9859 | 0 | 9573.3333 | 8791.8298 | 9079.3474 | 1208.1702 | 0
2019-07-23 04:00 | 548.5066 | 0 | 7873.3333 | 10000 | 7324.8268 | 0 | 0
2019-07-23 05:00 | 700.7588 | 531.5081 | 4266.6667 | 10000 | 4097.416 | 0 | 0
2019-07-23 06:00 | 917.0629 | 1863.4623 | 4266.6667 | 10000 | 5213.0661 | 0 | 0
2019-07-23 07:00 | 865.784 | 3528.2115 | 4266.6667 | 10000 | 6929.0942 | 0 | 0
2019-07-23 08:00 | 822.1765 | 5056.6109 | 4266.6667 | 10000 | 8501.1011 | 0 | 0
2019-07-23 09:00 | 839.763 | 6275.5948 | 2773.3333 | 10000 | 8209.1651 | 0 | 0
2019-07-23 10:00 | 857.4722 | 7255.9641 | 2773.3333 | 10000 | 9171.8253 | 0 | 0
2019-07-23 11:00 | 835.4142 | 7530.6336 | 2773.3333 | 10000 | 9468.5527 | 0 | 0
2019-07-23 12:00 | 806.6603 | 7474.0547 | 2773.3333 | 10000 | 9440.7278 | 0 | 0
2019-07-23 13:00 | 866.3959 | 6923.8889 | 2773.3333 | 10000 | 8830.8263 | 0 | 0
2019-07-23 14:00 | 991.191 | 6020.7054 | 1666.6667 | 10000 | 6696.1811 | 0 | 0
2019-07-23 15:00 | 1182.2416 | 4677.7722 | 1666.6667 | 10000 | 5162.1973 | 0 | 0
2019-07-23 16:00 | 1350.7669 | 2911.7942 | 1666.6667 | 10000 | 3227.694 | 0 | 0
2019-07-23 17:00 | 1473.4694 | 1312.9194 | 873.3333 | 10000 | 712.7833 | 0 | 0
2019-07-23 18:00 | 1502.1745 | 266.2273 | 873.3333 | 10000 | -362.6139 | -362.6139 | 0
2019-07-23 19:00 | 1644.5868 | 0 | 286.6667 | 9637.3861 | -1357.9201 | -1357.9201 | 0
2019-07-23 20:00 | 1802.3059 | 0 | 0 | 8279.466 | -1802.3059 | -1802.3059 | 0
2019-07-23 21:00 | 1457.7073 | 0 | 0 | 6477.1601 | -1457.7073 | -1457.7073 | 0
2019-07-23 22:00 | 1043.6238 | 0 | 0 | 5019.4528 | -1043.6238 | -1043.6238 | 0
2019-07-23 23:00 | 705.441 | 0 | 0 | 3975.829 | -705.441 | -705.441 | 0
2019-07-24 | 567.7749 | 0 | 0 | 3270.388 | -567.7749 | -567.7749 | 0
2019-07-24 01:00 | 505.3696 | 0 | 0 | 2702.6132 | -505.3696 | -505.3696 | 0
2019-07-24 02:00 | 492.5488 | 0 | 0 | 2197.2436 | -492.5488 | -492.5488 | 0
2019-07-24 03:00 | 491.0215 | 0 | 873.3333 | 1704.6948 | 382.3119 | 382.3119 | 0
2019-07-24 04:00 | 543.9601 | 0 | 873.3333 | 2087.0067 | 329.3733 | 329.3733 | 0
2019-07-24 05:00 | 688.9666 | 464.186 | 873.3333 | 2416.3799 | 648.5528 | 648.5528 | 0
2019-07-24 06:00 | 893.578 | 1893.6739 | 2773.3333 | 3064.9327 | 3773.4293 | 3773.4293 | 0
2019-07-24 07:00 | 829.785 | 1595.0764 | 2773.3333 | 6838.362 | 3538.6248 | 3161.638 | 0
2019-07-24 08:00 | 772.2009 | 762.642 | 7873.3333 | 10000 | 7863.7745 | 0 | 0
2019-07-24 09:00 | 783.2561 | 1850.1315 | 9060 | 10000 | 10126.8754 | 0 | 0
2019-07-24 10:00 | 799.2201 | 2215.2461 | 9060 | 10000 | 10476.0261 | 0 | 0
2019-07-24 11:00 | 782.354 | 4224.9769 | 6160 | 10000 | 9602.6229 | 0 | 0
2019-07-24 12:00 | 758.2862 | 5517.0732 | 6160 | 10000 | 10918.7871 | 0 | 0
2019-07-24 13:00 | 748.3139 | 6049 | 6160 | 10000 | 11460.6861 | 0 | 0
2019-07-24 14:00 | 774.304 | 4511.1659 | 4266.6667 | 10000 | 8003.5287 | 0 | 0
2019-07-24 15:00 | 888.9674 | 2977.7364 | 6160 | 10000 | 8248.769 | 0 | 0
2019-07-24 16:00 | 1076.3157 | 3019.6677 | 7873.3333 | 10000 | 9816.6853 | 0 | 0
2019-07-24 17:00 | 1165.804 | 1241.6573 | 6160 | 10000 | 6235.8533 | 0 | 0
2019-07-24 18:00 | 1206.631 | 210.6834 | 6160 | 10000 | 5164.0525 | 0 | 0
2019-07-24 19:00 | 1412.0819 | 0 | 4266.6667 | 10000 | 2854.5847 | 0 | 0
2019-07-24 20:00 | 1604.9949 | 0 | 1666.6667 | 10000 | 61.6718 | 0 | 0
2019-07-24 21:00 | 1354.3286 | 0 | 2773.3333 | 10000 | 1419.0047 | 0 | 0
2019-07-24 22:00 | 1026.3832 | 0 | 2773.3333 | 10000 | 1746.9501 | 0 | 0
2019-07-24 23:00 | 698.1455 | 0 | 1666.6667 | 10000 | 968.5212 | 0 | 0
2019-07-25 | 567.7749 | 0 | 2773.3333 | 10000 | 2205.5585 | 0 | 0
2019-07-25 01:00 | 505.3696 | 0 | 1666.6667 | 10000 | 1161.2971 | 0 | 0
2019-07-25 02:00 | 492.5488 | 0 | 873.3333 | 10000 | 380.7845 | 0 | 0
2019-07-25 03:00 | 491.0215 | 0 | 873.3333 | 10000 | 382.3119 | 0 | 0
2019-07-25 04:00 | 543.9601 | 0 | 873.3333 | 10000 | 329.3733 | 0 | 0
2019-07-25 05:00 | 688.9666 | 376.0672 | 286.6667 | 10000 | -26.2327 | -26.2327 | 0
2019-07-25 06:00 | 893.578 | 1995.9193 | 873.3333 | 9973.7673 | 1975.6747 | 26.2327 | 0
2019-07-25 07:00 | 829.785 | 4017.6285 | 873.3333 | 10000 | 4061.1768 | 0 | 0
2019-07-25 08:00 | 772.2009 | 5673.9827 | 873.3333 | 10000 | 5775.1151 | 0 | 0
2019-07-25 09:00 | 783.2561 | 6840.9026 | 873.3333 | 10000 | 6930.9799 | 0 | 0
2019-07-25 10:00 | 799.2201 | 7500.7439 | 1666.6667 | 10000 | 8368.1905 | 0 | 0
2019-07-25 11:00 | 782.354 | 7768.411 | 0 | 10000 | 6986.057 | 0 | 0
2019-07-25 12:00 | 758.2862 | 7662.1406 | 873.3333 | 10000 | 7777.1878 | 0 | 0
2019-07-25 13:00 | 748.3139 | 6921.4923 | 873.3333 | 10000 | 7046.5118 | 0 | 0
2019-07-25 14:00 | 774.304 | 5982.7209 | 873.3333 | 10000 | 6081.7503 | 0 | 0
2019-07-25 15:00 | 950.4351 | 4661.4158 | 1666.6667 | 10000 | 5377.6473 | 0 | 0
2019-07-25 16:00 | 1233.7698 | 2992.9405 | 1666.6667 | 10000 | 3425.8374 | 0 | 0
2019-07-25 17:00 | 1334.8223 | 1294.7827 | 0 | 10000 | -40.0396 | -40.0396 | 0
2019-07-25 18:00 | 1373.8221 | 210.6651 | 0 | 9959.9604 | -1163.157 | -1163.157 | 0
2019-07-25 19:00 | 1529.6439 | 0 | 0 | 8796.8033 | -1529.6439 | -1529.6439 | 0
2019-07-25 20:00 | 1685.1101 | 0 | 0 | 7267.1594 | -1685.1101 | -1685.1101 | 0
2019-07-25 21:00 | 1354.3286 | 0 | 0 | 5582.0492 | -1354.3286 | -1354.3286 | 0
2019-07-25 22:00 | 1026.3832 | 0 | 0 | 4227.7206 | -1026.3832 | -1026.3832 | 0
2019-07-25 23:00 | 698.1455 | 0 | 0 | 3201.3374 | -698.1455 | -698.1455 | 0
2019-07-26 | 567.7749 | 0 | 0 | 2503.1919 | -567.7749 | -567.7749 | 0
2019-07-26 01:00 | 505.3696 | 0 | 0 | 1935.417 | -505.3696 | -505.3696 | 0
2019-07-26 02:00 | 492.5488 | 0 | 0 | 1430.0475 | -492.5488 | -492.5488 | 0
2019-07-26 03:00 | 491.0215 | 0 | 0 | 937.4987 | -491.0215 | -491.0215 | 0
2019-07-26 04:00 | 543.9601 | 0 | 0 | 446.4772 | -543.9601 | -446.4772 | -97.4829
2019-07-26 05:00 | 688.9666 | 449.5247 | 0 | 0 | -239.4419 | 0 | -336.9248
2019-07-26 06:00 | 893.578 | 1439.7517 | 0 | 0 | 546.1737 | 546.1737 | 0
2019-07-26 07:00 | 829.785 | 3154.9238 | 0 | 546.1737 | 2325.1388 | 2325.1388 | 0
2019-07-26 08:00 | 772.2009 | 4603.3465 | 0 | 2871.3125 | 3831.1456 | 3831.1456 | 0
2019-07-26 09:00 | 783.2561 | 6629.9581 | 286.6667 | 6702.4581 | 6133.3687 | 3297.5419 | 0
2019-07-26 10:00 | 799.2201 | 7456.723 | 873.3333 | 10000 | 7530.8363 | 0 | 0
2019-07-26 11:00 | 782.354 | 7796.6205 | 873.3333 | 10000 | 7887.5998 | 0 | 0
2019-07-26 12:00 | 758.2862 | 7660.7526 | 873.3333 | 10000 | 7775.7997 | 0 | 0
2019-07-26 13:00 | 833.4397 | 6107.351 | 873.3333 | 10000 | 6147.2447 | 0 | 0
2019-07-26 14:00 | 1035.9681 | 4249.2787 | 873.3333 | 10000 | 4086.644 | 0 | 0
2019-07-26 15:00 | 1211.2617 | 3909.5963 | 4266.6667 | 10000 | 6965.0013 | 0 | 0
2019-07-26 16:00 | 1463.7679 | 2787.7932 | 2773.3333 | 10000 | 4097.3586 | 0 | 0
2019-07-26 17:00 | 1526.7899 | 1312.8457 | 873.3333 | 10000 | 659.3892 | 0 | 0
2019-07-26 18:00 | 1407.337 | 255.5829 | 286.6667 | 10000 | -865.0874 | -865.0874 | 0
2019-07-26 19:00 | 1412.0819 | 0 | 286.6667 | 9134.9126 | -1125.4153 | -1125.4153 | 0
2019-07-26 20:00 | 1759.5989 | 0 | 2773.3333 | 8009.4973 | 1013.7344 | 1013.7344 | 0
2019-07-26 21:00 | 1479.6683 | 0 | 1666.6667 | 9023.2317 | 186.9984 | 186.9984 | 0
2019-07-26 22:00 | 1061.0323 | 0 | 873.3333 | 9210.2301 | -187.699 | -187.699 | 0
2019-07-26 23:00 | 698.1455 | 0 | 873.3333 | 9022.5311 | 175.1879 | 175.1879 | 0
2019-07-27 | 567.7749 | 0 | 1666.6667 | 9197.719 | 1098.8918 | 802.281 | 0
2019-07-27 01:00 | 505.3696 | 0 | 873.3333 | 10000 | 367.9638 | 0 | 0
2019-07-27 02:00 | 492.5488 | 0 | 2773.3333 | 10000 | 2280.7845 | 0 | 0
2019-07-27 03:00 | 491.0215 | 0 | 873.3333 | 10000 | 382.3119 | 0 | 0
2019-07-27 04:00 | 543.9601 | 0 | 873.3333 | 10000 | 329.3733 | 0 | 0
2019-07-27 05:00 | 688.9666 | 438.0798 | 1666.6667 | 10000 | 1415.7799 | 0 | 0
2019-07-27 06:00 | 893.578 | 1091.6432 | 1666.6667 | 10000 | 1864.732 | 0 | 0
2019-07-27 07:00 | 829.785 | 2283.4205 | 1666.6667 | 10000 | 3120.3021 | 0 | 0
2019-07-27 08:00 | 774.9205 | 5193.3494 | 1666.6667 | 10000 | 6085.0956 | 0 | 0
2019-07-27 09:00 | 968.0404 | 3911.8572 | 6160 | 10000 | 9103.8169 | 0 | 0
2019-07-27 10:00 | 1070.276 | 527.6234 | 4266.6667 | 10000 | 3724.0141 | 0 | 0
2019-07-27 11:00 | 1176.5251 | 963.4389 | 4266.6667 | 10000 | 4053.5805 | 0 | 0
2019-07-27 12:00 | 1235.4373 | 2347.334 | 4266.6667 | 10000 | 5378.5634 | 0 | 0
2019-07-27 13:00 | 1328.5321 | 3937.002 | 2773.3333 | 10000 | 5381.8032 | 0 | 0
2019-07-27 14:00 | 1442.5049 | 3361.3683 | 4266.6667 | 10000 | 6185.5301 | 0 | 0
2019-07-27 15:00 | 1595.6058 | 3211.4509 | 873.3333 | 10000 | 2489.1784 | 0 | 0
2019-07-27 16:00 | 1815.8683 | 3016.7248 | 873.3333 | 10000 | 2074.1899 | 0 | 0
2019-07-27 17:00 | 1790.2931 | 1211.7677 | 873.3333 | 10000 | 294.8079 | 0 | 0
2019-07-27 18:00 | 1741.3249 | 192.717 | 1666.6667 | 10000 | 118.0587 | 0 | 0
2019-07-27 19:00 | 1842.7668 | 0 | 873.3333 | 10000 | -969.4334 | -969.4334 | 0
2019-07-27 20:00 | 1960.0222 | 0 | 1666.6667 | 9030.5666 | -293.3555 | -293.3555 | 0
2019-07-27 21:00 | 1565.9309 | 0 | 2773.3333 | 8737.211 | 1207.4024 | 1207.4024 | 0
2019-07-27 22:00 | 1098.3371 | 0 | 2773.3333 | 9944.6135 | 1674.9962 | 55.3865 | 0
2019-07-27 23:00 | 698.1455 | 0 | 1666.6667 | 10000 | 968.5212 | 0 | 0
2019-07-28 | 567.7749 | 0 | 286.6667 | 10000 | -281.1082 | -281.1082 | 0
2019-07-28 01:00 | 505.3696 | 0 | 286.6667 | 9718.8918 | -218.7029 | -218.7029 | 0
2019-07-28 02:00 | 492.5488 | 0 | 873.3333 | 9500.1889 | 380.7845 | 380.7845 | 0
2019-07-28 03:00 | 491.0215 | 0 | 0 | 9880.9734 | -491.0215 | -491.0215 | 0
2019-07-28 04:00 | 543.9601 | 0 | 286.6667 | 9389.952 | -257.2934 | -257.2934 | 0
2019-07-28 05:00 | 688.9666 | 353.5031 | 286.6667 | 9132.6586 | -48.7968 | -48.7968 | 0
2019-07-28 06:00 | 893.578 | 718.8328 | 286.6667 | 9083.8618 | 111.9215 | 111.9215 | 0
2019-07-28 07:00 | 829.785 | 158.516 | 873.3333 | 9195.7833 | 202.0643 | 202.0643 | 0
2019-07-28 08:00 | 772.2009 | 3162.9036 | 873.3333 | 9397.8476 | 3264.0361 | 602.1524 | 0
2019-07-28 09:00 | 783.2561 | 5466.3283 | 873.3333 | 10000 | 5556.4056 | 0 | 0
2019-07-28 10:00 | 799.2201 | 4889.8391 | 286.6667 | 10000 | 4377.2857 | 0 | 0
2019-07-28 11:00 | 782.354 | 7675.9545 | 0 | 10000 | 6893.6004 | 0 | 0
2019-07-28 12:00 | 758.2862 | 5817.7971 | 286.6667 | 10000 | 5346.1776 | 0 | 0
2019-07-28 13:00 | 748.3139 | 7073.9766 | 286.6667 | 10000 | 6612.3294 | 0 | 0
2019-07-28 14:00 | 774.304 | 6106.1745 | 873.3333 | 10000 | 6205.2039 | 0 | 0
2019-07-28 15:00 | 888.9674 | 4767.6263 | 1666.6667 | 10000 | 5545.3256 | 0 | 0
2019-07-28 16:00 | 1076.3157 | 3030.856 | 873.3333 | 10000 | 2827.8737 | 0 | 0
2019-07-28 17:00 | 1165.804 | 1277.0117 | 286.6667 | 10000 | 397.8744 | 0 | 0
2019-07-28 18:00 | 1206.631 | 244.3141 | 873.3333 | 10000 | -88.9836 | -88.9836 | 0
2019-07-28 19:00 | 1412.0819 | 0 | 0 | 9911.0164 | -1412.0819 | -1412.0819 | 0
2019-07-28 20:00 | 1604.9949 | 0 | 0 | 8498.9345 | -1604.9949 | -1604.9949 | 0
2019-07-28 21:00 | 1354.3286 | 0 | 0 | 6893.9396 | -1354.3286 | -1354.3286 | 0
2019-07-28 22:00 | 1026.3832 | 0 | 286.6667 | 5539.6109 | -739.7165 | -739.7165 | 0
2019-07-28 23:00 | 698.1455 | 0 | 873.3333 | 4799.8944 | 175.1879 | 175.1879 | 0
2019-07-29 | 572.1553 | 0 | 2773.3333 | 4975.0822 | 2201.178 | 2201.178 | 0
2019-07-29 01:00 | 508.2675 | 0 | 4266.6667 | 7176.2603 | 3758.3991 | 2823.7397 | 0
2019-07-29 02:00 | 494.0641 | 0 | 6160 | 10000 | 5665.9359 | 0 | 0
2019-07-29 03:00 | 493.9859 | 0 | 2773.3333 | 10000 | 2279.3474 | 0 | 0
2019-07-29 04:00 | 548.5066 | 0 | 2773.3333 | 10000 | 2224.8268 | 0 | 0
2019-07-29 05:00 | 700.7588 | 323.7629 | 4266.6667 | 10000 | 3889.6708 | 0 | 0
2019-07-29 06:00 | 917.0629 | 1557.6382 | 2773.3333 | 10000 | 3413.9087 | 0 | 0
2019-07-29 07:00 | 865.784 | 3950.9043 | 2773.3333 | 10000 | 5858.4537 | 0 | 0
2019-07-29 08:00 | 822.1765 | 5652.112 | 4266.6667 | 10000 | 9096.6022 | 0 | 0
2019-07-29 09:00 | 839.763 | 6913.8299 | 9060 | 10000 | 15134.0669 | 0 | 0
2019-07-29 10:00 | 857.4722 | 7675.7095 | 6160 | 10000 | 12978.2373 | 0 | 0
2019-07-29 11:00 | 835.4142 | 7977.0636 | 7873.3333 | 10000 | 15014.9827 | 0 | 0
2019-07-29 12:00 | 806.6603 | 7860.4811 | 6160 | 10000 | 13213.8209 | 0 | 0
2019-07-29 13:00 | 791.7355 | 5225.677 | 6160 | 10000 | 10593.9416 | 0 | 0
2019-07-29 14:00 | 815.4321 | 2296.5891 | 873.3333 | 10000 | 2354.4904 | 0 | 0
2019-07-29 15:00 | 928.8291 | 1982.6885 | 873.3333 | 10000 | 1927.1928 | 0 | 0
2019-07-29 16:00 | 1115.5493 | 2199.8775 | 1666.6667 | 10000 | 2750.9949 | 0 | 0
2019-07-29 17:00 | 1203.8816 | 1099.3586 | 4266.6667 | 10000 | 4162.1437 | 0 | 0
2019-07-29 18:00 | 1244.6359 | 225.8048 | 873.3333 | 10000 | -145.4977 | -145.4977 | 0
2019-07-29 19:00 | 1450.7645 | 0 | 873.3333 | 9854.5023 | -577.4311 | -577.4311 | 0
2019-07-29 20:00 | 1644.5115 | 0 | 873.3333 | 9277.0711 | -771.1781 | -771.1781 | 0
2019-07-29 21:00 | 1385.7285 | 0 | 286.6667 | 8505.893 | -1099.0618 | -1099.0618 | 0
2019-07-29 22:00 | 1043.6238 | 0 | 286.6667 | 7406.8312 | -756.9571 | -756.9571 | 0
2019-07-29 23:00 | 705.441 | 0 | 873.3333 | 6649.874 | 167.8924 | 167.8924 | 0
2019-07-30 | 575.0591 | 0 | 873.3333 | 6817.7664 | 298.2742 | 298.2742 | 0
2019-07-30 01:00 | 520.6897 | 0 | 286.6667 | 7116.0406 | -234.023 | -234.023 | 0
2019-07-30 02:00 | 512.8238 | 0 | 873.3333 | 6882.0176 | 360.5095 | 360.5095 | 0
2019-07-30 03:00 | 516.7141 | 0 | 2773.3333 | 7242.5271 | 2256.6192 | 2256.6192 | 0
2019-07-30 04:00 | 572.4099 | 0 | 1666.6667 | 9499.1463 | 1094.2568 | 500.8537 | 0
2019-07-30 05:00 | 721.6053 | 349.8219 | 1666.6667 | 10000 | 1294.8833 | 0 | 0
2019-07-30 06:00 | 932.7988 | 1614.7725 | 1666.6667 | 10000 | 2348.6404 | 0 | 0
2019-07-30 07:00 | 882.5356 | 3698.408 | 873.3333 | 10000 | 3689.2058 | 0 | 0
2019-07-30 08:00 | 833.8643 | 5364.5246 | 286.6667 | 10000 | 4817.327 | 0 | 0
2019-07-30 09:00 | 839.763 | 6576.6533 | 873.3333 | 10000 | 6610.2236 | 0 | 0
2019-07-30 10:00 | 857.4722 | 3876.412 | 1666.6667 | 10000 | 4685.6065 | 0 | 0
2019-07-30 11:00 | 835.4142 | 5935.9378 | 4266.6667 | 10000 | 9367.1902 | 0 | 0
2019-07-30 12:00 | 806.6603 | 7639.4546 | 2773.3333 | 10000 | 9606.1277 | 0 | 0
2019-07-30 13:00 | 791.7355 | 6401.5635 | 1666.6667 | 10000 | 7276.4947 | 0 | 0
2019-07-30 14:00 | 815.4321 | 6072.2334 | 2773.3333 | 10000 | 8030.1347 | 0 | 0
2019-07-30 15:00 | 928.8291 | 4696.3194 | 873.3333 | 10000 | 4640.8236 | 0 | 0
2019-07-30 16:00 | 1115.5493 | 2166.0307 | 873.3333 | 10000 | 1923.8147 | 0 | 0
2019-07-30 17:00 | 1203.8816 | 1294.1433 | 873.3333 | 10000 | 963.595 | 0 | 0
2019-07-30 18:00 | 1244.6359 | 218.5356 | 286.6667 | 10000 | -739.4335 | -739.4335 | 0
2019-07-30 19:00 | 1450.7645 | 0 | 0 | 9260.5665 | -1450.7645 | -1450.7645 | 0
2019-07-30 20:00 | 1644.5115 | 0 | 286.6667 | 7809.802 | -1357.8448 | -1357.8448 | 0
2019-07-30 21:00 | 1385.7285 | 0 | 286.6667 | 6451.9572 | -1099.0618 | -1099.0618 | 0
2019-07-30 22:00 | 1043.6238 | 0 | 286.6667 | 5352.8953 | -756.9571 | -756.9571 | 0
2019-07-30 23:00 | 705.441 | 0 | 286.6667 | 4595.9382 | -418.7743 | -418.7743 | 0
2019-07-31 | 567.7749 | 0 | 0 | 4177.1639 | -567.7749 | -567.7749 | 0
2019-07-31 01:00 | 505.3696 | 0 | 0 | 3609.3891 | -505.3696 | -505.3696 | 0
2019-07-31 02:00 | 492.5488 | 0 | 286.6667 | 3104.0195 | -205.8821 | -205.8821 | 0
2019-07-31 03:00 | 491.0215 | 0 | 286.6667 | 2898.1373 | -204.3548 | -204.3548 | 0
2019-07-31 04:00 | 543.9601 | 0 | 286.6667 | 2693.7825 | -257.2934 | -257.2934 | 0
2019-07-31 05:00 | 688.9666 | 430.2518 | 0 | 2436.4892 | -258.7148 | -258.7148 | 0
2019-07-31 06:00 | 893.578 | 1825.0741 | 0 | 2177.7744 | 931.4962 | 931.4962 | 0
2019-07-31 07:00 | 829.785 | 3662.3636 | 0 | 3109.2706 | 2832.5786 | 2832.5786 | 0
2019-07-31 08:00 | 772.2009 | 5290.7452 | 0 | 5941.8492 | 4518.5443 | 4058.1508 | 0
2019-07-31 09:00 | 783.2561 | 6513.2527 | 0 | 10000 | 5729.9966 | 0 | 0
2019-07-31 10:00 | 799.2201 | 7231.1712 | 286.6667 | 10000 | 6718.6179 | 0 | 0
2019-07-31 11:00 | 782.354 | 6687.6904 | 873.3333 | 10000 | 6778.6697 | 0 | 0
2019-07-31 12:00 | 758.2862 | 6651.0054 | 2773.3333 | 10000 | 8666.0526 | 0 | 0
2019-07-31 13:00 | 887.0109 | 3905.2114 | 2773.3333 | 10000 | 5791.5339 | 0 | 0
2019-07-31 14:00 | 1070.0909 | 6084.3855 | 4266.6667 | 10000 | 9280.9613 | 0 | 0
2019-07-31 15:00 | 1331.1871 | 4652.1145 | 2773.3333 | 10000 | 6094.2608 | 0 | 0
2019-07-31 16:00 | 1639.1031 | 2960.1793 | 1666.6667 | 10000 | 2987.7429 | 0 | 0
2019-07-31 17:00 | 1686.9489 | 1270.4062 | 873.3333 | 10000 | 456.7906 | 0 | 0
2019-07-31 18:00 | 1672.7343 | 203.1797 | 2773.3333 | 10000 | 1303.7787 | 0 | 0
2019-07-31 19:00 | 1646.7256 | 0 | 1666.6667 | 10000 | 19.941 | 0 | 0
2019-07-31 20:00 | 1734.5722 | 0 | 1666.6667 | 10000 | -67.9056 | -67.9056 | 0
2019-07-31 21:00 | 1354.3286 | 0 | 0 | 9932.0944 | -1354.3286 | -1354.3286 | 0
2019-07-31 22:00 | 1026.3832 | 0 | 0 | 8577.7658 | -1026.3832 | -1026.3832 | 0
2019-07-31 23:00 | 698.1455 | 0 | 873.3333 | 7551.3826 | 175.1879 | 175.1879 | 0
2019-08-01 | 563.3025 | 0 | 286.6667 | 7726.5704 | -276.6359 | -276.6359 | 0
2019-08-01 01:00 | 505.605 | 0 | 286.6667 | 7449.9346 | -218.9383 | -218.9383 | 0
2019-08-01 02:00 | 492.7842 | 0 | 0 | 7230.9963 | -492.7842 | -492.7842 | 0
2019-08-01 03:00 | 491.2568 | 0 | 286.6667 | 6738.2121 | -204.5902 | -204.5902 | 0
2019-08-01 04:00 | 544.7447 | 0 | 0 | 6533.6219 | -544.7447 | -544.7447 | 0
2019-08-01 05:00 | 709.4449 | 313.4705 | 286.6667 | 5988.8772 | -109.3078 | -109.3078 | 0
2019-08-01 06:00 | 944.3422 | 1912.7375 | 286.6667 | 5879.5694 | 1255.0619 | 1255.0619 | 0
2019-08-01 07:00 | 874.5079 | 4003.3121 | 0 | 7134.6313 | 3128.8043 | 2865.3687 | 0
2019-08-01 08:00 | 787.7362 | 5760.5248 | 0 | 10000 | 4972.7886 | 0 | 0
2019-08-01 09:00 | 792.0438 | 7026.1688 | 286.6667 | 10000 | 6520.7917 | 0 | 0
2019-08-01 10:00 | 808.0077 | 7848.7764 | 286.6667 | 10000 | 7327.4354 | 0 | 0
2019-08-01 11:00 | 791.1417 | 8172.0219 | 873.3333 | 10000 | 8254.2136 | 0 | 0
2019-08-01 12:00 | 767.0738 | 8079.9782 | 2773.3333 | 10000 | 10086.2377 | 0 | 0
2019-08-01 13:00 | 757.1015 | 7544.3013 | 2773.3333 | 10000 | 9560.5331 | 0 | 0
2019-08-01 14:00 | 783.0916 | 6541.3449 | 2773.3333 | 10000 | 8531.5866 | 0 | 0
2019-08-01 15:00 | 898.3042 | 5081.7821 | 2773.3333 | 10000 | 6956.8112 | 0 | 0
2019-08-01 16:00 | 1097.5002 | 3201.1446 | 1666.6667 | 10000 | 3770.3111 | 0 | 0
2019-08-01 17:00 | 1208.8791 | 1207.945 | 0 | 10000 | -0.93407 | -0.93407 | 0
2019-08-01 18:00 | 1296.2336 | 133.0791 | 0 | 9999.0659 | -1163.1545 | -1163.1545 | 0
2019-08-01 19:00 | 1538.7967 | 0 | 0 | 8835.9115 | -1538.7967 | -1538.7967 | 0
2019-08-01 20:00 | 1687.2222 | 0 | 0 | 7297.1148 | -1687.2222 | -1687.2222 | 0
2019-08-01 21:00 | 1350.8763 | 0 | 0 | 5609.8926 | -1350.8763 | -1350.8763 | 0
2019-08-01 22:00 | 1025.9125 | 0 | 0 | 4259.0163 | -1025.9125 | -1025.9125 | 0
2019-08-01 23:00 | 693.9086 | 0 | 286.6667 | 3233.1038 | -407.2419 | -407.2419 | 0
2019-08-02 | 563.3025 | 0 | 286.6667 | 2825.8619 | -276.6359 | -276.6359 | 0
2019-08-02 01:00 | 505.605 | 0 | 286.6667 | 2549.226 | -218.9383 | -218.9383 | 0
2019-08-02 02:00 | 492.7842 | 0 | 0 | 2330.2877 | -492.7842 | -492.7842 | 0
2019-08-02 03:00 | 491.2568 | 0 | 0 | 1837.5035 | -491.2568 | -491.2568 | 0
2019-08-02 04:00 | 544.7447 | 0 | 0 | 1346.2467 | -544.7447 | -544.7447 | 0
2019-08-02 05:00 | 709.4449 | 307.6871 | 286.6667 | 801.502 | -115.0912 | -115.0912 | 0
2019-08-02 06:00 | 944.3422 | 1873.1775 | 0 | 686.4108 | 928.8353 | 928.8353 | 0
2019-08-02 07:00 | 874.5079 | 3921.3011 | 0 | 1615.2461 | 3046.7932 | 3046.7932 | 0
2019-08-02 08:00 | 787.7362 | 5616.1446 | 286.6667 | 4662.0393 | 5115.075 | 5115.075 | 0
2019-08-02 09:00 | 792.0438 | 6863.4576 | 873.3333 | 9777.1143 | 6944.7472 | 222.8857 | 0
2019-08-02 10:00 | 808.0077 | 7638.706 | 873.3333 | 10000 | 7704.0316 | 0 | 0
2019-08-02 11:00 | 791.1417 | 7984.6972 | 1666.6667 | 10000 | 8860.2222 | 0 | 0
2019-08-02 12:00 | 767.0738 | 7848.8995 | 1666.6667 | 10000 | 8748.4923 | 0 | 0
2019-08-02 13:00 | 757.1015 | 7319.3912 | 2773.3333 | 10000 | 9335.623 | 0 | 0
2019-08-02 14:00 | 783.0916 | 6340.2398 | 0 | 10000 | 5557.1482 | 0 | 0
2019-08-02 15:00 | 898.3042 | 4926.8933 | 2773.3333 | 10000 | 6801.9223 | 0 | 0
2019-08-02 16:00 | 1097.5002 | 3107.2149 | 4266.6667 | 10000 | 6276.3814 | 0 | 0
2019-08-02 17:00 | 1221.8616 | 1183.3097 | 4266.6667 | 10000 | 4228.1148 | 0 | 0
2019-08-02 18:00 | 1296.2336 | 143.0462 | 873.3333 | 10000 | -279.8541 | -279.8541 | 0
2019-08-02 19:00 | 1538.7967 | 0 | 1666.6667 | 9720.1459 | 127.87 | 127.87 | 0
2019-08-02 20:00 | 1687.2222 | 0 | 286.6667 | 9848.0159 | -1400.5555 | -1400.5555 | 0
2019-08-02 21:00 | 1350.8763 | 0 | 0 | 8447.4604 | -1350.8763 | -1350.8763 | 0
2019-08-02 22:00 | 1025.9125 | 0 | 0 | 7096.5841 | -1025.9125 | -1025.9125 | 0
2019-08-02 23:00 | 693.9086 | 0 | 0 | 6070.6716 | -693.9086 | -693.9086 | 0
2019-08-03 | 563.3025 | 0 | 0 | 5376.763 | -563.3025 | -563.3025 | 0
2019-08-03 01:00 | 505.605 | 0 | 0 | 4813.4605 | -505.605 | -505.605 | 0
2019-08-03 02:00 | 492.7842 | 0 | 0 | 4307.8555 | -492.7842 | -492.7842 | 0
2019-08-03 03:00 | 491.2568 | 0 | 286.6667 | 3815.0713 | -204.5902 | -204.5902 | 0
2019-08-03 04:00 | 544.7447 | 0 | 286.6667 | 3610.4811 | -258.078 | -258.078 | 0
2019-08-03 05:00 | 709.4449 | 366.551 | 286.6667 | 3352.4031 | -56.2273 | -56.2273 | 0
2019-08-03 06:00 | 944.3422 | 1717.5319 | 873.3333 | 3296.1759 | 1646.523 | 1646.523 | 0
2019-08-03 07:00 | 874.5079 | 3860.8892 | 286.6667 | 4942.6988 | 3273.048 | 3273.048 | 0
2019-08-03 08:00 | 787.7362 | 5557.766 | 873.3333 | 8215.7469 | 5643.3631 | 1784.2531 | 0
2019-08-03 09:00 | 792.0438 | 6792.2231 | 873.3333 | 10000 | 6873.5127 | 0 | 0
2019-08-03 10:00 | 808.0077 | 7563.6454 | 1666.6667 | 10000 | 8422.3044 | 0 | 0
2019-08-03 11:00 | 884.8566 | 7906.0315 | 2773.3333 | 10000 | 9794.5083 | 0 | 0
2019-08-03 12:00 | 989.9029 | 7764.8471 | 2773.3333 | 10000 | 9548.2776 | 0 | 0
2019-08-03 13:00 | 1111.2732 | 7224.5795 | 1666.6667 | 10000 | 7779.9729 | 0 | 0
2019-08-03 14:00 | 1177.9525 | 6253.2009 | 1666.6667 | 10000 | 6741.915 | 0 | 0
2019-08-03 15:00 | 1361.6309 | 4817.611 | 2773.3333 | 10000 | 6229.3135 | 0 | 0
2019-08-03 16:00 | 1522.4834 | 3013.4232 | 2773.3333 | 10000 | 4264.2732 | 0 | 0
2019-08-03 17:00 | 1636.7849 | 1051.6037 | 2773.3333 | 10000 | 2188.1521 | 0 | 0
2019-08-03 18:00 | 1667.8495 | 161.9487 | 2773.3333 | 10000 | 1267.4326 | 0 | 0
2019-08-03 19:00 | 1867.5385 | 0 | 2773.3333 | 10000 | 905.7948 | 0 | 0
2019-08-03 20:00 | 1973.2678 | 0 | 4266.6667 | 10000 | 2293.3989 | 0 | 0
2019-08-03 21:00 | 1523.2685 | 0 | 286.6667 | 10000 | -1236.6018 | -1236.6018 | 0
2019-08-03 22:00 | 1090.7884 | 0 | 286.6667 | 8763.3982 | -804.1217 | -804.1217 | 0
2019-08-03 23:00 | 693.9086 | 0 | 286.6667 | 7959.2764 | -407.2419 | -407.2419 | 0
2019-08-04 | 563.3025 | 0 | 286.6667 | 7552.0345 | -276.6359 | -276.6359 | 0
2019-08-04 01:00 | 505.605 | 0 | 286.6667 | 7275.3986 | -218.9383 | -218.9383 | 0
2019-08-04 02:00 | 492.7842 | 0 | 286.6667 | 7056.4603 | -206.1175 | -206.1175 | 0
2019-08-04 03:00 | 491.2568 | 0 | 286.6667 | 6850.3428 | -204.5902 | -204.5902 | 0
2019-08-04 04:00 | 544.7447 | 0 | 0 | 6645.7526 | -544.7447 | -544.7447 | 0
2019-08-04 05:00 | 709.4449 | 350.9857 | 873.3333 | 6101.008 | 514.8742 | 514.8742 | 0
2019-08-04 06:00 | 944.3422 | 1795.2167 | 286.6667 | 6615.8821 | 1137.5411 | 1137.5411 | 0
2019-08-04 07:00 | 874.5079 | 3547.045 | 286.6667 | 7753.4232 | 2959.2038 | 2246.5768 | 0
2019-08-04 08:00 | 787.7362 | 4051.6685 | 873.3333 | 10000 | 4137.2656 | 0 | 0
2019-08-04 09:00 | 959.2433 | 5254.4926 | 873.3333 | 10000 | 5168.5826 | 0 | 0
2019-08-04 10:00 | 1096.374 | 5510.1629 | 873.3333 | 10000 | 5287.1222 | 0 | 0
2019-08-04 11:00 | 1212.7017 | 6297.4701 | 286.6667 | 10000 | 5371.4351 | 0 | 0
2019-08-04 12:00 | 1356.0475 | 7132.4679 | 2773.3333 | 10000 | 8549.7537 | 0 | 0
2019-08-04 13:00 | 1386.5234 | 6831.3967 | 2773.3333 | 10000 | 8218.2067 | 0 | 0
2019-08-04 14:00 | 1428.0803 | 6217.7027 | 6160 | 10000 | 10949.6224 | 0 | 0
2019-08-04 15:00 | 1566.8294 | 4837.598 | 6160 | 10000 | 9430.7686 | 0 | 0
2019-08-04 16:00 | 1900.5976 | 3044.9734 | 4266.6667 | 10000 | 5411.0425 | 0 | 0
2019-08-04 17:00 | 1901.6561 | 1157.4899 | 2773.3333 | 10000 | 2029.1672 | 0 | 0
2019-08-04 18:00 | 1915.322 | 134.8478 | 2773.3333 | 10000 | 992.8592 | 0 | 0
2019-08-04 19:00 | 2086.7865 | 0 | 1666.6667 | 10000 | -420.1199 | -420.1199 | 0
2019-08-04 20:00 | 2179.0206 | 0 | 873.3333 | 9579.8801 | -1305.6873 | -1305.6873 | 0
2019-08-04 21:00 | 1724.7902 | 0 | 286.6667 | 8274.1929 | -1438.1236 | -1438.1236 | 0
2019-08-04 22:00 | 1266.2013 | 0 | 286.6667 | 6836.0693 | -979.5346 | -979.5346 | 0
2019-08-04 23:00 | 824.5422 | 0 | 1666.6667 | 5856.5347 | 842.1245 | 842.1245 | 0
2019-08-05 | 610.3133 | 0 | 286.6667 | 6698.6592 | -323.6467 | -323.6467 | 0
2019-08-05 01:00 | 508.5029 | 0 | 873.3333 | 6375.0125 | 364.8304 | 364.8304 | 0
2019-08-05 02:00 | 494.2995 | 0 | 873.3333 | 6739.8429 | 379.0338 | 379.0338 | 0
2019-08-05 03:00 | 494.2213 | 0 | 286.6667 | 7118.8767 | -207.5546 | -207.5546 | 0
2019-08-05 04:00 | 549.2912 | 0 | 286.6667 | 6911.3221 | -262.6245 | -262.6245 | 0
2019-08-05 05:00 | 721.2371 | 348.7823 | 0 | 6648.6976 | -372.4548 | -372.4548 | 0
2019-08-05 06:00 | 967.8272 | 1583.8168 | 0 | 6276.2428 | 615.9896 | 615.9896 | 0
2019-08-05 07:00 | 922.5336 | 2945.7031 | 286.6667 | 6892.2324 | 2309.8362 | 2309.8362 | 0
2019-08-05 08:00 | 910.5296 | 4723.0661 | 873.3333 | 9202.0686 | 4685.8699 | 797.9314 | 0
2019-08-05 09:00 | 1010.5718 | 5200.3483 | 0 | 10000 | 4189.7765 | 0 | 0
2019-08-05 10:00 | 1109.8018 | 6406.3085 | 0 | 10000 | 5296.5066 | 0 | 0
2019-08-05 11:00 | 1127.7366 | 6195.3789 | 873.3333 | 10000 | 5940.9756 | 0 | 0
2019-08-05 12:00 | 1144.7592 | 6243.9169 | 0 | 10000 | 5099.1577 | 0 | 0
2019-08-05 13:00 | 1304.8827 | 5707.3753 | 286.6667 | 10000 | 4689.1592 | 0 | 0
2019-08-05 14:00 | 1558.5659 | 5484.9756 | 2773.3333 | 10000 | 6699.743 | 0 | 0
2019-08-05 15:00 | 1774.9657 | 4552.0231 | 873.3333 | 10000 | 3650.3908 | 0 | 0
2019-08-05 16:00 | 2107.1217 | 2278.6572 | 2773.3333 | 10000 | 2944.8687 | 0 | 0
2019-08-05 17:00 | 2244.1268 | 1140.601 | 873.3333 | 10000 | -230.1924 | -230.1924 | 0
2019-08-05 18:00 | 2160.7572 | 146.2823 | 873.3333 | 9769.8076 | -1141.1415 | -1141.1415 | 0
2019-08-05 19:00 | 2387.5356 | 0 | 1666.6667 | 8628.666 | -720.869 | -720.869 | 0
2019-08-05 20:00 | 2419.6324 | 0 | 1666.6667 | 7907.797 | -752.9658 | -752.9658 | 0
2019-08-05 21:00 | 1936.3918 | 0 | 1666.6667 | 7154.8313 | -269.7251 | -269.7251 | 0
2019-08-05 22:00 | 1439.8971 | 0 | 2773.3333 | 6885.1061 | 1333.4363 | 1333.4363 | 0
2019-08-05 23:00 | 901.5597 | 0 | 873.3333 | 8218.5424 | -28.2264 | -28.2264 | 0
2019-08-06 | 659.2143 | 0 | 2773.3333 | 8190.316 | 2114.119 | 1809.684 | 0
2019-08-06 01:00 | 528.2879 | 0 | 1666.6667 | 10000 | 1138.3788 | 0 | 0
2019-08-06 02:00 | 494.2995 | 0 | 2773.3333 | 10000 | 2279.0338 | 0 | 0
2019-08-06 03:00 | 494.2213 | 0 | 1666.6667 | 10000 | 1172.4454 | 0 | 0
2019-08-06 04:00 | 549.2912 | 0 | 1666.6667 | 10000 | 1117.3755 | 0 | 0
2019-08-06 05:00 | 721.2371 | 324.1298 | 2773.3333 | 10000 | 2376.226 | 0 | 0
2019-08-06 06:00 | 967.8272 | 1418.2858 | 2773.3333 | 10000 | 3223.792 | 0 | 0
2019-08-06 07:00 | 910.5069 | 3366.0684 | 6160 | 10000 | 8615.5615 | 0 | 0
2019-08-06 08:00 | 837.7118 | 4581.5068 | 7873.3333 | 10000 | 11617.1284 | 0 | 0
2019-08-06 09:00 | 848.5507 | 5281.9097 | 6160 | 10000 | 10593.3591 | 0 | 0
2019-08-06 10:00 | 917.2095 | 6514.2072 | 7873.3333 | 10000 | 13470.331 | 0 | 0
2019-08-06 11:00 | 1007.4377 | 7624.0365 | 4266.6667 | 10000 | 10883.2656 | 0 | 0
2019-08-06 12:00 | 1201.7816 | 7475.7682 | 2773.3333 | 10000 | 9047.32 | 0 | 0
2019-08-06 13:00 | 1418.7072 | 4528.4873 | 4266.6667 | 10000 | 7376.4467 | 0 | 0
2019-08-06 14:00 | 1628.9737 | 4961.0712 | 4266.6667 | 10000 | 7598.7642 | 0 | 0
2019-08-06 15:00 | 1893.8836 | 915.469 | 6160 | 10000 | 5181.5854 | 0 | 0
2019-08-06 16:00 | 2179.1627 | 707.8227 | 4266.6667 | 10000 | 2795.3267 | 0 | 0
2019-08-06 17:00 | 2012.395 | 265.8179 | 1666.6667 | 10000 | -79.9105 | -79.9105 | 0
2019-08-06 18:00 | 2056.5678 | 0 | 2773.3333 | 9920.0895 | 716.7655 | 79.9105 | 0
2019-08-06 19:00 | 2160.0684 | 0 | 1666.6667 | 10000 | -493.4017 | -493.4017 | 0
2019-08-06 20:00 | 2279.9314 | 0 | 873.3333 | 9506.5983 | -1406.5981 | -1406.5981 | 0
2019-08-06 21:00 | 1765.423 | 0 | 873.3333 | 8100.0002 | -892.0897 | -892.0897 | 0
2019-08-06 22:00 | 1294.2539 | 0 | 873.3333 | 7207.9105 | -420.9206 | -420.9206 | 0
2019-08-06 23:00 | 813.8086 | 0 | 1666.6667 | 6786.99 | 852.8581 | 852.8581 | 0
2019-08-07 | 584.8188 | 0 | 873.3333 | 7639.848 | 288.5145 | 288.5145 | 0
2019-08-07 01:00 | 505.605 | 0 | 286.6667 | 7928.3626 | -218.9383 | -218.9383 | 0
2019-08-07 02:00 | 492.7842 | 0 | 286.6667 | 7709.4243 | -206.1175 | -206.1175 | 0
2019-08-07 03:00 | 491.2568 | 0 | 286.6667 | 7503.3067 | -204.5902 | -204.5902 | 0
2019-08-07 04:00 | 544.7447 | 0 | 286.6667 | 7298.7165 | -258.078 | -258.078 | 0
2019-08-07 05:00 | 709.4449 | 0 | 0 | 7040.6385 | -709.4449 | -709.4449 | 0
2019-08-07 06:00 | 944.3422 | 1316.0761 | 286.6667 | 6331.1936 | 658.4005 | 658.4005 | 0
2019-08-07 07:00 | 874.5079 | 2810.5275 | 286.6667 | 6989.5941 | 2222.6863 | 2222.6863 | 0
2019-08-07 08:00 | 862.8647 | 3659.2436 | 286.6667 | 9212.2805 | 3083.0456 | 787.7195 | 0
2019-08-07 09:00 | 1179.7144 | 4081.9319 | 1666.6667 | 10000 | 4568.8842 | 0 | 0
2019-08-07 10:00 | 1179.1451 | 3712.2954 | 2773.3333 | 10000 | 5306.4837 | 0 | 0
2019-08-07 11:00 | 1314.4848 | 4740.055 | 2773.3333 | 10000 | 6198.9035 | 0 | 0
2019-08-07 12:00 | 1364.2859 | 2894.8018 | 4266.6667 | 10000 | 5797.1826 | 0 | 0
2019-08-07 13:00 | 1463.1734 | 5846.5563 | 4266.6667 | 10000 | 8650.0496 | 0 | 0
2019-08-07 14:00 | 1504.6061 | 3170.8306 | 2773.3333 | 10000 | 4439.5578 | 0 | 0
2019-08-07 15:00 | 1607.4448 | 2556.1671 | 873.3333 | 10000 | 1822.0556 | 0 | 0
2019-08-07 16:00 | 1736.1492 | 626.9099 | 873.3333 | 10000 | -235.906 | -235.906 | 0
2019-08-07 17:00 | 1826.588 | 790.5468 | 4266.6667 | 9764.094 | 3230.6254 | 235.906 | 0
2019-08-07 18:00 | 1811.5205 | 82.923 | 2773.3333 | 10000 | 1044.7359 | 0 | 0
2019-08-07 19:00 | 2001.4906 | 0 | 1666.6667 | 10000 | -334.824 | -334.824 | 0
2019-08-07 20:00 | 2059.3484 | 0 | 286.6667 | 9665.176 | -1772.6818 | -1772.6818 | 0
2019-08-07 21:00 | 1609.1644 | 0 | 286.6667 | 7892.4943 | -1322.4977 | -1322.4977 | 0
2019-08-07 22:00 | 1088.8141 | 0 | 286.6667 | 6569.9966 | -802.1474 | -802.1474 | 0
2019-08-07 23:00 | 693.9086 | 0 | 0 | 5767.8492 | -693.9086 | -693.9086 | 0
2019-08-08 | 563.3025 | 0 | 0 | 5073.9406 | -563.3025 | -563.3025 | 0
2019-08-08 01:00 | 505.605 | 0 | 0 | 4510.6381 | -505.605 | -505.605 | 0
2019-08-08 02:00 | 492.7842 | 0 | 0 | 4005.0331 | -492.7842 | -492.7842 | 0
2019-08-08 03:00 | 491.2568 | 0 | 0 | 3512.2489 | -491.2568 | -491.2568 | 0
2019-08-08 04:00 | 544.7447 | 0 | 286.6667 | 3020.9921 | -258.078 | -258.078 | 0
2019-08-08 05:00 | 709.4449 | 312.0375 | 0 | 2762.9141 | -397.4074 | -397.4074 | 0
2019-08-08 06:00 | 944.3422 | 1699.8518 | 0 | 2365.5067 | 755.5096 | 755.5096 | 0
2019-08-08 07:00 | 874.5079 | 3581.1471 | 0 | 3121.0162 | 2706.6393 | 2706.6393 | 0
2019-08-08 08:00 | 787.7362 | 5258.5314 | 0 | 5827.6555 | 4470.7952 | 4172.3445 | 0
2019-08-08 09:00 | 792.0438 | 6492.0559 | 873.3333 | 10000 | 6573.3455 | 0 | 0
2019-08-08 10:00 | 808.0077 | 7258.9426 | 873.3333 | 10000 | 7324.2682 | 0 | 0
2019-08-08 11:00 | 791.1417 | 7620.8303 | 2773.3333 | 10000 | 9603.022 | 0 | 0
2019-08-08 12:00 | 767.0738 | 7505.3071 | 2773.3333 | 10000 | 9511.5666 | 0 | 0
2019-08-08 13:00 | 757.1015 | 7016.2098 | 2773.3333 | 10000 | 9032.4416 | 0 | 0
2019-08-08 14:00 | 835.4817 | 6042.0045 | 873.3333 | 10000 | 6079.8562 | 0 | 0
2019-08-08 15:00 | 1036.3366 | 4649.5121 | 873.3333 | 10000 | 4486.5089 | 0 | 0
2019-08-08 16:00 | 1277.0286 | 2888.785 | 286.6667 | 10000 | 1898.4231 | 0 | 0
2019-08-08 17:00 | 1449.3416 | 1089.7802 | 873.3333 | 10000 | 513.772 | 0 | 0
2019-08-08 18:00 | 1494.9752 | 110.0148 | 873.3333 | 10000 | -511.6271 | -511.6271 | 0
2019-08-08 19:00 | 1705.5244 | 0 | 286.6667 | 9488.3729 | -1418.8577 | -1418.8577 | 0
2019-08-08 20:00 | 1799.6062 | 0 | 286.6667 | 8069.5151 | -1512.9396 | -1512.9396 | 0
2019-08-08 21:00 | 1350.8763 | 0 | 286.6667 | 6556.5756 | -1064.2096 | -1064.2096 | 0
2019-08-08 22:00 | 1025.9125 | 0 | 286.6667 | 5492.3659 | -739.2459 | -739.2459 | 0
2019-08-08 23:00 | 693.9086 | 0 | 286.6667 | 4753.1201 | -407.2419 | -407.2419 | 0
2019-08-09 | 563.3025 | 0 | 286.6667 | 4345.8782 | -276.6359 | -276.6359 | 0
2019-08-09 01:00 | 505.605 | 0 | 286.6667 | 4069.2423 | -218.9383 | -218.9383 | 0
2019-08-09 02:00 | 492.7842 | 0 | 286.6667 | 3850.304 | -206.1175 | -206.1175 | 0
2019-08-09 03:00 | 491.2568 | 0 | 286.6667 | 3644.1865 | -204.5902 | -204.5902 | 0
2019-08-09 04:00 | 544.7447 | 0 | 286.6667 | 3439.5963 | -258.078 | -258.078 | 0
2019-08-09 05:00 | 709.4449 | 280.2423 | 0 | 3181.5183 | -429.2026 | -429.2026 | 0
2019-08-09 06:00 | 944.3422 | 1724.6584 | 286.6667 | 2752.3157 | 1066.9829 | 1066.9829 | 0
2019-08-09 07:00 | 874.5079 | 3703.9867 | 0 | 3819.2986 | 2829.4788 | 2829.4788 | 0
2019-08-09 08:00 | 787.7362 | 5382.3358 | 0 | 6648.7774 | 4594.5996 | 3351.2226 | 0
2019-08-09 09:00 | 792.0438 | 6633.108 | 286.6667 | 10000 | 6127.7309 | 0 | 0
2019-08-09 10:00 | 808.0077 | 7361.1719 | 286.6667 | 10000 | 6839.8308 | 0 | 0
2019-08-09 11:00 | 791.1417 | 7660.7618 | 286.6667 | 10000 | 7156.2868 | 0 | 0
2019-08-09 12:00 | 767.0738 | 7564.1434 | 0 | 10000 | 6797.0696 | 0 | 0
2019-08-09 13:00 | 757.1015 | 7040.2253 | 0 | 10000 | 6283.1237 | 0 | 0
2019-08-09 14:00 | 783.0916 | 6113.6633 | 4266.6667 | 10000 | 9597.2384 | 0 | 0
2019-08-09 15:00 | 898.3042 | 4689.2837 | 286.6667 | 10000 | 4077.6461 | 0 | 0
2019-08-09 16:00 | 1097.5002 | 2894.8375 | 873.3333 | 10000 | 2670.6706 | 0 | 0
2019-08-09 17:00 | 1242.5535 | 1047.3602 | 2773.3333 | 10000 | 2578.14 | 0 | 0
2019-08-09 18:00 | 1312.8762 | 102.3879 | 2773.3333 | 10000 | 1562.845 | 0 | 0
2019-08-09 19:00 | 1560.1118 | 0 | 1666.6667 | 10000 | 106.5549 | 0 | 0
2019-08-09 20:00 | 1687.2222 | 0 | 1666.6667 | 10000 | -20.5555 | -20.5555 | 0
2019-08-09 21:00 | 1350.8763 | 0 | 873.3333 | 9979.4445 | -477.543 | -477.543 | 0
2019-08-09 22:00 | 1025.9125 | 0 | 286.6667 | 9501.9015 | -739.2459 | -739.2459 | 0
2019-08-09 23:00 | 693.9086 | 0 | 286.6667 | 8762.6557 | -407.2419 | -407.2419 | 0
2019-08-10 | 563.3025 | 0 | 286.6667 | 8355.4138 | -276.6359 | -276.6359 | 0
2019-08-10 01:00 | 505.605 | 0 | 0 | 8078.7779 | -505.605 | -505.605 | 0
2019-08-10 02:00 | 492.7842 | 0 | 286.6667 | 7573.1729 | -206.1175 | -206.1175 | 0
2019-08-10 03:00 | 491.2568 | 0 | 286.6667 | 7367.0554 | -204.5902 | -204.5902 | 0
2019-08-10 04:00 | 544.7447 | 0 | 286.6667 | 7162.4652 | -258.078 | -258.078 | 0
2019-08-10 05:00 | 709.4449 | 316.9009 | 286.6667 | 6904.3872 | -105.8774 | -105.8774 | 0
2019-08-10 06:00 | 944.3422 | 1663.4267 | 286.6667 | 6798.5098 | 1005.7511 | 1005.7511 | 0
2019-08-10 07:00 | 874.5079 | 3535.936 | 0 | 7804.261 | 2661.4282 | 2195.739 | 0
2019-08-10 08:00 | 787.7362 | 5220.6573 | 0 | 10000 | 4432.9211 | 0 | 0
2019-08-10 09:00 | 792.0438 | 6422.4176 | 286.6667 | 10000 | 5917.0406 | 0 | 0
2019-08-10 10:00 | 808.0077 | 7202.8134 | 286.6667 | 10000 | 6681.4724 | 0 | 0
2019-08-10 11:00 | 791.1417 | 7565.9822 | 873.3333 | 10000 | 7648.1739 | 0 | 0
2019-08-10 12:00 | 767.0738 | 7491.79 | 2773.3333 | 10000 | 9498.0495 | 0 | 0
2019-08-10 13:00 | 757.1015 | 4428.9915 | 4266.6667 | 10000 | 7938.5567 | 0 | 0
2019-08-10 14:00 | 783.0916 | 3127.5342 | 2773.3333 | 10000 | 5117.776 | 0 | 0
2019-08-10 15:00 | 989.6917 | 4614.59 | 2773.3333 | 10000 | 6398.2317 | 0 | 0
2019-08-10 16:00 | 1193.3878 | 2787.2722 | 873.3333 | 10000 | 2467.2177 | 0 | 0
2019-08-10 17:00 | 1394.9823 | 1030.0849 | 2773.3333 | 10000 | 2408.4359 | 0 | 0
2019-08-10 18:00 | 1458.5709 | 100.1431 | 873.3333 | 10000 | -485.0944 | -485.0944 | 0
2019-08-10 19:00 | 1685.5158 | 0 | 873.3333 | 9514.9056 | -812.1825 | -812.1825 | 0
2019-08-10 20:00 | 1819.0936 | 0 | 286.6667 | 8702.723 | -1532.4269 | -1532.4269 | 0
2019-08-10 21:00 | 1384.0235 | 0 | 286.6667 | 7170.2962 | -1097.3569 | -1097.3569 | 0
2019-08-10 22:00 | 1025.9125 | 0 | 286.6667 | 6072.9393 | -739.2459 | -739.2459 | 0
2019-08-10 23:00 | 693.9086 | 0 | 286.6667 | 5333.6934 | -407.2419 | -407.2419 | 0
2019-08-11 | 563.3025 | 0 | 286.6667 | 4926.4515 | -276.6359 | -276.6359 | 0
2019-08-11 01:00 | 505.605 | 0 | 286.6667 | 4649.8157 | -218.9383 | -218.9383 | 0
2019-08-11 02:00 | 492.7842 | 0 | 873.3333 | 4430.8774 | 380.5491 | 380.5491 | 0
2019-08-11 03:00 | 491.2568 | 0 | 0 | 4811.4265 | -491.2568 | -491.2568 | 0
2019-08-11 04:00 | 544.7447 | 0 | 0 | 4320.1697 | -544.7447 | -544.7447 | 0
2019-08-11 05:00 | 709.4449 | 160.4365 | 0 | 3775.425 | -549.0084 | -549.0084 | 0
2019-08-11 06:00 | 944.3422 | 533.7966 | 0 | 3226.4166 | -410.5456 | -410.5456 | 0
2019-08-11 07:00 | 874.5079 | 2535.7742 | 0 | 2815.871 | 1661.2663 | 1661.2663 | 0
2019-08-11 08:00 | 787.7362 | 2118.2551 | 0 | 4477.1372 | 1330.5189 | 1330.5189 | 0
2019-08-11 09:00 | 792.0438 | 2547.2005 | 286.6667 | 5807.6561 | 2041.8235 | 2041.8235 | 0
2019-08-11 10:00 | 808.0077 | 3629.7864 | 873.3333 | 7849.4796 | 3695.112 | 2150.5204 | 0
2019-08-11 11:00 | 791.1417 | 4030.183 | 2773.3333 | 10000 | 6012.3747 | 0 | 0
2019-08-11 12:00 | 767.0738 | 5315.7335 | 4266.6667 | 10000 | 8815.3264 | 0 | 0
2019-08-11 13:00 | 757.1015 | 4433.6789 | 4266.6667 | 10000 | 7943.2441 | 0 | 0
2019-08-11 14:00 | 783.0916 | 5904.4254 | 6160 | 10000 | 11281.3339 | 0 | 0
2019-08-11 15:00 | 898.3042 | 3081.724 | 6160 | 10000 | 8343.4198 | 0 | 0
2019-08-11 16:00 | 1097.5002 | 60.8143 | 4266.6667 | 10000 | 3229.9808 | 0 | 0
2019-08-11 17:00 | 1208.8791 | 911.7913 | 873.3333 | 10000 | 576.2455 | 0 | 0
2019-08-11 18:00 | 1296.2336 | 92.2024 | 873.3333 | 10000 | -330.6979 | -330.6979 | 0
2019-08-11 19:00 | 1538.7967 | 0 | 873.3333 | 9669.3021 | -665.4633 | -665.4633 | 0
2019-08-11 20:00 | 1687.2222 | 0 | 286.6667 | 9003.8388 | -1400.5555 | -1400.5555 | 0
2019-08-11 21:00 | 1350.8763 | 0 | 0 | 7603.2833 | -1350.8763 | -1350.8763 | 0
2019-08-11 22:00 | 1025.9125 | 0 | 0 | 6252.407 | -1025.9125 | -1025.9125 | 0
2019-08-11 23:00 | 693.9086 | 0 | 286.6667 | 5226.4944 | -407.2419 | -407.2419 | 0
2019-08-12 | 542.4289 | 0 | 873.3333 | 4819.2525 | 330.9044 | 330.9044 | 0
2019-08-12 01:00 | 491.6845 | 0 | 286.6667 | 5150.157 | -205.0179 | -205.0179 | 0
2019-08-12 02:00 | 485.3683 | 0 | 286.6667 | 4945.1391 | -198.7016 | -198.7016 | 0
2019-08-12 03:00 | 477.3544 | 0 | 873.3333 | 4746.4375 | 395.979 | 395.979 | 0
2019-08-12 04:00 | 522.4945 | 0 | 286.6667 | 5142.4165 | -235.8278 | -235.8278 | 0
2019-08-12 05:00 | 652.8607 | 0 | 0 | 4906.5887 | -652.8607 | -652.8607 | 0
2019-08-12 06:00 | 833.5182 | 852.9193 | 0 | 4253.728 | 19.4011 | 19.4011 | 0
2019-08-12 07:00 | 702.5987 | 2475.7246 | 0 | 4273.1291 | 1773.1259 | 1773.1259 | 0
2019-08-12 08:00 | 551.9992 | 1516.3601 | 286.6667 | 6046.255 | 1251.0276 | 1251.0276 | 0
2019-08-12 09:00 | 528.6546 | 988.1271 | 0 | 7297.2826 | 459.4726 | 459.4726 | 0
2019-08-12 10:00 | 538.3902 | 3596.3375 | 0 | 7756.7552 | 3057.9473 | 2243.2448 | 0
2019-08-12 11:00 | 546.0322 | 2077.8706 | 873.3333 | 10000 | 2405.1717 | 0 | 0
2019-08-12 12:00 | 541.9898 | 1370.8678 | 2773.3333 | 10000 | 3602.2114 | 0 | 0
2019-08-12 13:00 | 555.7691 | 1519.9561 | 873.3333 | 10000 | 1837.5204 | 0 | 0
2019-08-12 14:00 | 592.3428 | 1729.1572 | 873.3333 | 10000 | 2010.1478 | 0 | 0
2019-08-12 15:00 | 712.9064 | 2027.4189 | 873.3333 | 10000 | 2187.8459 | 0 | 0
2019-08-12 16:00 | 912.6975 | 899.9992 | 873.3333 | 10000 | 860.6351 | 0 | 0
2019-08-12 17:00 | 1022.2799 | 418.6092 | 2773.3333 | 10000 | 2169.6626 | 0 | 0
2019-08-12 18:00 | 1105.5251 | 142.9565 | 873.3333 | 10000 | -89.2353 | -89.2353 | 0
2019-08-12 19:00 | 1348.8568 | 0 | 1666.6667 | 9910.7647 | 317.8099 | 89.2353 | 0
2019-08-12 20:00 | 1497.9841 | 0 | 873.3333 | 10000 | -624.6508 | -624.6508 | 0
2019-08-12 21:00 | 1202.0895 | 0 | 873.3333 | 9375.3492 | -328.7562 | -328.7562 | 0
2019-08-12 22:00 | 943.0393 | 0 | 873.3333 | 9046.593 | -69.7059 | -69.7059 | 0
2019-08-12 23:00 | 658.403 | 0 | 4266.6667 | 8976.8871 | 3608.2637 | 1023.1129 | 0
2019-08-13 | 542.4289 | 0 | 4266.6667 | 10000 | 3724.2378 | 0 | 0
2019-08-13 01:00 | 491.6845 | 0 | 2773.3333 | 10000 | 2281.6488 | 0 | 0
2019-08-13 02:00 | 485.3683 | 0 | 286.6667 | 10000 | -198.7016 | -198.7016 | 0
2019-08-13 03:00 | 477.3544 | 0 | 286.6667 | 9801.2984 | -190.6877 | -190.6877 | 0
2019-08-13 04:00 | 522.4945 | 0 | 286.6667 | 9610.6107 | -235.8278 | -235.8278 | 0
2019-08-13 05:00 | 652.8607 | 218.492 | 286.6667 | 9374.7829 | -147.702 | -147.702 | 0
2019-08-13 06:00 | 833.5182 | 1315.7092 | 873.3333 | 9227.0809 | 1355.5243 | 772.9191 | 0
2019-08-13 07:00 | 702.5987 | 3916.7562 | 1666.6667 | 10000 | 4880.8242 | 0 | 0
2019-08-13 08:00 | 551.9992 | 5681.0954 | 873.3333 | 10000 | 6002.4296 | 0 | 0
2019-08-13 09:00 | 528.6546 | 6972.1199 | 2773.3333 | 10000 | 9216.7987 | 0 | 0
2019-08-13 10:00 | 538.3902 | 7746.3724 | 1666.6667 | 10000 | 8874.6489 | 0 | 0
2019-08-13 11:00 | 546.0322 | 6096.1937 | 4266.6667 | 10000 | 9816.8282 | 0 | 0
2019-08-13 12:00 | 541.9898 | 8005.1948 | 4266.6667 | 10000 | 11729.8717 | 0 | 0
2019-08-13 13:00 | 555.7691 | 3984.3843 | 4266.6667 | 10000 | 7695.2819 | 0 | 0
2019-08-13 14:00 | 592.3428 | 6426.292 | 2773.3333 | 10000 | 8607.2825 | 0 | 0
2019-08-13 15:00 | 712.9064 | 4864.8036 | 2773.3333 | 10000 | 6925.2305 | 0 | 0
2019-08-13 16:00 | 912.6975 | 2944.8613 | 1666.6667 | 10000 | 3698.8306 | 0 | 0
2019-08-13 17:00 | 1022.2799 | 992.8605 | 2773.3333 | 10000 | 2743.914 | 0 | 0
2019-08-13 18:00 | 1105.5251 | 52.9977 | 873.3333 | 10000 | -179.194 | -179.194 | 0
2019-08-13 19:00 | 1348.8568 | 0 | 286.6667 | 9820.806 | -1062.1901 | -1062.1901 | 0
2019-08-13 20:00 | 1497.9841 | 0 | 0 | 8758.6159 | -1497.9841 | -1497.9841 | 0
2019-08-13 21:00 | 1202.0895 | 0 | 0 | 7260.6317 | -1202.0895 | -1202.0895 | 0
2019-08-13 22:00 | 943.0393 | 0 | 0 | 6058.5422 | -943.0393 | -943.0393 | 0
2019-08-13 23:00 | 658.403 | 0 | 0 | 5115.503 | -658.403 | -658.403 | 0
2019-08-14 | 542.4289 | 0 | 0 | 4457.1 | -542.4289 | -542.4289 | 0
2019-08-14 01:00 | 491.6845 | 0 | 0 | 3914.6711 | -491.6845 | -491.6845 | 0
2019-08-14 02:00 | 485.3683 | 0 | 0 | 3422.9865 | -485.3683 | -485.3683 | 0
2019-08-14 03:00 | 477.3544 | 0 | 0 | 2937.6183 | -477.3544 | -477.3544 | 0
2019-08-14 04:00 | 522.4945 | 0 | 0 | 2460.2639 | -522.4945 | -522.4945 | 0
2019-08-14 05:00 | 652.8607 | 244.5199 | 0 | 1937.7694 | -408.3408 | -408.3408 | 0
2019-08-14 06:00 | 833.5182 | 1722.493 | 0 | 1529.4287 | 888.9748 | 888.9748 | 0
2019-08-14 07:00 | 702.5987 | 2851.4376 | 0 | 2418.4034 | 2148.8389 | 2148.8389 | 0
2019-08-14 08:00 | 551.9992 | 4850.4401 | 0 | 4567.2424 | 4298.4409 | 4298.4409 | 0
2019-08-14 09:00 | 528.6546 | 5739.727 | 0 | 8865.6833 | 5211.0725 | 1134.3167 | 0
2019-08-14 10:00 | 538.3902 | 7546.7841 | 0 | 10000 | 7008.394 | 0 | 0
2019-08-14 11:00 | 617.848 | 6493.6981 | 873.3333 | 10000 | 6749.1834 | 0 | 0
2019-08-14 12:00 | 801.3143 | 7229.3036 | 2773.3333 | 10000 | 9201.3227 | 0 | 0
2019-08-14 13:00 | 954.9321 | 7121.9052 | 1666.6667 | 10000 | 7833.6397 | 0 | 0
2019-08-14 14:00 | 1147.9796 | 3728.921 | 1666.6667 | 10000 | 4247.6081 | 0 | 0
2019-08-14 15:00 | 1289.2524 | 3565.3542 | 873.3333 | 10000 | 3149.4351 | 0 | 0
2019-08-14 16:00 | 1531.0438 | 2794.7748 | 873.3333 | 10000 | 2137.0644 | 0 | 0
2019-08-14 17:00 | 1582.6457 | 890.9073 | 286.6667 | 10000 | -405.0717 | -405.0717 | 0
2019-08-14 18:00 | 1566.4183 | 65.0061 | 286.6667 | 9594.9283 | -1214.7455 | -1214.7455 | 0
2019-08-14 19:00 | 1747.0511 | 0 | 286.6667 | 8380.1828 | -1460.3844 | -1460.3844 | 0
2019-08-14 20:00 | 1848.8756 | 0 | 0 | 6919.7983 | -1848.8756 | -1848.8756 | 0
2019-08-14 21:00 | 1444.253 | 0 | 0 | 5070.9228 | -1444.253 | -1444.253 | 0
2019-08-14 22:00 | 1067.3107 | 0 | 0 | 3626.6698 | -1067.3107 | -1067.3107 | 0
2019-08-14 23:00 | 672.6288 | 0 | 0 | 2559.359 | -672.6288 | -672.6288 | 0
2019-08-15 | 542.4289 | 0 | 0 | 1886.7302 | -542.4289 | -542.4289 | 0
2019-08-15 01:00 | 491.6845 | 0 | 0 | 1344.3013 | -491.6845 | -491.6845 | 0
2019-08-15 02:00 | 485.3683 | 0 | 0 | 852.6168 | -485.3683 | -485.3683 | 0
2019-08-15 03:00 | 477.3544 | 0 | 0 | 367.2485 | -477.3544 | -367.2485 | -110.1058
2019-08-15 04:00 | 522.4945 | 0 | 0 | 0 | -522.4945 | 0 | -632.6003
2019-08-15 05:00 | 652.8607 | 0 | 0 | 0 | -652.8607 | 0 | -1285.461
2019-08-15 06:00 | 833.5182 | 1033.5602 | 0 | 0 | 200.042 | 200.042 | -1085.419
2019-08-15 07:00 | 702.5987 | 430.4024 | 0 | 200.042 | -272.1963 | -200.042 | -1157.5733
2019-08-15 08:00 | 551.9992 | 1289.0085 | 873.3333 | 0 | 1610.3427 | 1610.3427 | 0
2019-08-15 09:00 | 528.6546 | 3105.2725 | 0 | 1610.3427 | 2576.618 | 2576.618 | 0
2019-08-15 10:00 | 554.3557 | 7305.8097 | 286.6667 | 4186.9607 | 7038.1207 | 5813.0393 | 0
2019-08-15 11:00 | 679.247 | 7527.9563 | 1666.6667 | 10000 | 8515.376 | 0 | 0
2019-08-15 12:00 | 784.5172 | 7463.0423 | 873.3333 | 10000 | 7551.8584 | 0 | 0
2019-08-15 13:00 | 978.5335 | 6890.6769 | 2773.3333 | 10000 | 8685.4768 | 0 | 0
2019-08-15 14:00 | 1026.5169 | 5947.6562 | 286.6667 | 10000 | 5207.806 | 0 | 0
2019-08-15 15:00 | 1114.2172 | 4509.9458 | 2773.3333 | 10000 | 6169.062 | 0 | 0
2019-08-15 16:00 | 1324.3963 | 2717.8525 | 2773.3333 | 10000 | 4166.7896 | 0 | 0
2019-08-15 17:00 | 1435.3459 | 937.9458 | 4266.6667 | 10000 | 3769.2666 | 0 | 0
2019-08-15 18:00 | 1435.7896 | 44.513 | 4266.6667 | 10000 | 2875.3902 | 0 | 0
2019-08-15 19:00 | 1649.5692 | 0 | 2773.3333 | 10000 | 1123.7642 | 0 | 0
2019-08-15 20:00 | 1749.2738 | 0 | 1666.6667 | 10000 | -82.6071 | -82.6071 | 0
2019-08-15 21:00 | 1370.5603 | 0 | 873.3333 | 9917.3929 | -497.227 | -497.227 | 0
2019-08-15 22:00 | 1028.2144 | 0 | 286.6667 | 9420.1659 | -741.5477 | -741.5477 | 0
2019-08-15 23:00 | 658.403 | 0 | 286.6667 | 8678.6181 | -371.7363 | -371.7363 | 0
2019-08-16 | 542.4289 | 0 | 873.3333 | 8306.8818 | 330.9044 | 330.9044 | 0
2019-08-16 01:00 | 491.6845 | 0 | 286.6667 | 8637.7863 | -205.0179 | -205.0179 | 0
2019-08-16 02:00 | 485.3683 | 0 | 286.6667 | 8432.7684 | -198.7016 | -198.7016 | 0
2019-08-16 03:00 | 477.3544 | 0 | 286.6667 | 8234.0668 | -190.6877 | -190.6877 | 0
2019-08-16 04:00 | 522.4945 | 0 | 286.6667 | 8043.3791 | -235.8278 | -235.8278 | 0
2019-08-16 05:00 | 652.8607 | 0 | 286.6667 | 7807.5513 | -366.194 | -366.194 | 0
2019-08-16 06:00 | 833.5182 | 735.1099 | 286.6667 | 7441.3573 | 188.2583 | 188.2583 | 0
2019-08-16 07:00 | 702.5987 | 963.7356 | 873.3333 | 7629.6156 | 1134.4703 | 1134.4703 | 0
2019-08-16 08:00 | 551.9992 | 4276.2186 | 1666.6667 | 8764.0859 | 5390.8861 | 1235.9141 | 0
2019-08-16 09:00 | 582.2856 | 5413.61 | 2773.3333 | 10000 | 7604.6578 | 0 | 0
2019-08-16 10:00 | 714.419 | 7006.2289 | 2773.3333 | 10000 | 9065.1433 | 0 | 0
2019-08-16 11:00 | 876.7197 | 7304.6551 | 873.3333 | 10000 | 7301.2687 | 0 | 0
2019-08-16 12:00 | 1075.7253 | 7212.5884 | 4266.6667 | 10000 | 10403.5298 | 0 | 0
2019-08-16 13:00 | 1292.7084 | 6645.1565 | 2773.3333 | 10000 | 8125.7815 | 0 | 0
2019-08-16 14:00 | 1441.1681 | 5192.5099 | 1666.6667 | 10000 | 5418.0084 | 0 | 0
2019-08-16 15:00 | 1595.3429 | 3859.055 | 4266.6667 | 10000 | 6530.3788 | 0 | 0
2019-08-16 16:00 | 1736.9377 | 2317.5007 | 4266.6667 | 10000 | 4847.2297 | 0 | 0
2019-08-16 17:00 | 1675.0803 | 864.0605 | 4266.6667 | 10000 | 3455.6469 | 0 | 0
2019-08-16 18:00 | 1587.7109 | 0 | 873.3333 | 10000 | -714.3776 | -714.3776 | 0
2019-08-16 19:00 | 1788.5391 | 0 | 286.6667 | 9285.6224 | -1501.8724 | -1501.8724 | 0
2019-08-16 20:00 | 1877.0651 | 0 | 0 | 7783.75 | -1877.0651 | -1877.0651 | 0
2019-08-16 21:00 | 1455.8218 | 0 | 873.3333 | 5906.685 | -582.4885 | -582.4885 | 0
2019-08-16 22:00 | 1067.3453 | 0 | 873.3333 | 5324.1965 | -194.0119 | -194.0119 | 0
2019-08-16 23:00 | 678.7529 | 0 | 873.3333 | 5130.1846 | 194.5805 | 194.5805 | 0
2019-08-17 | 542.4289 | 0 | 873.3333 | 5324.7651 | 330.9044 | 330.9044 | 0
2019-08-17 01:00 | 491.6845 | 0 | 873.3333 | 5655.6695 | 381.6488 | 381.6488 | 0
2019-08-17 02:00 | 485.3683 | 0 | 286.6667 | 6037.3183 | -198.7016 | -198.7016 | 0
2019-08-17 03:00 | 477.3544 | 0 | 286.6667 | 5838.6167 | -190.6877 | -190.6877 | 0
2019-08-17 04:00 | 522.4945 | 0 | 0 | 5647.929 | -522.4945 | -522.4945 | 0
2019-08-17 05:00 | 652.8607 | 229.042 | 0 | 5125.4345 | -423.8186 | -423.8186 | 0
2019-08-17 06:00 | 833.5182 | 835.2266 | 286.6667 | 4701.6159 | 288.375 | 288.375 | 0
2019-08-17 07:00 | 702.5987 | 1331.6183 | 286.6667 | 4989.991 | 915.6863 | 915.6863 | 0
2019-08-17 08:00 | 551.9992 | 2018.3236 | 0 | 5905.6773 | 1466.3244 | 1466.3244 | 0
2019-08-17 09:00 | 528.6546 | 1748.9108 | 0 | 7372.0017 | 1220.2562 | 1220.2562 | 0
2019-08-17 10:00 | 538.3902 | 1623.325 | 0 | 8592.2579 | 1084.9349 | 1084.9349 | 0
2019-08-17 11:00 | 546.9775 | 1483.6679 | 286.6667 | 9677.1928 | 1223.3571 | 322.8072 | 0
2019-08-17 12:00 | 617.6812 | 2067.8506 | 286.6667 | 10000 | 1736.8361 | 0 | 0
2019-08-17 13:00 | 734.2836 | 1339.7477 | 873.3333 | 10000 | 1478.7975 | 0 | 0
2019-08-17 14:00 | 843.1165 | 1610.6843 | 873.3333 | 10000 | 1640.9011 | 0 | 0
2019-08-17 15:00 | 1006.1235 | 1329.8692 | 873.3333 | 10000 | 1197.079 | 0 | 0
2019-08-17 16:00 | 1162.7626 | 1073.8999 | 873.3333 | 10000 | 784.4706 | 0 | 0
2019-08-17 17:00 | 1305.7673 | 590.8872 | 286.6667 | 10000 | -428.2134 | -428.2134 | 0
2019-08-17 18:00 | 1301.4915 | 0 | 873.3333 | 9571.7866 | -428.1582 | -428.1582 | 0
2019-08-17 19:00 | 1526.9762 | 0 | 873.3333 | 9143.6284 | -653.6429 | -653.6429 | 0
2019-08-17 20:00 | 1623.2619 | 0 | 873.3333 | 8489.9855 | -749.9285 | -749.9285 | 0
2019-08-17 21:00 | 1222.5414 | 0 | 286.6667 | 7740.057 | -935.8747 | -935.8747 | 0
2019-08-17 22:00 | 943.0393 | 0 | 286.6667 | 6804.1823 | -656.3726 | -656.3726 | 0
2019-08-17 23:00 | 658.403 | 0 | 0 | 6147.8097 | -658.403 | -658.403 | 0
2019-08-18 | 542.4289 | 0 | 286.6667 | 5489.4067 | -255.7622 | -255.7622 | 0
2019-08-18 01:00 | 491.6845 | 0 | 286.6667 | 5233.6445 | -205.0179 | -205.0179 | 0
2019-08-18 02:00 | 485.3683 | 0 | 286.6667 | 5028.6266 | -198.7016 | -198.7016 | 0
2019-08-18 03:00 | 477.3544 | 0 | 0 | 4829.925 | -477.3544 | -477.3544 | 0
2019-08-18 04:00 | 522.4945 | 0 | 0 | 4352.5707 | -522.4945 | -522.4945 | 0
2019-08-18 05:00 | 652.8607 | 227.6184 | 0 | 3830.0762 | -425.2423 | -425.2423 | 0
2019-08-18 06:00 | 833.5182 | 1574.7904 | 286.6667 | 3404.8339 | 1027.9389 | 1027.9389 | 0
2019-08-18 07:00 | 702.5987 | 3522.887 | 286.6667 | 4432.7728 | 3106.955 | 3106.955 | 0
2019-08-18 08:00 | 551.9992 | 5219.6211 | 286.6667 | 7539.7277 | 4954.2886 | 2460.2723 | 0
2019-08-18 09:00 | 528.6546 | 6439.9183 | 1666.6667 | 10000 | 7577.9305 | 0 | 0
2019-08-18 10:00 | 538.3902 | 7135.5004 | 2773.3333 | 10000 | 9370.4436 | 0 | 0
2019-08-18 11:00 | 546.0322 | 7425.7305 | 4266.6667 | 10000 | 11146.365 | 0 | 0
2019-08-18 12:00 | 541.9898 | 7288.8552 | 7873.3333 | 10000 | 14620.1988 | 0 | 0
2019-08-18 13:00 | 555.7691 | 3174.3645 | 9060 | 10000 | 11678.5955 | 0 | 0
2019-08-18 14:00 | 592.3428 | 3092.2488 | 6160 | 10000 | 8659.906 | 0 | 0
2019-08-18 15:00 | 712.9064 | 1395.9562 | 4266.6667 | 10000 | 4949.7165 | 0 | 0
2019-08-18 16:00 | 912.6975 | 1117.5332 | 4266.6667 | 10000 | 4471.5024 | 0 | 0
2019-08-18 17:00 | 1022.2799 | 612.1519 | 2773.3333 | 10000 | 2363.2053 | 0 | 0
2019-08-18 18:00 | 1105.5251 | 0 | 2773.3333 | 10000 | 1667.8082 | 0 | 0
2019-08-18 19:00 | 1348.8568 | 0 | 1666.6667 | 10000 | 317.8099 | 0 | 0
2019-08-18 20:00 | 1497.9841 | 0 | 873.3333 | 10000 | -624.6508 | -624.6508 | 0
2019-08-18 21:00 | 1202.0895 | 0 | 286.6667 | 9375.3492 | -915.4229 | -915.4229 | 0
2019-08-18 22:00 | 943.0393 | 0 | 286.6667 | 8459.9264 | -656.3726 | -656.3726 | 0
2019-08-18 23:00 | 658.403 | 0 | 286.6667 | 7803.5538 | -371.7363 | -371.7363 | 0
2019-08-19 | 567.6829 | 0 | 0 | 7431.8174 | -567.6829 | -567.6829 | 0
2019-08-19 01:00 | 508.5029 | 0 | 0 | 6864.1345 | -508.5029 | -508.5029 | 0
2019-08-19 02:00 | 494.2995 | 0 | 0 | 6355.6316 | -494.2995 | -494.2995 | 0
2019-08-19 03:00 | 494.2213 | 0 | 873.3333 | 5861.332 | 379.112 | 379.112 | 0
2019-08-19 04:00 | 549.2912 | 0 | 286.6667 | 6240.4441 | -262.6245 | -262.6245 | 0
2019-08-19 05:00 | 721.2371 | 180.7834 | 286.6667 | 5977.8196 | -253.787 | -253.787 | 0
2019-08-19 06:00 | 967.8272 | 1719.1557 | 0 | 5724.0325 | 751.3285 | 751.3285 | 0
2019-08-19 07:00 | 910.5069 | 2718.1411 | 0 | 6475.3611 | 1807.6343 | 1807.6343 | 0
2019-08-19 08:00 | 837.7118 | 5779.7643 | 0 | 8282.9954 | 4942.0525 | 1717.0046 | 0
2019-08-19 09:00 | 848.5507 | 7090.0283 | 286.6667 | 10000 | 6528.1443 | 0 | 0
2019-08-19 10:00 | 866.2598 | 7891.1183 | 286.6667 | 10000 | 7311.5252 | 0 | 0
2019-08-19 11:00 | 844.2019 | 8252.7737 | 873.3333 | 10000 | 8281.9052 | 0 | 0
2019-08-19 12:00 | 815.4479 | 8081.165 | 2773.3333 | 10000 | 10039.0504 | 0 | 0
2019-08-19 13:00 | 800.5231 | 7487.8041 | 1666.6667 | 10000 | 8353.9476 | 0 | 0
2019-08-19 14:00 | 824.2197 | 6410.9959 | 286.6667 | 10000 | 5873.4428 | 0 | 0
2019-08-19 15:00 | 938.166 | 4890.6752 | 873.3333 | 10000 | 4825.8425 | 0 | 0
2019-08-19 16:00 | 1136.7338 | 2895.0422 | 286.6667 | 10000 | 2044.975 | 0 | 0
2019-08-19 17:00 | 1256.8129 | 863.7822 | 0 | 10000 | -393.0306 | -393.0306 | 0
2019-08-19 18:00 | 1334.2385 | 0 | 0 | 9606.9694 | -1334.2385 | -1334.2385 | 0
2019-08-19 19:00 | 1577.4792 | 0 | 0 | 8272.7309 | -1577.4792 | -1577.4792 | 0
2019-08-19 20:00 | 1726.7387 | 0 | 0 | 6695.2517 | -1726.7387 | -1726.7387 | 0
2019-08-19 21:00 | 1382.2762 | 0 | 0 | 4968.5129 | -1382.2762 | -1382.2762 | 0
2019-08-19 22:00 | 1043.1531 | 0 | 0 | 3586.2368 | -1043.1531 | -1043.1531 | 0
2019-08-19 23:00 | 701.2041 | 0 | 286.6667 | 2543.0837 | -414.5374 | -414.5374 | 0
2019-08-20 | 567.6829 | 0 | 286.6667 | 2128.5463 | -281.0163 | -281.0163 | 0
2019-08-20 01:00 | 508.5029 | 0 | 286.6667 | 1847.53 | -221.8363 | -221.8363 | 0
2019-08-20 02:00 | 494.2995 | 0 | 873.3333 | 1625.6937 | 379.0338 | 379.0338 | 0
2019-08-20 03:00 | 494.2213 | 0 | 286.6667 | 2004.7275 | -207.5546 | -207.5546 | 0
2019-08-20 04:00 | 549.2912 | 0 | 873.3333 | 1797.1729 | 324.0421 | 324.0421 | 0
2019-08-20 05:00 | 721.2371 | 182.4233 | 873.3333 | 2121.2151 | 334.5195 | 334.5195 | 0
2019-08-20 06:00 | 967.8272 | 1706.93 | 4266.6667 | 2455.7346 | 5005.7696 | 5005.7696 | 0
2019-08-20 07:00 | 910.5069 | 3868.5034 | 2773.3333 | 7461.5042 | 5731.3299 | 2538.4958 | 0
2019-08-20 08:00 | 837.7118 | 5681.7095 | 6160 | 10000 | 11003.9978 | 0 | 0
2019-08-20 09:00 | 848.5507 | 6998.7919 | 2773.3333 | 10000 | 8923.5746 | 0 | 0
2019-08-20 10:00 | 866.2598 | 7798.9458 | 1666.6667 | 10000 | 8599.3527 | 0 | 0
2019-08-20 11:00 | 844.2019 | 8114.6472 | 2773.3333 | 10000 | 10043.7787 | 0 | 0
2019-08-20 12:00 | 832.4086 | 7988.1633 | 2773.3333 | 10000 | 9929.0881 | 0 | 0
2019-08-20 13:00 | 951.4452 | 7386.3465 | 2773.3333 | 10000 | 9208.2346 | 0 | 0
2019-08-20 14:00 | 1133.2537 | 6312.3052 | 2773.3333 | 10000 | 7952.3848 | 0 | 0
2019-08-20 15:00 | 1364.2685 | 4769.3478 | 4266.6667 | 10000 | 7671.746 | 0 | 0
2019-08-20 16:00 | 1652.2303 | 2807.0672 | 4266.6667 | 10000 | 5421.5036 | 0 | 0
2019-08-20 17:00 | 1755.4979 | 828.1046 | 2773.3333 | 10000 | 1845.9401 | 0 | 0
2019-08-20 18:00 | 1783.7772 | 0 | 286.6667 | 10000 | -1497.1105 | -1497.1105 | 0
2019-08-20 19:00 | 1993.5834 | 0 | 286.6667 | 8502.8895 | -1706.9168 | -1706.9168 | 0
2019-08-20 20:00 | 2104.3254 | 0 | 286.6667 | 6795.9727 | -1817.6587 | -1817.6587 | 0
2019-08-20 21:00 | 1658.4039 | 0 | 0 | 4978.314 | -1658.4039 | -1658.4039 | 0
2019-08-20 22:00 | 1211.8636 | 0 | 0 | 3319.9101 | -1211.8636 | -1211.8636 | 0
2019-08-20 23:00 | 748.9568 | 0 | 0 | 2108.0465 | -748.9568 | -748.9568 | 0
2019-08-21 | 563.3025 | 0 | 286.6667 | 1359.0897 | -276.6359 | -276.6359 | 0
2019-08-21 01:00 | 505.605 | 0 | 286.6667 | 1082.4538 | -218.9383 | -218.9383 | 0
2019-08-21 02:00 | 492.7842 | 0 | 873.3333 | 863.5155 | 380.5491 | 380.5491 | 0
2019-08-21 03:00 | 491.2568 | 0 | 286.6667 | 1244.0646 | -204.5902 | -204.5902 | 0
2019-08-21 04:00 | 544.7447 | 0 | 286.6667 | 1039.4745 | -258.078 | -258.078 | 0
2019-08-21 05:00 | 709.4449 | 189.7017 | 286.6667 | 781.3964 | -233.0766 | -233.0766 | 0
2019-08-21 06:00 | 944.3422 | 1599.2015 | 286.6667 | 548.3199 | 941.5259 | 941.5259 | 0
2019-08-21 07:00 | 874.5079 | 2380.0216 | 0 | 1489.8458 | 1505.5137 | 1505.5137 | 0
2019-08-21 08:00 | 787.7362 | 4029.0871 | 286.6667 | 2995.3595 | 3528.0175 | 3528.0175 | 0
2019-08-21 09:00 | 1033.5822 | 2181.7961 | 0 | 6523.3771 | 1148.2139 | 1148.2139 | 0
2019-08-21 10:00 | 1107.4956 | 5756.325 | 0 | 7671.591 | 4648.8294 | 2328.409 | 0
2019-08-21 11:00 | 1239.6207 | 7836.2783 | 286.6667 | 10000 | 6883.3243 | 0 | 0
2019-08-21 12:00 | 1398.652 | 7623.8962 | 1666.6667 | 10000 | 7891.911 | 0 | 0
2019-08-21 13:00 | 1525.7172 | 7064.9422 | 1666.6667 | 10000 | 7205.8917 | 0 | 0
2019-08-21 14:00 | 1636.1137 | 6012.2414 | 2773.3333 | 10000 | 7149.461 | 0 | 0
2019-08-21 15:00 | 1484.4891 | 1717.8688 | 873.3333 | 10000 | 1106.7131 | 0 | 0
2019-08-21 16:00 | 1858.2803 | 2660.1386 | 873.3333 | 10000 | 1675.1916 | 0 | 0
2019-08-21 17:00 | 1916.2542 | 639.3839 | 1666.6667 | 10000 | 389.7963 | 0 | 0
2019-08-21 18:00 | 1904.8502 | 0 | 873.3333 | 10000 | -1031.5169 | -1031.5169 | 0
2019-08-21 19:00 | 2082.5563 | 0 | 873.3333 | 8968.4831 | -1209.2229 | -1209.2229 | 0
2019-08-21 20:00 | 2164.3519 | 0 | 2773.3333 | 7759.2602 | 608.9814 | 608.9814 | 0
2019-08-21 21:00 | 1738.9959 | 0 | 4266.6667 | 8368.2416 | 2527.6708 | 1631.7584 | 0
2019-08-21 22:00 | 1252.8076 | 0 | 1666.6667 | 10000 | 413.8591 | 0 | 0
2019-08-21 23:00 | 822.4311 | 0 | 1666.6667 | 10000 | 844.2356 | 0 | 0
2019-08-22 | 609.3697 | 0 | 873.3333 | 10000 | 263.9636 | 0 | 0
2019-08-22 01:00 | 505.605 | 0 | 873.3333 | 10000 | 367.7284 | 0 | 0
2019-08-22 02:00 | 492.7842 | 0 | 0 | 10000 | -492.7842 | -492.7842 | 0
2019-08-22 03:00 | 491.2568 | 0 | 286.6667 | 9507.2158 | -204.5902 | -204.5902 | 0
2019-08-22 04:00 | 544.7447 | 0 | 286.6667 | 9302.6256 | -258.078 | -258.078 | 0
2019-08-22 05:00 | 709.4449 | 184.5623 | 0 | 9044.5476 | -524.8826 | -524.8826 | 0
2019-08-22 06:00 | 944.3422 | 1587.5554 | 0 | 8519.665 | 643.2132 | 643.2132 | 0
2019-08-22 07:00 | 874.5079 | 3622.5943 | 286.6667 | 9162.8782 | 3034.7531 | 837.1218 | 0
2019-08-22 08:00 | 819.8383 | 5398.0724 | 2773.3333 | 10000 | 7351.5674 | 0 | 0
2019-08-22 09:00 | 964.8066 | 6696.7214 | 2773.3333 | 10000 | 8505.2482 | 0 | 0
2019-08-22 10:00 | 1078.9074 | 7499.7077 | 1666.6667 | 10000 | 8087.467 | 0 | 0
2019-08-22 11:00 | 1170.9144 | 7849.5435 | 2773.3333 | 10000 | 9451.9624 | 0 | 0
2019-08-22 12:00 | 1254.911 | 7696.9419 | 4266.6667 | 10000 | 10708.6976 | 0 | 0
2019-08-22 13:00 | 1421.8858 | 7084.0518 | 4266.6667 | 10000 | 9928.8326 | 0 | 0
2019-08-22 14:00 | 1513.5739 | 6075.895 | 7873.3333 | 10000 | 12435.6545 | 0 | 0
2019-08-22 15:00 | 1706.0535 | 4522.2692 | 4266.6667 | 10000 | 7082.8824 | 0 | 0
2019-08-22 16:00 | 1686.8443 | 2607.9608 | 7873.3333 | 10000 | 8794.4498 | 0 | 0
2019-08-22 17:00 | 1761.2179 | 759.7441 | 6160 | 10000 | 5158.5262 | 0 | 0
2019-08-22 18:00 | 1757.9431 | 0 | 6160 | 10000 | 4402.0569 | 0 | 0
2019-08-22 19:00 | 1921.7866 | 0 | 4266.6667 | 10000 | 2344.8801 | 0 | 0
2019-08-22 20:00 | 2019.711 | 0 | 4266.6667 | 10000 | 2246.9557 | 0 | 0
2019-08-22 21:00 | 1577.2501 | 0 | 2773.3333 | 10000 | 1196.0832 | 0 | 0
2019-08-22 22:00 | 1117.284 | 0 | 4266.6667 | 10000 | 3149.3827 | 0 | 0
2019-08-22 23:00 | 693.9086 | 0 | 2773.3333 | 10000 | 2079.4248 | 0 | 0
2019-08-23 | 563.3025 | 0 | 873.3333 | 10000 | 310.0308 | 0 | 0
2019-08-23 01:00 | 505.605 | 0 | 2773.3333 | 10000 | 2267.7284 | 0 | 0
2019-08-23 02:00 | 492.7842 | 0 | 873.3333 | 10000 | 380.5491 | 0 | 0
2019-08-23 03:00 | 491.2568 | 0 | 2773.3333 | 10000 | 2282.0765 | 0 | 0
2019-08-23 04:00 | 544.7447 | 0 | 1666.6667 | 10000 | 1121.922 | 0 | 0
2019-08-23 05:00 | 709.4449 | 173.7765 | 1666.6667 | 10000 | 1130.9982 | 0 | 0
2019-08-23 06:00 | 944.3422 | 747.7357 | 1666.6667 | 10000 | 1470.0602 | 0 | 0
2019-08-23 07:00 | 874.5079 | 1573.591 | 873.3333 | 10000 | 1572.4164 | 0 | 0
2019-08-23 08:00 | 787.7362 | 1698.6339 | 2773.3333 | 10000 | 3684.231 | 0 | 0
2019-08-23 09:00 | 792.0438 | 2404.2245 | 2773.3333 | 10000 | 4385.5141 | 0 | 0
2019-08-23 10:00 | 834.6337 | 4282.8128 | 2773.3333 | 10000 | 6221.5123 | 0 | 0
2019-08-23 11:00 | 905.5093 | 4178.7791 | 4266.6667 | 10000 | 7539.9365 | 0 | 0
2019-08-23 12:00 | 1014.9819 | 3607.1096 | 1666.6667 | 10000 | 4258.7943 | 0 | 0
2019-08-23 13:00 | 1246.6308 | 4527.9134 | 2773.3333 | 10000 | 6054.6159 | 0 | 0
2019-08-23 14:00 | 1374.1413 | 4460.7338 | 2773.3333 | 10000 | 5859.9259 | 0 | 0
2019-08-23 15:00 | 1614.2242 | 1360.7766 | 4266.6667 | 10000 | 4013.219 | 0 | 0
2019-08-23 16:00 | 1666.7549 | 1170.8334 | 2773.3333 | 10000 | 2277.4118 | 0 | 0
2019-08-23 17:00 | 1745.6785 | 545.246 | 2773.3333 | 10000 | 1572.9009 | 0 | 0
2019-08-23 18:00 | 1762.8043 | 0 | 873.3333 | 10000 | -889.471 | -889.471 | 0
2019-08-23 19:00 | 1919.1094 | 0 | 873.3333 | 9110.529 | -1045.7761 | -1045.7761 | 0
2019-08-23 20:00 | 1972.2261 | 0 | 286.6667 | 8064.7529 | -1685.5595 | -1685.5595 | 0
2019-08-23 21:00 | 1350.8763 | 0 | 873.3333 | 6379.1934 | -477.543 | -477.543 | 0
2019-08-23 22:00 | 1025.9125 | 0 | 873.3333 | 5901.6504 | -152.5792 | -152.5792 | 0
2019-08-23 23:00 | 693.9086 | 0 | 873.3333 | 5749.0712 | 179.4248 | 179.4248 | 0
2019-08-24 | 563.3025 | 0 | 873.3333 | 5928.496 | 310.0308 | 310.0308 | 0
2019-08-24 01:00 | 505.605 | 0 | 286.6667 | 6238.5268 | -218.9383 | -218.9383 | 0
2019-08-24 02:00 | 492.7842 | 0 | 286.6667 | 6019.5885 | -206.1175 | -206.1175 | 0
2019-08-24 03:00 | 491.2568 | 0 | 873.3333 | 5813.471 | 382.0765 | 382.0765 | 0
2019-08-24 04:00 | 544.7447 | 0 | 286.6667 | 6195.5475 | -258.078 | -258.078 | 0
2019-08-24 05:00 | 709.4449 | 185.2604 | 0 | 5937.4695 | -524.1845 | -524.1845 | 0
2019-08-24 06:00 | 944.3422 | 1488.0356 | 0 | 5413.2849 | 543.6934 | 543.6934 | 0
2019-08-24 07:00 | 874.5079 | 3416.6075 | 286.6667 | 5956.9783 | 2828.7662 | 2828.7662 | 0
2019-08-24 08:00 | 787.7362 | 5148.0842 | 873.3333 | 8785.7445 | 5233.6813 | 1214.2555 | 0
2019-08-24 09:00 | 792.0438 | 6427.4615 | 873.3333 | 10000 | 6508.7511 | 0 | 0
2019-08-24 10:00 | 808.0077 | 7189.6631 | 1666.6667 | 10000 | 8048.3221 | 0 | 0
2019-08-24 11:00 | 791.1417 | 6599.1577 | 2773.3333 | 10000 | 8581.3494 | 0 | 0
2019-08-24 12:00 | 795.3047 | 7265.0261 | 2773.3333 | 10000 | 9243.0547 | 0 | 0
2019-08-24 13:00 | 898.1199 | 6053.9657 | 2773.3333 | 10000 | 7929.1791 | 0 | 0
2019-08-24 14:00 | 1032.0594 | 5573.6348 | 1666.6667 | 10000 | 6208.2421 | 0 | 0
2019-08-24 15:00 | 1225.5569 | 2878.2832 | 0 | 10000 | 1652.7264 | 0 | 0
2019-08-24 16:00 | 1481.2755 | 1344.9871 | 0 | 10000 | -136.2884 | -136.2884 | 0
2019-08-24 17:00 | 1564.731 | 61.5814 | 873.3333 | 9863.7116 | -629.8163 | -629.8163 | 0
2019-08-24 18:00 | 1571.8451 | 0 | 0 | 9233.8952 | -1571.8451 | -1571.8451 | 0
2019-08-24 19:00 | 1713.4077 | 0 | 0 | 7662.0502 | -1713.4077 | -1713.4077 | 0
2019-08-24 20:00 | 1782.2691 | 0 | 0 | 5948.6425 | -1782.2691 | -1782.2691 | 0
2019-08-24 21:00 | 1350.8763 | 0 | 0 | 4166.3734 | -1350.8763 | -1350.8763 | 0
2019-08-24 22:00 | 1025.9125 | 0 | 0 | 2815.4971 | -1025.9125 | -1025.9125 | 0
2019-08-24 23:00 | 693.9086 | 0 | 873.3333 | 1789.5846 | 179.4248 | 179.4248 | 0
2019-08-25 | 563.3025 | 0 | 286.6667 | 1969.0093 | -276.6359 | -276.6359 | 0
2019-08-25 01:00 | 505.605 | 0 | 286.6667 | 1692.3735 | -218.9383 | -218.9383 | 0
2019-08-25 02:00 | 492.7842 | 0 | 286.6667 | 1473.4352 | -206.1175 | -206.1175 | 0
2019-08-25 03:00 | 491.2568 | 0 | 286.6667 | 1267.3176 | -204.5902 | -204.5902 | 0
2019-08-25 04:00 | 544.7447 | 0 | 286.6667 | 1062.7274 | -258.078 | -258.078 | 0
2019-08-25 05:00 | 709.4449 | 8.0695 | 873.3333 | 804.6494 | 171.958 | 171.958 | 0
2019-08-25 06:00 | 944.3422 | 839.5172 | 286.6667 | 976.6074 | 181.8417 | 181.8417 | 0
2019-08-25 07:00 | 874.5079 | 3389.2811 | 873.3333 | 1158.4491 | 3388.1066 | 3388.1066 | 0
2019-08-25 08:00 | 787.7362 | 5067.3278 | 286.6667 | 4546.5557 | 4566.2582 | 4566.2582 | 0
2019-08-25 09:00 | 792.0438 | 2623.4087 | 873.3333 | 9112.8139 | 2704.6983 | 887.1861 | 0
2019-08-25 10:00 | 808.0077 | 1437.7725 | 873.3333 | 10000 | 1503.0982 | 0 | 0
2019-08-25 11:00 | 791.1417 | 1833.0586 | 286.6667 | 10000 | 1328.5836 | 0 | 0
2019-08-25 12:00 | 767.0738 | 5345.3265 | 873.3333 | 10000 | 5451.586 | 0 | 0
2019-08-25 13:00 | 757.1015 | 6749.925 | 286.6667 | 10000 | 6279.4902 | 0 | 0
2019-08-25 14:00 | 783.0916 | 2026.4782 | 286.6667 | 10000 | 1530.0533 | 0 | 0
2019-08-25 15:00 | 898.3042 | 3200.5972 | 286.6667 | 10000 | 2588.9596 | 0 | 0
2019-08-25 16:00 | 1097.5002 | 1617.69 | 0 | 10000 | 520.1898 | 0 | 0
2019-08-25 17:00 | 1208.8791 | 491.9355 | 0 | 10000 | -716.9436 | -716.9436 | 0
2019-08-25 18:00 | 1296.2336 | 0 | 873.3333 | 9283.0564 | -422.9003 | -422.9003 | 0
2019-08-25 19:00 | 1538.7967 | 0 | 286.6667 | 8860.1561 | -1252.13 | -1252.13 | 0
2019-08-25 20:00 | 1687.2222 | 0 | 286.6667 | 7608.0261 | -1400.5555 | -1400.5555 | 0
2019-08-25 21:00 | 1350.8763 | 0 | 286.6667 | 6207.4706 | -1064.2096 | -1064.2096 | 0
2019-08-25 22:00 | 1025.9125 | 0 | 286.6667 | 5143.2609 | -739.2459 | -739.2459 | 0
2019-08-25 23:00 | 693.9086 | 0 | 286.6667 | 4404.0151 | -407.2419 | -407.2419 | 0
2019-08-26 | 567.6829 | 0 | 286.6667 | 3996.7732 | -281.0163 | -281.0163 | 0
2019-08-26 01:00 | 508.5029 | 0 | 286.6667 | 3715.7569 | -221.8363 | -221.8363 | 0
2019-08-26 02:00 | 494.2995 | 0 | 286.6667 | 3493.9206 | -207.6329 | -207.6329 | 0
2019-08-26 03:00 | 494.2213 | 0 | 286.6667 | 3286.2878 | -207.5546 | -207.5546 | 0
2019-08-26 04:00 | 549.2912 | 0 | 286.6667 | 3078.7331 | -262.6245 | -262.6245 | 0
2019-08-26 05:00 | 721.2371 | 0 | 286.6667 | 2816.1086 | -434.5705 | -434.5705 | 0
2019-08-26 06:00 | 967.8272 | 499.9303 | 873.3333 | 2381.5382 | 405.4365 | 405.4365 | 0
2019-08-26 07:00 | 910.5069 | 2253.4859 | 873.3333 | 2786.9746 | 2216.3124 | 2216.3124 | 0
2019-08-26 08:00 | 837.7118 | 1766.5392 | 286.6667 | 5003.2871 | 1215.494 | 1215.494 | 0
2019-08-26 09:00 | 848.5507 | 2032.7101 | 873.3333 | 6218.7811 | 2057.4928 | 2057.4928 | 0
2019-08-26 10:00 | 866.2598 | 6502.2667 | 873.3333 | 8276.2739 | 6509.3403 | 1723.7261 | 0
2019-08-26 11:00 | 844.2019 | 1591.1158 | 286.6667 | 10000 | 1033.5807 | 0 | 0
2019-08-26 12:00 | 815.4479 | 3584.8087 | 873.3333 | 10000 | 3642.6942 | 0 | 0
2019-08-26 13:00 | 800.5231 | 4025.5796 | 286.6667 | 10000 | 3511.7231 | 0 | 0
2019-08-26 14:00 | 824.2197 | 3980.9423 | 873.3333 | 10000 | 4030.056 | 0 | 0
2019-08-26 15:00 | 938.166 | 2787.9657 | 873.3333 | 10000 | 2723.133 | 0 | 0
2019-08-26 16:00 | 1136.7338 | 1764.0126 | 1666.6667 | 10000 | 2293.9454 | 0 | 0
2019-08-26 17:00 | 1246.9568 | 406.6205 | 873.3333 | 10000 | 32.997 | 0 | 0
2019-08-26 18:00 | 1334.2385 | 0 | 286.6667 | 10000 | -1047.5718 | -1047.5718 | 0
2019-08-26 19:00 | 1577.4792 | 0 | 0 | 8952.4282 | -1577.4792 | -1577.4792 | 0
2019-08-26 20:00 | 1726.7387 | 0 | 0 | 7374.949 | -1726.7387 | -1726.7387 | 0
2019-08-26 21:00 | 1382.2762 | 0 | 0 | 5648.2102 | -1382.2762 | -1382.2762 | 0
2019-08-26 22:00 | 1043.1531 | 0 | 0 | 4265.9341 | -1043.1531 | -1043.1531 | 0
2019-08-26 23:00 | 701.2041 | 0 | 0 | 3222.7809 | -701.2041 | -701.2041 | 0
2019-08-27 | 567.6829 | 0 | 0 | 2521.5769 | -567.6829 | -567.6829 | 0
2019-08-27 01:00 | 508.5029 | 0 | 0 | 1953.8939 | -508.5029 | -508.5029 | 0
2019-08-27 02:00 | 494.2995 | 0 | 286.6667 | 1445.391 | -207.6329 | -207.6329 | 0
2019-08-27 03:00 | 494.2213 | 0 | 873.3333 | 1237.7582 | 379.112 | 379.112 | 0
2019-08-27 04:00 | 549.2912 | 0 | 286.6667 | 1616.8702 | -262.6245 | -262.6245 | 0
2019-08-27 05:00 | 721.2371 | 161.4071 | 286.6667 | 1354.2457 | -273.1634 | -273.1634 | 0
2019-08-27 06:00 | 967.8272 | 1145.661 | 286.6667 | 1081.0823 | 464.5006 | 464.5006 | 0
2019-08-27 07:00 | 910.5069 | 3284.607 | 0 | 1545.5829 | 2374.1001 | 2374.1001 | 0
2019-08-27 08:00 | 837.7118 | 5357.4923 | 0 | 3919.683 | 4519.7806 | 4519.7806 | 0
2019-08-27 09:00 | 848.5507 | 6631.0714 | 286.6667 | 8439.4636 | 6069.1873 | 1560.5364 | 0
2019-08-27 10:00 | 866.2598 | 7413.521 | 286.6667 | 10000 | 6833.9279 | 0 | 0
2019-08-27 11:00 | 844.2019 | 7707.8819 | 873.3333 | 10000 | 7737.0134 | 0 | 0
2019-08-27 12:00 | 815.4479 | 7537.6221 | 2773.3333 | 10000 | 9495.5075 | 0 | 0
2019-08-27 13:00 | 800.5231 | 6945.4365 | 2773.3333 | 10000 | 8918.2467 | 0 | 0
2019-08-27 14:00 | 824.2197 | 5952.3241 | 4266.6667 | 10000 | 9394.7711 | 0 | 0
2019-08-27 15:00 | 938.166 | 4407.5417 | 2773.3333 | 10000 | 6242.7091 | 0 | 0
2019-08-27 16:00 | 1136.7338 | 2482.6269 | 1666.6667 | 10000 | 3012.5597 | 0 | 0
2019-08-27 17:00 | 1246.9568 | 633.175 | 286.6667 | 10000 | -327.115 | -327.115 | 0
2019-08-27 18:00 | 1334.2385 | 0 | 0 | 9672.885 | -1334.2385 | -1334.2385 | 0
2019-08-27 19:00 | 1577.4792 | 0 | 0 | 8338.6464 | -1577.4792 | -1577.4792 | 0
2019-08-27 20:00 | 1726.7387 | 0 | 0 | 6761.1672 | -1726.7387 | -1726.7387 | 0
2019-08-27 21:00 | 1382.2762 | 0 | 0 | 5034.4285 | -1382.2762 | -1382.2762 | 0
2019-08-27 22:00 | 1043.1531 | 0 | 0 | 3652.1523 | -1043.1531 | -1043.1531 | 0
2019-08-27 23:00 | 701.2041 | 0 | 0 | 2608.9992 | -701.2041 | -701.2041 | 0
2019-08-28 | 563.3025 | 0 | 0 | 1907.7952 | -563.3025 | -563.3025 | 0
2019-08-28 01:00 | 505.605 | 0 | 0 | 1344.4926 | -505.605 | -505.605 | 0
2019-08-28 02:00 | 492.7842 | 0 | 0 | 838.8877 | -492.7842 | -492.7842 | 0
2019-08-28 03:00 | 491.2568 | 0 | 0 | 346.1035 | -491.2568 | -346.1035 | -145.1534
2019-08-28 04:00 | 544.7447 | 0 | 0 | 0 | -544.7447 | 0 | -689.898
2019-08-28 05:00 | 709.4449 | 131.2414 | 0 | 0 | -578.2035 | 0 | -1268.1015
2019-08-28 06:00 | 944.3422 | 1517.0006 | 0 | 0 | 572.6584 | 572.6584 | -695.4431
2019-08-28 07:00 | 874.5079 | 3601.1088 | 0 | 572.6584 | 2726.601 | 2726.601 | 0
2019-08-28 08:00 | 787.7362 | 5343.9936 | 286.6667 | 3299.2594 | 4842.9241 | 4842.9241 | 0
2019-08-28 09:00 | 792.0438 | 6587.4817 | 286.6667 | 8142.1834 | 6082.1047 | 1857.8166 | 0
2019-08-28 10:00 | 808.0077 | 7367.6187 | 873.3333 | 10000 | 7432.9444 | 0 | 0
2019-08-28 11:00 | 791.1417 | 7635.7366 | 2773.3333 | 10000 | 9617.9283 | 0 | 0
2019-08-28 12:00 | 767.0738 | 7512.1392 | 2773.3333 | 10000 | 9518.3987 | 0 | 0
2019-08-28 13:00 | 757.1015 | 6920.8368 | 2773.3333 | 10000 | 8937.0687 | 0 | 0
2019-08-28 14:00 | 783.0916 | 3275.6692 | 1666.6667 | 10000 | 4159.2443 | 0 | 0
2019-08-28 15:00 | 898.3042 | 3763.7269 | 873.3333 | 10000 | 3738.756 | 0 | 0
2019-08-28 16:00 | 1097.5002 | 2417.7565 | 873.3333 | 10000 | 2193.5897 | 0 | 0
2019-08-28 17:00 | 1208.8791 | 612.0058 | 0 | 10000 | -596.8733 | -596.8733 | 0
2019-08-28 18:00 | 1296.2336 | 0 | 0 | 9403.1267 | -1296.2336 | -1296.2336 | 0
2019-08-28 19:00 | 1538.7967 | 0 | 0 | 8106.8931 | -1538.7967 | -1538.7967 | 0
2019-08-28 20:00 | 1687.2222 | 0 | 0 | 6568.0964 | -1687.2222 | -1687.2222 | 0
2019-08-28 21:00 | 1350.8763 | 0 | 0 | 4880.8743 | -1350.8763 | -1350.8763 | 0
2019-08-28 22:00 | 1025.9125 | 0 | 0 | 3529.9979 | -1025.9125 | -1025.9125 | 0
2019-08-28 23:00 | 693.9086 | 0 | 0 | 2504.0854 | -693.9086 | -693.9086 | 0
2019-08-29 | 563.3025 | 0 | 0 | 1810.1769 | -563.3025 | -563.3025 | 0
2019-08-29 01:00 | 505.605 | 0 | 0 | 1246.8743 | -505.605 | -505.605 | 0
2019-08-29 02:00 | 492.7842 | 0 | 0 | 741.2694 | -492.7842 | -492.7842 | 0
2019-08-29 03:00 | 491.2568 | 0 | 0 | 248.4852 | -491.2568 | -248.4852 | -242.7717
2019-08-29 04:00 | 544.7447 | 0 | 0 | 0 | -544.7447 | 0 | -787.5164
2019-08-29 05:00 | 709.4449 | 0 | 0 | 0 | -709.4449 | 0 | -1496.9613
2019-08-29 06:00 | 944.3422 | 259.5711 | 286.6667 | 0 | -398.1045 | 0 | -1895.0658
2019-08-29 07:00 | 874.5079 | 400.3357 | 0 | 0 | -474.1722 | 0 | -2369.2379
2019-08-29 08:00 | 787.7362 | 1312.2638 | 286.6667 | 0 | 811.1943 | 811.1943 | -1558.0437
2019-08-29 09:00 | 792.0438 | 1758.7858 | 1666.6667 | 811.1943 | 2633.4088 | 2633.4088 | 0
2019-08-29 10:00 | 808.0077 | 2199.3531 | 1666.6667 | 3444.603 | 3058.0121 | 3058.0121 | 0
2019-08-29 11:00 | 791.1417 | 1434.909 | 2773.3333 | 6502.6152 | 3417.1007 | 3417.1007 | 0
2019-08-29 12:00 | 767.0738 | 4249.3282 | 873.3333 | 9919.7159 | 4355.5877 | 80.2841 | 0
2019-08-29 13:00 | 757.1015 | 2551.1991 | 1666.6667 | 10000 | 3460.7643 | 0 | 0
2019-08-29 14:00 | 783.0916 | 4581.3435 | 873.3333 | 10000 | 4671.5853 | 0 | 0
2019-08-29 15:00 | 898.3042 | 3813.2033 | 873.3333 | 10000 | 3788.2324 | 0 | 0
2019-08-29 16:00 | 1097.5002 | 87.6035 | 873.3333 | 10000 | -136.5633 | -136.5633 | 0
2019-08-29 17:00 | 1208.8791 | 621.4082 | 873.3333 | 9863.4367 | 285.8625 | 136.5633 | 0
2019-08-29 18:00 | 1296.2336 | 0 | 286.6667 | 10000 | -1009.567 | -1009.567 | 0
2019-08-29 19:00 | 1538.7967 | 0 | 286.6667 | 8990.433 | -1252.13 | -1252.13 | 0
2019-08-29 20:00 | 1687.2222 | 0 | 873.3333 | 7738.303 | -813.8888 | -813.8888 | 0
2019-08-29 21:00 | 1350.8763 | 0 | 286.6667 | 6924.4142 | -1064.2096 | -1064.2096 | 0
2019-08-29 22:00 | 1025.9125 | 0 | 286.6667 | 5860.2046 | -739.2459 | -739.2459 | 0
2019-08-29 23:00 | 693.9086 | 0 | 0 | 5120.9587 | -693.9086 | -693.9086 | 0
2019-08-30 | 563.3025 | 0 | 0 | 4427.0501 | -563.3025 | -563.3025 | 0
2019-08-30 01:00 | 505.605 | 0 | 286.6667 | 3863.7476 | -218.9383 | -218.9383 | 0
2019-08-30 02:00 | 492.7842 | 0 | 286.6667 | 3644.8093 | -206.1175 | -206.1175 | 0
2019-08-30 03:00 | 491.2568 | 0 | 286.6667 | 3438.6918 | -204.5902 | -204.5902 | 0
2019-08-30 04:00 | 544.7447 | 0 | 873.3333 | 3234.1016 | 328.5887 | 328.5887 | 0
2019-08-30 05:00 | 709.4449 | 129.2197 | 873.3333 | 3562.6902 | 293.1082 | 293.1082 | 0
2019-08-30 06:00 | 944.3422 | 1433.7027 | 1666.6667 | 3855.7984 | 2156.0271 | 2156.0271 | 0
2019-08-30 07:00 | 874.5079 | 3382.641 | 1666.6667 | 6011.8255 | 4174.7998 | 3988.1745 | 0
2019-08-30 08:00 | 787.7362 | 5084.1741 | 4266.6667 | 10000 | 8563.1046 | 0 | 0
2019-08-30 09:00 | 792.0438 | 3387.026 | 873.3333 | 10000 | 3468.3156 | 0 | 0
2019-08-30 10:00 | 808.0077 | 5086.7984 | 1666.6667 | 10000 | 5945.4574 | 0 | 0
2019-08-30 11:00 | 793.8011 | 5750.552 | 2773.3333 | 10000 | 7730.0842 | 0 | 0
2019-08-30 12:00 | 958.7037 | 4710.3827 | 873.3333 | 10000 | 4625.0123 | 0 | 0
2019-08-30 13:00 | 1142.6456 | 4556.6761 | 873.3333 | 10000 | 4287.3638 | 0 | 0
2019-08-30 14:00 | 1263.1965 | 5361.5783 | 2773.3333 | 10000 | 6871.7151 | 0 | 0
2019-08-30 15:00 | 1433.1599 | 3890.4281 | 2773.3333 | 10000 | 5230.6016 | 0 | 0
2019-08-30 16:00 | 1774.5914 | 2145.0433 | 873.3333 | 10000 | 1243.7852 | 0 | 0
2019-08-30 17:00 | 1788.6356 | 579.792 | 0 | 10000 | -1208.8435 | -1208.8435 | 0
2019-08-30 18:00 | 1739.8305 | 0 | 0 | 8791.1565 | -1739.8305 | -1739.8305 | 0
2019-08-30 19:00 | 1751.9435 | 0 | 0 | 7051.326 | -1751.9435 | -1751.9435 | 0
2019-08-30 20:00 | 1687.2222 | 0 | 286.6667 | 5299.3824 | -1400.5555 | -1400.5555 | 0
2019-08-30 21:00 | 1350.8763 | 0 | 0 | 3898.8269 | -1350.8763 | -1350.8763 | 0
2019-08-30 22:00 | 1025.9125 | 0 | 286.6667 | 2547.9506 | -739.2459 | -739.2459 | 0
2019-08-30 23:00 | 693.9086 | 0 | 0 | 1808.7047 | -693.9086 | -693.9086 | 0
2019-08-31 | 563.3025 | 0 | 286.6667 | 1114.7962 | -276.6359 | -276.6359 | 0
2019-08-31 01:00 | 505.605 | 0 | 286.6667 | 838.1603 | -218.9383 | -218.9383 | 0
2019-08-31 02:00 | 492.7842 | 0 | 873.3333 | 619.222 | 380.5491 | 380.5491 | 0
2019-08-31 03:00 | 491.2568 | 0 | 873.3333 | 999.7711 | 382.0765 | 382.0765 | 0
2019-08-31 04:00 | 544.7447 | 0 | 873.3333 | 1381.8476 | 328.5887 | 328.5887 | 0
2019-08-31 05:00 | 709.4449 | 87.7691 | 873.3333 | 1710.4363 | 251.6576 | 251.6576 | 0
2019-08-31 06:00 | 944.3422 | 481.965 | 873.3333 | 1962.0939 | 410.9561 | 410.9561 | 0
2019-08-31 07:00 | 874.5079 | 794.7949 | 873.3333 | 2373.0499 | 793.6203 | 793.6203 | 0
2019-08-31 08:00 | 787.7362 | 848.723 | 1666.6667 | 3166.6703 | 1727.6534 | 1727.6534 | 0
2019-08-31 09:00 | 792.0438 | 1621.0595 | 873.3333 | 4894.3237 | 1702.3491 | 1702.3491 | 0
2019-08-31 10:00 | 808.0077 | 2892.9124 | 1666.6667 | 6596.6728 | 3751.5714 | 3403.3272 | 0
2019-08-31 11:00 | 791.1417 | 3671.0944 | 4266.6667 | 10000 | 7146.6194 | 0 | 0
2019-08-31 12:00 | 767.0738 | 4007.6568 | 4266.6667 | 10000 | 7507.2497 | 0 | 0
2019-08-31 13:00 | 807.3845 | 6601.7348 | 2773.3333 | 10000 | 8567.6837 | 0 | 0
2019-08-31 14:00 | 887.1798 | 5486.6546 | 2773.3333 | 10000 | 7372.8082 | 0 | 0
2019-08-31 15:00 | 1066.8809 | 4055.2726 | 2773.3333 | 10000 | 5761.7251 | 0 | 0
2019-08-31 16:00 | 1305.2855 | 2265.3677 | 2773.3333 | 10000 | 3733.4156 | 0 | 0
2019-08-31 17:00 | 1413.8047 | 557.6442 | 4266.6667 | 10000 | 3410.5062 | 0 | 0
2019-08-31 18:00 | 1465.8874 | 0 | 873.3333 | 10000 | -592.5541 | -592.5541 | 0
2019-08-31 19:00 | 1698.2568 | 0 | 873.3333 | 9407.4459 | -824.9235 | -824.9235 | 0
2019-08-31 20:00 | 1759.9233 | 0 | 873.3333 | 8582.5224 | -886.5899 | -886.5899 | 0
2019-08-31 21:00 | 1350.8763 | 0 | 873.3333 | 7695.9325 | -477.543 | -477.543 | 0
2019-08-31 22:00 | 1025.9125 | 0 | 2773.3333 | 7218.3895 | 1747.4208 | 1747.4208 | 0
2019-08-31 23:00 | 693.9086 | 0 | 6160 | 8965.8103 | 5466.0914 | 1034.1897 | 0
2019-09-01 | 566.5941 | 0 | 4266.6667 | 10000 | 3700.0725 | 0 | 0
2019-09-01 01:00 | 506.5827 | 0 | 4266.6667 | 10000 | 3760.084 | 0 | 0
2019-09-01 02:00 | 493.7415 | 0 | 4266.6667 | 10000 | 3772.9251 | 0 | 0
2019-09-01 03:00 | 492.1242 | 0 | 4266.6667 | 10000 | 3774.5425 | 0 | 0
2019-09-01 04:00 | 546.7972 | 0 | 4266.6667 | 10000 | 3719.8695 | 0 | 0
2019-09-01 05:00 | 735.5954 | 121.3307 | 4266.6667 | 10000 | 3652.402 | 0 | 0
2019-09-01 06:00 | 1012.2696 | 1557.6451 | 4266.6667 | 10000 | 4812.0422 | 0 | 0
2019-09-01 07:00 | 942.7518 | 3747.9846 | 2773.3333 | 10000 | 5578.5661 | 0 | 0
2019-09-01 08:00 | 822.1611 | 5617.4176 | 4266.6667 | 10000 | 9061.9232 | 0 | 0
2019-09-01 09:00 | 816.1489 | 6937.2727 | 9060 | 10000 | 15181.1237 | 0 | 0
2019-09-01 10:00 | 832.0413 | 7791.5869 | 7873.3333 | 10000 | 14832.879 | 0 | 0
2019-09-01 11:00 | 815.08 | 8084.477 | 7873.3333 | 10000 | 15142.7304 | 0 | 0
2019-09-01 12:00 | 791.1673 | 7935.5256 | 6160 | 10000 | 13304.3583 | 0 | 0
2019-09-01 13:00 | 798.6484 | 7231.4633 | 6160 | 10000 | 12592.8149 | 0 | 0
2019-09-01 14:00 | 840.9937 | 6145.4482 | 6160 | 10000 | 11464.4545 | 0 | 0
2019-09-01 15:00 | 1042.8724 | 4481.4557 | 6160 | 10000 | 9598.5833 | 0 | 0
2019-09-01 16:00 | 1158.5647 | 2431.9016 | 6160 | 10000 | 7433.3369 | 0 | 0
2019-09-01 17:00 | 1474.6892 | 533.2515 | 2773.3333 | 10000 | 1831.8957 | 0 | 0
2019-09-01 18:00 | 1674.6483 | 0 | 873.3333 | 10000 | -801.315 | -801.315 | 0
2019-09-01 19:00 | 1940.967 | 0 | 873.3333 | 9198.685 | -1067.6336 | -1067.6336 | 0
2019-09-01 20:00 | 1804.9698 | 0 | 0 | 8131.0514 | -1804.9698 | -1804.9698 | 0
2019-09-01 21:00 | 1381.707 | 0 | 873.3333 | 6326.0815 | -508.3736 | -508.3736 | 0
2019-09-01 22:00 | 1034.6953 | 0 | 873.3333 | 5817.7079 | -161.362 | -161.362 | 0
2019-09-01 23:00 | 696.8921 | 0 | 873.3333 | 5656.3459 | 176.4413 | 176.4413 | 0
2019-09-02 | 570.9746 | 0 | 873.3333 | 5832.7872 | 302.3588 | 302.3588 | 0
2019-09-02 01:00 | 509.4806 | 0 | 873.3333 | 6135.146 | 363.8527 | 363.8527 | 0
2019-09-02 02:00 | 495.2568 | 0 | 873.3333 | 6498.9987 | 378.0765 | 378.0765 | 0
2019-09-02 03:00 | 495.0887 | 0 | 2773.3333 | 6877.0752 | 2278.2447 | 2278.2447 | 0
2019-09-02 04:00 | 551.3437 | 0 | 1666.6667 | 9155.3198 | 1115.323 | 844.6802 | 0
2019-09-02 05:00 | 747.3876 | 102.4305 | 2773.3333 | 10000 | 2128.3762 | 0 | 0
2019-09-02 06:00 | 1035.7545 | 1514.8973 | 2773.3333 | 10000 | 3252.4761 | 0 | 0
2019-09-02 07:00 | 978.7508 | 3635.6732 | 1666.6667 | 10000 | 4323.5891 | 0 | 0
2019-09-02 08:00 | 872.1367 | 5489.0581 | 873.3333 | 10000 | 5490.2548 | 0 | 0
2019-09-02 09:00 | 872.6558 | 6831.7486 | 873.3333 | 10000 | 6832.4262 | 0 | 0
2019-09-02 10:00 | 890.2934 | 7637.7446 | 286.6667 | 10000 | 7034.1178 | 0 | 0
2019-09-02 11:00 | 868.1401 | 7930.3402 | 1666.6667 | 10000 | 8728.8667 | 0 | 0
2019-09-02 12:00 | 839.5413 | 7782.0097 | 873.3333 | 10000 | 7815.8018 | 0 | 0
2019-09-02 13:00 | 824.7175 | 7123.9729 | 873.3333 | 10000 | 7172.5887 | 0 | 0
2019-09-02 14:00 | 848.3673 | 5980.4059 | 873.3333 | 10000 | 6005.372 | 0 | 0
2019-09-02 15:00 | 969.4648 | 4351.1204 | 873.3333 | 10000 | 4254.989 | 0 | 0
2019-09-02 16:00 | 1200.6209 | 2332.2908 | 873.3333 | 10000 | 2005.0033 | 0 | 0
2019-09-02 17:00 | 1379.937 | 508.1896 | 286.6667 | 10000 | -585.0807 | -585.0807 | 0
2019-09-02 18:00 | 1554.3325 | 0 | 873.3333 | 9414.9193 | -680.9992 | -680.9992 | 0
2019-09-02 19:00 | 1827.4188 | 0 | 873.3333 | 8733.9201 | -954.0855 | -954.0855 | 0
2019-09-02 20:00 | 1736.6081 | 0 | 873.3333 | 7779.8346 | -863.2748 | -863.2748 | 0
2019-09-02 21:00 | 1392.5539 | 0 | 286.6667 | 6916.5598 | -1105.8872 | -1105.8872 | 0
2019-09-02 22:00 | 1055.6227 | 0 | 0 | 5810.6726 | -1055.6227 | -1055.6227 | 0
2019-09-02 23:00 | 720.1527 | 0 | 0 | 4755.0499 | -720.1527 | -720.1527 | 0
2019-09-03 | 597.9517 | 0 | 0 | 4034.8972 | -597.9517 | -597.9517 | 0
2019-09-03 01:00 | 544.6031 | 0 | 0 | 3436.9455 | -544.6031 | -544.6031 | 0
2019-09-03 02:00 | 536.8763 | 0 | 873.3333 | 2892.3423 | 336.457 | 336.457 | 0
2019-09-03 03:00 | 543.4596 | 0 | 2773.3333 | 3228.7994 | 2229.8737 | 2229.8737 | 0
2019-09-03 04:00 | 602.543 | 0 | 2773.3333 | 5458.6731 | 2170.7903 | 2170.7903 | 0
2019-09-03 05:00 | 794.9132 | 147.5254 | 286.6667 | 7629.4634 | -360.7211 | -360.7211 | 0
2019-09-03 06:00 | 1075.4681 | 1460.4586 | 1666.6667 | 7268.7423 | 2051.6571 | 2051.6571 | 0
2019-09-03 07:00 | 1015.1178 | 3324.5154 | 1666.6667 | 9320.3994 | 3976.0643 | 679.6006 | 0
2019-09-03 08:00 | 897.1276 | 4696.953 | 7873.3333 | 10000 | 11673.1588 | 0 | 0
2019-09-03 09:00 | 889.5336 | 5843.3202 | 9573.3333 | 10000 | 14527.1199 | 0 | 0
2019-09-03 10:00 | 890.2934 | 4782.1094 | 9060 | 10000 | 12951.816 | 0 | 0
2019-09-03 11:00 | 868.1401 | 6070.1726 | 7873.3333 | 10000 | 13075.3658 | 0 | 0
2019-09-03 12:00 | 839.5413 | 4758.1399 | 2773.3333 | 10000 | 6691.932 | 0 | 0
2019-09-03 13:00 | 824.7175 | 7154.5548 | 286.6667 | 10000 | 6616.5039 | 0 | 0
2019-09-03 14:00 | 848.3673 | 5981.3754 | 873.3333 | 10000 | 6006.3414 | 0 | 0
2019-09-03 15:00 | 969.4648 | 4361.2105 | 873.3333 | 10000 | 4265.0791 | 0 | 0
2019-09-03 16:00 | 1197.7983 | 2182.0664 | 286.6667 | 10000 | 1270.9347 | 0 | 0
2019-09-03 17:00 | 1379.937 | 467.2024 | 4266.6667 | 10000 | 3353.9321 | 0 | 0
2019-09-03 18:00 | 1554.3325 | 0 | 2773.3333 | 10000 | 1219.0008 | 0 | 0
2019-09-03 19:00 | 1827.4188 | 0 | 4266.6667 | 10000 | 2439.2478 | 0 | 0
2019-09-03 20:00 | 1736.6081 | 0 | 4266.6667 | 10000 | 2530.0586 | 0 | 0
2019-09-03 21:00 | 1392.5539 | 0 | 4266.6667 | 10000 | 2874.1128 | 0 | 0
2019-09-03 22:00 | 1051.9359 | 0 | 4266.6667 | 10000 | 3214.7308 | 0 | 0
2019-09-03 23:00 | 704.1876 | 0 | 6160 | 10000 | 5455.8124 | 0 | 0
2019-09-04 | 567.4246 | 0 | 2773.3333 | 10000 | 2205.9087 | 0 | 0
2019-09-04 01:00 | 517.1632 | 0 | 4266.6667 | 10000 | 3749.5034 | 0 | 0
2019-09-04 02:00 | 514.4986 | 0 | 2773.3333 | 10000 | 2258.8347 | 0 | 0
2019-09-04 03:00 | 520.2015 | 0 | 2773.3333 | 10000 | 2253.1319 | 0 | 0
2019-09-04 04:00 | 579.4622 | 0 | 1666.6667 | 10000 | 1087.2044 | 0 | 0
2019-09-04 05:00 | 774.2539 | 73.4022 | 4266.6667 | 10000 | 3565.815 | 0 | 0
2019-09-04 06:00 | 1040.2518 | 1447.1393 | 4266.6667 | 10000 | 4673.5541 | 0 | 0
2019-09-04 07:00 | 964.6345 | 3552.7295 | 4266.6667 | 10000 | 6854.7617 | 0 | 0
2019-09-04 08:00 | 830.6416 | 5379.5792 | 1666.6667 | 10000 | 6215.6043 | 0 | 0
2019-09-04 09:00 | 816.1489 | 6672.0734 | 2773.3333 | 10000 | 8629.2579 | 0 | 0
2019-09-04 10:00 | 832.0413 | 7498.0276 | 1666.6667 | 10000 | 8332.653 | 0 | 0
2019-09-04 11:00 | 815.08 | 7827.8303 | 4266.6667 | 10000 | 11279.417 | 0 | 0
2019-09-04 12:00 | 791.1673 | 7619.3514 | 2773.3333 | 10000 | 9601.5175 | 0 | 0
2019-09-04 13:00 | 781.2959 | 6903.7467 | 2773.3333 | 10000 | 8895.7841 | 0 | 0
2019-09-04 14:00 | 807.2392 | 5777.5563 | 6160 | 10000 | 11130.3171 | 0 | 0
2019-09-04 15:00 | 929.603 | 4168.0301 | 7873.3333 | 10000 | 11111.7604 | 0 | 0
2019-09-04 16:00 | 1158.5647 | 2211.7777 | 6160 | 10000 | 7213.2131 | 0 | 0
2019-09-04 17:00 | 1341.8593 | 451.1772 | 4266.6667 | 10000 | 3375.9845 | 0 | 0
2019-09-04 18:00 | 1516.3276 | 0 | 4266.6667 | 10000 | 2750.339 | 0 | 0
2019-09-04 19:00 | 1788.7363 | 0 | 4266.6667 | 10000 | 2477.9304 | 0 | 0
2019-09-04 20:00 | 1697.0916 | 0 | 1666.6667 | 10000 | -30.4249 | -30.4249 | 0
2019-09-04 21:00 | 1361.1541 | 0 | 1666.6667 | 9969.5751 | 305.5126 | 30.4249 | 0
2019-09-04 22:00 | 1034.6953 | 0 | 2773.3333 | 10000 | 1738.638 | 0 | 0
2019-09-04 23:00 | 696.8921 | 0 | 2773.3333 | 10000 | 2076.4413 | 0 | 0
2019-09-05 | 566.5941 | 0 | 2773.3333 | 10000 | 2206.7392 | 0 | 0
2019-09-05 01:00 | 506.5827 | 0 | 2773.3333 | 10000 | 2266.7507 | 0 | 0
2019-09-05 02:00 | 493.7415 | 0 | 2773.3333 | 10000 | 2279.5918 | 0 | 0
2019-09-05 03:00 | 492.1242 | 0 | 4266.6667 | 10000 | 3774.5425 | 0 | 0
2019-09-05 04:00 | 546.7972 | 0 | 4266.6667 | 10000 | 3719.8695 | 0 | 0
2019-09-05 05:00 | 735.5954 | 72.4557 | 4266.6667 | 10000 | 3603.527 | 0 | 0
2019-09-05 06:00 | 1012.2696 | 381.8701 | 6160 | 10000 | 5529.6006 | 0 | 0
2019-09-05 07:00 | 942.7518 | 2032.3846 | 6160 | 10000 | 7249.6329 | 0 | 0
2019-09-05 08:00 | 822.1611 | 5237.1207 | 7873.3333 | 10000 | 12288.2929 | 0 | 0
2019-09-05 09:00 | 816.1489 | 4006.6655 | 2773.3333 | 10000 | 5963.85 | 0 | 0
2019-09-05 10:00 | 832.0413 | 7331.4685 | 2773.3333 | 10000 | 9272.7605 | 0 | 0
2019-09-05 11:00 | 815.08 | 7593.9019 | 9060 | 10000 | 15838.822 | 0 | 0
2019-09-05 12:00 | 791.1673 | 7422.5715 | 6160 | 10000 | 12791.4042 | 0 | 0
2019-09-05 13:00 | 781.2959 | 6738.1398 | 7873.3333 | 10000 | 13830.1772 | 0 | 0
2019-09-05 14:00 | 807.2392 | 5609.7356 | 7873.3333 | 10000 | 12675.8298 | 0 | 0
2019-09-05 15:00 | 929.603 | 4022.0825 | 7873.3333 | 10000 | 10965.8127 | 0 | 0
2019-09-05 16:00 | 1158.5647 | 2124.3317 | 7873.3333 | 10000 | 8839.1004 | 0 | 0
2019-09-05 17:00 | 1341.8593 | 418.7115 | 9060 | 10000 | 8136.8522 | 0 | 0
2019-09-05 18:00 | 1516.3276 | 0 | 9060 | 10000 | 7543.6724 | 0 | 0
2019-09-05 19:00 | 1788.7363 | 0 | 9060 | 10000 | 7271.2637 | 0 | 0
2019-09-05 20:00 | 1697.0916 | 0 | 4266.6667 | 10000 | 2569.5751 | 0 | 0
2019-09-05 21:00 | 1361.1541 | 0 | 2773.3333 | 10000 | 1412.1793 | 0 | 0
2019-09-05 22:00 | 1034.6953 | 0 | 2773.3333 | 10000 | 1738.638 | 0 | 0
2019-09-05 23:00 | 696.8921 | 0 | 1666.6667 | 10000 | 969.7746 | 0 | 0
2019-09-06 | 566.5941 | 0 | 1666.6667 | 10000 | 1100.0725 | 0 | 0
2019-09-06 01:00 | 506.5827 | 0 | 1666.6667 | 10000 | 1160.084 | 0 | 0
2019-09-06 02:00 | 500.2025 | 0 | 0 | 10000 | -500.2025 | -500.2025 | 0
2019-09-06 03:00 | 508.2813 | 0 | 873.3333 | 9499.7975 | 365.052 | 365.052 | 0
2019-09-06 04:00 | 569.9575 | 0 | 286.6667 | 9864.8495 | -283.2908 | -283.2908 | 0
2019-09-06 05:00 | 759.5104 | 76.5152 | 286.6667 | 9581.5587 | -396.3285 | -396.3285 | 0
2019-09-06 06:00 | 1036.2043 | 1455.9299 | 0 | 9185.2302 | 419.7256 | 419.7256 | 0
2019-09-06 07:00 | 966.6075 | 3676.55 | 0 | 9604.9559 | 2709.9425 | 395.0441 | 0
2019-09-06 08:00 | 837.3074 | 5602.7551 | 286.6667 | 10000 | 5052.1144 | 0 | 0
2019-09-06 09:00 | 828.7399 | 6945.4733 | 1666.6667 | 10000 | 7783.4 | 0 | 0
2019-09-06 10:00 | 832.0413 | 7782.2144 | 1666.6667 | 10000 | 8616.8398 | 0 | 0
2019-09-06 11:00 | 815.08 | 8124.0301 | 2773.3333 | 10000 | 10082.2835 | 0 | 0
2019-09-06 12:00 | 791.1673 | 7964.5193 | 873.3333 | 10000 | 8046.6854 | 0 | 0
2019-09-06 13:00 | 781.2959 | 7290.6251 | 873.3333 | 10000 | 7382.6625 | 0 | 0
2019-09-06 14:00 | 807.2392 | 6144.7133 | 0 | 10000 | 5337.4741 | 0 | 0
2019-09-06 15:00 | 929.603 | 4474.5074 | 0 | 10000 | 3544.9044 | 0 | 0
2019-09-06 16:00 | 1158.5647 | 2341.753 | 0 | 10000 | 1183.1884 | 0 | 0
2019-09-06 17:00 | 1341.8593 | 413.9862 | 0 | 10000 | -927.8731 | -927.8731 | 0
2019-09-06 18:00 | 1516.3276 | 0 | 0 | 9072.1269 | -1516.3276 | -1516.3276 | 0
2019-09-06 19:00 | 1788.7363 | 0 | 286.6667 | 7555.7992 | -1502.0696 | -1502.0696 | 0
2019-09-06 20:00 | 1697.0916 | 0 | 873.3333 | 6053.7296 | -823.7582 | -823.7582 | 0
2019-09-06 21:00 | 1361.1541 | 0 | 286.6667 | 5229.9714 | -1074.4874 | -1074.4874 | 0
2019-09-06 22:00 | 1034.6953 | 0 | 0 | 4155.484 | -1034.6953 | -1034.6953 | 0
2019-09-06 23:00 | 696.8921 | 0 | 286.6667 | 3120.7887 | -410.2254 | -410.2254 | 0
2019-09-07 | 574.1877 | 0 | 286.6667 | 2710.5633 | -287.5211 | -287.5211 | 0
2019-09-07 01:00 | 529.3589 | 0 | 873.3333 | 2423.0422 | 343.9744 | 343.9744 | 0
2019-09-07 02:00 | 524.6515 | 0 | 286.6667 | 2767.0166 | -237.9848 | -237.9848 | 0
2019-09-07 03:00 | 530.336 | 0 | 2773.3333 | 2529.0318 | 2242.9973 | 2242.9973 | 0
2019-09-07 04:00 | 594.0815 | 0 | 1666.6667 | 4772.0292 | 1072.5852 | 1072.5852 | 0
2019-09-07 05:00 | 780.2832 | 65.1555 | 0 | 5844.6143 | -715.1276 | -715.1276 | 0
2019-09-07 06:00 | 1050.2159 | 1064.5872 | 1666.6667 | 5129.4867 | 1681.0379 | 1681.0379 | 0
2019-09-07 07:00 | 972.9603 | 3605.511 | 873.3333 | 6810.5246 | 3505.884 | 3189.4754 | 0
2019-09-07 08:00 | 839.219 | 5478.7368 | 873.3333 | 10000 | 5512.8511 | 0 | 0
2019-09-07 09:00 | 821.9941 | 5794.5165 | 873.3333 | 10000 | 5845.8557 | 0 | 0
2019-09-07 10:00 | 832.0413 | 6553.1991 | 2773.3333 | 10000 | 8494.4911 | 0 | 0
2019-09-07 11:00 | 815.08 | 6430.7218 | 2773.3333 | 10000 | 8388.9752 | 0 | 0
2019-09-07 12:00 | 791.1673 | 6584.2813 | 4266.6667 | 10000 | 10059.7807 | 0 | 0
2019-09-07 13:00 | 781.2959 | 5500.4132 | 4266.6667 | 10000 | 8985.784 | 0 | 0
2019-09-07 14:00 | 807.2392 | 5474.7509 | 1666.6667 | 10000 | 6334.1784 | 0 | 0
2019-09-07 15:00 | 929.603 | 4005.5098 | 1666.6667 | 10000 | 4742.5734 | 0 | 0
2019-09-07 16:00 | 1158.5647 | 2013.8949 | 2773.3333 | 10000 | 3628.6636 | 0 | 0
2019-09-07 17:00 | 1341.8593 | 377.2322 | 873.3333 | 10000 | -91.2938 | -91.2938 | 0
2019-09-07 18:00 | 1516.3276 | 0 | 2773.3333 | 9908.7062 | 1257.0057 | 91.2938 | 0
2019-09-07 19:00 | 1788.7363 | 0 | 4266.6667 | 10000 | 2477.9304 | 0 | 0
2019-09-07 20:00 | 1697.0916 | 0 | 0 | 10000 | -1697.0916 | -1697.0916 | 0
2019-09-07 21:00 | 1361.1541 | 0 | 286.6667 | 8302.9084 | -1074.4874 | -1074.4874 | 0
2019-09-07 22:00 | 1034.6953 | 0 | 286.6667 | 7228.421 | -748.0286 | -748.0286 | 0
2019-09-07 23:00 | 696.8921 | 0 | 873.3333 | 6480.3924 | 176.4413 | 176.4413 | 0
2019-09-08 | 566.5941 | 0 | 873.3333 | 6656.8337 | 306.7392 | 306.7392 | 0
2019-09-08 01:00 | 506.5827 | 0 | 873.3333 | 6963.5729 | 366.7507 | 366.7507 | 0
2019-09-08 02:00 | 493.7415 | 0 | 1666.6667 | 7330.3235 | 1172.9251 | 1172.9251 | 0
2019-09-08 03:00 | 493.7194 | 0 | 286.6667 | 8503.2487 | -207.0528 | -207.0528 | 0
2019-09-08 04:00 | 554.7864 | 0 | 286.6667 | 8296.1959 | -268.1197 | -268.1197 | 0
2019-09-08 05:00 | 751.6734 | 0.1909 | 873.3333 | 8028.0762 | 121.8508 | 121.8508 | 0
2019-09-08 06:00 | 1019.9166 | 990.0729 | 873.3333 | 8149.927 | 843.4897 | 843.4897 | 0
2019-09-08 07:00 | 945.0147 | 2473.0255 | 873.3333 | 8993.4167 | 2401.3442 | 1006.5833 | 0
2019-09-08 08:00 | 822.1611 | 3326.9258 | 2773.3333 | 10000 | 5278.098 | 0 | 0
2019-09-08 09:00 | 816.1489 | 4720.4717 | 873.3333 | 10000 | 4777.6561 | 0 | 0
2019-09-08 10:00 | 832.0413 | 6159.9474 | 873.3333 | 10000 | 6201.2394 | 0 | 0
2019-09-08 11:00 | 815.08 | 6192.9202 | 1666.6667 | 10000 | 7044.5069 | 0 | 0
2019-09-08 12:00 | 791.1673 | 6323.8247 | 4266.6667 | 10000 | 9799.3241 | 0 | 0
2019-09-08 13:00 | 781.2959 | 5537.9457 | 1666.6667 | 10000 | 6423.3165 | 0 | 0
2019-09-08 14:00 | 807.2392 | 4298.0146 | 1666.6667 | 10000 | 5157.4421 | 0 | 0
2019-09-08 15:00 | 929.603 | 3572.3968 | 873.3333 | 10000 | 3516.1271 | 0 | 0
2019-09-08 16:00 | 1158.5647 | 888.4152 | 873.3333 | 10000 | 603.1839 | 0 | 0
2019-09-08 17:00 | 1341.8593 | 299.2369 | 1666.6667 | 10000 | 624.0442 | 0 | 0
2019-09-08 18:00 | 1516.3276 | 0 | 1666.6667 | 10000 | 150.339 | 0 | 0
2019-09-08 19:00 | 1788.7363 | 0 | 1666.6667 | 10000 | -122.0696 | -122.0696 | 0
2019-09-08 20:00 | 1697.0916 | 0 | 873.3333 | 9877.9304 | -823.7582 | -823.7582 | 0
2019-09-08 21:00 | 1361.1541 | 0 | 286.6667 | 9054.1721 | -1074.4874 | -1074.4874 | 0
2019-09-08 22:00 | 1034.6953 | 0 | 286.6667 | 7979.6847 | -748.0286 | -748.0286 | 0
2019-09-08 23:00 | 696.8921 | 0 | 286.6667 | 7231.6561 | -410.2254 | -410.2254 | 0
2019-09-09 | 572.6371 | 0 | 1666.6667 | 6821.4307 | 1094.0295 | 1094.0295 | 0
2019-09-09 01:00 | 519.3267 | 0 | 873.3333 | 7915.4602 | 354.0067 | 354.0067 | 0
2019-09-09 02:00 | 519.0204 | 0 | 873.3333 | 8269.4669 | 354.313 | 354.313 | 0
2019-09-09 03:00 | 529.8632 | 0 | 873.3333 | 8623.7798 | 343.4701 | 343.4701 | 0
2019-09-09 04:00 | 591.3111 | 0 | 286.6667 | 8967.25 | -304.6444 | -304.6444 | 0
2019-09-09 05:00 | 786.2479 | 0 | 873.3333 | 8662.6055 | 87.0854 | 87.0854 | 0
2019-09-09 06:00 | 1069.5569 | 405.6751 | 873.3333 | 8749.6909 | 209.4516 | 209.4516 | 0
2019-09-09 07:00 | 1003.6735 | 1310.9885 | 873.3333 | 8959.1426 | 1180.6483 | 1040.8574 | 0
2019-09-09 08:00 | 885.0327 | 4090.7087 | 286.6667 | 10000 | 3492.3427 | 0 | 0
2019-09-09 09:00 | 877.5491 | 2930.2299 | 873.3333 | 10000 | 2926.0142 | 0 | 0
2019-09-09 10:00 | 890.2934 | 6043.1488 | 873.3333 | 10000 | 6026.1887 | 0 | 0
2019-09-09 11:00 | 868.1401 | 6179.1995 | 1666.6667 | 10000 | 6977.7261 | 0 | 0
2019-09-09 12:00 | 839.5413 | 6708.9988 | 873.3333 | 10000 | 6742.7908 | 0 | 0
2019-09-09 13:00 | 824.7175 | 6767.474 | 873.3333 | 10000 | 6816.0898 | 0 | 0
2019-09-09 14:00 | 848.3673 | 5379.953 | 873.3333 | 10000 | 5404.919 | 0 | 0
2019-09-09 15:00 | 969.4648 | 3872.9711 | 286.6667 | 10000 | 3190.173 | 0 | 0
2019-09-09 16:00 | 1197.7983 | 1711.2713 | 0 | 10000 | 513.473 | 0 | 0
2019-09-09 17:00 | 1379.937 | 365.1802 | 0 | 10000 | -1014.7568 | -1014.7568 | 0
2019-09-09 18:00 | 1554.3325 | 0 | 0 | 8985.2432 | -1554.3325 | -1554.3325 | 0
2019-09-09 19:00 | 1827.4188 | 0 | 0 | 7430.9107 | -1827.4188 | -1827.4188 | 0
2019-09-09 20:00 | 1736.6081 | 0 | 286.6667 | 5603.4919 | -1449.9414 | -1449.9414 | 0
2019-09-09 21:00 | 1392.5539 | 0 | 873.3333 | 4153.5504 | -519.2206 | -519.2206 | 0
2019-09-09 22:00 | 1051.9359 | 0 | 286.6667 | 3634.3298 | -765.2692 | -765.2692 | 0
2019-09-09 23:00 | 704.1876 | 0 | 873.3333 | 2869.0606 | 169.1458 | 169.1458 | 0
2019-09-10 | 570.9746 | 0 | 286.6667 | 3038.2064 | -284.3079 | -284.3079 | 0
2019-09-10 01:00 | 509.4806 | 0 | 873.3333 | 2753.8985 | 363.8527 | 363.8527 | 0
2019-09-10 02:00 | 501.9828 | 0 | 286.6667 | 3117.7512 | -215.3162 | -215.3162 | 0
2019-09-10 03:00 | 509.8418 | 0 | 873.3333 | 2902.435 | 363.4915 | 363.4915 | 0
2019-09-10 04:00 | 569.7853 | 0 | 873.3333 | 3265.9266 | 303.548 | 303.548 | 0
2019-09-10 05:00 | 765.0555 | 50.9945 | 286.6667 | 3569.4746 | -427.3944 | -427.3944 | 0
2019-09-10 06:00 | 1048.0805 | 1400.4758 | 873.3333 | 3142.0802 | 1225.7286 | 1225.7286 | 0
2019-09-10 07:00 | 985.5895 | 2238.5026 | 873.3333 | 4367.8088 | 2126.2464 | 2126.2464 | 0
2019-09-10 08:00 | 872.1367 | 4954.1471 | 1666.6667 | 6494.0553 | 5748.6771 | 3505.9447 | 0
2019-09-10 09:00 | 872.6558 | 5737.3281 | 1666.6667 | 10000 | 6531.339 | 0 | 0
2019-09-10 10:00 | 890.2934 | 5811.8976 | 873.3333 | 10000 | 5794.9375 | 0 | 0
2019-09-10 11:00 | 868.1401 | 6288.5208 | 2773.3333 | 10000 | 8193.714 | 0 | 0
2019-09-10 12:00 | 839.5413 | 6214.9438 | 1666.6667 | 10000 | 7042.0692 | 0 | 0
2019-09-10 13:00 | 824.7175 | 4942.7011 | 873.3333 | 10000 | 4991.317 | 0 | 0
2019-09-10 14:00 | 848.3673 | 4655.139 | 0 | 10000 | 3806.7717 | 0 | 0
2019-09-10 15:00 | 969.4648 | 3423.6282 | 286.6667 | 10000 | 2740.8301 | 0 | 0
2019-09-10 16:00 | 1197.7983 | 1780.8233 | 0 | 10000 | 583.025 | 0 | 0
2019-09-10 17:00 | 1379.937 | 291.617 | 0 | 10000 | -1088.32 | -1088.32 | 0
2019-09-10 18:00 | 1554.3325 | 0 | 0 | 8911.68 | -1554.3325 | -1554.3325 | 0
2019-09-10 19:00 | 1827.4188 | 0 | 0 | 7357.3475 | -1827.4188 | -1827.4188 | 0
2019-09-10 20:00 | 1736.6081 | 0 | 286.6667 | 5529.9287 | -1449.9414 | -1449.9414 | 0
2019-09-10 21:00 | 1392.5539 | 0 | 873.3333 | 4079.9872 | -519.2206 | -519.2206 | 0
2019-09-10 22:00 | 1051.9359 | 0 | 873.3333 | 3560.7666 | -178.6026 | -178.6026 | 0
2019-09-10 23:00 | 704.1876 | 0 | 2773.3333 | 3382.1641 | 2069.1458 | 2069.1458 | 0
2019-09-11 | 566.5941 | 0 | 1666.6667 | 5451.3099 | 1100.0725 | 1100.0725 | 0
2019-09-11 01:00 | 506.5827 | 0 | 1666.6667 | 6551.3824 | 1160.084 | 1160.084 | 0
2019-09-11 02:00 | 493.7415 | 0 | 1666.6667 | 7711.4664 | 1172.9251 | 1172.9251 | 0
2019-09-11 03:00 | 492.1242 | 0 | 2773.3333 | 8884.3915 | 2281.2091 | 1115.6085 | 0
2019-09-11 04:00 | 546.7972 | 0 | 1666.6667 | 10000 | 1119.8695 | 0 | 0
2019-09-11 05:00 | 740.6854 | 0 | 873.3333 | 10000 | 132.6479 | 0 | 0
2019-09-11 06:00 | 1012.2696 | 59.0145 | 2773.3333 | 10000 | 1820.0783 | 0 | 0
2019-09-11 07:00 | 942.7518 | 532.412 | 2773.3333 | 10000 | 2362.9936 | 0 | 0
2019-09-11 08:00 | 822.1611 | 622.6733 | 1666.6667 | 10000 | 1467.1788 | 0 | 0
2019-09-11 09:00 | 816.1489 | 791.8992 | 1666.6667 | 10000 | 1642.4169 | 0 | 0
2019-09-11 10:00 | 832.0413 | 1537.2705 | 873.3333 | 10000 | 1578.5626 | 0 | 0
2019-09-11 11:00 | 815.08 | 2054.1587 | 286.6667 | 10000 | 1525.7454 | 0 | 0
2019-09-11 12:00 | 791.1673 | 2680.0462 | 0 | 10000 | 1888.879 | 0 | 0
2019-09-11 13:00 | 781.2959 | 2359.685 | 0 | 10000 | 1578.3891 | 0 | 0
2019-09-11 14:00 | 807.2392 | 1963.1903 | 286.6667 | 10000 | 1442.6178 | 0 | 0
2019-09-11 15:00 | 929.603 | 389.16 | 873.3333 | 10000 | 332.8903 | 0 | 0
2019-09-11 16:00 | 1158.5647 | 76.989 | 873.3333 | 10000 | -208.2423 | -208.2423 | 0
2019-09-11 17:00 | 1341.8593 | 38.9045 | 873.3333 | 9791.7577 | -429.6215 | -429.6215 | 0
2019-09-11 18:00 | 1516.3276 | 0 | 873.3333 | 9362.1362 | -642.9943 | -642.9943 | 0
2019-09-11 19:00 | 1788.7363 | 0 | 873.3333 | 8719.1419 | -915.403 | -915.403 | 0
2019-09-11 20:00 | 1697.0916 | 0 | 286.6667 | 7803.7389 | -1410.4249 | -1410.4249 | 0
2019-09-11 21:00 | 1361.1541 | 0 | 286.6667 | 6393.3141 | -1074.4874 | -1074.4874 | 0
2019-09-11 22:00 | 1034.6953 | 0 | 286.6667 | 5318.8267 | -748.0286 | -748.0286 | 0
2019-09-11 23:00 | 696.8921 | 0 | 286.6667 | 4570.798 | -410.2254 | -410.2254 | 0
2019-09-12 | 566.5941 | 0 | 0 | 4160.5726 | -566.5941 | -566.5941 | 0
2019-09-12 01:00 | 514.9565 | 0 | 0 | 3593.9785 | -514.9565 | -514.9565 | 0
2019-09-12 02:00 | 509.9256 | 0 | 0 | 3079.022 | -509.9256 | -509.9256 | 0
2019-09-12 03:00 | 517.0204 | 0 | 286.6667 | 2569.0963 | -230.3537 | -230.3537 | 0
2019-09-12 04:00 | 577.5929 | 0 | 286.6667 | 2338.7426 | -290.9262 | -290.9262 | 0
2019-09-12 05:00 | 765.4076 | 0 | 286.6667 | 2047.8164 | -478.7409 | -478.7409 | 0
2019-09-12 06:00 | 1041.0381 | 895.0404 | 0 | 1569.0755 | -145.9977 | -145.9977 | 0
2019-09-12 07:00 | 968.0568 | 428.1082 | 0 | 1423.0778 | -539.9486 | -539.9486 | 0
2019-09-12 08:00 | 836.364 | 47.1649 | 286.6667 | 883.1292 | -502.5324 | -502.5324 | 0
2019-09-12 09:00 | 822.1614 | 75.7792 | 0 | 380.5969 | -746.3821 | -380.5969 | -365.7852
2019-09-12 10:00 | 832.0413 | 719.3089 | 0 | 0 | -112.7324 | 0 | -478.5176
2019-09-12 11:00 | 815.08 | 665.321 | 286.6667 | 0 | 136.9077 | 136.9077 | -341.6099
2019-09-12 12:00 | 791.1673 | 924.8599 | 873.3333 | 136.9077 | 1007.026 | 1007.026 | 0
2019-09-12 13:00 | 781.2959 | 1095.6004 | 873.3333 | 1143.9337 | 1187.6378 | 1187.6378 | 0
2019-09-12 14:00 | 807.2392 | 1029.534 | 2773.3333 | 2331.5715 | 2995.6282 | 2995.6282 | 0
2019-09-12 15:00 | 929.603 | 510.0181 | 2773.3333 | 5327.1997 | 2353.7484 | 2353.7484 | 0
2019-09-12 16:00 | 1158.5647 | 76.2484 | 4266.6667 | 7680.9481 | 3184.3505 | 2319.0519 | 0
2019-09-12 17:00 | 1341.8593 | 0 | 873.3333 | 10000 | -468.526 | -468.526 | 0
2019-09-12 18:00 | 1516.3276 | 0 | 873.3333 | 9531.474 | -642.9943 | -642.9943 | 0
2019-09-12 19:00 | 1788.7363 | 0 | 873.3333 | 8888.4797 | -915.403 | -915.403 | 0
2019-09-12 20:00 | 1697.0916 | 0 | 1666.6667 | 7973.0767 | -30.4249 | -30.4249 | 0
2019-09-12 21:00 | 1361.1541 | 0 | 286.6667 | 7942.6518 | -1074.4874 | -1074.4874 | 0
2019-09-12 22:00 | 1034.6953 | 0 | 286.6667 | 6868.1644 | -748.0286 | -748.0286 | 0
2019-09-12 23:00 | 696.8921 | 0 | 873.3333 | 6120.1358 | 176.4413 | 176.4413 | 0
2019-09-13 | 566.5941 | 0 | 286.6667 | 6296.5771 | -279.9275 | -279.9275 | 0
2019-09-13 01:00 | 506.5827 | 0 | 873.3333 | 6016.6496 | 366.7507 | 366.7507 | 0
2019-09-13 02:00 | 493.7415 | 0 | 873.3333 | 6383.4003 | 379.5918 | 379.5918 | 0
2019-09-13 03:00 | 495.7492 | 0 | 873.3333 | 6762.9921 | 377.5842 | 377.5842 | 0
2019-09-13 04:00 | 557.5622 | 0 | 873.3333 | 7140.5762 | 315.7712 | 315.7712 | 0
2019-09-13 05:00 | 746.9951 | 0 | 873.3333 | 7456.3474 | 126.3382 | 126.3382 | 0
2019-09-13 06:00 | 1019.627 | 562.8295 | 0 | 7582.6856 | -456.7974 | -456.7974 | 0
2019-09-13 07:00 | 946.8923 | 1497.4978 | 0 | 7125.8882 | 550.6055 | 550.6055 | 0
2019-09-13 08:00 | 822.1611 | 1992.4244 | 0 | 7676.4937 | 1170.2633 | 1170.2633 | 0
2019-09-13 09:00 | 816.1489 | 6537.4234 | 286.6667 | 8846.757 | 6007.9411 | 1153.243 | 0
2019-09-13 10:00 | 832.0413 | 7223.0017 | 286.6667 | 10000 | 6677.627 | 0 | 0
2019-09-13 11:00 | 815.08 | 7499.5824 | 873.3333 | 10000 | 7557.8358 | 0 | 0
2019-09-13 12:00 | 791.1673 | 7320.4779 | 873.3333 | 10000 | 7402.644 | 0 | 0
2019-09-13 13:00 | 781.2959 | 6654.5095 | 873.3333 | 10000 | 6746.5469 | 0 | 0
2019-09-13 14:00 | 807.2392 | 5452.6778 | 1666.6667 | 10000 | 6312.1053 | 0 | 0
2019-09-13 15:00 | 1012.7042 | 2094.6146 | 873.3333 | 10000 | 1955.2438 | 0 | 0
2019-09-13 16:00 | 1385.2061 | 602.0687 | 286.6667 | 10000 | -496.4707 | -496.4707 | 0
2019-09-13 17:00 | 1572.9978 | 65.366 | 0 | 9503.5293 | -1507.6318 | -1507.6318 | 0
2019-09-13 18:00 | 1739.1109 | 0 | 0 | 7995.8975 | -1739.1109 | -1739.1109 | 0
2019-09-13 19:00 | 1992.4794 | 0 | 286.6667 | 6256.7866 | -1705.8127 | -1705.8127 | 0
2019-09-13 20:00 | 1831.4478 | 0 | 2773.3333 | 4550.9739 | 941.8855 | 941.8855 | 0
2019-09-13 21:00 | 1395.8203 | 0 | 286.6667 | 5492.8594 | -1109.1537 | -1109.1537 | 0
2019-09-13 22:00 | 1034.6953 | 0 | 873.3333 | 4383.7057 | -161.362 | -161.362 | 0
2019-09-13 23:00 | 696.8921 | 0 | 873.3333 | 4222.3438 | 176.4413 | 176.4413 | 0
2019-09-14 | 566.5941 | 0 | 4266.6667 | 4398.785 | 3700.0725 | 3700.0725 | 0
2019-09-14 01:00 | 506.5827 | 0 | 1666.6667 | 8098.8576 | 1160.084 | 1160.084 | 0
2019-09-14 02:00 | 493.7415 | 0 | 2773.3333 | 9258.9416 | 2279.5918 | 741.0584 | 0
2019-09-14 03:00 | 492.1242 | 0 | 0 | 10000 | -492.1242 | -492.1242 | 0
2019-09-14 04:00 | 546.7972 | 0 | 0 | 9507.8758 | -546.7972 | -546.7972 | 0
2019-09-14 05:00 | 735.5954 | 0 | 873.3333 | 8961.0786 | 137.7379 | 137.7379 | 0
2019-09-14 06:00 | 1012.2696 | 938.6461 | 873.3333 | 9098.8166 | 799.7099 | 799.7099 | 0
2019-09-14 07:00 | 942.7518 | 2991.181 | 873.3333 | 9898.5264 | 2921.7626 | 101.4736 | 0
2019-09-14 08:00 | 822.1611 | 5285.653 | 2773.3333 | 10000 | 7236.8252 | 0 | 0
2019-09-14 09:00 | 816.1489 | 6605.8967 | 4266.6667 | 10000 | 10056.4144 | 0 | 0
2019-09-14 10:00 | 832.0413 | 7364.01 | 2773.3333 | 10000 | 9305.3021 | 0 | 0
2019-09-14 11:00 | 865.8044 | 7627.1116 | 6160 | 10000 | 12921.3073 | 0 | 0
2019-09-14 12:00 | 1044.454 | 7409.1084 | 4266.6667 | 10000 | 10631.3211 | 0 | 0
2019-09-14 13:00 | 1263.7279 | 6754.9574 | 4266.6667 | 10000 | 9757.8962 | 0 | 0
2019-09-14 14:00 | 1427.2647 | 5575.0896 | 1666.6667 | 10000 | 5814.4916 | 0 | 0
2019-09-14 15:00 | 1586.2999 | 2797.8373 | 1666.6667 | 10000 | 2878.2041 | 0 | 0
2019-09-14 16:00 | 1932.7818 | 1761.1054 | 1666.6667 | 10000 | 1494.9902 | 0 | 0
2019-09-14 17:00 | 1925.6861 | 218.132 | 7873.3333 | 10000 | 6165.7792 | 0 | 0
2019-09-14 18:00 | 1980.5814 | 0 | 1666.6667 | 10000 | -313.9148 | -313.9148 | 0
2019-09-14 19:00 | 2198.8694 | 0 | 873.3333 | 9686.0852 | -1325.5361 | -1325.5361 | 0
2019-09-14 20:00 | 2004.0054 | 0 | 0 | 8360.5492 | -2004.0054 | -2004.0054 | 0
2019-09-14 21:00 | 1549.2909 | 0 | 0 | 6356.5438 | -1549.2909 | -1549.2909 | 0
2019-09-14 22:00 | 1125.6211 | 0 | 286.6667 | 4807.2529 | -838.9545 | -838.9545 | 0
2019-09-14 23:00 | 696.8921 | 0 | 286.6667 | 3968.2985 | -410.2254 | -410.2254 | 0
2019-09-15 | 566.5941 | 0 | 0 | 3558.0731 | -566.5941 | -566.5941 | 0
2019-09-15 01:00 | 506.5827 | 0 | 0 | 2991.4789 | -506.5827 | -506.5827 | 0
2019-09-15 02:00 | 493.7415 | 0 | 0 | 2484.8963 | -493.7415 | -493.7415 | 0
2019-09-15 03:00 | 492.1242 | 0 | 0 | 1991.1547 | -492.1242 | -492.1242 | 0
2019-09-15 04:00 | 546.7972 | 0 | 0 | 1499.0305 | -546.7972 | -546.7972 | 0
2019-09-15 05:00 | 735.5954 | 0 | 0 | 952.2334 | -735.5954 | -735.5954 | 0
2019-09-15 06:00 | 1012.2696 | 1246.7794 | 286.6667 | 216.638 | 521.1765 | 521.1765 | 0
2019-09-15 07:00 | 942.7518 | 3364.9425 | 286.6667 | 737.8144 | 2708.8574 | 2708.8574 | 0
2019-09-15 08:00 | 822.1611 | 5208.5317 | 0 | 3446.6719 | 4386.3706 | 4386.3706 | 0
2019-09-15 09:00 | 816.1489 | 6556.3386 | 286.6667 | 7833.0424 | 6026.8563 | 2166.9576 | 0
2019-09-15 10:00 | 832.0413 | 7335.9696 | 286.6667 | 10000 | 6790.595 | 0 | 0
2019-09-15 11:00 | 815.08 | 7665.21 | 1666.6667 | 10000 | 8516.7967 | 0 | 0
2019-09-15 12:00 | 791.1673 | 7474.203 | 1666.6667 | 10000 | 8349.7025 | 0 | 0
2019-09-15 13:00 | 846.4903 | 6780.178 | 1666.6667 | 10000 | 7600.3544 | 0 | 0
2019-09-15 14:00 | 943.7595 | 5623.9807 | 1666.6667 | 10000 | 6346.8879 | 0 | 0
2019-09-15 15:00 | 1119.2132 | 3925.1075 | 0 | 10000 | 2805.8943 | 0 | 0
2019-09-15 16:00 | 1415.0177 | 1843.9951 | 0 | 10000 | 428.9774 | 0 | 0
2019-09-15 17:00 | 1599.6242 | 218.876 | 873.3333 | 10000 | -507.4149 | -507.4149 | 0
2019-09-15 18:00 | 1764.5042 | 0 | 0 | 9492.5851 | -1764.5042 | -1764.5042 | 0
2019-09-15 19:00 | 2003.0493 | 0 | 0 | 7728.081 | -2003.0493 | -2003.0493 | 0
2019-09-15 20:00 | 1875.3266 | 0 | 0 | 5725.0317 | -1875.3266 | -1875.3266 | 0
2019-09-15 21:00 | 1444.8648 | 0 | 0 | 3849.7051 | -1444.8648 | -1444.8648 | 0
2019-09-15 22:00 | 1034.6953 | 0 | 0 | 2404.8403 | -1034.6953 | -1034.6953 | 0
2019-09-15 23:00 | 696.8921 | 0 | 0 | 1370.145 | -696.8921 | -696.8921 | 0
2019-09-16 | 570.9746 | 0 | 0 | 673.2529 | -570.9746 | -570.9746 | 0
2019-09-16 01:00 | 509.4806 | 0 | 0 | 102.2783 | -509.4806 | -102.2783 | -407.2023
2019-09-16 02:00 | 495.2568 | 0 | 0 | 0 | -495.2568 | 0 | -902.4591
2019-09-16 03:00 | 495.0887 | 0 | 286.6667 | 0 | -208.422 | 0 | -1110.8811
2019-09-16 04:00 | 551.3437 | 0 | 0 | 0 | -551.3437 | 0 | -1662.2248
2019-09-16 05:00 | 747.3876 | 0 | 0 | 0 | -747.3876 | 0 | -2409.6124
2019-09-16 06:00 | 1035.7545 | 652.4525 | 0 | 0 | -383.302 | 0 | -2792.9144
2019-09-16 07:00 | 978.7508 | 261.3076 | 0 | 0 | -717.4432 | 0 | -3510.3576
2019-09-16 08:00 | 872.1367 | 633.5948 | 0 | 0 | -238.5419 | 0 | -3748.8994
2019-09-16 09:00 | 872.6558 | 787.8339 | 0 | 0 | -84.8219 | 0 | -3833.7213
2019-09-16 10:00 | 890.2934 | 2509.4541 | 0 | 0 | 1619.1607 | 1619.1607 | -2214.5606
2019-09-16 11:00 | 868.1401 | 2623.3397 | 0 | 1619.1607 | 1755.1996 | 1755.1996 | 0
2019-09-16 12:00 | 839.5413 | 2327.1676 | 0 | 3374.3603 | 1487.6263 | 1487.6263 | 0
2019-09-16 13:00 | 824.7175 | 2077.0265 | 0 | 4861.9866 | 1252.309 | 1252.309 | 0
2019-09-16 14:00 | 848.3673 | 3231.4828 | 286.6667 | 6114.2955 | 2669.7821 | 2669.7821 | 0
2019-09-16 15:00 | 969.4648 | 1826.0735 | 286.6667 | 8784.0776 | 1143.2754 | 1143.2754 | 0
2019-09-16 16:00 | 1197.7983 | 1199.956 | 286.6667 | 9927.353 | 288.8244 | 72.647 | 0
2019-09-16 17:00 | 1379.937 | 209.1332 | 0 | 10000 | -1170.8037 | -1170.8037 | 0
2019-09-16 18:00 | 1554.3325 | 0 | 0 | 8829.1963 | -1554.3325 | -1554.3325 | 0
2019-09-16 19:00 | 1827.4188 | 0 | 0 | 7274.8638 | -1827.4188 | -1827.4188 | 0
2019-09-16 20:00 | 1736.6081 | 0 | 0 | 5447.4449 | -1736.6081 | -1736.6081 | 0
2019-09-16 21:00 | 1392.5539 | 0 | 0 | 3710.8368 | -1392.5539 | -1392.5539 | 0
2019-09-16 22:00 | 1051.9359 | 0 | 0 | 2318.2829 | -1051.9359 | -1051.9359 | 0
2019-09-16 23:00 | 704.1876 | 0 | 0 | 1266.347 | -704.1876 | -704.1876 | 0
2019-09-17 | 570.9746 | 0 | 0 | 562.1594 | -570.9746 | -562.1594 | -8.8151
2019-09-17 01:00 | 509.4806 | 0 | 0 | 0 | -509.4806 | 0 | -518.2957
2019-09-17 02:00 | 495.2568 | 0 | 0 | 0 | -495.2568 | 0 | -1013.5526
2019-09-17 03:00 | 495.0887 | 0 | 0 | 0 | -495.0887 | 0 | -1508.6413
2019-09-17 04:00 | 551.3437 | 0 | 0 | 0 | -551.3437 | 0 | -2059.9849
2019-09-17 05:00 | 747.3876 | 0 | 0 | 0 | -747.3876 | 0 | -2807.3726
2019-09-17 06:00 | 1035.7545 | 217.9963 | 0 | 0 | -817.7582 | 0 | -3625.1307
2019-09-17 07:00 | 978.7508 | 850.034 | 0 | 0 | -128.7168 | 0 | -3753.8475
2019-09-17 08:00 | 872.1367 | 1956.8584 | 0 | 0 | 1084.7217 | 1084.7217 | -2669.1258
2019-09-17 09:00 | 872.7539 | 2422.705 | 0 | 1084.7217 | 1549.9511 | 1549.9511 | -34.4529
2019-09-17 10:00 | 890.2934 | 2983.33 | 0 | 2634.6729 | 2093.0366 | 2093.0366 | 0
2019-09-17 11:00 | 868.1401 | 3720.043 | 0 | 4727.7094 | 2851.9029 | 2851.9029 | 0
2019-09-17 12:00 | 839.5413 | 2361.3904 | 286.6667 | 7579.6123 | 1808.5158 | 1808.5158 | 0
2019-09-17 13:00 | 824.7175 | 1376.9157 | 286.6667 | 9388.1281 | 838.8648 | 611.8719 | 0
2019-09-17 14:00 | 848.3673 | 2146.0265 | 873.3333 | 10000 | 2170.9925 | 0 | 0
2019-09-17 15:00 | 969.4648 | 693.4132 | 873.3333 | 10000 | 597.2817 | 0 | 0
2019-09-17 16:00 | 1197.7983 | 281.8627 | 873.3333 | 10000 | -42.6023 | -42.6023 | 0
2019-09-17 17:00 | 1379.937 | 180.5845 | 286.6667 | 9957.3977 | -912.6858 | -912.6858 | 0
2019-09-17 18:00 | 1554.3325 | 0 | 0 | 9044.7119 | -1554.3325 | -1554.3325 | 0
2019-09-17 19:00 | 1827.4188 | 0 | 0 | 7490.3794 | -1827.4188 | -1827.4188 | 0
2019-09-17 20:00 | 1736.6081 | 0 | 0 | 5662.9606 | -1736.6081 | -1736.6081 | 0
2019-09-17 21:00 | 1392.5539 | 0 | 0 | 3926.3525 | -1392.5539 | -1392.5539 | 0
2019-09-17 22:00 | 1051.9359 | 0 | 0 | 2533.7985 | -1051.9359 | -1051.9359 | 0
2019-09-17 23:00 | 704.1876 | 0 | 286.6667 | 1481.8627 | -417.5209 | -417.5209 | 0
2019-09-18 | 566.5941 | 0 | 0 | 1064.3418 | -566.5941 | -566.5941 | 0
2019-09-18 01:00 | 506.5827 | 0 | 0 | 497.7476 | -506.5827 | -497.7476 | -8.8351
2019-09-18 02:00 | 493.7415 | 0 | 0 | 0 | -493.7415 | 0 | -502.5766
2019-09-18 03:00 | 492.1242 | 0 | 0 | 0 | -492.1242 | 0 | -994.7008
2019-09-18 04:00 | 546.7972 | 0 | 0 | 0 | -546.7972 | 0 | -1541.4979
2019-09-18 05:00 | 735.5954 | 0 | 0 | 0 | -735.5954 | 0 | -2277.0934
2019-09-18 06:00 | 1012.2696 | 1266.1189 | 0 | 0 | 253.8494 | 253.8494 | -2023.244
2019-09-18 07:00 | 942.7518 | 3454.6287 | 0 | 253.8494 | 2511.877 | 2511.877 | 0
2019-09-18 08:00 | 822.1611 | 5322.4564 | 286.6667 | 2765.7263 | 4786.962 | 4786.962 | 0
2019-09-18 09:00 | 816.1489 | 6680.4627 | 286.6667 | 7552.6883 | 6150.9804 | 2447.3117 | 0
2019-09-18 10:00 | 832.0413 | 7421.6101 | 286.6667 | 10000 | 6876.2355 | 0 | 0
2019-09-18 11:00 | 815.08 | 7641.9363 | 873.3333 | 10000 | 7700.1897 | 0 | 0
2019-09-18 12:00 | 791.1673 | 7342.9202 | 873.3333 | 10000 | 7425.0863 | 0 | 0
2019-09-18 13:00 | 790.4769 | 6597.8225 | 873.3333 | 10000 | 6680.679 | 0 | 0
2019-09-18 14:00 | 904.1572 | 1607.7598 | 286.6667 | 10000 | 990.2693 | 0 | 0
2019-09-18 15:00 | 1123.7581 | 1465.7382 | 0 | 10000 | 341.9802 | 0 | 0
2019-09-18 16:00 | 1365.4461 | 1768.3021 | 0 | 10000 | 402.856 | 0 | 0
2019-09-18 17:00 | 1547.7031 | 161.9418 | 873.3333 | 10000 | -512.4279 | -512.4279 | 0
2019-09-18 18:00 | 1707.2966 | 0 | 873.3333 | 9487.5721 | -833.9633 | -833.9633 | 0
2019-09-18 19:00 | 1971.9988 | 0 | 873.3333 | 8653.6088 | -1098.6655 | -1098.6655 | 0
2019-09-18 20:00 | 1823.3741 | 0 | 873.3333 | 7554.9433 | -950.0407 | -950.0407 | 0
2019-09-18 21:00 | 1386.9388 | 0 | 873.3333 | 6604.9026 | -513.6055 | -513.6055 | 0
2019-09-18 22:00 | 1034.6953 | 0 | 873.3333 | 6091.2971 | -161.362 | -161.362 | 0
2019-09-18 23:00 | 696.8921 | 0 | 873.3333 | 5929.9351 | 176.4413 | 176.4413 | 0
2019-09-19 | 566.5941 | 0 | 286.6667 | 6106.3764 | -279.9275 | -279.9275 | 0
2019-09-19 01:00 | 506.5827 | 0 | 286.6667 | 5826.4489 | -219.916 | -219.916 | 0
2019-09-19 02:00 | 493.7415 | 0 | 873.3333 | 5606.5329 | 379.5918 | 379.5918 | 0
2019-09-19 03:00 | 492.1242 | 0 | 1666.6667 | 5986.1247 | 1174.5425 | 1174.5425 | 0
2019-09-19 04:00 | 546.7972 | 0 | 873.3333 | 7160.6672 | 326.5362 | 326.5362 | 0
2019-09-19 05:00 | 735.5954 | 0 | 1666.6667 | 7487.2034 | 931.0713 | 931.0713 | 0
2019-09-19 06:00 | 1012.2696 | 1339.2555 | 1666.6667 | 8418.2746 | 1993.6526 | 1581.7254 | 0
2019-09-19 07:00 | 942.7518 | 3672.9229 | 1666.6667 | 10000 | 4396.8378 | 0 | 0
2019-09-19 08:00 | 822.1611 | 5652.7583 | 1666.6667 | 10000 | 6497.2638 | 0 | 0
2019-09-19 09:00 | 816.1489 | 7040.4495 | 4266.6667 | 10000 | 10490.9672 | 0 | 0
2019-09-19 10:00 | 832.0413 | 7862.2131 | 4266.6667 | 10000 | 11296.8384 | 0 | 0
2019-09-19 11:00 | 817.1454 | 8123.9404 | 4266.6667 | 10000 | 11573.4617 | 0 | 0
2019-09-19 12:00 | 940.1958 | 7859.683 | 4266.6667 | 10000 | 11186.154 | 0 | 0
2019-09-19 13:00 | 1040.2722 | 7113.9138 | 4266.6667 | 10000 | 10340.3083 | 0 | 0
2019-09-19 14:00 | 1099.5157 | 5834.3617 | 4266.6667 | 10000 | 9001.5126 | 0 | 0
2019-09-19 15:00 | 1281.9005 | 4021.2015 | 4266.6667 | 10000 | 7005.9677 | 0 | 0
2019-09-19 16:00 | 1541.861 | 1814.3159 | 4266.6667 | 10000 | 4539.1215 | 0 | 0
2019-09-19 17:00 | 1694.1049 | 153.8631 | 4266.6667 | 10000 | 2726.4249 | 0 | 0
2019-09-19 18:00 | 1805.3188 | 0 | 2773.3333 | 10000 | 968.0145 | 0 | 0
2019-09-19 19:00 | 2025.0994 | 0 | 4266.6667 | 10000 | 2241.5673 | 0 | 0
2019-09-19 20:00 | 1889.7435 | 0 | 4266.6667 | 10000 | 2376.9232 | 0 | 0
2019-09-19 21:00 | 1450.1478 | 0 | 4266.6667 | 10000 | 2816.5188 | 0 | 0
2019-09-19 22:00 | 1034.6953 | 0 | 4266.6667 | 10000 | 3231.9714 | 0 | 0
2019-09-19 23:00 | 696.8921 | 0 | 4266.6667 | 10000 | 3569.7746 | 0 | 0
2019-09-20 | 566.5941 | 0 | 4266.6667 | 10000 | 3700.0725 | 0 | 0
2019-09-20 01:00 | 506.5827 | 0 | 4266.6667 | 10000 | 3760.084 | 0 | 0
2019-09-20 02:00 | 493.7415 | 0 | 6160 | 10000 | 5666.2585 | 0 | 0
2019-09-20 03:00 | 492.1242 | 0 | 7873.3333 | 10000 | 7381.2091 | 0 | 0
2019-09-20 04:00 | 546.7972 | 0 | 9060 | 10000 | 8513.2028 | 0 | 0
2019-09-20 05:00 | 735.5954 | 0 | 7873.3333 | 10000 | 7137.7379 | 0 | 0
2019-09-20 06:00 | 1012.2696 | 1278.1572 | 9573.3333 | 10000 | 9839.2209 | 0 | 0
2019-09-20 07:00 | 942.7518 | 3572.7429 | 9573.3333 | 10000 | 12203.3245 | 0 | 0
2019-09-20 08:00 | 822.1611 | 5508.7461 | 9060 | 10000 | 13746.585 | 0 | 0
2019-09-20 09:00 | 816.1489 | 6838.958 | 9060 | 10000 | 15082.8091 | 0 | 0
2019-09-20 10:00 | 832.0413 | 7654.7266 | 9060 | 10000 | 15882.6853 | 0 | 0
2019-09-20 11:00 | 867.9426 | 7929.1304 | 9573.3333 | 10000 | 16634.5211 | 0 | 0
2019-09-20 12:00 | 1054.9446 | 7673.6613 | 9573.3333 | 10000 | 16192.0501 | 0 | 0
2019-09-20 13:00 | 1147.7623 | 6904.7449 | 9573.3333 | 10000 | 15330.316 | 0 | 0
2019-09-20 14:00 | 1235.3037 | 5641.1996 | 9573.3333 | 10000 | 13979.2293 | 0 | 0
2019-09-20 15:00 | 1377.8854 | 3874.9745 | 9573.3333 | 10000 | 12070.4224 | 0 | 0
2019-09-20 16:00 | 1632.3534 | 1714.1566 | 9060 | 10000 | 9141.8032 | 0 | 0
2019-09-20 17:00 | 1537.5973 | 122.506 | 9573.3333 | 10000 | 8158.2421 | 0 | 0
2019-09-20 18:00 | 1816.0378 | 0 | 4266.6667 | 10000 | 2450.6289 | 0 | 0
2019-09-20 19:00 | 2082.6449 | 0 | 2773.3333 | 10000 | 690.6885 | 0 | 0
2019-09-20 20:00 | 1697.0916 | 0 | 4266.6667 | 10000 | 2569.5751 | 0 | 0
2019-09-20 21:00 | 1429.146 | 0 | 7873.3333 | 10000 | 6444.1873 | 0 | 0
2019-09-20 22:00 | 1034.6953 | 0 | 7873.3333 | 10000 | 6838.638 | 0 | 0
2019-09-20 23:00 | 696.8921 | 0 | 9060 | 10000 | 8363.1079 | 0 | 0
2019-09-21 | 566.5941 | 0 | 9060 | 10000 | 8493.4059 | 0 | 0
2019-09-21 01:00 | 506.5827 | 0 | 9060 | 10000 | 8553.4173 | 0 | 0
2019-09-21 02:00 | 493.7415 | 0 | 9873.3333 | 10000 | 9379.5918 | 0 | 0
2019-09-21 03:00 | 492.1242 | 0 | 9573.3333 | 10000 | 9081.2091 | 0 | 0
2019-09-21 04:00 | 546.7972 | 0 | 9873.3333 | 10000 | 9326.5362 | 0 | 0
2019-09-21 05:00 | 735.5954 | 0 | 9873.3333 | 10000 | 9137.7379 | 0 | 0
2019-09-21 06:00 | 1012.2696 | 1255.6781 | 9573.3333 | 10000 | 9816.7419 | 0 | 0
2019-09-21 07:00 | 942.7518 | 3488.6894 | 9873.3333 | 10000 | 12419.271 | 0 | 0
2019-09-21 08:00 | 822.1611 | 5426.49 | 9873.3333 | 10000 | 14477.6622 | 0 | 0
2019-09-21 09:00 | 816.1489 | 6742.2257 | 9873.3333 | 10000 | 15799.4102 | 0 | 0
2019-09-21 10:00 | 832.0413 | 7466.6337 | 9960 | 10000 | 16594.5924 | 0 | 0
2019-09-21 11:00 | 815.08 | 7728.3795 | 9873.3333 | 10000 | 16786.6329 | 0 | 0
2019-09-21 12:00 | 791.1673 | 7515.7767 | 9960 | 10000 | 16684.6094 | 0 | 0
2019-09-21 13:00 | 807.681 | 6814.8379 | 9573.3333 | 10000 | 15580.4903 | 0 | 0
2019-09-21 14:00 | 841.8024 | 5574.2225 | 9573.3333 | 10000 | 14305.7534 | 0 | 0
2019-09-21 15:00 | 967.166 | 3789.3305 | 9060 | 10000 | 11882.1645 | 0 | 0
2019-09-21 16:00 | 1158.5647 | 1670.0749 | 7873.3333 | 10000 | 8384.8435 | 0 | 0
2019-09-21 17:00 | 1397.1041 | 104.09 | 4266.6667 | 10000 | 2973.6525 | 0 | 0
2019-09-21 18:00 | 1552.7149 | 0 | 2773.3333 | 10000 | 1220.6184 | 0 | 0
2019-09-21 19:00 | 1803.0343 | 0 | 4266.6667 | 10000 | 2463.6323 | 0 | 0
2019-09-21 20:00 | 1697.0916 | 0 | 7873.3333 | 10000 | 6176.2418 | 0 | 0
2019-09-21 21:00 | 1361.1541 | 0 | 9060 | 10000 | 7698.8459 | 0 | 0
2019-09-21 22:00 | 1034.6953 | 0 | 9060 | 10000 | 8025.3047 | 0 | 0
2019-09-21 23:00 | 696.8921 | 0 | 10000 | 10000 | 9303.1079 | 0 | 0
2019-09-22 | 566.5941 | 0 | 9573.3333 | 10000 | 9006.7392 | 0 | 0
2019-09-22 01:00 | 506.5827 | 0 | 9573.3333 | 10000 | 9066.7507 | 0 | 0
2019-09-22 02:00 | 493.7415 | 0 | 9873.3333 | 10000 | 9379.5918 | 0 | 0
2019-09-22 03:00 | 493.7862 | 0 | 9060 | 10000 | 8566.2138 | 0 | 0
2019-09-22 04:00 | 557.0813 | 0 | 9060 | 10000 | 8502.9187 | 0 | 0
2019-09-22 05:00 | 758.3335 | 0 | 9060 | 10000 | 8301.6665 | 0 | 0
2019-09-22 06:00 | 1026.689 | 233.6443 | 9060 | 10000 | 8266.9553 | 0 | 0
2019-09-22 07:00 | 954.4379 | 1593.8299 | 9573.3333 | 10000 | 10212.7253 | 0 | 0
2019-09-22 08:00 | 829.0482 | 3543.5743 | 9060 | 10000 | 11774.5261 | 0 | 0
2019-09-22 09:00 | 821.3765 | 4862.3645 | 9060 | 10000 | 13100.9879 | 0 | 0
2019-09-22 10:00 | 832.0413 | 5864.5124 | 9573.3333 | 10000 | 14605.8044 | 0 | 0
2019-09-22 11:00 | 815.08 | 5675.0154 | 9873.3333 | 10000 | 14733.2688 | 0 | 0
2019-09-22 12:00 | 791.1673 | 5098.9873 | 9573.3333 | 10000 | 13881.1534 | 0 | 0
2019-09-22 13:00 | 781.2959 | 2983.9176 | 9573.3333 | 10000 | 11775.9551 | 0 | 0
2019-09-22 14:00 | 807.2392 | 2242.63 | 9573.3333 | 10000 | 11008.7241 | 0 | 0
2019-09-22 15:00 | 929.603 | 998.7474 | 9873.3333 | 10000 | 9942.4777 | 0 | 0
2019-09-22 16:00 | 1158.5647 | 724.2988 | 9573.3333 | 10000 | 9139.0674 | 0 | 0
2019-09-22 17:00 | 1341.8593 | 0 | 9573.3333 | 10000 | 8231.474 | 0 | 0
2019-09-22 18:00 | 1516.3276 | 0 | 9060 | 10000 | 7543.6724 | 0 | 0
2019-09-22 19:00 | 1788.7363 | 0 | 9060 | 10000 | 7271.2637 | 0 | 0
2019-09-22 20:00 | 1697.0916 | 0 | 9573.3333 | 10000 | 7876.2418 | 0 | 0
2019-09-22 21:00 | 1361.1541 | 0 | 6160 | 10000 | 4798.8459 | 0 | 0
2019-09-22 22:00 | 1034.6953 | 0 | 6160 | 10000 | 5125.3047 | 0 | 0
2019-09-22 23:00 | 701.6688 | 0 | 7873.3333 | 10000 | 7171.6646 | 0 | 0
2019-09-23 | 588.0833 | 0 | 4266.6667 | 10000 | 3678.5834 | 0 | 0
2019-09-23 01:00 | 536.4438 | 0 | 4266.6667 | 10000 | 3730.2229 | 0 | 0
2019-09-23 02:00 | 532.7179 | 0 | 6160 | 10000 | 5627.2821 | 0 | 0
2019-09-23 03:00 | 543.6277 | 0 | 6160 | 10000 | 5616.3723 | 0 | 0
2019-09-23 04:00 | 605.1572 | 0 | 2773.3333 | 10000 | 2168.1762 | 0 | 0
2019-09-23 05:00 | 812.7707 | 0 | 873.3333 | 10000 | 60.5627 | 0 | 0
2019-09-23 06:00 | 1087.3992 | 1008.7363 | 2773.3333 | 10000 | 2694.6705 | 0 | 0
2019-09-23 07:00 | 1019.0949 | 1615.0163 | 2773.3333 | 10000 | 3369.2547 | 0 | 0
2019-09-23 08:00 | 898.672 | 1590.8249 | 873.3333 | 10000 | 1565.4862 | 0 | 0
2019-09-23 09:00 | 893.1215 | 3810.4295 | 1666.6667 | 10000 | 4583.9747 | 0 | 0
2019-09-23 10:00 | 890.2934 | 4827.8507 | 1666.6667 | 10000 | 5604.2239 | 0 | 0
2019-09-23 11:00 | 868.1401 | 4859.9782 | 873.3333 | 10000 | 4865.1714 | 0 | 0
2019-09-23 12:00 | 839.5413 | 5918.8936 | 2773.3333 | 10000 | 7852.6856 | 0 | 0
2019-09-23 13:00 | 824.7175 | 6212.6737 | 2773.3333 | 10000 | 8161.2896 | 0 | 0
2019-09-23 14:00 | 848.3673 | 4228.811 | 286.6667 | 10000 | 3667.1104 | 0 | 0
2019-09-23 15:00 | 969.4648 | 3169.5334 | 286.6667 | 10000 | 2486.7353 | 0 | 0
2019-09-23 16:00 | 1197.7983 | 217.3603 | 286.6667 | 10000 | -693.7713 | -693.7713 | 0
2019-09-23 17:00 | 1379.937 | 0 | 0 | 9306.2287 | -1379.937 | -1379.937 | 0
2019-09-23 18:00 | 1554.3325 | 0 | 0 | 7926.2917 | -1554.3325 | -1554.3325 | 0
2019-09-23 19:00 | 1827.4188 | 0 | 0 | 6371.9592 | -1827.4188 | -1827.4188 | 0
2019-09-23 20:00 | 1736.6081 | 0 | 0 | 4544.5404 | -1736.6081 | -1736.6081 | 0
2019-09-23 21:00 | 1392.5539 | 0 | 0 | 2807.9323 | -1392.5539 | -1392.5539 | 0
2019-09-23 22:00 | 1051.9359 | 0 | 0 | 1415.3784 | -1051.9359 | -1051.9359 | 0
2019-09-23 23:00 | 704.1876 | 0 | 0 | 363.4425 | -704.1876 | -363.4425 | -340.7451
2019-09-24 | 570.9746 | 0 | 0 | 0 | -570.9746 | 0 | -911.7196
2019-09-24 01:00 | 509.4806 | 0 | 0 | 0 | -509.4806 | 0 | -1421.2003
2019-09-24 02:00 | 495.2568 | 0 | 0 | 0 | -495.2568 | 0 | -1916.4571
2019-09-24 03:00 | 498.3317 | 0 | 0 | 0 | -498.3317 | 0 | -2414.7888
2019-09-24 04:00 | 561.3924 | 0 | 0 | 0 | -561.3924 | 0 | -2976.1812
2019-09-24 05:00 | 764.5516 | 0 | 0 | 0 | -764.5516 | 0 | -3740.7328
2019-09-24 06:00 | 1047.3208 | 1001.4706 | 0 | 0 | -45.8502 | 0 | -3786.5831
2019-09-24 07:00 | 993.8256 | 3008.9623 | 0 | 0 | 2015.1367 | 2015.1367 | -1771.4463
2019-09-24 08:00 | 890.6635 | 4880.9956 | 0 | 2015.1367 | 3990.3321 | 3990.3321 | 0
2019-09-24 09:00 | 898.6338 | 441.9737 | 0 | 6005.4688 | -456.66 | -456.66 | 0
2019-09-24 10:00 | 895.8189 | 2513.7608 | 0 | 5548.8088 | 1617.9419 | 1617.9419 | 0
2019-09-24 11:00 | 868.1401 | 3530.6081 | 0 | 7166.7507 | 2662.468 | 2662.468 | 0
2019-09-24 12:00 | 839.5413 | 935.6135 | 286.6667 | 9829.2186 | 382.7389 | 170.7814 | 0
2019-09-24 13:00 | 824.7175 | 2381.2602 | 286.6667 | 10000 | 1843.2093 | 0 | 0
2019-09-24 14:00 | 848.3673 | 2492.3674 | 0 | 10000 | 1644.0001 | 0 | 0
2019-09-24 15:00 | 969.4648 | 3566.1523 | 0 | 10000 | 2596.6875 | 0 | 0
2019-09-24 16:00 | 1197.7983 | 1159.806 | 0 | 10000 | -37.9922 | -37.9922 | 0
2019-09-24 17:00 | 1379.937 | 0 | 0 | 9962.0078 | -1379.937 | -1379.937 | 0
2019-09-24 18:00 | 1554.3325 | 0 | 0 | 8582.0708 | -1554.3325 | -1554.3325 | 0
2019-09-24 19:00 | 1827.4188 | 0 | 0 | 7027.7383 | -1827.4188 | -1827.4188 | 0
2019-09-24 20:00 | 1736.6081 | 0 | 0 | 5200.3194 | -1736.6081 | -1736.6081 | 0
2019-09-24 21:00 | 1392.5539 | 0 | 0 | 3463.7113 | -1392.5539 | -1392.5539 | 0
2019-09-24 22:00 | 1053.5998 | 0 | 0 | 2071.1574 | -1053.5998 | -1053.5998 | 0
2019-09-24 23:00 | 722.6986 | 0 | 0 | 1017.5576 | -722.6986 | -722.6986 | 0
2019-09-25 | 601.0428 | 0 | 0 | 294.8589 | -601.0428 | -294.8589 | -306.1839
2019-09-25 01:00 | 555.1308 | 0 | 0 | 0 | -555.1308 | 0 | -861.3147
2019-09-25 02:00 | 556.1833 | 0 | 0 | 0 | -556.1833 | 0 | -1417.498
2019-09-25 03:00 | 562.7862 | 0 | 0 | 0 | -562.7862 | 0 | -1980.2843
2019-09-25 04:00 | 621.5183 | 0 | 0 | 0 | -621.5183 | 0 | -2601.8026
2019-09-25 05:00 | 821.9241 | 0 | 0 | 0 | -821.9241 | 0 | -3423.7267
2019-09-25 06:00 | 1081.7553 | 1189.0241 | 0 | 0 | 107.2688 | 107.2688 | -3316.4579
2019-09-25 07:00 | 1000.3735 | 3505.7301 | 0 | 107.2688 | 2505.3567 | 2505.3567 | -703.8324
2019-09-25 08:00 | 864.214 | 5634.3755 | 0 | 2612.6255 | 4770.1615 | 4770.1615 | 0
2019-09-25 09:00 | 848.4413 | 6889.8949 | 0 | 7382.7871 | 6041.4536 | 2617.2129 | 0
2019-09-25 10:00 | 836.6032 | 7686.8415 | 0 | 10000 | 6850.2383 | 0 | 0
2019-09-25 11:00 | 815.08 | 5513.8429 | 286.6667 | 10000 | 4985.4296 | 0 | 0
2019-09-25 12:00 | 791.1673 | 3321.4093 | 873.3333 | 10000 | 3403.5754 | 0 | 0
2019-09-25 13:00 | 781.2959 | 7026.577 | 873.3333 | 10000 | 7118.6145 | 0 | 0
2019-09-25 14:00 | 807.2392 | 5650.6078 | 873.3333 | 10000 | 5716.7019 | 0 | 0
2019-09-25 15:00 | 929.603 | 3766.6548 | 286.6667 | 10000 | 3123.7184 | 0 | 0
2019-09-25 16:00 | 1158.5647 | 1561.5954 | 286.6667 | 10000 | 689.6974 | 0 | 0
2019-09-25 17:00 | 1341.8593 | 0 | 873.3333 | 10000 | -468.526 | -468.526 | 0
2019-09-25 18:00 | 1516.3276 | 0 | 0 | 9531.474 | -1516.3276 | -1516.3276 | 0
2019-09-25 19:00 | 1788.7363 | 0 | 0 | 8015.1464 | -1788.7363 | -1788.7363 | 0
2019-09-25 20:00 | 1697.0916 | 0 | 0 | 6226.4101 | -1697.0916 | -1697.0916 | 0
2019-09-25 21:00 | 1361.1541 | 0 | 0 | 4529.3185 | -1361.1541 | -1361.1541 | 0
2019-09-25 22:00 | 1034.6953 | 0 | 0 | 3168.1644 | -1034.6953 | -1034.6953 | 0
2019-09-25 23:00 | 704.4749 | 0 | 0 | 2133.4691 | -704.4749 | -704.4749 | 0
2019-09-26 | 587.9887 | 0 | 0 | 1428.9942 | -587.9887 | -587.9887 | 0
2019-09-26 01:00 | 537.5222 | 0 | 0 | 841.0056 | -537.5222 | -537.5222 | 0
2019-09-26 02:00 | 535.0587 | 0 | 0 | 303.4834 | -535.0587 | -303.4834 | -231.5753
2019-09-26 03:00 | 541.6081 | 0 | 0 | 0 | -541.6081 | 0 | -773.1834
2019-09-26 04:00 | 599.6279 | 0 | 0 | 0 | -599.6279 | 0 | -1372.8113
2019-09-26 05:00 | 787.4594 | 0 | 0 | 0 | -787.4594 | 0 | -2160.2707
2019-09-26 06:00 | 1056.6492 | 1203.8821 | 0 | 0 | 147.2329 | 147.2329 | -2013.0378
2019-09-26 07:00 | 983.9708 | 3510.6383 | 0 | 147.2329 | 2526.6676 | 2526.6676 | 0
2019-09-26 08:00 | 851.4828 | 5509.8961 | 0 | 2673.9005 | 4658.4133 | 4658.4133 | 0
2019-09-26 09:00 | 846.0342 | 6895.6772 | 286.6667 | 7332.3138 | 6336.3096 | 2667.6862 | 0
2019-09-26 10:00 | 837.7782 | 7714.3081 | 286.6667 | 10000 | 7163.1966 | 0 | 0
2019-09-26 11:00 | 815.08 | 7970.4752 | 873.3333 | 10000 | 8028.7286 | 0 | 0
2019-09-26 12:00 | 791.1673 | 7726.0761 | 286.6667 | 10000 | 7221.5755 | 0 | 0
2019-09-26 13:00 | 781.2959 | 6906.3917 | 286.6667 | 10000 | 6411.7625 | 0 | 0
2019-09-26 14:00 | 807.2392 | 5621.4104 | 286.6667 | 10000 | 5100.8379 | 0 | 0
2019-09-26 15:00 | 929.603 | 3731.0014 | 286.6667 | 10000 | 3088.065 | 0 | 0
2019-09-26 16:00 | 1158.5647 | 1514.458 | 286.6667 | 10000 | 642.56 | 0 | 0
2019-09-26 17:00 | 1341.8593 | 0 | 0 | 10000 | -1341.8593 | -1341.8593 | 0
2019-09-26 18:00 | 1516.3276 | 0 | 0 | 8658.1407 | -1516.3276 | -1516.3276 | 0
2019-09-26 19:00 | 1788.7363 | 0 | 0 | 7141.813 | -1788.7363 | -1788.7363 | 0
2019-09-26 20:00 | 1697.0916 | 0 | 0 | 5353.0767 | -1697.0916 | -1697.0916 | 0
2019-09-26 21:00 | 1361.1541 | 0 | 286.6667 | 3655.9852 | -1074.4874 | -1074.4874 | 0
2019-09-26 22:00 | 1034.6953 | 0 | 286.6667 | 2581.4978 | -748.0286 | -748.0286 | 0
2019-09-26 23:00 | 696.8921 | 0 | 286.6667 | 1833.4691 | -410.2254 | -410.2254 | 0
2019-09-27 | 566.5941 | 0 | 286.6667 | 1423.2437 | -279.9275 | -279.9275 | 0
2019-09-27 01:00 | 507.6848 | 0 | 0 | 1143.3163 | -507.6848 | -507.6848 | 0
2019-09-27 02:00 | 499.1909 | 0 | 0 | 635.6315 | -499.1909 | -499.1909 | 0
2019-09-27 03:00 | 499.8417 | 0 | 286.6667 | 136.4406 | -213.1751 | -136.4406 | -76.7345
2019-09-27 04:00 | 554.926 | 0 | 0 | 0 | -554.926 | 0 | -631.6604
2019-09-27 05:00 | 740.2041 | 0 | 286.6667 | 0 | -453.5374 | 0 | -1085.1979
2019-09-27 06:00 | 1012.2696 | 39.8578 | 0 | 0 | -972.4117 | 0 | -2057.6096
2019-09-27 07:00 | 942.7518 | 29.6596 | 286.6667 | 0 | -626.4255 | 0 | -2684.0351
2019-09-27 08:00 | 822.1611 | 571.0164 | 0 | 0 | -251.1447 | 0 | -2935.1798
2019-09-27 09:00 | 816.1489 | 939.6351 | 873.3333 | 0 | 996.8195 | 996.8195 | -1938.3603
2019-09-27 10:00 | 832.0413 | 1513.5897 | 286.6667 | 996.8195 | 968.2151 | 968.2151 | 0
2019-09-27 11:00 | 815.08 | 1028.5841 | 1666.6667 | 1965.0346 | 1880.1708 | 1880.1708 | 0
2019-09-27 12:00 | 791.1673 | 1183.3017 | 286.6667 | 3845.2055 | 678.8011 | 678.8011 | 0
2019-09-27 13:00 | 781.2959 | 775.1034 | 873.3333 | 4524.0066 | 867.1409 | 867.1409 | 0
2019-09-27 14:00 | 807.2392 | 561.1896 | 1666.6667 | 5391.1475 | 1420.6171 | 1420.6171 | 0
2019-09-27 15:00 | 929.603 | 950.9534 | 2773.3333 | 6811.7646 | 2794.6837 | 2794.6837 | 0
2019-09-27 16:00 | 1158.5647 | 422.6871 | 2773.3333 | 9606.4483 | 2037.4558 | 393.5517 | 0
2019-09-27 17:00 | 1341.8593 | 0 | 1666.6667 | 10000 | 324.8073 | 0 | 0
2019-09-27 18:00 | 1516.3276 | 0 | 873.3333 | 10000 | -642.9943 | -642.9943 | 0
2019-09-27 19:00 | 1788.7363 | 0 | 873.3333 | 9357.0057 | -915.403 | -915.403 | 0
2019-09-27 20:00 | 1697.0916 | 0 | 873.3333 | 8441.6027 | -823.7582 | -823.7582 | 0
2019-09-27 21:00 | 1361.1541 | 0 | 873.3333 | 7617.8445 | -487.8207 | -487.8207 | 0
2019-09-27 22:00 | 1034.6953 | 0 | 873.3333 | 7130.0238 | -161.362 | -161.362 | 0
2019-09-27 23:00 | 696.8921 | 0 | 286.6667 | 6968.6618 | -410.2254 | -410.2254 | 0
2019-09-28 | 566.5941 | 0 | 286.6667 | 6558.4364 | -279.9275 | -279.9275 | 0
2019-09-28 01:00 | 513.4775 | 0 | 0 | 6278.5089 | -513.4775 | -513.4775 | 0
2019-09-28 02:00 | 510.1132 | 0 | 286.6667 | 5765.0314 | -223.4466 | -223.4466 | 0
2019-09-28 03:00 | 515.4983 | 0 | 0 | 5541.5849 | -515.4983 | -515.4983 | 0
2019-09-28 04:00 | 575.7715 | 0 | 0 | 5026.0865 | -575.7715 | -575.7715 | 0
2019-09-28 05:00 | 762.5513 | 0 | 873.3333 | 4450.315 | 110.782 | 110.782 | 0
2019-09-28 06:00 | 1045.8103 | 1026.9661 | 873.3333 | 4561.097 | 854.4892 | 854.4892 | 0
2019-09-28 07:00 | 972.119 | 3163.9754 | 2773.3333 | 5415.5862 | 4965.1898 | 4584.4138 | 0
2019-09-28 08:00 | 840.4585 | 5050.7919 | 7873.3333 | 10000 | 12083.6668 | 0 | 0
2019-09-28 09:00 | 829.585 | 6399.2865 | 4266.6667 | 10000 | 9836.3682 | 0 | 0
2019-09-28 10:00 | 832.0413 | 7185.6025 | 4266.6667 | 10000 | 10620.2279 | 0 | 0
2019-09-28 11:00 | 815.08 | 7406.1012 | 873.3333 | 10000 | 7464.3546 | 0 | 0
2019-09-28 12:00 | 791.1673 | 7097.7758 | 4266.6667 | 10000 | 10573.2753 | 0 | 0
2019-09-28 13:00 | 781.2959 | 6362.5739 | 6160 | 10000 | 11741.278 | 0 | 0
2019-09-28 14:00 | 807.2392 | 5048.5414 | 6160 | 10000 | 10401.3022 | 0 | 0
2019-09-28 15:00 | 929.603 | 3213.1345 | 2773.3333 | 10000 | 5056.8648 | 0 | 0
2019-09-28 16:00 | 1158.5647 | 1150.8613 | 4266.6667 | 10000 | 4258.9634 | 0 | 0
2019-09-28 17:00 | 1341.8593 | 0 | 2773.3333 | 10000 | 1431.474 | 0 | 0
2019-09-28 18:00 | 1516.3276 | 0 | 4266.6667 | 10000 | 2750.339 | 0 | 0
2019-09-28 19:00 | 1788.7363 | 0 | 6160 | 10000 | 4371.2637 | 0 | 0
2019-09-28 20:00 | 1697.0916 | 0 | 2773.3333 | 10000 | 1076.2418 | 0 | 0
2019-09-28 21:00 | 1361.1541 | 0 | 2773.3333 | 10000 | 1412.1793 | 0 | 0
2019-09-28 22:00 | 1042.9632 | 0 | 1666.6667 | 10000 | 623.7034 | 0 | 0
2019-09-28 23:00 | 723.495 | 0 | 2773.3333 | 10000 | 2049.8383 | 0 | 0
2019-09-29 | 611.8512 | 0 | 2773.3333 | 10000 | 2161.4821 | 0 | 0
2019-09-29 01:00 | 564.5433 | 0 | 2773.3333 | 10000 | 2208.79 | 0 | 0
2019-09-29 02:00 | 562.2033 | 0 | 873.3333 | 10000 | 311.1301 | 0 | 0
2019-09-29 03:00 | 570.6193 | 0 | 1666.6667 | 10000 | 1096.0473 | 0 | 0
2019-09-29 04:00 | 628.0037 | 0 | 1666.6667 | 10000 | 1038.663 | 0 | 0
2019-09-29 05:00 | 829.8815 | 0 | 873.3333 | 10000 | 43.4519 | 0 | 0
2019-09-29 06:00 | 1089.955 | 1044.6393 | 873.3333 | 10000 | 828.0177 | 0 | 0
2019-09-29 07:00 | 1011.5385 | 3199.4299 | 873.3333 | 10000 | 3061.2248 | 0 | 0
2019-09-29 08:00 | 875.6595 | 5117.6391 | 286.6667 | 10000 | 4528.6463 | 0 | 0
2019-09-29 09:00 | 863.6282 | 6517.5203 | 0 | 10000 | 5653.8922 | 0 | 0
2019-09-29 10:00 | 847.5859 | 7315.0189 | 0 | 10000 | 6467.433 | 0 | 0
2019-09-29 11:00 | 815.08 | 7557.1744 | 1666.6667 | 10000 | 8408.7611 | 0 | 0
2019-09-29 12:00 | 791.1673 | 7319.1163 | 873.3333 | 10000 | 7401.2824 | 0 | 0
2019-09-29 13:00 | 781.2959 | 4070.6251 | 873.3333 | 10000 | 4162.6625 | 0 | 0
2019-09-29 14:00 | 807.2392 | 4707.4916 | 286.6667 | 10000 | 4186.9191 | 0 | 0
2019-09-29 15:00 | 929.603 | 583.2478 | 2773.3333 | 10000 | 2426.9781 | 0 | 0
2019-09-29 16:00 | 1158.5647 | 387.6236 | 1666.6667 | 10000 | 895.7256 | 0 | 0
2019-09-29 17:00 | 1341.8593 | 0 | 1666.6667 | 10000 | 324.8073 | 0 | 0
2019-09-29 18:00 | 1516.3276 | 0 | 873.3333 | 10000 | -642.9943 | -642.9943 | 0
2019-09-29 19:00 | 1788.7363 | 0 | 873.3333 | 9357.0057 | -915.403 | -915.403 | 0
2019-09-29 20:00 | 1697.0916 | 0 | 0 | 8441.6027 | -1697.0916 | -1697.0916 | 0
2019-09-29 21:00 | 1361.1541 | 0 | 0 | 6744.5112 | -1361.1541 | -1361.1541 | 0
2019-09-29 22:00 | 1041.888 | 0 | 0 | 5383.3571 | -1041.888 | -1041.888 | 0
2019-09-29 23:00 | 718.8559 | 0 | 873.3333 | 4341.4691 | 154.4774 | 154.4774 | 0
2019-09-30 | 604.8875 | 0 | 286.6667 | 4495.9465 | -318.2209 | -318.2209 | 0
2019-09-30 01:00 | 552.0091 | 0 | 0 | 4177.7256 | -552.0091 | -552.0091 | 0
2019-09-30 02:00 | 544.2701 | 0 | 0 | 3625.7165 | -544.2701 | -544.2701 | 0
2019-09-30 03:00 | 551.8744 | 0 | 0 | 3081.4465 | -551.8744 | -551.8744 | 0
2019-09-30 04:00 | 609.6788 | 0 | 0 | 2529.5721 | -609.6788 | -609.6788 | 0
2019-09-30 05:00 | 802.1888 | 0 | 873.3333 | 1919.8933 | 71.1445 | 71.1445 | 0
2019-09-30 06:00 | 1082.3613 | 40.7687 | 6160 | 1991.0378 | 5118.4074 | 5118.4074 | 0
2019-09-30 07:00 | 1015.4982 | 197.0479 | 7873.3333 | 7109.4452 | 7054.883 | 2890.5548 | 0
2019-09-30 08:00 | 894.6784 | 302.8168 | 4266.6667 | 10000 | 3674.8051 | 0 | 0
2019-09-30 09:00 | 886.878 | 2009.3421 | 2773.3333 | 10000 | 3895.7974 | 0 | 0
2019-09-30 10:00 | 890.2934 | 1983.3567 | 2773.3333 | 10000 | 3866.3966 | 0 | 0
2019-09-30 11:00 | 868.1401 | 7735.7395 | 873.3333 | 10000 | 7740.9327 | 0 | 0
2019-09-30 12:00 | 839.5413 | 1965.6214 | 4266.6667 | 10000 | 5392.7467 | 0 | 0
2019-09-30 13:00 | 824.7175 | 2030.8241 | 4266.6667 | 10000 | 5472.7732 | 0 | 0
2019-09-30 14:00 | 848.3673 | 2605.1571 | 6160 | 10000 | 7916.7898 | 0 | 0
2019-09-30 15:00 | 969.4648 | 711.9224 | 2773.3333 | 10000 | 2515.791 | 0 | 0
2019-09-30 16:00 | 1197.7983 | 355.3534 | 2773.3333 | 10000 | 1930.8885 | 0 | 0
2019-09-30 17:00 | 1379.937 | 0 | 873.3333 | 10000 | -506.6037 | -506.6037 | 0
2019-09-30 18:00 | 1554.3325 | 0 | 873.3333 | 9493.3963 | -680.9992 | -680.9992 | 0
2019-09-30 19:00 | 1827.4188 | 0 | 286.6667 | 8812.3972 | -1540.7522 | -1540.7522 | 0
2019-09-30 20:00 | 1736.6081 | 0 | 286.6667 | 7271.645 | -1449.9414 | -1449.9414 | 0
2019-09-30 21:00 | 1392.5539 | 0 | 873.3333 | 5821.7035 | -519.2206 | -519.2206 | 0
2019-09-30 22:00 | 1051.9359 | 0 | 286.6667 | 5302.483 | -765.2692 | -765.2692 | 0
2019-09-30 23:00 | 704.1876 | 0 | 873.3333 | 4537.2137 | 169.1458 | 169.1458 | 0
2019-10-01 | 599.6597 | 0 | 286.6667 | 4706.3595 | -312.993 | -312.993 | 0
2019-10-01 01:00 | 535.8208 | 0 | 286.6667 | 4393.3665 | -249.1542 | -249.1542 | 0
2019-10-01 02:00 | 521.4157 | 0 | 873.3333 | 4144.2123 | 351.9177 | 351.9177 | 0
2019-10-01 03:00 | 521.2374 | 0 | 873.3333 | 4496.13 | 352.096 | 352.096 | 0
2019-10-01 04:00 | 583.2978 | 0 | 873.3333 | 4848.2259 | 290.0355 | 290.0355 | 0
2019-10-01 05:00 | 811.6572 | 0 | 873.3333 | 5138.2615 | 61.6761 | 61.6761 | 0
2019-10-01 06:00 | 1159.7308 | 384.6048 | 873.3333 | 5199.9375 | 98.2074 | 98.2074 | 0
2019-10-01 07:00 | 1108.305 | 820.4123 | 873.3333 | 5298.1449 | 585.4406 | 585.4406 | 0
2019-10-01 08:00 | 948.092 | 2337.7372 | 286.6667 | 5883.5855 | 1676.3119 | 1676.3119 | 0
2019-10-01 09:00 | 941.9113 | 3292.9997 | 286.6667 | 7559.8975 | 2637.7551 | 2440.1025 | 0
2019-10-01 10:00 | 961.6601 | 4326.4633 | 873.3333 | 10000 | 4238.1366 | 0 | 0
2019-10-01 11:00 | 940.6123 | 2538.2202 | 0 | 10000 | 1597.6079 | 0 | 0
2019-10-01 12:00 | 909.9079 | 3674.9446 | 286.6667 | 10000 | 3051.7033 | 0 | 0
2019-10-01 13:00 | 896.3553 | 2688.1997 | 286.6667 | 10000 | 2078.5112 | 0 | 0
2019-10-01 14:00 | 932.872 | 2911.7551 | 0 | 10000 | 1978.8831 | 0 | 0
2019-10-01 15:00 | 1094.8808 | 363.914 | 286.6667 | 10000 | -444.3001 | -444.3001 | 0
2019-10-01 16:00 | 1410.8665 | 449.029 | 286.6667 | 9555.6999 | -675.1708 | -675.1708 | 0
2019-10-01 17:00 | 1689.9706 | 0 | 286.6667 | 8880.5291 | -1403.3039 | -1403.3039 | 0
2019-10-01 18:00 | 1901.8268 | 0 | 286.6667 | 7477.2252 | -1615.1602 | -1615.1602 | 0
2019-10-01 19:00 | 1968.733 | 0 | 286.6667 | 5862.065 | -1682.0663 | -1682.0663 | 0
2019-10-01 20:00 | 1780.3507 | 0 | 873.3333 | 4179.9987 | -907.0174 | -907.0174 | 0
2019-10-01 21:00 | 1430.5826 | 0 | 286.6667 | 3272.9814 | -1143.9159 | -1143.9159 | 0
2019-10-01 22:00 | 1083.1953 | 0 | 286.6667 | 2129.0655 | -796.5286 | -796.5286 | 0
2019-10-01 23:00 | 730.3347 | 0 | 1666.6667 | 1332.5368 | 936.3319 | 936.3319 | 0
2019-10-02 | 595.2793 | 0 | 873.3333 | 2268.8688 | 278.054 | 278.054 | 0
2019-10-02 01:00 | 532.9229 | 0 | 873.3333 | 2546.9228 | 340.4105 | 340.4105 | 0
2019-10-02 02:00 | 519.9003 | 0 | 873.3333 | 2887.3333 | 353.433 | 353.433 | 0
2019-10-02 03:00 | 518.2729 | 0 | 286.6667 | 3240.7663 | -231.6063 | -231.6063 | 0
2019-10-02 04:00 | 578.7513 | 0 | 286.6667 | 3009.16 | -292.0846 | -292.0846 | 0
2019-10-02 05:00 | 799.865 | 0 | 286.6667 | 2717.0754 | -513.1984 | -513.1984 | 0
2019-10-02 06:00 | 1136.2459 | 120.7293 | 873.3333 | 2203.877 | -142.1833 | -142.1833 | 0
2019-10-02 07:00 | 1072.3061 | 358.8356 | 286.6667 | 2061.6938 | -426.8038 | -426.8038 | 0
2019-10-02 08:00 | 898.1164 | 1643.3718 | 873.3333 | 1634.89 | 1618.5887 | 1618.5887 | 0
2019-10-02 09:00 | 885.4044 | 723.7594 | 873.3333 | 3253.4788 | 711.6884 | 711.6884 | 0
2019-10-02 10:00 | 903.408 | 1367.0981 | 873.3333 | 3965.1671 | 1337.0235 | 1337.0235 | 0
2019-10-02 11:00 | 887.5521 | 2441.6156 | 2773.3333 | 5302.1906 | 4327.3968 | 4327.3968 | 0
2019-10-02 12:00 | 861.5338 | 1529.5851 | 2773.3333 | 9629.5874 | 3441.3846 | 370.4126 | 0
2019-10-02 13:00 | 852.9336 | 1587.0506 | 2773.3333 | 10000 | 3507.4503 | 0 | 0
2019-10-02 14:00 | 891.7439 | 1526.2616 | 4266.6667 | 10000 | 4901.1843 | 0 | 0
2019-10-02 15:00 | 1055.019 | 1476.9289 | 1666.6667 | 10000 | 2088.5766 | 0 | 0
2019-10-02 16:00 | 1371.6329 | 109.3546 | 873.3333 | 10000 | -388.9449 | -388.9449 | 0
2019-10-02 17:00 | 1651.8929 | 0 | 286.6667 | 9611.0551 | -1365.2262 | -1365.2262 | 0
2019-10-02 18:00 | 1863.822 | 0 | 0 | 8245.8289 | -1863.822 | -1863.822 | 0
2019-10-02 19:00 | 1930.0504 | 0 | 0 | 6382.0069 | -1930.0504 | -1930.0504 | 0
2019-10-02 20:00 | 1740.8342 | 0 | 0 | 4451.9565 | -1740.8342 | -1740.8342 | 0
2019-10-02 21:00 | 1399.1827 | 0 | 0 | 2711.1223 | -1399.1827 | -1399.1827 | 0
2019-10-02 22:00 | 1072.6758 | 0 | 0 | 1311.9396 | -1072.6758 | -1072.6758 | 0
2019-10-02 23:00 | 744.7371 | 0 | 0 | 239.2638 | -744.7371 | -239.2638 | -505.4733
2019-10-03 | 628.3714 | 0 | 0 | 0 | -628.3714 | 0 | -1133.8447
2019-10-03 01:00 | 575.3378 | 0 | 0 | 0 | -575.3378 | 0 | -1709.1825
2019-10-03 02:00 | 568.6319 | 0 | 0 | 0 | -568.6319 | 0 | -2277.8145
2019-10-03 03:00 | 574.4839 | 0 | 0 | 0 | -574.4839 | 0 | -2852.2984
2019-10-03 04:00 | 637.615 | 0 | 0 | 0 | -637.615 | 0 | -3489.9134
2019-10-03 05:00 | 869.516 | 0 | 0 | 0 | -869.516 | 0 | -4359.4294
2019-10-03 06:00 | 1186.3391 | 71.4886 | 0 | 0 | -1114.8505 | 0 | -5474.2799
2019-10-03 07:00 | 1114.0419 | 428.1461 | 0 | 0 | -685.8958 | 0 | -6160.1757
2019-10-03 08:00 | 935.9018 | 812.8499 | 0 | 0 | -123.0519 | 0 | -6283.2276
2019-10-03 09:00 | 926.9428 | 1191.1631 | 0 | 0 | 264.2203 | 264.2203 | -6019.0073
2019-10-03 10:00 | 927.0036 | 1592.5763 | 286.6667 | 264.2203 | 952.2394 | 952.2394 | -4802.5476
2019-10-03 11:00 | 902.5156 | 1290.5208 | 873.3333 | 1216.4597 | 1261.3385 | 1261.3385 | -2324.7494
2019-10-03 12:00 | 871.0925 | 2092.456 | 2773.3333 | 2477.7982 | 3994.6969 | 3994.6969 | 0
2019-10-03 13:00 | 863.5143 | 1890.2423 | 2773.3333 | 6472.4952 | 3800.0614 | 3527.5048 | 0
2019-10-03 14:00 | 903.2791 | 1753.1152 | 6160 | 10000 | 7009.8361 | 0 | 0
2019-10-03 15:00 | 1066.4119 | 739.6478 | 4266.6667 | 10000 | 3939.9026 | 0 | 0
2019-10-03 16:00 | 1393.8697 | 1119.4238 | 4266.6667 | 10000 | 3992.2207 | 0 | 0
2019-10-03 17:00 | 1658.4993 | 0 | 2773.3333 | 10000 | 1114.8341 | 0 | 0
2019-10-03 18:00 | 1867.7099 | 0 | 4266.6667 | 10000 | 2398.9568 | 0 | 0
2019-10-03 19:00 | 1932.8788 | 0 | 4266.6667 | 10000 | 2333.7878 | 0 | 0
2019-10-03 20:00 | 1747.3136 | 0 | 4266.6667 | 10000 | 2519.3531 | 0 | 0
2019-10-03 21:00 | 1413.3976 | 0 | 6160 | 10000 | 4746.6024 | 0 | 0
2019-10-03 22:00 | 1088.0245 | 0 | 4266.6667 | 10000 | 3178.6422 | 0 | 0
2019-10-03 23:00 | 752.9986 | 0 | 873.3333 | 10000 | 120.3347 | 0 | 0
2019-10-04 | 630.1287 | 0 | 873.3333 | 10000 | 243.2047 | 0 | 0
2019-10-04 01:00 | 570.9457 | 0 | 1666.6667 | 10000 | 1095.721 | 0 | 0
2019-10-04 02:00 | 560.3876 | 0 | 1666.6667 | 10000 | 1106.2791 | 0 | 0
2019-10-04 03:00 | 559.0957 | 0 | 4266.6667 | 10000 | 3707.571 | 0 | 0
2019-10-04 04:00 | 617.3949 | 0 | 1666.6667 | 10000 | 1049.2718 | 0 | 0
2019-10-04 05:00 | 830.3907 | 0 | 2773.3333 | 10000 | 1942.9426 | 0 | 0
2019-10-04 06:00 | 1161.0537 | 335.7034 | 1666.6667 | 10000 | 841.3164 | 0 | 0
2019-10-04 07:00 | 1097.7126 | 3230.925 | 1666.6667 | 10000 | 3799.8791 | 0 | 0
2019-10-04 08:00 | 917.5333 | 3806.3321 | 2773.3333 | 10000 | 5662.1321 | 0 | 0
2019-10-04 09:00 | 893.021 | 4913.9488 | 2773.3333 | 10000 | 6794.2611 | 0 | 0
2019-10-04 10:00 | 903.408 | 3381.414 | 2773.3333 | 10000 | 5251.3394 | 0 | 0
2019-10-04 11:00 | 887.5521 | 3563.6004 | 4266.6667 | 10000 | 6942.715 | 0 | 0
2019-10-04 12:00 | 861.5338 | 2471.5869 | 6160 | 10000 | 7770.0531 | 0 | 0
2019-10-04 13:00 | 852.9336 | 1433.7866 | 4266.6667 | 10000 | 4847.5197 | 0 | 0
2019-10-04 14:00 | 891.7439 | 1370.2319 | 6160 | 10000 | 6638.488 | 0 | 0
2019-10-04 15:00 | 1055.019 | 1948.7727 | 7873.3333 | 10000 | 8767.0871 | 0 | 0
2019-10-04 16:00 | 1371.6329 | 412.0013 | 6160 | 10000 | 5200.3684 | 0 | 0
2019-10-04 17:00 | 1651.8929 | 0 | 6160 | 10000 | 4508.1071 | 0 | 0
2019-10-04 18:00 | 1863.822 | 0 | 6160 | 10000 | 4296.178 | 0 | 0
2019-10-04 19:00 | 1930.0504 | 0 | 6160 | 10000 | 4229.9496 | 0 | 0
2019-10-04 20:00 | 1740.8342 | 0 | 7873.3333 | 10000 | 6132.4992 | 0 | 0
2019-10-04 21:00 | 1399.1827 | 0 | 9060 | 10000 | 7660.8173 | 0 | 0
2019-10-04 22:00 | 1065.9547 | 0 | 9573.3333 | 10000 | 8507.3786 | 0 | 0
2019-10-04 23:00 | 724.8192 | 0 | 9060 | 10000 | 8335.1808 | 0 | 0
2019-10-05 | 606.0436 | 0 | 7873.3333 | 10000 | 7267.2897 | 0 | 0
2019-10-05 01:00 | 558.4548 | 0 | 7873.3333 | 10000 | 7314.8785 | 0 | 0
2019-10-05 02:00 | 554.1138 | 0 | 4266.6667 | 10000 | 3712.5529 | 0 | 0
2019-10-05 03:00 | 561.8064 | 0 | 1666.6667 | 10000 | 1104.8602 | 0 | 0
2019-10-05 04:00 | 626.5703 | 0 | 1666.6667 | 10000 | 1040.0964 | 0 | 0
2019-10-05 05:00 | 843.4443 | 0 | 873.3333 | 10000 | 29.889 | 0 | 0
2019-10-05 06:00 | 1180.2557 | 883.4588 | 1666.6667 | 10000 | 1369.8697 | 0 | 0
2019-10-05 07:00 | 1116.5553 | 3089.782 | 1666.6667 | 10000 | 3639.8935 | 0 | 0
2019-10-05 08:00 | 938.247 | 5044.3991 | 873.3333 | 10000 | 4979.4854 | 0 | 0
2019-10-05 09:00 | 925.8038 | 4927.8063 | 873.3333 | 10000 | 4875.3359 | 0 | 0
2019-10-05 10:00 | 933.0988 | 4255.3737 | 873.3333 | 10000 | 4195.6083 | 0 | 0
2019-10-05 11:00 | 909.4732 | 4296.4046 | 873.3333 | 10000 | 4260.2648 | 0 | 0
2019-10-05 12:00 | 875.0931 | 2901.9893 | 2773.3333 | 10000 | 4800.2295 | 0 | 0
2019-10-05 13:00 | 865.8443 | 2542.3728 | 2773.3333 | 10000 | 4449.8619 | 0 | 0
2019-10-05 14:00 | 904.9752 | 1142.6952 | 1666.6667 | 10000 | 1904.3867 | 0 | 0
2019-10-05 15:00 | 1068.3772 | 1624.7648 | 2773.3333 | 10000 | 3329.721 | 0 | 0
2019-10-05 16:00 | 1394.1944 | 174.3319 | 1666.6667 | 10000 | 446.8042 | 0 | 0
2019-10-05 17:00 | 1660.4903 | 0 | 873.3333 | 10000 | -787.1569 | -787.1569 | 0
2019-10-05 18:00 | 1872.5687 | 0 | 286.6667 | 9212.8431 | -1585.902 | -1585.902 | 0
2019-10-05 19:00 | 1945.9662 | 0 | 0 | 7626.941 | -1945.9662 | -1945.9662 | 0
2019-10-05 20:00 | 1763.7505 | 0 | 0 | 5680.9748 | -1763.7505 | -1763.7505 | 0
2019-10-05 21:00 | 1434.3671 | 0 | 0 | 3917.2243 | -1434.3671 | -1434.3671 | 0
2019-10-05 22:00 | 1115.1235 | 0 | 286.6667 | 2482.8572 | -828.4568 | -828.4568 | 0
2019-10-05 23:00 | 782.6364 | 0 | 286.6667 | 1654.4004 | -495.9698 | -495.9698 | 0
2019-10-06 | 665.6345 | 0 | 0 | 1158.4306 | -665.6345 | -665.6345 | 0
2019-10-06 01:00 | 616.157 | 0 | 0 | 492.7961 | -616.157 | -492.7961 | -123.3609
2019-10-06 02:00 | 609.0446 | 0 | 0 | 0 | -609.0446 | 0 | -732.4055
2019-10-06 03:00 | 611.1836 | 0 | 0 | 0 | -611.1836 | 0 | -1343.5891
2019-10-06 04:00 | 670.3753 | 0 | 0 | 0 | -670.3753 | 0 | -2013.9644
2019-10-06 05:00 | 891.226 | 0 | 286.6667 | 0 | -604.5593 | 0 | -2618.5238
2019-10-06 06:00 | 1212.9401 | 948.6718 | 286.6667 | 0 | 22.3983 | 22.3983 | -2596.1254
2019-10-06 07:00 | 1145.961 | 3146.8255 | 286.6667 | 22.3983 | 2287.5311 | 2287.5311 | -286.1959
2019-10-06 08:00 | 968.088 | 5072.1256 | 0 | 2309.9295 | 4104.0376 | 4104.0376 | 0
2019-10-06 09:00 | 953.7475 | 6385.4865 | 873.3333 | 6413.9671 | 6305.0724 | 3586.0329 | 0
2019-10-06 10:00 | 948.1854 | 7179.4052 | 286.6667 | 10000 | 6517.8864 | 0 | 0
2019-10-06 11:00 | 923.8496 | 7464.5269 | 2773.3333 | 10000 | 9314.0107 | 0 | 0
2019-10-06 12:00 | 890.8623 | 7176.3519 | 1666.6667 | 10000 | 7952.1563 | 0 | 0
2019-10-06 13:00 | 879.3934 | 6359.3976 | 873.3333 | 10000 | 6353.3376 | 0 | 0
2019-10-06 14:00 | 919.0402 | 5079.4177 | 873.3333 | 10000 | 5033.7109 | 0 | 0
2019-10-06 15:00 | 1089.0802 | 3194.3228 | 873.3333 | 10000 | 2978.576 | 0 | 0
2019-10-06 16:00 | 1428.9549 | 1051.8969 | 873.3333 | 10000 | 496.2754 | 0 | 0
2019-10-06 17:00 | 1698.2179 | 0 | 0 | 10000 | -1698.2179 | -1698.2179 | 0
2019-10-06 18:00 | 1917.9177 | 0 | 0 | 8301.7821 | -1917.9177 | -1917.9177 | 0
2019-10-06 19:00 | 1993.3611 | 0 | 0 | 6383.8644 | -1993.3611 | -1993.3611 | 0
2019-10-06 20:00 | 1806.1075 | 0 | 0 | 4390.5033 | -1806.1075 | -1806.1075 | 0
2019-10-06 21:00 | 1479.9615 | 0 | 0 | 2584.3958 | -1479.9615 | -1479.9615 | 0
2019-10-06 22:00 | 1160.517 | 0 | 0 | 1104.4343 | -1160.517 | -1104.4343 | -56.0827
2019-10-06 23:00 | 831.9701 | 0 | 0 | 0 | -831.9701 | 0 | -888.0528
2019-10-07 | 723.8237 | 0 | 0 | 0 | -723.8237 | 0 | -1611.8765
2019-10-07 01:00 | 665.4898 | 0 | 0 | 0 | -665.4898 | 0 | -2277.3663
2019-10-07 02:00 | 660.6032 | 0 | 0 | 0 | -660.6032 | 0 | -2937.9695
2019-10-07 03:00 | 667.2366 | 0 | 0 | 0 | -667.2366 | 0 | -3605.2061
2019-10-07 04:00 | 729.2724 | 0 | 0 | 0 | -729.2724 | 0 | -4334.4785
2019-10-07 05:00 | 972.4866 | 0 | 0 | 0 | -972.4866 | 0 | -5306.9651
2019-10-07 06:00 | 1295.8813 | 479.8662 | 0 | 0 | -816.015 | 0 | -6122.9802
2019-10-07 07:00 | 1229.7962 | 3050.1991 | 0 | 0 | 1820.4029 | 1820.4029 | -4302.5773
2019-10-07 08:00 | 1054.5337 | 4944.1467 | 286.6667 | 1820.4029 | 4176.2796 | 4176.2796 | 0
2019-10-07 09:00 | 1047.1394 | 6316.7602 | 0 | 5996.6825 | 5269.6209 | 4003.3175 | 0
2019-10-07 10:00 | 1023.9947 | 7141.7863 | 0 | 10000 | 6117.7916 | 0 | 0
2019-10-07 11:00 | 981.6661 | 7365.3463 | 2773.3333 | 10000 | 9157.0136 | 0 | 0
2019-10-07 12:00 | 935.8084 | 7059.7039 | 873.3333 | 10000 | 6997.2289 | 0 | 0
2019-10-07 13:00 | 908.7158 | 6240.6785 | 873.3333 | 10000 | 6205.2961 | 0 | 0
2019-10-07 14:00 | 946.0071 | 4953.4962 | 873.3333 | 10000 | 4880.8224 | 0 | 0
2019-10-07 15:00 | 1105.2663 | 3075.0425 | 2773.3333 | 10000 | 4743.1096 | 0 | 0
2019-10-07 16:00 | 1439.6872 | 976.4362 | 2773.3333 | 10000 | 2310.0824 | 0 | 0
2019-10-07 17:00 | 1705.838 | 0 | 2773.3333 | 10000 | 1067.4954 | 0 | 0
2019-10-07 18:00 | 1917.3663 | 0 | 2773.3333 | 10000 | 855.9671 | 0 | 0
2019-10-07 19:00 | 1991.1122 | 0 | 2773.3333 | 10000 | 782.2211 | 0 | 0
2019-10-07 20:00 | 1815.297 | 0 | 4266.6667 | 10000 | 2451.3697 | 0 | 0
2019-10-07 21:00 | 1483.6333 | 0 | 2773.3333 | 10000 | 1289.7001 | 0 | 0
2019-10-07 22:00 | 1153.3067 | 0 | 4266.6667 | 10000 | 3113.36 | 0 | 0
2019-10-07 23:00 | 815.9924 | 0 | 1666.6667 | 10000 | 850.6742 | 0 | 0
2019-10-08 | 701.9111 | 0 | 4266.6667 | 10000 | 3564.7555 | 0 | 0
2019-10-08 01:00 | 648.7692 | 0 | 4266.6667 | 10000 | 3617.8975 | 0 | 0
2019-10-08 02:00 | 639.9187 | 0 | 4266.6667 | 10000 | 3626.748 | 0 | 0
2019-10-08 03:00 | 644.3178 | 0 | 4266.6667 | 10000 | 3622.3489 | 0 | 0
2019-10-08 04:00 | 704.4232 | 0 | 4266.6667 | 10000 | 3562.2434 | 0 | 0
2019-10-08 05:00 | 935.1457 | 0 | 6160 | 10000 | 5224.8543 | 0 | 0
2019-10-08 06:00 | 1266.0925 | 942.1892 | 4266.6667 | 10000 | 3942.7634 | 0 | 0
2019-10-08 07:00 | 1189.2323 | 3213.2713 | 7873.3333 | 10000 | 9897.3724 | 0 | 0
2019-10-08 08:00 | 1001.9362 | 5203.244 | 4266.6667 | 10000 | 8467.9745 | 0 | 0
2019-10-08 09:00 | 979.8546 | 6604.5857 | 2773.3333 | 10000 | 8398.0645 | 0 | 0
2019-10-08 10:00 | 968.4253 | 7398.5123 | 4266.6667 | 10000 | 10696.7537 | 0 | 0
2019-10-08 11:00 | 940.6123 | 7618.8834 | 7873.3333 | 10000 | 14551.6044 | 0 | 0
2019-10-08 12:00 | 909.9079 | 7324.687 | 4266.6667 | 10000 | 10681.4457 | 0 | 0
2019-10-08 13:00 | 896.3553 | 6449.7589 | 4266.6667 | 10000 | 9820.0703 | 0 | 0
2019-10-08 14:00 | 932.872 | 5108.9785 | 4266.6667 | 10000 | 8442.7731 | 0 | 0
2019-10-08 15:00 | 1094.8808 | 3162.799 | 2773.3333 | 10000 | 4841.2516 | 0 | 0
2019-10-08 16:00 | 1410.8665 | 979.5171 | 2773.3333 | 10000 | 2341.9839 | 0 | 0
2019-10-08 17:00 | 1689.9706 | 0 | 1666.6667 | 10000 | -23.3039 | -23.3039 | 0
2019-10-08 18:00 | 1901.8268 | 0 | 873.3333 | 9976.6961 | -1028.4935 | -1028.4935 | 0
2019-10-08 19:00 | 1968.733 | 0 | 286.6667 | 8948.2026 | -1682.0663 | -1682.0663 | 0
2019-10-08 20:00 | 1780.3507 | 0 | 286.6667 | 7266.1363 | -1493.684 | -1493.684 | 0
2019-10-08 21:00 | 1430.5826 | 0 | 286.6667 | 5772.4523 | -1143.9159 | -1143.9159 | 0
2019-10-08 22:00 | 1085.3227 | 0 | 286.6667 | 4628.5364 | -798.6561 | -798.6561 | 0
2019-10-08 23:00 | 747.7339 | 0 | 286.6667 | 3829.8803 | -461.0673 | -461.0673 | 0
2019-10-09 | 624.426 | 0 | 286.6667 | 3368.813 | -337.7593 | -337.7593 | 0
2019-10-09 01:00 | 568.153 | 0 | 0 | 3031.0537 | -568.153 | -568.153 | 0
2019-10-09 02:00 | 559.2931 | 0 | 286.6667 | 2462.9007 | -272.6264 | -272.6264 | 0
2019-10-09 03:00 | 560.8932 | 0 | 0 | 2190.2742 | -560.8932 | -560.8932 | 0
2019-10-09 04:00 | 622.7425 | 0 | 0 | 1629.381 | -622.7425 | -622.7425 | 0
2019-10-09 05:00 | 838.9551 | 0 | 0 | 1006.6386 | -838.9551 | -838.9551 | 0
2019-10-09 06:00 | 1168.0892 | 128.4792 | 0 | 167.6835 | -1039.6101 | -167.6835 | -871.9266
2019-10-09 07:00 | 1092.322 | 2572.4614 | 0 | 0 | 1480.1395 | 1480.1395 | 0
2019-10-09 08:00 | 902.4813 | 4377.4014 | 873.3333 | 1480.1395 | 4348.2535 | 4348.2535 | 0
2019-10-09 09:00 | 885.4044 | 2826.056 | 286.6667 | 5828.3929 | 2227.3183 | 2227.3183 | 0
2019-10-09 10:00 | 903.408 | 1218.7654 | 873.3333 | 8055.7112 | 1188.6908 | 1188.6908 | 0
2019-10-09 11:00 | 887.5521 | 992.366 | 1666.6667 | 9244.402 | 1771.4806 | 755.598 | 0
2019-10-09 12:00 | 861.5338 | 2799.3036 | 2773.3333 | 10000 | 4711.103 | 0 | 0
2019-10-09 13:00 | 852.9336 | 2858.7539 | 2773.3333 | 10000 | 4779.1537 | 0 | 0
2019-10-09 14:00 | 891.7439 | 1010.1393 | 2773.3333 | 10000 | 2891.7287 | 0 | 0
2019-10-09 15:00 | 1055.019 | 246.1759 | 9060 | 10000 | 8251.1569 | 0 | 0
2019-10-09 16:00 | 1371.6329 | 316.7019 | 7873.3333 | 10000 | 6818.4024 | 0 | 0
2019-10-09 17:00 | 1651.8929 | 0 | 9573.3333 | 10000 | 7921.4404 | 0 | 0
2019-10-09 18:00 | 1863.822 | 0 | 6160 | 10000 | 4296.178 | 0 | 0
2019-10-09 19:00 | 1930.0504 | 0 | 6160 | 10000 | 4229.9496 | 0 | 0
2019-10-09 20:00 | 1740.8342 | 0 | 2773.3333 | 10000 | 1032.4992 | 0 | 0
2019-10-09 21:00 | 1399.1827 | 0 | 4266.6667 | 10000 | 2867.484 | 0 | 0
2019-10-09 22:00 | 1079.4458 | 0 | 2773.3333 | 10000 | 1693.8875 | 0 | 0
2019-10-09 23:00 | 758.2389 | 0 | 873.3333 | 10000 | 115.0944 | 0 | 0
2019-10-10 | 656.0507 | 0 | 873.3333 | 10000 | 217.2826 | 0 | 0
2019-10-10 01:00 | 606.5387 | 0 | 1666.6667 | 10000 | 1060.128 | 0 | 0
2019-10-10 02:00 | 609.4364 | 0 | 1666.6667 | 10000 | 1057.2302 | 0 | 0
2019-10-10 03:00 | 624.8835 | 0 | 2773.3333 | 10000 | 2148.4498 | 0 | 0
2019-10-10 04:00 | 691.9109 | 0 | 1666.6667 | 10000 | 974.7557 | 0 | 0
2019-10-10 05:00 | 931.5926 | 0 | 2773.3333 | 10000 | 1841.7407 | 0 | 0
2019-10-10 06:00 | 1257.5904 | 932.8547 | 4266.6667 | 10000 | 3941.9309 | 0 | 0
2019-10-10 07:00 | 1188.1095 | 3258.6446 | 1666.6667 | 10000 | 3737.2017 | 0 | 0
2019-10-10 08:00 | 1001.192 | 5343.9798 | 2773.3333 | 10000 | 7116.1212 | 0 | 0
2019-10-10 09:00 | 993.4127 | 6712.0463 | 4266.6667 | 10000 | 9985.3003 | 0 | 0
2019-10-10 10:00 | 966.2047 | 7510.1543 | 2773.3333 | 10000 | 9317.283 | 0 | 0
2019-10-10 11:00 | 931.4378 | 7758.3784 | 1666.6667 | 10000 | 8493.6073 | 0 | 0
2019-10-10 12:00 | 893.8129 | 7421.8378 | 873.3333 | 10000 | 7401.3583 | 0 | 0
2019-10-10 13:00 | 878.5702 | 6503.2201 | 1666.6667 | 10000 | 7291.3166 | 0 | 0
2019-10-10 14:00 | 918.9859 | 5099.8843 | 2773.3333 | 10000 | 6954.2317 | 0 | 0
2019-10-10 15:00 | 1088.9769 | 3122.6766 | 873.3333 | 10000 | 2907.0331 | 0 | 0
2019-10-10 16:00 | 1435.7017 | 935.6457 | 1666.6667 | 10000 | 1166.6108 | 0 | 0
2019-10-10 17:00 | 1699.4669 | 0 | 873.3333 | 10000 | -826.1336 | -826.1336 | 0
2019-10-10 18:00 | 1913.1658 | 0 | 0 | 9173.8664 | -1913.1658 | -1913.1658 | 0
2019-10-10 19:00 | 1985.1641 | 0 | 286.6667 | 7260.7006 | -1698.4974 | -1698.4974 | 0
2019-10-10 20:00 | 1806.4166 | 0 | 0 | 5562.2032 | -1806.4166 | -1806.4166 | 0
2019-10-10 21:00 | 1478.138 | 0 | 286.6667 | 3755.7866 | -1191.4713 | -1191.4713 | 0
2019-10-10 22:00 | 1160.4034 | 0 | 286.6667 | 2564.3153 | -873.7367 | -873.7367 | 0
2019-10-10 23:00 | 835.3748 | 0 | 286.6667 | 1690.5786 | -548.7082 | -548.7082 | 0
2019-10-11 | 716.2907 | 0 | 873.3333 | 1141.8704 | 157.0426 | 157.0426 | 0
2019-10-11 01:00 | 668.2712 | 0 | 286.6667 | 1298.913 | -381.6046 | -381.6046 | 0
2019-10-11 02:00 | 664.324 | 0 | 286.6667 | 917.3084 | -377.6574 | -377.6574 | 0
2019-10-11 03:00 | 667.7297 | 0 | 286.6667 | 539.6511 | -381.063 | -381.063 | 0
2019-10-11 04:00 | 727.3597 | 0 | 286.6667 | 158.5881 | -440.693 | -158.5881 | -282.1049
2019-10-11 05:00 | 942.8327 | 0 | 286.6667 | 0 | -656.1661 | 0 | -938.271
2019-10-11 06:00 | 1269.5906 | 791.024 | 286.6667 | 0 | -191.8999 | 0 | -1130.1709
2019-10-11 07:00 | 1196.0096 | 2243.1279 | 286.6667 | 0 | 1333.7849 | 1333.7849 | 0
2019-10-11 08:00 | 1002.5765 | 4584.6693 | 1666.6667 | 1333.7849 | 5248.7595 | 5248.7595 | 0
2019-10-11 09:00 | 991.5649 | 5177.1401 | 2773.3333 | 6582.5444 | 6958.9086 | 3417.4556 | 0
2019-10-11 10:00 | 989.8438 | 7115.9631 | 1666.6667 | 10000 | 7792.786 | 0 | 0
2019-10-11 11:00 | 948.8291 | 7324.7836 | 873.3333 | 10000 | 7249.2878 | 0 | 0
2019-10-11 12:00 | 900.0659 | 6996.2849 | 1666.6667 | 10000 | 7762.8857 | 0 | 0
2019-10-11 13:00 | 884.3584 | 6152.5172 | 1666.6667 | 10000 | 6934.8255 | 0 | 0
2019-10-11 14:00 | 924.0515 | 4768.2967 | 2773.3333 | 10000 | 6617.5786 | 0 | 0
2019-10-11 15:00 | 1086.9289 | 2876.6548 | 1666.6667 | 10000 | 3456.3927 | 0 | 0
2019-10-11 16:00 | 1426.7677 | 790.6376 | 873.3333 | 10000 | 237.2032 | 0 | 0
2019-10-11 17:00 | 1689.1669 | 0 | 0 | 10000 | -1689.1669 | -1689.1669 | 0
2019-10-11 18:00 | 1902.6506 | 0 | 286.6667 | 8310.8331 | -1615.984 | -1615.984 | 0
2019-10-11 19:00 | 1971.8585 | 0 | 286.6667 | 6694.8492 | -1685.1918 | -1685.1918 | 0
2019-10-11 20:00 | 1790.7449 | 0 | 873.3333 | 5009.6574 | -917.4116 | -917.4116 | 0
2019-10-11 21:00 | 1458.3768 | 0 | 4266.6667 | 4092.2458 | 2808.2899 | 2808.2899 | 0
2019-10-11 22:00 | 1139.9521 | 0 | 4266.6667 | 6900.5357 | 3126.7146 | 3099.4643 | 0
2019-10-11 23:00 | 806.5968 | 0 | 6160 | 10000 | 5353.4032 | 0 | 0
2019-10-12 | 685.7636 | 0 | 2773.3333 | 10000 | 2087.5697 | 0 | 0
2019-10-12 01:00 | 637.6795 | 0 | 6160 | 10000 | 5522.3205 | 0 | 0
2019-10-12 02:00 | 630.7342 | 0 | 6160 | 10000 | 5529.2658 | 0 | 0
2019-10-12 03:00 | 632.4085 | 0 | 4266.6667 | 10000 | 3634.2582 | 0 | 0
2019-10-12 04:00 | 693.4838 | 0 | 6160 | 10000 | 5466.5162 | 0 | 0
2019-10-12 05:00 | 908.9443 | 0 | 4266.6667 | 10000 | 3357.7224 | 0 | 0
2019-10-12 06:00 | 1251.7733 | 778.726 | 4266.6667 | 10000 | 3793.6194 | 0 | 0
2019-10-12 07:00 | 1172.2921 | 2963.167 | 4266.6667 | 10000 | 6057.5416 | 0 | 0
2019-10-12 08:00 | 993.43 | 4889.6723 | 6160 | 10000 | 10056.2423 | 0 | 0
2019-10-12 09:00 | 997.7378 | 6170.3664 | 9060 | 10000 | 14232.6286 | 0 | 0
2019-10-12 10:00 | 981.4633 | 6880.6949 | 7873.3333 | 10000 | 13772.565 | 0 | 0
2019-10-12 11:00 | 951.5208 | 7084.4174 | 4266.6667 | 10000 | 10399.5633 | 0 | 0
2019-10-12 12:00 | 915.4354 | 6796.5472 | 4266.6667 | 10000 | 10147.7785 | 0 | 0
2019-10-12 13:00 | 894.5868 | 5963.3951 | 4266.6667 | 10000 | 9335.475 | 0 | 0
2019-10-12 14:00 | 931.8267 | 4627.8047 | 2773.3333 | 10000 | 6469.3114 | 0 | 0
2019-10-12 15:00 | 1089.0789 | 2801.6289 | 2773.3333 | 10000 | 4485.8832 | 0 | 0
2019-10-12 16:00 | 1420.8259 | 758.3261 | 1666.6667 | 10000 | 1004.1669 | 0 | 0
2019-10-12 17:00 | 1681.2895 | 0 | 873.3333 | 10000 | -807.9562 | -807.9562 | 0
2019-10-12 18:00 | 1889.1999 | 0 | 873.3333 | 9192.0438 | -1015.8666 | -1015.8666 | 0
2019-10-12 19:00 | 1958.4013 | 0 | 873.3333 | 8176.1772 | -1085.0679 | -1085.0679 | 0
2019-10-12 20:00 | 1772.773 | 0 | 0 | 7091.1093 | -1772.773 | -1772.773 | 0
2019-10-12 21:00 | 1439.4297 | 0 | 0 | 5318.3363 | -1439.4297 | -1439.4297 | 0
2019-10-12 22:00 | 1117.8428 | 0 | 0 | 3878.9066 | -1117.8428 | -1117.8428 | 0
2019-10-12 23:00 | 788.2746 | 0 | 0 | 2761.0638 | -788.2746 | -788.2746 | 0
2019-10-13 | 666.1768 | 0 | 286.6667 | 1972.7892 | -379.5102 | -379.5102 | 0
2019-10-13 01:00 | 607.0842 | 0 | 0 | 1593.279 | -607.0842 | -607.0842 | 0
2019-10-13 02:00 | 600.4429 | 0 | 0 | 986.1948 | -600.4429 | -600.4429 | 0
2019-10-13 03:00 | 598.5516 | 0 | 0 | 385.7519 | -598.5516 | -385.7519 | -212.7997
2019-10-13 04:00 | 658.5725 | 0 | 286.6667 | 0 | -371.9059 | 0 | -584.7056
2019-10-13 05:00 | 871.6676 | 0 | 286.6667 | 0 | -585.001 | 0 | -1169.7065
2019-10-13 06:00 | 1197.2063 | 188.0192 | 2773.3333 | 0 | 1764.1463 | 1764.1463 | 0
2019-10-13 07:00 | 1130.6661 | 1678.3629 | 2773.3333 | 1764.1463 | 3321.0302 | 3321.0302 | 0
2019-10-13 08:00 | 942.6203 | 315.7773 | 2773.3333 | 5085.1765 | 2146.4904 | 2146.4904 | 0
2019-10-13 09:00 | 939.9168 | 1995.8192 | 2773.3333 | 7231.6668 | 3829.2358 | 2768.3332 | 0
2019-10-13 10:00 | 934.948 | 3970.0771 | 1666.6667 | 10000 | 4701.7958 | 0 | 0
2019-10-13 11:00 | 902.8102 | 3992.524 | 4266.6667 | 10000 | 7356.3805 | 0 | 0
2019-10-13 12:00 | 869.2066 | 4414.099 | 4266.6667 | 10000 | 7811.5592 | 0 | 0
2019-10-13 13:00 | 859.8394 | 3012.7102 | 4266.6667 | 10000 | 6419.5374 | 0 | 0
2019-10-13 14:00 | 895.0477 | 3624.5481 | 6160 | 10000 | 8889.5005 | 0 | 0
2019-10-13 15:00 | 1055.6608 | 1841.3627 | 6160 | 10000 | 6945.7019 | 0 | 0
2019-10-13 16:00 | 1376.6688 | 651.5037 | 4266.6667 | 10000 | 3541.5016 | 0 | 0
2019-10-13 17:00 | 1651.8929 | 0 | 1666.6667 | 10000 | 14.7738 | 0 | 0
2019-10-13 18:00 | 1863.822 | 0 | 873.3333 | 10000 | -990.4886 | -990.4886 | 0
2019-10-13 19:00 | 1930.0504 | 0 | 873.3333 | 9009.5114 | -1056.7171 | -1056.7171 | 0
2019-10-13 20:00 | 1740.8342 | 0 | 0 | 7952.7943 | -1740.8342 | -1740.8342 | 0
2019-10-13 21:00 | 1400.9966 | 0 | 0 | 6211.9601 | -1400.9966 | -1400.9966 | 0
2019-10-13 22:00 | 1077.8677 | 0 | 0 | 4810.9635 | -1077.8677 | -1077.8677 | 0
2019-10-13 23:00 | 744.7129 | 0 | 0 | 3733.0958 | -744.7129 | -744.7129 | 0
2019-10-14 | 627.2198 | 0 | 0 | 2988.3829 | -627.2198 | -627.2198 | 0
2019-10-14 01:00 | 568.8887 | 0 | 0 | 2361.1632 | -568.8887 | -568.8887 | 0
2019-10-14 02:00 | 560.7455 | 0 | 0 | 1792.2745 | -560.7455 | -560.7455 | 0
2019-10-14 03:00 | 562.2724 | 0 | 0 | 1231.529 | -562.2724 | -562.2724 | 0
2019-10-14 04:00 | 624.0127 | 0 | 0 | 669.2565 | -624.0127 | -624.0127 | 0
2019-10-14 05:00 | 847.948 | 0 | 0 | 45.2438 | -847.948 | -45.2438 | -802.7041
2019-10-14 06:00 | 1198.6704 | 752.9027 | 0 | 0 | -445.7677 | 0 | -1248.4719
2019-10-14 07:00 | 1141.7203 | 2310.1177 | 0 | 0 | 1168.3974 | 1168.3974 | -80.0745
2019-10-14 08:00 | 985.2632 | 4823.284 | 0 | 1168.3974 | 3838.0208 | 3838.0208 | 0
2019-10-14 09:00 | 982.1524 | 6168.0192 | 0 | 5006.4181 | 5185.8669 | 4993.5819 | 0
2019-10-14 10:00 | 984.4631 | 5953.7144 | 0 | 10000 | 4969.2514 | 0 | 0
2019-10-14 11:00 | 953.6595 | 3039.2269 | 0 | 10000 | 2085.5674 | 0 | 0
2019-10-14 12:00 | 910.9964 | 4011.4714 | 0 | 10000 | 3100.475 | 0 | 0
2019-10-14 13:00 | 896.3553 | 3520.9147 | 0 | 10000 | 2624.5595 | 0 | 0
2019-10-14 14:00 | 932.872 | 4663.9998 | 0 | 10000 | 3731.1278 | 0 | 0
2019-10-14 15:00 | 1094.8808 | 2732.3068 | 286.6667 | 10000 | 1924.0927 | 0 | 0
2019-10-14 16:00 | 1410.8665 | 699.6623 | 0 | 10000 | -711.2042 | -711.2042 | 0
2019-10-14 17:00 | 1689.9706 | 0 | 0 | 9288.7958 | -1689.9706 | -1689.9706 | 0
2019-10-14 18:00 | 1901.8268 | 0 | 0 | 7598.8253 | -1901.8268 | -1901.8268 | 0
2019-10-14 19:00 | 1968.733 | 0 | 0 | 5696.9984 | -1968.733 | -1968.733 | 0
2019-10-14 20:00 | 1780.3507 | 0 | 0 | 3728.2654 | -1780.3507 | -1780.3507 | 0
2019-10-14 21:00 | 1430.5826 | 0 | 0 | 1947.9147 | -1430.5826 | -1430.5826 | 0
2019-10-14 22:00 | 1083.1953 | 0 | 0 | 517.3322 | -1083.1953 | -517.3322 | -565.8631
2019-10-14 23:00 | 731.6677 | 0 | 0 | 0 | -731.6677 | 0 | -1297.5309
2019-10-15 | 613.5278 | 0 | 0 | 0 | -613.5278 | 0 | -1911.0587
2019-10-15 01:00 | 567.3851 | 0 | 0 | 0 | -567.3851 | 0 | -2478.4438
2019-10-15 02:00 | 563.4783 | 0 | 0 | 0 | -563.4783 | 0 | -3041.9221
2019-10-15 03:00 | 575.7095 | 0 | 0 | 0 | -575.7095 | 0 | -3617.6315
2019-10-15 04:00 | 646.8908 | 0 | 0 | 0 | -646.8908 | 0 | -4264.5223
2019-10-15 05:00 | 884.5484 | 0 | 0 | 0 | -884.5484 | 0 | -5149.0707
2019-10-15 06:00 | 1232.4542 | 816.5632 | 0 | 0 | -415.891 | 0 | -5564.9617
2019-10-15 07:00 | 1170.4708 | 3075.9268 | 0 | 0 | 1905.4561 | 1905.4561 | -3659.5056
2019-10-15 08:00 | 994.3842 | 5108.039 | 873.3333 | 1905.4561 | 4986.988 | 4986.988 | 0
2019-10-15 09:00 | 987.654 | 6475.6327 | 1666.6667 | 6892.4441 | 7154.6454 | 3107.5559 | 0
2019-10-15 10:00 | 977.2088 | 7280.0336 | 2773.3333 | 10000 | 9076.1581 | 0 | 0
2019-10-15 11:00 | 943.2047 | 7504.8506 | 2773.3333 | 10000 | 9334.9792 | 0 | 0
2019-10-15 12:00 | 910.692 | 7159.1628 | 6160 | 10000 | 12408.4709 | 0 | 0
2019-10-15 13:00 | 896.3553 | 6299.0307 | 9060 | 10000 | 14462.6754 | 0 | 0
2019-10-15 14:00 | 933.184 | 4883.9672 | 9060 | 10000 | 13010.7832 | 0 | 0
2019-10-15 15:00 | 1095.687 | 2888.2181 | 9060 | 10000 | 10852.5311 | 0 | 0
2019-10-15 16:00 | 1431.518 | 753.8986 | 7873.3333 | 10000 | 7195.7139 | 0 | 0
2019-10-15 17:00 | 1698.3482 | 0 | 6160 | 10000 | 4461.6518 | 0 | 0
2019-10-15 18:00 | 1915.2884 | 0 | 7873.3333 | 10000 | 5958.0449 | 0 | 0
2019-10-15 19:00 | 1988.5297 | 0 | 9060 | 10000 | 7071.4703 | 0 | 0
2019-10-15 20:00 | 1811.6793 | 0 | 9573.3333 | 10000 | 7761.654 | 0 | 0
2019-10-15 21:00 | 1475.6183 | 0 | 9573.3333 | 10000 | 8097.715 | 0 | 0
2019-10-15 22:00 | 1145.0046 | 0 | 9573.3333 | 10000 | 8428.3287 | 0 | 0
2019-10-15 23:00 | 807.0369 | 0 | 4266.6667 | 10000 | 3459.6298 | 0 | 0
2019-10-16 | 682.166 | 0 | 4266.6667 | 10000 | 3584.5007 | 0 | 0
2019-10-16 01:00 | 627.6629 | 0 | 1666.6667 | 10000 | 1039.0038 | 0 | 0
2019-10-16 02:00 | 623.0075 | 0 | 1666.6667 | 10000 | 1043.6592 | 0 | 0
2019-10-16 03:00 | 624.4554 | 0 | 2773.3333 | 10000 | 2148.878 | 0 | 0
2019-10-16 04:00 | 687.6122 | 0 | 2773.3333 | 10000 | 2085.7212 | 0 | 0
2019-10-16 05:00 | 920.9292 | 0 | 2773.3333 | 10000 | 1852.4041 | 0 | 0
2019-10-16 06:00 | 1252.8428 | 41.0021 | 2773.3333 | 10000 | 1561.4926 | 0 | 0
2019-10-16 07:00 | 1169.714 | 1408.3785 | 1666.6667 | 10000 | 1905.3312 | 0 | 0
2019-10-16 08:00 | 971.9374 | 668.8009 | 4266.6667 | 10000 | 3963.5301 | 0 | 0
2019-10-16 09:00 | 957.372 | 1828.3114 | 873.3333 | 10000 | 1744.2727 | 0 | 0
2019-10-16 10:00 | 941.0031 | 4892.7463 | 1666.6667 | 10000 | 5618.4099 | 0 | 0
2019-10-16 11:00 | 907.5841 | 7390.8258 | 2773.3333 | 10000 | 9256.5749 | 0 | 0
2019-10-16 12:00 | 872.4995 | 7035.8219 | 4266.6667 | 10000 | 10429.9891 | 0 | 0
2019-10-16 13:00 | 860.346 | 3465.1535 | 2773.3333 | 10000 | 5378.1409 | 0 | 0
2019-10-16 14:00 | 899.5074 | 4845.1547 | 2773.3333 | 10000 | 6718.9806 | 0 | 0
2019-10-16 15:00 | 1064.2639 | 2818.1037 | 2773.3333 | 10000 | 4527.1732 | 0 | 0
2019-10-16 16:00 | 1400.09 | 722.7359 | 1666.6667 | 10000 | 989.3126 | 0 | 0
2019-10-16 17:00 | 1667.0211 | 0 | 7873.3333 | 10000 | 6206.3122 | 0 | 0
2019-10-16 18:00 | 1880.634 | 0 | 2773.3333 | 10000 | 892.6993 | 0 | 0
2019-10-16 19:00 | 1951.6825 | 0 | 4266.6667 | 10000 | 2314.9841 | 0 | 0
2019-10-16 20:00 | 1771.1417 | 0 | 4266.6667 | 10000 | 2495.5249 | 0 | 0
2019-10-16 21:00 | 1442.593 | 0 | 4266.6667 | 10000 | 2824.0737 | 0 | 0
2019-10-16 22:00 | 1125.5543 | 0 | 2773.3333 | 10000 | 1647.7791 | 0 | 0
2019-10-16 23:00 | 798.1201 | 0 | 873.3333 | 10000 | 75.2132 | 0 | 0
2019-10-17 | 680.902 | 0 | 873.3333 | 10000 | 192.4313 | 0 | 0
2019-10-17 01:00 | 628.7978 | 0 | 1666.6667 | 10000 | 1037.8688 | 0 | 0
2019-10-17 02:00 | 621.812 | 0 | 2773.3333 | 10000 | 2151.5213 | 0 | 0
2019-10-17 03:00 | 625.256 | 0 | 2773.3333 | 10000 | 2148.0773 | 0 | 0
2019-10-17 04:00 | 687.4106 | 0 | 4266.6667 | 10000 | 3579.2561 | 0 | 0
2019-10-17 05:00 | 921.588 | 0 | 873.3333 | 10000 | -48.2547 | -48.2547 | 0
2019-10-17 06:00 | 1255.5517 | 505.8792 | 873.3333 | 9951.7453 | 123.6608 | 48.2547 | 0
2019-10-17 07:00 | 1162.2309 | 2169.7418 | 873.3333 | 10000 | 1880.8442 | 0 | 0
2019-10-17 08:00 | 972.125 | 5043.7804 | 0 | 10000 | 4071.6554 | 0 | 0
2019-10-17 09:00 | 996.6055 | 6500.4152 | 286.6667 | 10000 | 5790.4764 | 0 | 0
2019-10-17 10:00 | 1020.046 | 7364.7783 | 0 | 10000 | 6344.7322 | 0 | 0
2019-10-17 11:00 | 980.9336 | 7630.764 | 0 | 10000 | 6649.8305 | 0 | 0
2019-10-17 12:00 | 945.5826 | 7315.5801 | 0 | 10000 | 6369.9975 | 0 | 0
2019-10-17 13:00 | 937.4155 | 1011.0375 | 0 | 10000 | 73.6219 | 0 | 0
2019-10-17 14:00 | 975.8367 | 1324.0513 | 0 | 10000 | 348.2146 | 0 | 0
2019-10-17 15:00 | 1134.2855 | 1298.4558 | 873.3333 | 10000 | 1037.5037 | 0 | 0
2019-10-17 16:00 | 1473.4161 | 213.6953 | 873.3333 | 10000 | -386.3874 | -386.3874 | 0
2019-10-17 17:00 | 1728.2992 | 0 | 873.3333 | 9613.6126 | -854.9659 | -854.9659 | 0
2019-10-17 18:00 | 1937.7087 | 0 | 2773.3333 | 8758.6466 | 835.6247 | 835.6247 | 0
2019-10-17 19:00 | 2002.5121 | 0 | 4266.6667 | 9594.2713 | 2264.1546 | 405.7287 | 0
2019-10-17 20:00 | 1823.2099 | 0 | 4266.6667 | 10000 | 2443.4568 | 0 | 0
2019-10-17 21:00 | 1490.7347 | 0 | 873.3333 | 10000 | -617.4014 | -617.4014 | 0
2019-10-17 22:00 | 1169.9879 | 0 | 2773.3333 | 9382.5986 | 1603.3454 | 617.4014 | 0
2019-10-17 23:00 | 838.2203 | 0 | 2773.3333 | 10000 | 1935.113 | 0 | 0
2019-10-18 | 721.2085 | 0 | 4266.6667 | 10000 | 3545.4582 | 0 | 0
2019-10-18 01:00 | 664.5923 | 0 | 4266.6667 | 10000 | 3602.0744 | 0 | 0
2019-10-18 02:00 | 654.0135 | 0 | 2773.3333 | 10000 | 2119.3198 | 0 | 0
2019-10-18 03:00 | 653.4319 | 0 | 2773.3333 | 10000 | 2119.9014 | 0 | 0
2019-10-18 04:00 | 714.4765 | 0 | 2773.3333 | 10000 | 2058.8568 | 0 | 0
2019-10-18 05:00 | 927.9735 | 0 | 2773.3333 | 10000 | 1845.3598 | 0 | 0
2019-10-18 06:00 | 1271.678 | 814.5841 | 1666.6667 | 10000 | 1209.5727 | 0 | 0
2019-10-18 07:00 | 1187.1949 | 3161.1441 | 873.3333 | 10000 | 2847.2826 | 0 | 0
2019-10-18 08:00 | 992.7686 | 5273.2054 | 873.3333 | 10000 | 5153.7702 | 0 | 0
2019-10-18 09:00 | 990.1643 | 6764.0435 | 2773.3333 | 10000 | 8547.2126 | 0 | 0
2019-10-18 10:00 | 970.533 | 7599.8037 | 1666.6667 | 10000 | 8295.9374 | 0 | 0
2019-10-18 11:00 | 941.4625 | 7859.7394 | 286.6667 | 10000 | 7204.9435 | 0 | 0
2019-10-18 12:00 | 907.9001 | 1673.074 | 286.6667 | 10000 | 1051.8406 | 0 | 0
2019-10-18 13:00 | 903.1981 | 2896.1117 | 873.3333 | 10000 | 2866.2469 | 0 | 0
2019-10-18 14:00 | 943.0718 | 3420.6739 | 0 | 10000 | 2477.6021 | 0 | 0
2019-10-18 15:00 | 1106.4957 | 1719.2201 | 0 | 10000 | 612.7244 | 0 | 0
2019-10-18 16:00 | 1452.8035 | 680.677 | 286.6667 | 10000 | -485.4599 | -485.4599 | 0
2019-10-18 17:00 | 1715.8499 | 0 | 0 | 9514.5401 | -1715.8499 | -1715.8499 | 0
2019-10-18 18:00 | 1928.3497 | 0 | 0 | 7798.6903 | -1928.3497 | -1928.3497 | 0
2019-10-18 19:00 | 1999.1976 | 0 | 0 | 5870.3406 | -1999.1976 | -1999.1976 | 0
2019-10-18 20:00 | 1816.3257 | 0 | 0 | 3871.143 | -1816.3257 | -1816.3257 | 0
2019-10-18 21:00 | 1489.3613 | 0 | 0 | 2054.8173 | -1489.3613 | -1489.3613 | 0
2019-10-18 22:00 | 1170.4217 | 0 | 0 | 565.456 | -1170.4217 | -565.456 | -604.9656
2019-10-18 23:00 | 843.2119 | 0 | 286.6667 | 0 | -556.5452 | 0 | -1161.5108
2019-10-19 | 726.7226 | 0 | 873.3333 | 0 | 146.6107 | 146.6107 | -1014.9001
2019-10-19 01:00 | 674.5619 | 0 | 286.6667 | 146.6107 | -387.8952 | -146.6107 | -1256.1847
2019-10-19 02:00 | 668.4113 | 0 | 0 | 0 | -668.4113 | 0 | -1924.596
2019-10-19 03:00 | 674.3289 | 0 | 286.6667 | 0 | -387.6622 | 0 | -2312.2583
2019-10-19 04:00 | 737.2329 | 0 | 0 | 0 | -737.2329 | 0 | -3049.4912
2019-10-19 05:00 | 954.1909 | 0 | 286.6667 | 0 | -667.5243 | 0 | -3717.0155
2019-10-19 06:00 | 1280.4079 | 805.598 | 0 | 0 | -474.8099 | 0 | -4191.8254
2019-10-19 07:00 | 1198.8539 | 3147.5224 | 0 | 0 | 1948.6685 | 1948.6685 | -2243.1568
2019-10-19 08:00 | 998.4698 | 5242.5579 | 2773.3333 | 1948.6685 | 7017.4215 | 7017.4215 | 0
2019-10-19 09:00 | 981.7296 | 6712.5695 | 6160 | 8966.09 | 11890.8399 | 1033.91 | 0
2019-10-19 10:00 | 957.2549 | 7529.8193 | 6160 | 10000 | 12732.5644 | 0 | 0
2019-10-19 11:00 | 932.0411 | 7725.7506 | 6160 | 10000 | 12953.7095 | 0 | 0
2019-10-19 12:00 | 893.669 | 7344.6762 | 4266.6667 | 10000 | 10717.6739 | 0 | 0
2019-10-19 13:00 | 873.5257 | 6395.3075 | 4266.6667 | 10000 | 9788.4486 | 0 | 0
2019-10-19 14:00 | 905.9898 | 4897.0059 | 6160 | 10000 | 10151.0161 | 0 | 0
2019-10-19 15:00 | 1067.125 | 2810.0825 | 9060 | 10000 | 10802.9575 | 0 | 0
2019-10-19 16:00 | 1394.962 | 656.5937 | 7873.3333 | 10000 | 7134.965 | 0 | 0
2019-10-19 17:00 | 1662.9326 | 0 | 2773.3333 | 10000 | 1110.4008 | 0 | 0
2019-10-19 18:00 | 1877.5256 | 0 | 4266.6667 | 10000 | 2389.141 | 0 | 0
2019-10-19 19:00 | 1945.7291 | 0 | 7873.3333 | 10000 | 5927.6042 | 0 | 0
2019-10-19 20:00 | 1770.0132 | 0 | 6160 | 10000 | 4389.9868 | 0 | 0
2019-10-19 21:00 | 1441.5226 | 0 | 4266.6667 | 10000 | 2825.1441 | 0 | 0
2019-10-19 22:00 | 1121.7271 | 0 | 4266.6667 | 10000 | 3144.9395 | 0 | 0
2019-10-19 23:00 | 794.2311 | 0 | 1666.6667 | 10000 | 872.4355 | 0 | 0
2019-10-20 | 677.5984 | 0 | 2773.3333 | 10000 | 2095.7349 | 0 | 0
2019-10-20 01:00 | 625.1471 | 0 | 2773.3333 | 10000 | 2148.1863 | 0 | 0
2019-10-20 02:00 | 618.6443 | 0 | 4266.6667 | 10000 | 3648.0224 | 0 | 0
2019-10-20 03:00 | 621.1686 | 0 | 2773.3333 | 10000 | 2152.1648 | 0 | 0
2019-10-20 04:00 | 685.4444 | 0 | 4266.6667 | 10000 | 3581.2223 | 0 | 0
2019-10-20 05:00 | 913.3082 | 0 | 1666.6667 | 10000 | 753.3585 | 0 | 0
2019-10-20 06:00 | 1232.6134 | 52.5872 | 873.3333 | 10000 | -306.6928 | -306.6928 | 0
2019-10-20 07:00 | 1155.5851 | 133.4518 | 873.3333 | 9693.3072 | -148.8 | -148.8 | 0
2019-10-20 08:00 | 958.2079 | 717.5747 | 6160 | 9544.5072 | 5919.3668 | 455.4928 | 0
2019-10-20 09:00 | 939.1675 | 2823.1074 | 2773.3333 | 10000 | 4657.2732 | 0 | 0
2019-10-20 10:00 | 926.1435 | 3705.5898 | 2773.3333 | 10000 | 5552.7797 | 0 | 0
2019-10-20 11:00 | 898.7055 | 2727.2434 | 4266.6667 | 10000 | 6095.2046 | 0 | 0
2019-10-20 12:00 | 866.2777 | 2269.6112 | 873.3333 | 10000 | 2276.6669 | 0 | 0
2019-10-20 13:00 | 855.271 | 1940.9298 | 1666.6667 | 10000 | 2752.3255 | 0 | 0
2019-10-20 14:00 | 898.2953 | 4247.3387 | 2773.3333 | 10000 | 6122.3767 | 0 | 0
2019-10-20 15:00 | 1066.5953 | 1043.9286 | 6160 | 10000 | 6137.3333 | 0 | 0
2019-10-20 16:00 | 1409.3389 | 404.0444 | 2773.3333 | 10000 | 1768.0388 | 0 | 0
2019-10-20 17:00 | 1676.1783 | 0 | 873.3333 | 10000 | -802.845 | -802.845 | 0
2019-10-20 18:00 | 1890.7677 | 0 | 873.3333 | 9197.155 | -1017.4344 | -1017.4344 | 0
2019-10-20 19:00 | 1965.3828 | 0 | 1666.6667 | 8179.7207 | -298.7161 | -298.7161 | 0
2019-10-20 20:00 | 1789.8106 | 0 | 873.3333 | 7881.0046 | -916.4773 | -916.4773 | 0
2019-10-20 21:00 | 1461.3721 | 0 | 1666.6667 | 6964.5273 | 205.2946 | 205.2946 | 0
2019-10-20 22:00 | 1143.6673 | 0 | 873.3333 | 7169.8218 | -270.3339 | -270.3339 | 0
2019-10-20 23:00 | 814.9002 | 0 | 286.6667 | 6899.4879 | -528.2335 | -528.2335 | 0
2019-10-21 | 703.9159 | 0 | 0 | 6371.2544 | -703.9159 | -703.9159 | 0
2019-10-21 01:00 | 647.3883 | 0 | 0 | 5667.3385 | -647.3883 | -647.3883 | 0
2019-10-21 02:00 | 637.5216 | 0 | 0 | 5019.9502 | -637.5216 | -637.5216 | 0
2019-10-21 03:00 | 638.5313 | 0 | 286.6667 | 4382.4286 | -351.8647 | -351.8647 | 0
2019-10-21 04:00 | 696.4608 | 0 | 0 | 4030.5639 | -696.4608 | -696.4608 | 0
2019-10-21 05:00 | 927.2697 | 0 | 0 | 3334.1031 | -927.2697 | -927.2697 | 0
2019-10-21 06:00 | 1259.7424 | 0 | 0 | 2406.8334 | -1259.7424 | -1259.7424 | 0
2019-10-21 07:00 | 1202.4025 | 0.7751 | 0 | 1147.091 | -1201.6274 | -1147.091 | -54.5364
2019-10-21 08:00 | 1020.72 | 741.1842 | 0 | 0 | -279.5358 | 0 | -334.0722
2019-10-21 09:00 | 1003.9812 | 982.4944 | 0 | 0 | -21.4867 | 0 | -355.559
2019-10-21 10:00 | 986.8035 | 1128.5571 | 0 | 0 | 141.7536 | 141.7536 | -213.8054
2019-10-21 11:00 | 945.161 | 2666.1439 | 286.6667 | 141.7536 | 2007.6496 | 2007.6496 | 0
2019-10-21 12:00 | 909.9079 | 3036.5957 | 0 | 2149.4032 | 2126.6878 | 2126.6878 | 0
2019-10-21 13:00 | 896.3553 | 2293.4416 | 286.6667 | 4276.0909 | 1683.753 | 1683.753 | 0
2019-10-21 14:00 | 932.872 | 1479.759 | 1666.6667 | 5959.8439 | 2213.5537 | 2213.5537 | 0
2019-10-21 15:00 | 1094.8808 | 240.956 | 1666.6667 | 8173.3976 | 812.7419 | 812.7419 | 0
2019-10-21 16:00 | 1410.8665 | 0 | 873.3333 | 8986.1395 | -537.5332 | -537.5332 | 0
2019-10-21 17:00 | 1689.9706 | 0 | 873.3333 | 8448.6064 | -816.6372 | -816.6372 | 0
2019-10-21 18:00 | 1901.8268 | 0 | 873.3333 | 7631.9691 | -1028.4935 | -1028.4935 | 0
2019-10-21 19:00 | 1968.733 | 0 | 286.6667 | 6603.4756 | -1682.0663 | -1682.0663 | 0
2019-10-21 20:00 | 1780.3507 | 0 | 873.3333 | 4921.4093 | -907.0174 | -907.0174 | 0
2019-10-21 21:00 | 1430.5826 | 0 | 0 | 4014.392 | -1430.5826 | -1430.5826 | 0
2019-10-21 22:00 | 1090.5826 | 0 | 0 | 2583.8094 | -1090.5826 | -1090.5826 | 0
2019-10-21 23:00 | 752.344 | 0 | 0 | 1493.2268 | -752.344 | -752.344 | 0
2019-10-22 | 634.4006 | 0 | 0 | 740.8828 | -634.4006 | -634.4006 | 0
2019-10-22 01:00 | 580.4658 | 0 | 0 | 106.4822 | -580.4658 | -106.4822 | -473.9835
2019-10-22 02:00 | 574.9527 | 0 | 0 | 0 | -574.9527 | 0 | -1048.9362
2019-10-22 03:00 | 582.1893 | 0 | 0 | 0 | -582.1893 | 0 | -1631.1256
2019-10-22 04:00 | 650.1839 | 0 | 0 | 0 | -650.1839 | 0 | -2281.3094
2019-10-22 05:00 | 885.5958 | 0 | 0 | 0 | -885.5958 | 0 | -3166.9052
2019-10-22 06:00 | 1228.2553 | 169.3858 | 0 | 0 | -1058.8695 | 0 | -4225.7748
2019-10-22 07:00 | 1156.7903 | 1861.298 | 0 | 0 | 704.5077 | 704.5077 | -3521.2671
2019-10-22 08:00 | 975.9758 | 3000.3638 | 0 | 704.5077 | 2024.388 | 2024.388 | -792.3713
2019-10-22 09:00 | 964.2462 | 1453.6644 | 0 | 2728.8958 | 489.4182 | 489.4182 | 0
2019-10-22 10:00 | 961.6601 | 5143.4428 | 0 | 3218.314 | 4181.7828 | 4181.7828 | 0
2019-10-22 11:00 | 940.6123 | 3588.2633 | 873.3333 | 7400.0967 | 3520.9844 | 2599.9033 | 0
2019-10-22 12:00 | 909.9079 | 5530.8169 | 1666.6667 | 10000 | 6287.5756 | 0 | 0
2019-10-22 13:00 | 896.3553 | 4538.521 | 1666.6667 | 10000 | 5308.8324 | 0 | 0
2019-10-22 14:00 | 932.872 | 2243.1555 | 873.3333 | 10000 | 2183.6168 | 0 | 0
2019-10-22 15:00 | 1094.8808 | 943.667 | 286.6667 | 10000 | 135.4529 | 0 | 0
2019-10-22 16:00 | 1410.8665 | 66.2895 | 286.6667 | 10000 | -1057.9104 | -1057.9104 | 0
2019-10-22 17:00 | 1689.9706 | 0 | 286.6667 | 8942.0896 | -1403.3039 | -1403.3039 | 0
2019-10-22 18:00 | 1901.8268 | 0 | 286.6667 | 7538.7857 | -1615.1602 | -1615.1602 | 0
2019-10-22 19:00 | 1968.733 | 0 | 0 | 5923.6256 | -1968.733 | -1968.733 | 0
2019-10-22 20:00 | 1780.3507 | 0 | 0 | 3954.8926 | -1780.3507 | -1780.3507 | 0
2019-10-22 21:00 | 1430.5826 | 0 | 0 | 2174.5419 | -1430.5826 | -1430.5826 | 0
2019-10-22 22:00 | 1091.0998 | 0 | 0 | 743.9593 | -1091.0998 | -743.9593 | -347.1404
2019-10-22 23:00 | 757.6199 | 0 | 0 | 0 | -757.6199 | 0 | -1104.7604
2019-10-23 | 638.9414 | 0 | 0 | 0 | -638.9414 | 0 | -1743.7018
2019-10-23 01:00 | 589.0412 | 0 | 0 | 0 | -589.0412 | 0 | -2332.743
2019-10-23 02:00 | 583.1597 | 0 | 0 | 0 | -583.1597 | 0 | -2915.9027
2019-10-23 03:00 | 590.0177 | 0 | 0 | 0 | -590.0177 | 0 | -3505.9203
2019-10-23 04:00 | 652.0126 | 0 | 0 | 0 | -652.0126 | 0 | -4157.9329
2019-10-23 05:00 | 868.552 | 0 | 0 | 0 | -868.552 | 0 | -5026.485
2019-10-23 06:00 | 1194.9322 | 601.0004 | 0 | 0 | -593.9318 | 0 | -5620.4168
2019-10-23 07:00 | 1119.9876 | 2790.6026 | 0 | 0 | 1670.6151 | 1670.6151 | -3949.8017
2019-10-23 08:00 | 928.6123 | 4882.0616 | 0 | 1670.6151 | 3953.4493 | 3953.4493 | 0
2019-10-23 09:00 | 901.6953 | 6347.6642 | 0 | 5624.0644 | 5445.9689 | 4375.9356 | 0
2019-10-23 10:00 | 903.408 | 7161.51 | 0 | 10000 | 6258.102 | 0 | 0
2019-10-23 11:00 | 887.5521 | 7416.0786 | 0 | 10000 | 6528.5265 | 0 | 0
2019-10-23 12:00 | 861.5338 | 5960.7444 | 286.6667 | 10000 | 5385.8772 | 0 | 0
2019-10-23 13:00 | 852.9336 | 6189.2379 | 286.6667 | 10000 | 5622.9709 | 0 | 0
2019-10-23 14:00 | 891.7439 | 4653.1334 | 286.6667 | 10000 | 4048.0562 | 0 | 0
2019-10-23 15:00 | 1055.019 | 2595.9847 | 0 | 10000 | 1540.9657 | 0 | 0
2019-10-23 16:00 | 1371.6329 | 489.3756 | 0 | 10000 | -882.2573 | -882.2573 | 0
2019-10-23 17:00 | 1651.8929 | 0 | 0 | 9117.7427 | -1651.8929 | -1651.8929 | 0
2019-10-23 18:00 | 1863.822 | 0 | 0 | 7465.8498 | -1863.822 | -1863.822 | 0
2019-10-23 19:00 | 1930.0504 | 0 | 0 | 5602.0279 | -1930.0504 | -1930.0504 | 0
2019-10-23 20:00 | 1740.8342 | 0 | 0 | 3671.9774 | -1740.8342 | -1740.8342 | 0
2019-10-23 21:00 | 1399.1827 | 0 | 0 | 1931.1433 | -1399.1827 | -1399.1827 | 0
2019-10-23 22:00 | 1076.2287 | 0 | 0 | 531.9606 | -1076.2287 | -531.9606 | -544.2681
2019-10-23 23:00 | 752.0947 | 0 | 286.6667 | 0 | -465.4281 | 0 | -1009.6961
2019-10-24 | 642.4841 | 0 | 873.3333 | 0 | 230.8492 | 230.8492 | -778.8469
2019-10-24 01:00 | 594.8671 | 0 | 873.3333 | 230.8492 | 278.4662 | 278.4662 | -269.5315
2019-10-24 02:00 | 592.2048 | 0 | 1666.6667 | 509.3155 | 1074.4618 | 1074.4618 | 0
2019-10-24 03:00 | 601.0664 | 0 | 1666.6667 | 1583.7773 | 1065.6002 | 1065.6002 | 0
2019-10-24 04:00 | 665.6367 | 0 | 1666.6667 | 2649.3775 | 1001.0299 | 1001.0299 | 0
2019-10-24 05:00 | 897.6864 | 0 | 873.3333 | 3650.4074 | -24.353 | -24.353 | 0
2019-10-24 06:00 | 1226.3503 | 0 | 873.3333 | 3626.0544 | -353.017 | -353.017 | 0
2019-10-24 07:00 | 1154.9817 | 537.7112 | 1666.6667 | 3273.0374 | 1049.3962 | 1049.3962 | 0
2019-10-24 08:00 | 965.3327 | 1219.9625 | 2773.3333 | 4322.4336 | 3027.9632 | 3027.9632 | 0
2019-10-24 09:00 | 953.8476 | 1510.0788 | 7873.3333 | 7350.3969 | 8429.5645 | 2649.6031 | 0
2019-10-24 10:00 | 934.1293 | 1717.4571 | 7873.3333 | 10000 | 8656.6612 | 0 | 0
2019-10-24 11:00 | 902.6009 | 1006.9446 | 9060 | 10000 | 9164.3437 | 0 | 0
2019-10-24 12:00 | 865.9877 | 2985.2263 | 9060 | 10000 | 11179.2387 | 0 | 0
2019-10-24 13:00 | 852.9336 | 2121.106 | 9060 | 10000 | 10328.1724 | 0 | 0
2019-10-24 14:00 | 894.792 | 1124.3676 | 9060 | 10000 | 9289.5756 | 0 | 0
2019-10-24 15:00 | 1064.6601 | 580.8121 | 9573.3333 | 10000 | 9089.4853 | 0 | 0
2019-10-24 16:00 | 1406.8839 | 22.057 | 9573.3333 | 10000 | 8188.5065 | 0 | 0
2019-10-24 17:00 | 1675.6854 | 0 | 9873.3333 | 10000 | 8197.6479 | 0 | 0
2019-10-24 18:00 | 1892.2445 | 0 | 9960 | 10000 | 8067.7555 | 0 | 0
2019-10-24 19:00 | 1972.6713 | 0 | 9960 | 10000 | 7987.3287 | 0 | 0
2019-10-24 20:00 | 1796.5553 | 0 | 9573.3333 | 10000 | 7776.778 | 0 | 0
2019-10-24 21:00 | 1473.3179 | 0 | 9060 | 10000 | 7586.6821 | 0 | 0
2019-10-24 22:00 | 1157.0103 | 0 | 9573.3333 | 10000 | 8416.323 | 0 | 0
2019-10-24 23:00 | 832.8831 | 0 | 9573.3333 | 10000 | 8740.4503 | 0 | 0
2019-10-25 | 717.7835 | 0 | 9060 | 10000 | 8342.2165 | 0 | 0
2019-10-25 01:00 | 668.1827 | 0 | 9573.3333 | 10000 | 8905.1507 | 0 | 0
2019-10-25 02:00 | 661.4093 | 0 | 9060 | 10000 | 8398.5907 | 0 | 0
2019-10-25 03:00 | 666.4261 | 0 | 2773.3333 | 10000 | 2106.9072 | 0 | 0
2019-10-25 04:00 | 730.5825 | 0 | 873.3333 | 10000 | 142.7509 | 0 | 0
2019-10-25 05:00 | 963.6484 | 0 | 0 | 10000 | -963.6484 | -963.6484 | 0
2019-10-25 06:00 | 1277.2179 | 0 | 0 | 9036.3516 | -1277.2179 | -1277.2179 | 0
2019-10-25 07:00 | 1196.5516 | 280.0399 | 286.6667 | 7759.1337 | -629.845 | -629.845 | 0
2019-10-25 08:00 | 994.5359 | 813.8573 | 2773.3333 | 7129.2887 | 2592.6547 | 2592.6547 | 0
2019-10-25 09:00 | 982.2302 | 1343.1689 | 2773.3333 | 9721.9434 | 3134.2721 | 278.0566 | 0
2019-10-25 10:00 | 959.1202 | 1219.7866 | 2773.3333 | 10000 | 3033.9997 | 0 | 0
2019-10-25 11:00 | 919.783 | 1382.3793 | 6160 | 10000 | 6622.5964 | 0 | 0
2019-10-25 12:00 | 874.1338 | 2848.803 | 1666.6667 | 10000 | 3641.3359 | 0 | 0
2019-10-25 13:00 | 856.9576 | 1630.9909 | 1666.6667 | 10000 | 2440.7 | 0 | 0
2019-10-25 14:00 | 892.4052 | 1862.7965 | 2773.3333 | 10000 | 3743.7246 | 0 | 0
2019-10-25 15:00 | 1059.6378 | 435.3934 | 0 | 10000 | -624.2444 | -624.2444 | 0
2019-10-25 16:00 | 1393.0424 | 0.29785 | 873.3333 | 9375.7556 | -519.4112 | -519.4112 | 0
2019-10-25 17:00 | 1667.7099 | 0 | 2773.3333 | 8856.3445 | 1105.6234 | 1105.6234 | 0
2019-10-25 18:00 | 1883.9699 | 0 | 286.6667 | 9961.9679 | -1597.3033 | -1597.3033 | 0
2019-10-25 19:00 | 1956.4951 | 0 | 286.6667 | 8364.6646 | -1669.8285 | -1669.8285 | 0
2019-10-25 20:00 | 1777.9403 | 0 | 286.6667 | 6694.8361 | -1491.2737 | -1491.2737 | 0
2019-10-25 21:00 | 1450.611 | 0 | 0 | 5203.5625 | -1450.611 | -1450.611 | 0
2019-10-25 22:00 | 1129.0451 | 0 | 0 | 3752.9515 | -1129.0451 | -1129.0451 | 0
2019-10-25 23:00 | 800.9114 | 0 | 286.6667 | 2623.9064 | -514.2447 | -514.2447 | 0
2019-10-26 | 680.2914 | 0 | 873.3333 | 2109.6617 | 193.0419 | 193.0419 | 0
2019-10-26 01:00 | 625.7624 | 0 | 873.3333 | 2302.7036 | 247.5709 | 247.5709 | 0
2019-10-26 02:00 | 616.3447 | 0 | 873.3333 | 2550.2745 | 256.9887 | 256.9887 | 0
2019-10-26 03:00 | 615.1049 | 0 | 0 | 2807.2632 | -615.1049 | -615.1049 | 0
2019-10-26 04:00 | 678.1632 | 0 | 0 | 2192.1583 | -678.1632 | -678.1632 | 0
2019-10-26 05:00 | 906.1145 | 0 | 873.3333 | 1513.995 | -32.7811 | -32.7811 | 0
2019-10-26 06:00 | 1237.787 | 573.3383 | 1666.6667 | 1481.2139 | 1002.2179 | 1002.2179 | 0
2019-10-26 07:00 | 1161.111 | 2763.4396 | 873.3333 | 2483.4318 | 2475.662 | 2475.662 | 0
2019-10-26 08:00 | 987.2646 | 4867.0381 | 873.3333 | 4959.0938 | 4753.1068 | 4753.1068 | 0
2019-10-26 09:00 | 1000.089 | 6315.1571 | 286.6667 | 9712.2006 | 5601.7348 | 287.7994 | 0
2019-10-26 10:00 | 995.4198 | 7193.0982 | 286.6667 | 10000 | 6484.3451 | 0 | 0
2019-10-26 11:00 | 970.7775 | 7416.0889 | 1666.6667 | 10000 | 8111.9781 | 0 | 0
2019-10-26 12:00 | 938.7921 | 7046.625 | 286.6667 | 10000 | 6394.4995 | 0 | 0
2019-10-26 13:00 | 924.6962 | 6095.115 | 873.3333 | 10000 | 6043.7522 | 0 | 0
2019-10-26 14:00 | 961.5104 | 4617.5225 | 4266.6667 | 10000 | 7922.6788 | 0 | 0
2019-10-26 15:00 | 1123.837 | 2520.2951 | 4266.6667 | 10000 | 5663.1249 | 0 | 0
2019-10-26 16:00 | 1461.4654 | 431.1729 | 2773.3333 | 10000 | 1743.0409 | 0 | 0
2019-10-26 17:00 | 1721.9772 | 0 | 4266.6667 | 10000 | 2544.6894 | 0 | 0
2019-10-26 18:00 | 1929.7286 | 0 | 6160 | 10000 | 4230.2714 | 0 | 0
2019-10-26 19:00 | 1994.1904 | 0 | 7873.3333 | 10000 | 5879.143 | 0 | 0
2019-10-26 20:00 | 1805.8637 | 0 | 9060 | 10000 | 7254.1363 | 0 | 0
2019-10-26 21:00 | 1474.268 | 0 | 9060 | 10000 | 7585.732 | 0 | 0
2019-10-26 22:00 | 1156.331 | 0 | 9060 | 10000 | 7903.669 | 0 | 0
2019-10-26 23:00 | 822.0213 | 0 | 6160 | 10000 | 5337.9787 | 0 | 0
2019-10-27 | 698.9072 | 0 | 6160 | 10000 | 5461.0928 | 0 | 0
2019-10-27 01:00 | 640.1661 | 0 | 4266.6667 | 10000 | 3626.5006 | 0 | 0
2019-10-27 02:00 | 629.9982 | 0 | 4266.6667 | 10000 | 3636.6685 | 0 | 0
2019-10-27 03:00 | 624.3455 | 0 | 1666.6667 | 10000 | 1042.3211 | 0 | 0
2019-10-27 04:00 | 683.0669 | 0 | 2773.3333 | 10000 | 2090.2665 | 0 | 0
2019-10-27 05:00 | 896.8281 | 0 | 2773.3333 | 10000 | 1876.5052 | 0 | 0
2019-10-27 06:00 | 1238.2458 | 514.1662 | 873.3333 | 10000 | 149.2537 | 0 | 0
2019-10-27 07:00 | 1163.2937 | 2668.8383 | 873.3333 | 10000 | 2378.878 | 0 | 0
2019-10-27 08:00 | 988.9345 | 4713.6303 | 873.3333 | 10000 | 4598.0292 | 0 | 0
2019-10-27 09:00 | 988.9221 | 4563.0287 | 1666.6667 | 10000 | 5240.7732 | 0 | 0
2019-10-27 10:00 | 985.5746 | 6938.9965 | 873.3333 | 10000 | 6826.7552 | 0 | 0
2019-10-27 11:00 | 957.7049 | 5529.0264 | 1666.6667 | 10000 | 6237.9881 | 0 | 0
2019-10-27 12:00 | 925.8906 | 5579.6011 | 873.3333 | 10000 | 5527.0438 | 0 | 0
2019-10-27 13:00 | 912.3984 | 5281.6705 | 286.6667 | 10000 | 4655.9388 | 0 | 0
2019-10-27 14:00 | 950.5935 | 3821.5328 | 873.3333 | 10000 | 3744.2726 | 0 | 0
2019-10-27 15:00 | 1111.0508 | 1632.1789 | 873.3333 | 10000 | 1394.4615 | 0 | 0
2019-10-27 16:00 | 1446.189 | 70.0626 | 286.6667 | 10000 | -1089.4597 | -1089.4597 | 0
2019-10-27 17:00 | 1704.1319 | 0 | 286.6667 | 8910.5403 | -1417.4652 | -1417.4652 | 0
2019-10-27 18:00 | 1911.7399 | 0 | 286.6667 | 7493.0751 | -1625.0732 | -1625.0732 | 0
2019-10-27 19:00 | 1978.9476 | 0 | 0 | 5868.0018 | -1978.9476 | -1978.9476 | 0
2019-10-27 20:00 | 1794.0952 | 0 | 873.3333 | 3889.0542 | -920.7619 | -920.7619 | 0
2019-10-27 21:00 | 1460.1559 | 0 | 1666.6667 | 2968.2923 | 206.5107 | 206.5107 | 0
2019-10-27 22:00 | 1135.4693 | 0 | 873.3333 | 3174.8031 | -262.136 | -262.136 | 0
2019-10-27 23:00 | 801.7701 | 0 | 2773.3333 | 2912.6671 | 1971.5632 | 1971.5632 | 0
2019-10-28 | 685.2649 | 0 | 286.6667 | 4884.2303 | -398.5983 | -398.5983 | 0
2019-10-28 01:00 | 624.1633 | 0 | 286.6667 | 4485.632 | -337.4966 | -337.4966 | 0
2019-10-28 02:00 | 612.5352 | 0 | 0 | 4148.1354 | -612.5352 | -612.5352 | 0
2019-10-28 03:00 | 613.0734 | 0 | 0 | 3535.6002 | -613.0734 | -613.0734 | 0
2019-10-28 04:00 | 674.4874 | 0 | 0 | 2922.5268 | -674.4874 | -674.4874 | 0
2019-10-28 05:00 | 894.7236 | 0 | 0 | 2248.0394 | -894.7236 | -894.7236 | 0
2019-10-28 06:00 | 1235.9838 | 72.9203 | 0 | 1353.3158 | -1163.0635 | -1163.0635 | 0
2019-10-28 07:00 | 1182.4755 | 692.0251 | 0 | 190.2523 | -490.4503 | -190.2523 | -300.198
2019-10-28 08:00 | 1018.3652 | 1251.7566 | 0 | 0 | 233.3914 | 233.3914 | -66.8066
2019-10-28 09:00 | 1018.1387 | 3393.9283 | 873.3333 | 233.3914 | 3249.1229 | 3249.1229 | 0
2019-10-28 10:00 | 1006.0231 | 2991.6019 | 873.3333 | 3482.5144 | 2858.9122 | 2858.9122 | 0
2019-10-28 11:00 | 978.4827 | 1900.2002 | 2773.3333 | 6341.4265 | 3695.0508 | 3658.5735 | 0
2019-10-28 12:00 | 943.7277 | 714.2408 | 1666.6667 | 10000 | 1437.1798 | 0 | 0
2019-10-28 13:00 | 918.6676 | 803.1669 | 2773.3333 | 10000 | 2657.8326 | 0 | 0
2019-10-28 14:00 | 954.685 | 865.4693 | 2773.3333 | 10000 | 2684.1176 | 0 | 0
2019-10-28 15:00 | 1112.4629 | 345.161 | 4266.6667 | 10000 | 3499.3648 | 0 | 0
2019-10-28 16:00 | 1433.4006 | 0 | 2773.3333 | 10000 | 1339.9328 | 0 | 0
2019-10-28 17:00 | 1702.8127 | 0 | 2773.3333 | 10000 | 1070.5206 | 0 | 0
2019-10-28 18:00 | 1912.5941 | 0 | 286.6667 | 10000 | -1625.9274 | -1625.9274 | 0
2019-10-28 19:00 | 1982.5377 | 0 | 286.6667 | 8374.0726 | -1695.871 | -1695.871 | 0
2019-10-28 20:00 | 1800.1257 | 0 | 286.6667 | 6678.2016 | -1513.459 | -1513.459 | 0
2019-10-28 21:00 | 1462.6729 | 0 | 286.6667 | 5164.7425 | -1176.0062 | -1176.0062 | 0
2019-10-28 22:00 | 1129.2029 | 0 | 286.6667 | 3988.7363 | -842.5362 | -842.5362 | 0
2019-10-28 23:00 | 791.1641 | 0 | 286.6667 | 3146.2001 | -504.4974 | -504.4974 | 0
2019-10-29 | 800.6388 | 0 | 873.3333 | 2641.7027 | 72.6945 | 72.6945 | 0
2019-10-29 01:00 | 679.6725 | 0 | 873.3333 | 2714.3972 | 193.6608 | 193.6608 | 0
2019-10-29 02:00 | 626.8547 | 0 | 873.3333 | 2908.058 | 246.4786 | 246.4786 | 0
2019-10-29 03:00 | 617.0887 | 0 | 873.3333 | 3154.5366 | 256.2447 | 256.2447 | 0
2019-10-29 04:00 | 626.6859 | 0 | 286.6667 | 3410.7813 | -340.0193 | -340.0193 | 0
2019-10-29 05:00 | 687.5306 | 0 | 286.6667 | 3070.762 | -400.8639 | -400.8639 | 0
2019-10-29 06:00 | 910.1293 | 0 | 1666.6667 | 2669.8981 | 756.5373 | 756.5373 | 0
2019-10-29 07:00 | 1234.9678 | 76.0322 | 873.3333 | 3426.4354 | -285.6022 | -285.6022 | 0
2019-10-29 08:00 | 1154.8452 | 1498.3994 | 2773.3333 | 3140.8332 | 3116.8876 | 3116.8876 | 0
2019-10-29 09:00 | 970.8839 | 3292.7237 | 873.3333 | 6257.7207 | 3195.1731 | 3195.1731 | 0
2019-10-29 10:00 | 947.8804 | 6288.2931 | 1666.6667 | 9452.8938 | 7007.0794 | 547.1062 | 0
2019-10-29 11:00 | 961.6601 | 6571.2656 | 6160 | 10000 | 11769.6055 | 0 | 0
2019-10-29 12:00 | 940.6123 | 5139.6007 | 6160 | 10000 | 10358.9884 | 0 | 0
2019-10-29 13:00 | 909.9079 | 4122.244 | 6160 | 10000 | 9372.3361 | 0 | 0
2019-10-29 14:00 | 896.3553 | 2540.396 | 4266.6667 | 10000 | 5910.7074 | 0 | 0
2019-10-29 15:00 | 932.872 | 1739.3371 | 6160 | 10000 | 6966.465 | 0 | 0
2019-10-29 16:00 | 1094.8808 | 46.1552 | 6160 | 10000 | 5111.2745 | 0 | 0
2019-10-29 17:00 | 1410.8665 | 0 | 7873.3333 | 10000 | 6462.4668 | 0 | 0
2019-10-29 18:00 | 1689.9706 | 0 | 9060 | 10000 | 7370.0294 | 0 | 0
2019-10-29 19:00 | 1901.8268 | 0 | 7873.3333 | 10000 | 5971.5065 | 0 | 0
2019-10-29 20:00 | 1968.733 | 0 | 9060 | 10000 | 7091.267 | 0 | 0
2019-10-29 21:00 | 1780.5874 | 0 | 9873.3333 | 10000 | 8092.7459 | 0 | 0
2019-10-29 22:00 | 1439.8092 | 0 | 10000 | 10000 | 8560.1908 | 0 | 0
2019-10-29 23:00 | 1107.3472 | 0 | 10000 | 10000 | 8892.6528 | 0 | 0
2019-10-30 | 762.1894 | 0 | 10000 | 10000 | 9237.8106 | 0 | 0
2019-10-30 01:00 | 643.2948 | 0 | 10000 | 10000 | 9356.7052 | 0 | 0
2019-10-30 02:00 | 588.6328 | 0 | 10000 | 10000 | 9411.3672 | 0 | 0
2019-10-30 03:00 | 580.5967 | 0 | 4266.6667 | 10000 | 3686.0699 | 0 | 0
2019-10-30 04:00 | 583.9516 | 0 | 6160 | 10000 | 5576.0484 | 0 | 0
2019-10-30 05:00 | 644.9303 | 0 | 6160 | 10000 | 5515.0697 | 0 | 0
2019-10-30 06:00 | 858.0551 | 377.7083 | 4266.6667 | 10000 | 3786.3199 | 0 | 0
2019-10-30 07:00 | 1177.6841 | 2464.4868 | 9060 | 10000 | 10346.8027 | 0 | 0
2019-10-30 08:00 | 1088.7599 | 4490.7845 | 9960 | 10000 | 13362.0246 | 0 | 0
2019-10-30 09:00 | 899.162 | 5939.6005 | 10000 | 10000 | 15040.4385 | 0 | 0
2019-10-30 10:00 | 885.4044 | 6910.6593 | 10000 | 10000 | 16025.255 | 0 | 0
2019-10-30 11:00 | 903.408 | 7128.6234 | 9873.3333 | 10000 | 16098.5488 | 0 | 0
2019-10-30 12:00 | 887.5521 | 6764.7117 | 9873.3333 | 10000 | 15750.4929 | 0 | 0
2019-10-30 13:00 | 861.5338 | 5884.5592 | 9573.3333 | 10000 | 14596.3587 | 0 | 0
2019-10-30 14:00 | 852.9336 | 4408.1685 | 9060 | 10000 | 12615.2349 | 0 | 0
2019-10-30 15:00 | 891.7439 | 2332.3886 | 9573.3333 | 10000 | 11013.978 | 0 | 0
2019-10-30 16:00 | 1055.5408 | 292.9567 | 9060 | 10000 | 8297.4159 | 0 | 0
2019-10-30 17:00 | 1406.919 | 0 | 2773.3333 | 10000 | 1366.4143 | 0 | 0
2019-10-30 18:00 | 1682.8903 | 0 | 2773.3333 | 10000 | 1090.4431 | 0 | 0
2019-10-30 19:00 | 1905.3156 | 0 | 2773.3333 | 10000 | 868.0177 | 0 | 0
2019-10-30 20:00 | 1984.1795 | 0 | 2773.3333 | 10000 | 789.1538 | 0 | 0
2019-10-30 21:00 | 1810.8811 | 0 | 6160 | 10000 | 4349.1189 | 0 | 0
2019-10-30 22:00 | 1490.7683 | 0 | 6160 | 10000 | 4669.2317 | 0 | 0
2019-10-30 23:00 | 1176.0202 | 0 | 2773.3333 | 10000 | 1597.3131 | 0 | 0
2019-10-31 | 854.3392 | 0 | 4266.6667 | 10000 | 3412.3275 | 0 | 0
2019-10-31 01:00 | 737.2599 | 0 | 4266.6667 | 10000 | 3529.4068 | 0 | 0
2019-10-31 02:00 | 687.2981 | 0 | 2773.3333 | 10000 | 2086.0352 | 0 | 0
2019-10-31 03:00 | 682.4775 | 0 | 2773.3333 | 10000 | 2090.8558 | 0 | 0
2019-10-31 04:00 | 686.1628 | 0 | 2773.3333 | 10000 | 2087.1706 | 0 | 0
2019-10-31 05:00 | 752.0696 | 0 | 2773.3333 | 10000 | 2021.2637 | 0 | 0
2019-10-31 06:00 | 965.1758 | 408.4984 | 2773.3333 | 10000 | 2216.6559 | 0 | 0
2019-10-31 07:00 | 1276.3926 | 2587.247 | 2773.3333 | 10000 | 4084.1878 | 0 | 0
2019-10-31 08:00 | 1181.089 | 4690.7189 | 2773.3333 | 10000 | 6282.9633 | 0 | 0
2019-10-31 09:00 | 981.3443 | 6113.2447 | 4266.6667 | 10000 | 9398.5671 | 0 | 0
2019-10-31 10:00 | 980.2177 | 6936.9311 | 2773.3333 | 10000 | 8730.0468 | 0 | 0
2019-10-31 11:00 | 960.3916 | 7109.1597 | 4266.6667 | 10000 | 10415.4348 | 0 | 0
2019-10-31 12:00 | 930.2595 | 6081.6519 | 9060 | 10000 | 14211.3924 | 0 | 0
2019-10-31 13:00 | 897.172 | 4607.7257 | 7873.3333 | 10000 | 11583.887 | 0 | 0
2019-10-31 14:00 | 892.7297 | 3630.9789 | 6160 | 10000 | 8898.2492 | 0 | 0
2019-10-31 15:00 | 944.6201 | 2227.5235 | 2773.3333 | 10000 | 4056.2368 | 0 | 0
2019-10-31 16:00 | 1123.5201 | 0 | 2773.3333 | 10000 | 1649.8132 | 0 | 0
2019-10-31 17:00 | 1478.4339 | 0 | 873.3333 | 10000 | -605.1006 | -605.1006 | 0
2019-10-31 18:00 | 1740.7819 | 0 | 873.3333 | 9394.8994 | -867.4485 | -867.4485 | 0
2019-10-31 19:00 | 1951.7705 | 0 | 1666.6667 | 8527.4509 | -285.1038 | -285.1038 | 0
2019-10-31 20:00 | 2027.3452 | 0 | 286.6667 | 8242.3471 | -1740.6785 | -1740.6785 | 0
2019-10-31 21:00 | 1844.7515 | 0 | 0 | 6501.6686 | -1844.7515 | -1844.7515 | 0
2019-10-31 22:00 | 1509.5533 | 0 | 0 | 4656.9171 | -1509.5533 | -1509.5533 | 0
2019-10-31 23:00 | 1181.9509 | 0 | 0 | 3147.3637 | -1181.9509 | -1181.9509 | 0
2019-11-01 | 847.1552 | 0 | 0 | 1965.4128 | -847.1552 | -847.1552 | 0
2019-11-01 01:00 | 715.2146 | 0 | 0 | 1118.2576 | -715.2146 | -715.2146 | 0
2019-11-01 02:00 | 652.7307 | 0 | 873.3333 | 403.0431 | 220.6027 | 220.6027 | 0
2019-11-01 03:00 | 637.2769 | 0 | 873.3333 | 623.6458 | 236.0564 | 236.0564 | 0
2019-11-01 04:00 | 636.1978 | 0 | 286.6667 | 859.7022 | -349.5312 | -349.5312 | 0
2019-11-01 05:00 | 698.0979 | 0 | 0 | 510.171 | -698.0979 | -510.171 | -187.9269
2019-11-01 06:00 | 889.9735 | 20.9369 | 0 | 0 | -869.0366 | 0 | -1056.9635
2019-11-01 07:00 | 1152.9105 | 1687.9608 | 0 | 0 | 535.0503 | 535.0503 | -521.9132
2019-11-01 08:00 | 1099.3034 | 2286.8888 | 0 | 535.0503 | 1187.5855 | 1187.5855 | 0
2019-11-01 09:00 | 970.8754 | 4414.2819 | 0 | 1722.6358 | 3443.4065 | 3443.4065 | 0
2019-11-01 10:00 | 971.279 | 3831.486 | 0 | 5166.0423 | 2860.207 | 2860.207 | 0
2019-11-01 11:00 | 954.7337 | 4416.6739 | 0 | 8026.2493 | 3461.9402 | 1973.7507 | 0
2019-11-01 12:00 | 924.6485 | 4551.7862 | 286.6667 | 10000 | 3913.8045 | 0 | 0
2019-11-01 13:00 | 894.4986 | 3348.9288 | 286.6667 | 10000 | 2741.0968 | 0 | 0
2019-11-01 14:00 | 906.3896 | 2403.5471 | 286.6667 | 10000 | 1783.8243 | 0 | 0
2019-11-01 15:00 | 1017.1961 | 779.0272 | 286.6667 | 10000 | 48.4978 | 0 | 0
2019-11-01 16:00 | 1348.0261 | 0 | 286.6667 | 10000 | -1061.3594 | -1061.3594 | 0
2019-11-01 17:00 | 1910.358 | 0 | 0 | 8938.6406 | -1910.358 | -1910.358 | 0
2019-11-01 18:00 | 2198.0396 | 0 | 873.3333 | 7028.2825 | -1324.7062 | -1324.7062 | 0
2019-11-01 19:00 | 2098.3567 | 0 | 873.3333 | 5703.5763 | -1225.0234 | -1225.0234 | 0
2019-11-01 20:00 | 2007.0991 | 0 | 1666.6667 | 4478.5529 | -340.4324 | -340.4324 | 0
2019-11-01 21:00 | 1834.701 | 0 | 873.3333 | 4138.1205 | -961.3677 | -961.3677 | 0
2019-11-01 22:00 | 1494.2085 | 0 | 286.6667 | 3176.7528 | -1207.5418 | -1207.5418 | 0
2019-11-01 23:00 | 1176.8361 | 0 | 873.3333 | 1969.211 | -303.5028 | -303.5028 | 0
2019-11-02 | 852.2616 | 0 | 286.6667 | 1665.7082 | -565.5949 | -565.5949 | 0
2019-11-02 01:00 | 727.3781 | 0 | 0 | 1100.1133 | -727.3781 | -727.3781 | 0
2019-11-02 02:00 | 672.5936 | 0 | 286.6667 | 372.7352 | -385.9269 | -372.7352 | -13.1917
2019-11-02 03:00 | 664.1471 | 0 | 286.6667 | 0 | -377.4804 | 0 | -390.6721
2019-11-02 04:00 | 662.6869 | 0 | 286.6667 | 0 | -376.0202 | 0 | -766.6923
2019-11-02 05:00 | 721.5008 | 0 | 286.6667 | 0 | -434.8341 | 0 | -1201.5265
2019-11-02 06:00 | 901.4016 | 1.2696 | 873.3333 | 0 | -26.7987 | 0 | -1228.3251
2019-11-02 07:00 | 1166.086 | 1294.0214 | 873.3333 | 0 | 1001.2688 | 1001.2688 | -227.0564
2019-11-02 08:00 | 1104.8152 | 3523.7737 | 873.3333 | 1001.2688 | 3292.2918 | 3292.2918 | 0
2019-11-02 09:00 | 947.7298 | 4943.6177 | 0 | 4293.5606 | 3995.8879 | 3995.8879 | 0
2019-11-02 10:00 | 928.574 | 6126.2581 | 286.6667 | 8289.4485 | 5484.3508 | 1710.5515 | 0
2019-11-02 11:00 | 913.6378 | 6408.3313 | 1666.6667 | 10000 | 7161.3602 | 0 | 0
2019-11-02 12:00 | 894.5446 | 1604.6743 | 873.3333 | 10000 | 1583.4631 | 0 | 0
2019-11-02 13:00 | 868.4857 | 221.3899 | 1666.6667 | 10000 | 1019.5709 | 0 | 0
2019-11-02 14:00 | 877.3244 | 304.0692 | 873.3333 | 10000 | 300.0782 | 0 | 0
2019-11-02 15:00 | 978.7144 | 109.1591 | 2773.3333 | 10000 | 1903.7781 | 0 | 0
2019-11-02 16:00 | 1297.4233 | 0 | 2773.3333 | 10000 | 1475.9101 | 0 | 0
2019-11-02 17:00 | 1833.457 | 0 | 2773.3333 | 10000 | 939.8764 | 0 | 0
2019-11-02 18:00 | 2137.8143 | 0 | 286.6667 | 10000 | -1851.1477 | -1851.1477 | 0
2019-11-02 19:00 | 2032.5705 | 0 | 286.6667 | 8148.8523 | -1745.9038 | -1745.9038 | 0
2019-11-02 20:00 | 1938.0993 | 0 | 873.3333 | 6402.9485 | -1064.766 | -1064.766 | 0
2019-11-02 21:00 | 1765.6705 | 0 | 286.6667 | 5338.1825 | -1479.0038 | -1479.0038 | 0
2019-11-02 22:00 | 1428.1703 | 0 | 286.6667 | 3859.1787 | -1141.5036 | -1141.5036 | 0
2019-11-02 23:00 | 1112.0174 | 0 | 286.6667 | 2717.6751 | -825.3508 | -825.3508 | 0
2019-11-03 | 792.9153 | 0 | 0 | 1892.3243 | -792.9153 | -792.9153 | 0
2019-11-03 01:00 | 672.1726 | 0 | 286.6667 | 1099.4091 | -385.5059 | -385.5059 | 0
2019-11-03 02:00 | 620.3441 | 0 | 0 | 713.9031 | -620.3441 | -620.3441 | 0
2019-11-03 03:00 | 613.9086 | 0 | 0 | 93.559 | -613.9086 | -93.559 | -520.3496
2019-11-03 04:00 | 625.0617 | 0 | 286.6667 | 0 | -338.395 | 0 | -858.7447
2019-11-03 05:00 | 693.6052 | 0 | 873.3333 | 0 | 179.7282 | 179.7282 | -679.0165
2019-11-03 06:00 | 876.2801 | 0 | 1666.6667 | 179.7282 | 790.3866 | 790.3866 | 0
2019-11-03 07:00 | 1147.8889 | 189.5407 | 1666.6667 | 970.1148 | 708.3185 | 708.3185 | 0
2019-11-03 08:00 | 1093.2922 | 1185.175 | 2773.3333 | 1678.4333 | 2865.2161 | 2865.2161 | 0
2019-11-03 09:00 | 938.3424 | 3627.5818 | 7873.3333 | 4543.6494 | 10562.5728 | 5456.3506 | 0
2019-11-03 10:00 | 929.2796 | 5809.2377 | 7873.3333 | 10000 | 12753.2914 | 0 | 0
2019-11-03 11:00 | 920.3788 | 5990.0038 | 6160 | 10000 | 11229.625 | 0 | 0
2019-11-03 12:00 | 894.5446 | 5614.3471 | 7873.3333 | 10000 | 12593.1359 | 0 | 0
2019-11-03 13:00 | 868.4857 | 4750.1129 | 6160 | 10000 | 10041.6273 | 0 | 0
2019-11-03 14:00 | 879.6694 | 3290.2259 | 4266.6667 | 10000 | 6677.2232 | 0 | 0
2019-11-03 15:00 | 989.3888 | 926.8574 | 1666.6667 | 10000 | 1604.1353 | 0 | 0
2019-11-03 16:00 | 1322.1816 | 0 | 2773.3333 | 10000 | 1451.1518 | 0 | 0
2019-11-03 17:00 | 1880.5952 | 0 | 7873.3333 | 10000 | 5992.7381 | 0 | 0
2019-11-03 18:00 | 2171.9345 | 0 | 9060 | 10000 | 6888.0655 | 0 | 0
2019-11-03 19:00 | 2072.9716 | 0 | 7873.3333 | 10000 | 5800.3617 | 0 | 0
2019-11-03 20:00 | 1984.9616 | 0 | 6160 | 10000 | 4175.0384 | 0 | 0
2019-11-03 21:00 | 1811.9819 | 0 | 6160 | 10000 | 4348.0181 | 0 | 0
2019-11-03 22:00 | 1475.388 | 0 | 4266.6667 | 10000 | 2791.2787 | 0 | 0
2019-11-03 23:00 | 1157.0432 | 0 | 9873.3333 | 10000 | 8716.2902 | 0 | 0
2019-11-04 | 842.3982 | 0 | 6160 | 10000 | 5317.6018 | 0 | 0
2019-11-04 01:00 | 715.3493 | 0 | 2773.3333 | 10000 | 2057.984 | 0 | 0
2019-11-04 02:00 | 661.0342 | 0 | 4266.6667 | 10000 | 3605.6324 | 0 | 0
2019-11-04 03:00 | 650.9293 | 0 | 2773.3333 | 10000 | 2122.4041 | 0 | 0
2019-11-04 04:00 | 656.484 | 0 | 1666.6667 | 10000 | 1010.1826 | 0 | 0
2019-11-04 05:00 | 720.4736 | 0 | 873.3333 | 10000 | 152.8597 | 0 | 0
2019-11-04 06:00 | 909.144 | 0 | 1666.6667 | 10000 | 757.5227 | 0 | 0
2019-11-04 07:00 | 1200.1735 | 202.9669 | 873.3333 | 10000 | -123.8732 | -123.8732 | 0
2019-11-04 08:00 | 1183.0844 | 292.6336 | 1666.6667 | 9876.1268 | 776.2159 | 123.8732 | 0
2019-11-04 09:00 | 1062.5034 | 412.0542 | 0 | 10000 | -650.4492 | -650.4492 | 0
2019-11-04 10:00 | 1078.9407 | 599.7135 | 0 | 9349.5508 | -479.2272 | -479.2272 | 0
2019-11-04 11:00 | 1062.4484 | 1373.2817 | 873.3333 | 8870.3236 | 1184.1666 | 1129.6764 | 0
2019-11-04 12:00 | 1030.7926 | 864.5251 | 286.6667 | 10000 | 120.3992 | 0 | 0
2019-11-04 13:00 | 994.7507 | 392.2098 | 286.6667 | 10000 | -315.8742 | -315.8742 | 0
2019-11-04 14:00 | 995.7926 | 244.9466 | 286.6667 | 9684.1258 | -464.1794 | -464.1794 | 0
2019-11-04 15:00 | 1091.0715 | 1484.504 | 286.6667 | 9219.9464 | 680.0991 | 680.0991 | 0
2019-11-04 16:00 | 1406.6966 | 0 | 286.6667 | 9900.0455 | -1120.03 | -1120.03 | 0
2019-11-04 17:00 | 1953.5636 | 0 | 286.6667 | 8780.0156 | -1666.8969 | -1666.8969 | 0
2019-11-04 18:00 | 2235.456 | 0 | 873.3333 | 7113.1187 | -1362.1227 | -1362.1227 | 0
2019-11-04 19:00 | 2126.9289 | 0 | 873.3333 | 5750.996 | -1253.5956 | -1253.5956 | 0
2019-11-04 20:00 | 2030.9635 | 0 | 1666.6667 | 4497.4004 | -364.2968 | -364.2968 | 0
2019-11-04 21:00 | 1854.3912 | 0 | 4266.6667 | 4133.1036 | 2412.2755 | 2412.2755 | 0
2019-11-04 22:00 | 1502.6475 | 0 | 2773.3333 | 6545.3791 | 1270.6859 | 1270.6859 | 0
2019-11-04 23:00 | 1166.0687 | 0 | 2773.3333 | 7816.0649 | 1607.2646 | 1607.2646 | 0
2019-11-05 | 833.1916 | 0 | 873.3333 | 9423.3296 | 40.1417 | 40.1417 | 0
2019-11-05 01:00 | 706.069 | 0 | 1666.6667 | 9463.4713 | 960.5977 | 536.5287 | 0
2019-11-05 02:00 | 647.0417 | 0 | 1666.6667 | 10000 | 1019.6249 | 0 | 0
2019-11-05 03:00 | 636.4791 | 0 | 2773.3333 | 10000 | 2136.8542 | 0 | 0
2019-11-05 04:00 | 640.1363 | 0 | 2773.3333 | 10000 | 2133.197 | 0 | 0
2019-11-05 05:00 | 701.8432 | 0 | 4266.6667 | 10000 | 3564.8235 | 0 | 0
2019-11-05 06:00 | 891.0972 | 0 | 4266.6667 | 10000 | 3375.5694 | 0 | 0
2019-11-05 07:00 | 1184.6226 | 0 | 4266.6667 | 10000 | 3082.0441 | 0 | 0
2019-11-05 08:00 | 1167.4872 | 32.1206 | 4266.6667 | 10000 | 3131.3001 | 0 | 0
2019-11-05 09:00 | 1050.9456 | 706.5128 | 2773.3333 | 10000 | 2428.9006 | 0 | 0
2019-11-05 10:00 | 1078.4148 | 475.2628 | 2773.3333 | 10000 | 2170.1814 | 0 | 0
2019-11-05 11:00 | 1068.1812 | 1284.0555 | 2773.3333 | 10000 | 2989.2076 | 0 | 0
2019-11-05 12:00 | 1035.9011 | 1882.2521 | 1666.6667 | 10000 | 2513.0177 | 0 | 0
2019-11-05 13:00 | 975.2713 | 1316.0427 | 873.3333 | 10000 | 1214.1047 | 0 | 0
2019-11-05 14:00 | 974.1373 | 698.5755 | 286.6667 | 10000 | 11.1049 | 0 | 0
2019-11-05 15:00 | 1076.9382 | 316.3961 | 286.6667 | 10000 | -473.8755 | -473.8755 | 0
2019-11-05 16:00 | 1398.7892 | 0 | 286.6667 | 9526.1245 | -1112.1225 | -1112.1225 | 0
2019-11-05 17:00 | 1948.171 | 0 | 0 | 8414.0019 | -1948.171 | -1948.171 | 0
2019-11-05 18:00 | 2234.8003 | 0 | 0 | 6465.8309 | -2234.8003 | -2234.8003 | 0
2019-11-05 19:00 | 2126.2973 | 0 | 0 | 4231.0306 | -2126.2973 | -2126.2973 | 0
2019-11-05 20:00 | 2030.179 | 0 | 0 | 2104.7333 | -2030.179 | -2030.179 | 0
2019-11-05 21:00 | 1855.2471 | 0 | 0 | 74.5543 | -1855.2471 | -74.5543 | -1780.6928
2019-11-05 22:00 | 1503.4794 | 0 | 0 | 0 | -1503.4794 | 0 | -3284.1722
2019-11-05 23:00 | 1167.0315 | 0 | 873.3333 | 0 | -293.6982 | 0 | -3577.8704
2019-11-06 | 823.0642 | 0 | 1666.6667 | 0 | 843.6025 | 843.6025 | -2734.2679
2019-11-06 01:00 | 696.1895 | 0 | 2773.3333 | 843.6025 | 2077.1438 | 2077.1438 | 0
2019-11-06 02:00 | 639.0068 | 0 | 4266.6667 | 2920.7463 | 3627.6599 | 3627.6599 | 0
2019-11-06 03:00 | 628.2703 | 0 | 4266.6667 | 6548.4062 | 3638.3964 | 3451.5938 | 0
2019-11-06 04:00 | 629.4328 | 0 | 2773.3333 | 10000 | 2143.9006 | 0 | 0
2019-11-06 05:00 | 690.7038 | 0 | 2773.3333 | 10000 | 2082.6295 | 0 | 0
2019-11-06 06:00 | 886.9743 | 0 | 1666.6667 | 10000 | 779.6923 | 0 | 0
2019-11-06 07:00 | 1169.0595 | 972.4929 | 2773.3333 | 10000 | 2576.7668 | 0 | 0
2019-11-06 08:00 | 1108.2118 | 1469.9863 | 4266.6667 | 10000 | 4628.4413 | 0 | 0
2019-11-06 09:00 | 957.3122 | 2068.9075 | 4266.6667 | 10000 | 5378.2619 | 0 | 0
2019-11-06 10:00 | 949.5851 | 2842.9162 | 2773.3333 | 10000 | 4666.6644 | 0 | 0
2019-11-06 11:00 | 930.6926 | 2904.7206 | 4266.6667 | 10000 | 6240.6947 | 0 | 0
2019-11-06 12:00 | 902.2339 | 1677.9351 | 873.3333 | 10000 | 1649.0345 | 0 | 0
2019-11-06 13:00 | 872.1986 | 1371.6636 | 873.3333 | 10000 | 1372.7984 | 0 | 0
2019-11-06 14:00 | 877.3244 | 294.0377 | 873.3333 | 10000 | 290.0467 | 0 | 0
2019-11-06 15:00 | 978.7144 | 289.3837 | 873.3333 | 10000 | 184.0027 | 0 | 0
2019-11-06 16:00 | 1302.7842 | 0 | 873.3333 | 10000 | -429.4508 | -429.4508 | 0
2019-11-06 17:00 | 1850.0698 | 0 | 4266.6667 | 9570.5492 | 2416.5968 | 429.4508 | 0
2019-11-06 18:00 | 2143.4035 | 0 | 1666.6667 | 10000 | -476.7368 | -476.7368 | 0
2019-11-06 19:00 | 2043.7851 | 0 | 4266.6667 | 9523.2632 | 2222.8816 | 476.7368 | 0
2019-11-06 20:00 | 1949.6226 | 0 | 4266.6667 | 10000 | 2317.044 | 0 | 0
2019-11-06 21:00 | 1776.5402 | 0 | 4266.6667 | 10000 | 2490.1264 | 0 | 0
2019-11-06 22:00 | 1435.7877 | 0 | 2773.3333 | 10000 | 1337.5456 | 0 | 0
2019-11-06 23:00 | 1114.7395 | 0 | 873.3333 | 10000 | -241.4062 | -241.4062 | 0
2019-11-07 | 790.9048 | 0 | 873.3333 | 9758.5938 | 82.4285 | 82.4285 | 0
2019-11-07 01:00 | 665.4133 | 0 | 2773.3333 | 9841.0223 | 2107.92 | 158.9777 | 0
2019-11-07 02:00 | 609.8541 | 0 | 4266.6667 | 10000 | 3656.8126 | 0 | 0
2019-11-07 03:00 | 600.128 | 0 | 2773.3333 | 10000 | 2173.2054 | 0 | 0
2019-11-07 04:00 | 602.683 | 0 | 2773.3333 | 10000 | 2170.6504 | 0 | 0
2019-11-07 05:00 | 667.1473 | 0 | 1666.6667 | 10000 | 999.5194 | 0 | 0
2019-11-07 06:00 | 857.7228 | 0 | 4266.6667 | 10000 | 3408.9439 | 0 | 0
2019-11-07 07:00 | 1122.0741 | 93.8032 | 2773.3333 | 10000 | 1745.0624 | 0 | 0
2019-11-07 08:00 | 1073.2507 | 3860.5235 | 873.3333 | 10000 | 3660.6062 | 0 | 0
2019-11-07 09:00 | 923.5389 | 5406.1454 | 873.3333 | 10000 | 5355.9398 | 0 | 0
2019-11-07 10:00 | 930.1472 | 6478.3628 | 286.6667 | 10000 | 5834.8823 | 0 | 0
2019-11-07 11:00 | 957.5657 | 6751.1359 | 286.6667 | 10000 | 6080.2369 | 0 | 0
2019-11-07 12:00 | 928.9577 | 6452.4315 | 286.6667 | 10000 | 5810.1404 | 0 | 0
2019-11-07 13:00 | 903.0049 | 5522.0217 | 0 | 10000 | 4619.0168 | 0 | 0
2019-11-07 14:00 | 918.5843 | 3986.6164 | 0 | 10000 | 3068.0321 | 0 | 0
2019-11-07 15:00 | 1024.9851 | 1951.5511 | 873.3333 | 10000 | 1799.8994 | 0 | 0
2019-11-07 16:00 | 1348.4096 | 0 | 873.3333 | 10000 | -475.0762 | -475.0762 | 0
2019-11-07 17:00 | 1896.3265 | 0 | 286.6667 | 9524.9238 | -1609.6598 | -1609.6598 | 0
2019-11-07 18:00 | 2185.4885 | 0 | 286.6667 | 7915.264 | -1898.8218 | -1898.8218 | 0
2019-11-07 19:00 | 2082.5631 | 0 | 286.6667 | 6016.4422 | -1795.8964 | -1795.8964 | 0
2019-11-07 20:00 | 1987.1754 | 0 | 873.3333 | 4220.5458 | -1113.842 | -1113.842 | 0
2019-11-07 21:00 | 1813.8438 | 0 | 2773.3333 | 3106.7037 | 959.4895 | 959.4895 | 0
2019-11-07 22:00 | 1474.3024 | 0 | 1666.6667 | 4066.1933 | 192.3643 | 192.3643 | 0
2019-11-07 23:00 | 1152.9493 | 0 | 873.3333 | 4258.5576 | -279.616 | -279.616 | 0
2019-11-08 | 824.1218 | 0 | 873.3333 | 3978.9416 | 49.2116 | 49.2116 | 0
2019-11-08 01:00 | 701.3012 | 0 | 2773.3333 | 4028.1531 | 2072.0321 | 2072.0321 | 0
2019-11-08 02:00 | 645.3624 | 0 | 4266.6667 | 6100.1853 | 3621.3043 | 3621.3043 | 0
2019-11-08 03:00 | 636.5657 | 0 | 2773.3333 | 9721.4895 | 2136.7676 | 278.5105 | 0
2019-11-08 04:00 | 639.1319 | 0 | 2773.3333 | 10000 | 2134.2014 | 0 | 0
2019-11-08 05:00 | 702.1021 | 0 | 4266.6667 | 10000 | 3564.5646 | 0 | 0
2019-11-08 06:00 | 885.1983 | 0 | 4266.6667 | 10000 | 3381.4684 | 0 | 0
2019-11-08 07:00 | 1182.2261 | 2292.0523 | 2773.3333 | 10000 | 3883.1596 | 0 | 0
2019-11-08 08:00 | 1144.8906 | 4538.6923 | 2773.3333 | 10000 | 6167.1351 | 0 | 0
2019-11-08 09:00 | 1009.778 | 6199.7742 | 4266.6667 | 10000 | 9456.6629 | 0 | 0
2019-11-08 10:00 | 1031.0938 | 7207.0569 | 4266.6667 | 10000 | 10442.6298 | 0 | 0
2019-11-08 11:00 | 1021.3646 | 7608.4011 | 4266.6667 | 10000 | 10853.7033 | 0 | 0
2019-11-08 12:00 | 994.1359 | 7288.0158 | 6160 | 10000 | 12453.8798 | 0 | 0
2019-11-08 13:00 | 964.8396 | 6313.0354 | 4266.6667 | 10000 | 9614.8624 | 0 | 0
2019-11-08 14:00 | 973.1002 | 4623.36 | 1666.6667 | 10000 | 5316.9264 | 0 | 0
2019-11-08 15:00 | 1072.0283 | 2297.4194 | 286.6667 | 10000 | 1512.0578 | 0 | 0
2019-11-08 16:00 | 1387.7639 | 0 | 286.6667 | 10000 | -1101.0972 | -1101.0972 | 0
2019-11-08 17:00 | 1937.2934 | 0 | 286.6667 | 8898.9028 | -1650.6268 | -1650.6268 | 0
2019-11-08 18:00 | 2220.486 | 0 | 286.6667 | 7248.276 | -1933.8193 | -1933.8193 | 0
2019-11-08 19:00 | 2112.7722 | 0 | 286.6667 | 5314.4567 | -1826.1055 | -1826.1055 | 0
2019-11-08 20:00 | 2014.1552 | 0 | 0 | 3488.3512 | -2014.1552 | -2014.1552 | 0
2019-11-08 21:00 | 1836.5684 | 0 | 0 | 1474.1961 | -1836.5684 | -1474.1961 | -362.3723
2019-11-08 22:00 | 1490.9129 | 0 | 0 | 0 | -1490.9129 | 0 | -1853.2852
2019-11-08 23:00 | 1168.8944 | 0 | 0 | 0 | -1168.8944 | 0 | -3022.1796
2019-11-09 | 841.5873 | 0 | 0 | 0 | -841.5873 | 0 | -3863.7669
2019-11-09 01:00 | 714.3654 | 0 | 286.6667 | 0 | -427.6987 | 0 | -4291.4656
2019-11-09 02:00 | 660.0023 | 0 | 286.6667 | 0 | -373.3356 | 0 | -4664.8012
2019-11-09 03:00 | 656.1333 | 0 | 286.6667 | 0 | -369.4667 | 0 | -5034.2679
2019-11-09 04:00 | 655.8011 | 0 | 286.6667 | 0 | -369.1344 | 0 | -5403.4022
2019-11-09 05:00 | 719.8332 | 0 | 286.6667 | 0 | -433.1665 | 0 | -5836.5688
2019-11-09 06:00 | 902.68 | 0 | 286.6667 | 0 | -616.0134 | 0 | -6452.5821
2019-11-09 07:00 | 1177.9061 | 2437.7827 | 0 | 0 | 1259.8765 | 1259.8765 | -5192.7056
2019-11-09 08:00 | 1126.5777 | 4687.8151 | 0 | 1259.8765 | 3561.2375 | 3561.2375 | -371.5916
2019-11-09 09:00 | 972.5239 | 6235.2218 | 0 | 4821.114 | 5262.6979 | 5178.886 | 0
2019-11-09 10:00 | 959.4634 | 7103.9789 | 0 | 10000 | 6144.5156 | 0 | 0
2019-11-09 11:00 | 939.9324 | 7337.5163 | 286.6667 | 10000 | 6684.2506 | 0 | 0
2019-11-09 12:00 | 903.3801 | 6947.0281 | 0 | 10000 | 6043.648 | 0 | 0
2019-11-09 13:00 | 868.4857 | 5916.4234 | 0 | 10000 | 5047.9377 | 0 | 0
2019-11-09 14:00 | 877.3244 | 4322.6108 | 873.3333 | 10000 | 4318.6198 | 0 | 0
2019-11-09 15:00 | 981.6061 | 2108.4813 | 873.3333 | 10000 | 2000.2085 | 0 | 0
2019-11-09 16:00 | 1310.3792 | 0 | 873.3333 | 10000 | -437.0458 | -437.0458 | 0
2019-11-09 17:00 | 1859.2264 | 0 | 873.3333 | 9562.9542 | -985.8931 | -985.8931 | 0
2019-11-09 18:00 | 2155.4863 | 0 | 286.6667 | 8577.0611 | -1868.8196 | -1868.8196 | 0
2019-11-09 19:00 | 2054.2237 | 0 | 873.3333 | 6708.2414 | -1180.8904 | -1180.8904 | 0
2019-11-09 20:00 | 1959.7743 | 0 | 873.3333 | 5527.351 | -1086.441 | -1086.441 | 0
2019-11-09 21:00 | 1787.5365 | 0 | 873.3333 | 4440.91 | -914.2032 | -914.2032 | 0
2019-11-09 22:00 | 1446.2672 | 0 | 873.3333 | 3526.7069 | -572.9339 | -572.9339 | 0
2019-11-09 23:00 | 1132.3806 | 0 | 873.3333 | 2953.773 | -259.0473 | -259.0473 | 0
2019-11-10 | 807.9067 | 0 | 286.6667 | 2694.7257 | -521.2401 | -521.2401 | 0
2019-11-10 01:00 | 687.0487 | 0 | 286.6667 | 2173.4856 | -400.382 | -400.382 | 0
2019-11-10 02:00 | 634.1494 | 0 | 286.6667 | 1773.1036 | -347.4828 | -347.4828 | 0
2019-11-10 03:00 | 630.7504 | 0 | 2773.3333 | 1425.6209 | 2142.5829 | 2142.5829 | 0
2019-11-10 04:00 | 634.1757 | 0 | 2773.3333 | 3568.2038 | 2139.1576 | 2139.1576 | 0
2019-11-10 05:00 | 696.2025 | 0 | 9873.3333 | 5707.3614 | 9177.1308 | 4292.6386 | 0
2019-11-10 06:00 | 878.5764 | 0 | 9873.3333 | 10000 | 8994.757 | 0 | 0
2019-11-10 07:00 | 1154.2323 | 2215.1196 | 9573.3333 | 10000 | 10634.2206 | 0 | 0
2019-11-10 08:00 | 1105.8163 | 4377.3565 | 9873.3333 | 10000 | 13144.8735 | 0 | 0
2019-11-10 09:00 | 957.186 | 5937.8352 | 9873.3333 | 10000 | 14853.9825 | 0 | 0
2019-11-10 10:00 | 946.9249 | 6780.7047 | 9873.3333 | 10000 | 15707.1132 | 0 | 0
2019-11-10 11:00 | 931.7283 | 6983.7591 | 9060 | 10000 | 15112.0308 | 0 | 0
2019-11-10 12:00 | 903.1983 | 6653.6746 | 7873.3333 | 10000 | 13623.8097 | 0 | 0
2019-11-10 13:00 | 871.0868 | 5665.6532 | 9060 | 10000 | 13854.5664 | 0 | 0
2019-11-10 14:00 | 885.8227 | 3407.8559 | 9060 | 10000 | 11582.0332 | 0 | 0
2019-11-10 15:00 | 996.7954 | 1310.7355 | 4266.6667 | 10000 | 4580.6068 | 0 | 0
2019-11-10 16:00 | 1327.8317 | 0 | 6160 | 10000 | 4832.1683 | 0 | 0
2019-11-10 17:00 | 1885.8109 | 0 | 6160 | 10000 | 4274.1891 | 0 | 0
2019-11-10 18:00 | 2178.1027 | 0 | 4266.6667 | 10000 | 2088.5639 | 0 | 0
2019-11-10 19:00 | 2076.4006 | 0 | 7873.3333 | 10000 | 5796.9328 | 0 | 0
2019-11-10 20:00 | 1983.2556 | 0 | 7873.3333 | 10000 | 5890.0778 | 0 | 0
2019-11-10 21:00 | 1811.1437 | 0 | 6160 | 10000 | 4348.8563 | 0 | 0
2019-11-10 22:00 | 1470.133 | 0 | 4266.6667 | 10000 | 2796.5337 | 0 | 0
2019-11-10 23:00 | 1147.5375 | 0 | 2773.3333 | 10000 | 1625.7959 | 0 | 0
2019-11-11 | 827.8109 | 0 | 6160 | 10000 | 5332.1891 | 0 | 0
2019-11-11 01:00 | 697.5355 | 0 | 4266.6667 | 10000 | 3569.1311 | 0 | 0
2019-11-11 02:00 | 637.5748 | 0 | 1666.6667 | 10000 | 1029.0919 | 0 | 0
2019-11-11 03:00 | 624.8805 | 0 | 286.6667 | 10000 | -338.2139 | -338.2139 | 0
2019-11-11 04:00 | 627.6788 | 0 | 1666.6667 | 9661.7861 | 1038.9879 | 338.2139 | 0
2019-11-11 05:00 | 691.3161 | 0 | 4266.6667 | 10000 | 3575.3506 | 0 | 0
2019-11-11 06:00 | 878.9818 | 0 | 4266.6667 | 10000 | 3387.6849 | 0 | 0
2019-11-11 07:00 | 1170.7606 | 1903.9653 | 4266.6667 | 10000 | 4999.8714 | 0 | 0
2019-11-11 08:00 | 1154.5286 | 3791.8455 | 4266.6667 | 10000 | 6903.9837 | 0 | 0
2019-11-11 09:00 | 1034.0469 | 3089.3577 | 2773.3333 | 10000 | 4828.6441 | 0 | 0
2019-11-11 10:00 | 1056.003 | 2029.0749 | 1666.6667 | 10000 | 2639.7387 | 0 | 0
2019-11-11 11:00 | 1042.0228 | 1222.7271 | 1666.6667 | 10000 | 1847.371 | 0 | 0
2019-11-11 12:00 | 996.5776 | 1042.2151 | 286.6667 | 10000 | 332.3042 | 0 | 0
2019-11-11 13:00 | 958.3625 | 925.3176 | 286.6667 | 10000 | 253.6218 | 0 | 0
2019-11-11 14:00 | 958.5061 | 774.3709 | 286.6667 | 10000 | 102.5314 | 0 | 0
2019-11-11 15:00 | 1060.839 | 267.3313 | 286.6667 | 10000 | -506.841 | -506.841 | 0
2019-11-11 16:00 | 1385.8381 | 0 | 286.6667 | 9493.159 | -1099.1715 | -1099.1715 | 0
2019-11-11 17:00 | 1940.0913 | 0 | 0 | 8393.9875 | -1940.0913 | -1940.0913 | 0
2019-11-11 18:00 | 2226.8451 | 0 | 0 | 6453.8962 | -2226.8451 | -2226.8451 | 0
2019-11-11 19:00 | 2124.1638 | 0 | 0 | 4227.0511 | -2124.1638 | -2124.1638 | 0
2019-11-11 20:00 | 2028.8826 | 0 | 0 | 2102.8872 | -2028.8826 | -2028.8826 | 0
2019-11-11 21:00 | 1852.5795 | 0 | 0 | 74.0047 | -1852.5795 | -74.0047 | -1778.5748
2019-11-11 22:00 | 1500.3315 | 0 | 0 | 0 | -1500.3315 | 0 | -3278.9063
2019-11-11 23:00 | 1164.6734 | 0 | 0 | 0 | -1164.6734 | 0 | -4443.5797
2019-11-12 | 828.1599 | 0 | 0 | 0 | -828.1599 | 0 | -5271.7396
2019-11-12 01:00 | 697.3785 | 0 | 0 | 0 | -697.3785 | 0 | -5969.1181
2019-11-12 02:00 | 639.9061 | 0 | 0 | 0 | -639.9061 | 0 | -6609.0242
2019-11-12 03:00 | 628.0017 | 0 | 0 | 0 | -628.0017 | 0 | -7237.0259
2019-11-12 04:00 | 632.5429 | 0 | 0 | 0 | -632.5429 | 0 | -7869.5688
2019-11-12 05:00 | 697.2868 | 0 | 0 | 0 | -697.2868 | 0 | -8566.8556
2019-11-12 06:00 | 901.3988 | 0 | 0 | 0 | -901.3988 | 0 | -9468.2543
2019-11-12 07:00 | 1198.2235 | 134.3959 | 0 | 0 | -1063.8276 | 0 | -10532.0819
2019-11-12 08:00 | 1171.6987 | 910.2008 | 0 | 0 | -261.4978 | 0 | -10793.5797
2019-11-12 09:00 | 1057.9159 | 997.9447 | 0 | 0 | -59.9712 | 0 | -10853.5509
2019-11-12 10:00 | 1089.8826 | 642.022 | 0 | 0 | -447.8606 | 0 | -11301.4115
2019-11-12 11:00 | 1119.5144 | 2749.4315 | 0 | 0 | 1629.9171 | 1629.9171 | -9671.4945
2019-11-12 12:00 | 1061.8357 | 3457.2875 | 0 | 1629.9171 | 2395.4518 | 2395.4518 | -5646.1256
2019-11-12 13:00 | 1027.3007 | 4689.6655 | 0 | 4025.3689 | 3662.3648 | 3662.3648 | 0
2019-11-12 14:00 | 1031.4292 | 3193.0497 | 286.6667 | 7687.7337 | 2448.2872 | 2312.2663 | 0
2019-11-12 15:00 | 1134.649 | 1359.1183 | 0 | 10000 | 224.4693 | 0 | 0
2019-11-12 16:00 | 1454.7871 | 0 | 0 | 10000 | -1454.7871 | -1454.7871 | 0
2019-11-12 17:00 | 2014.0243 | 0 | 0 | 8545.2129 | -2014.0243 | -2014.0243 | 0
2019-11-12 18:00 | 2292.9885 | 0 | 0 | 6531.1886 | -2292.9885 | -2292.9885 | 0
2019-11-12 19:00 | 2185.7499 | 0 | 0 | 4238.2001 | -2185.7499 | -2185.7499 | 0
2019-11-12 20:00 | 2089.407 | 0 | 0 | 2052.4503 | -2089.407 | -2052.4503 | -36.9568
2019-11-12 21:00 | 1911.0186 | 0 | 0 | 0 | -1911.0186 | 0 | -1947.9754
2019-11-12 22:00 | 1565.3028 | 0 | 0 | 0 | -1565.3028 | 0 | -3513.2782
2019-11-12 23:00 | 1234.2034 | 0 | 0 | 0 | -1234.2034 | 0 | -4747.4816
2019-11-13 | 897.9994 | 0 | 0 | 0 | -897.9994 | 0 | -5645.481
2019-11-13 01:00 | 773.3314 | 0 | 0 | 0 | -773.3314 | 0 | -6418.8124
2019-11-13 02:00 | 723.0068 | 0 | 0 | 0 | -723.0068 | 0 | -7141.8193
2019-11-13 03:00 | 714.9836 | 0 | 0 | 0 | -714.9836 | 0 | -7856.8029
2019-11-13 04:00 | 717.3781 | 0 | 0 | 0 | -717.3781 | 0 | -8574.1809
2019-11-13 05:00 | 779.9252 | 0 | 0 | 0 | -779.9252 | 0 | -9354.1062
2019-11-13 06:00 | 962.7383 | 0 | 0 | 0 | -962.7383 | 0 | -10316.8445
2019-11-13 07:00 | 1238.9578 | 0 | 0 | 0 | -1238.9578 | 0 | -11555.8023
2019-11-13 08:00 | 1203.0925 | 759.2162 | 873.3333 | 0 | 429.457 | 429.457 | -11126.3453
2019-11-13 09:00 | 1063.7397 | 2737.5992 | 286.6667 | 429.457 | 1960.5261 | 1960.5261 | -8736.3621
2019-11-13 10:00 | 1077.1252 | 2915.3937 | 286.6667 | 2389.9831 | 2124.9352 | 2124.9352 | -4221.4438
2019-11-13 11:00 | 1064.355 | 4285.4853 | 873.3333 | 4514.9183 | 4094.4637 | 4094.4637 | 0
2019-11-13 12:00 | 1035.198 | 197.578 | 286.6667 | 8609.382 | -550.9533 | -550.9533 | 0
2019-11-13 13:00 | 1005.4002 | 2701.91 | 873.3333 | 8058.4287 | 2569.8432 | 1941.5713 | 0
2019-11-13 14:00 | 1010.571 | 280.3274 | 2773.3333 | 10000 | 2043.0898 | 0 | 0
2019-11-13 15:00 | 1108.6018 | 297.6625 | 1666.6667 | 10000 | 855.7274 | 0 | 0
2019-11-13 16:00 | 1432.5061 | 0 | 1666.6667 | 10000 | 234.1606 | 0 | 0
2019-11-13 17:00 | 1987.9483 | 0 | 873.3333 | 10000 | -1114.615 | -1114.615 | 0
2019-11-13 18:00 | 2266.505 | 0 | 2773.3333 | 8885.385 | 506.8284 | 506.8284 | 0
2019-11-13 19:00 | 2158.6506 | 0 | 1666.6667 | 9392.2134 | -491.9839 | -491.9839 | 0
2019-11-13 20:00 | 2054.0419 | 0 | 2773.3333 | 8900.2295 | 719.2915 | 719.2915 | 0
2019-11-13 21:00 | 1872.3146 | 0 | 2773.3333 | 9619.5209 | 901.0187 | 380.4791 | 0
2019-11-13 22:00 | 1526.8467 | 0 | 2773.3333 | 10000 | 1246.4866 | 0 | 0
2019-11-13 23:00 | 1201.8538 | 0 | 2773.3333 | 10000 | 1571.4796 | 0 | 0
2019-11-14 | 870.4024 | 0 | 873.3333 | 10000 | 2.9309 | 0 | 0
2019-11-14 01:00 | 743.659 | 0 | 873.3333 | 10000 | 129.6743 | 0 | 0
2019-11-14 02:00 | 680.0799 | 0 | 1666.6667 | 10000 | 986.5868 | 0 | 0
2019-11-14 03:00 | 664.3998 | 0 | 1666.6667 | 10000 | 1002.2669 | 0 | 0
2019-11-14 04:00 | 661.9736 | 0 | 873.3333 | 10000 | 211.3597 | 0 | 0
2019-11-14 05:00 | 719.9781 | 0 | 286.6667 | 10000 | -433.3114 | -433.3114 | 0
2019-11-14 06:00 | 910.8407 | 0 | 873.3333 | 9566.6886 | -37.5074 | -37.5074 | 0
2019-11-14 07:00 | 1175.8927 | 1899.3066 | 873.3333 | 9529.1812 | 1596.7473 | 470.8188 | 0
2019-11-14 08:00 | 1133.4256 | 2583.6486 | 286.6667 | 10000 | 1736.8897 | 0 | 0
2019-11-14 09:00 | 982.3845 | 4807.6222 | 873.3333 | 10000 | 4698.571 | 0 | 0
2019-11-14 10:00 | 978.056 | 7011.3407 | 873.3333 | 10000 | 6906.618 | 0 | 0
2019-11-14 11:00 | 958.6032 | 7344.782 | 873.3333 | 10000 | 7259.5122 | 0 | 0
2019-11-14 12:00 | 922.6958 | 6967.827 | 2773.3333 | 10000 | 8818.4645 | 0 | 0
2019-11-14 13:00 | 884.5596 | 5989.2299 | 1666.6667 | 10000 | 6771.3369 | 0 | 0
2019-11-14 14:00 | 896.6497 | 4274.0475 | 873.3333 | 10000 | 4250.731 | 0 | 0
2019-11-14 15:00 | 1000.8524 | 1971.1575 | 873.3333 | 10000 | 1843.6385 | 0 | 0
2019-11-14 16:00 | 1321.6027 | 0 | 873.3333 | 10000 | -448.2694 | -448.2694 | 0
2019-11-14 17:00 | 1859.5839 | 0 | 286.6667 | 9551.7306 | -1572.9172 | -1572.9172 | 0
2019-11-14 18:00 | 2159.4258 | 0 | 286.6667 | 7978.8134 | -1872.7591 | -1872.7591 | 0
2019-11-14 19:00 | 2051.8146 | 0 | 873.3333 | 6106.0543 | -1178.4812 | -1178.4812 | 0
2019-11-14 20:00 | 1953.4959 | 0 | 873.3333 | 4927.5731 | -1080.1626 | -1080.1626 | 0
2019-11-14 21:00 | 1775.2416 | 0 | 873.3333 | 3847.4105 | -901.9082 | -901.9082 | 0
2019-11-14 22:00 | 1430.7961 | 0 | 873.3333 | 2945.5023 | -557.4628 | -557.4628 | 0
2019-11-14 23:00 | 1106.2072 | 0 | 873.3333 | 2388.0395 | -232.8738 | -232.8738 | 0
2019-11-15 | 776.4125 | 0 | 873.3333 | 2155.1657 | 96.9208 | 96.9208 | 0
2019-11-15 01:00 | 647.2254 | 0 | 873.3333 | 2252.0865 | 226.1079 | 226.1079 | 0
2019-11-15 02:00 | 595.8888 | 0 | 873.3333 | 2478.1944 | 277.4445 | 277.4445 | 0
2019-11-15 03:00 | 592.2104 | 0 | 873.3333 | 2755.6389 | 281.1229 | 281.1229 | 0
2019-11-15 04:00 | 599.0558 | 0 | 286.6667 | 3036.7618 | -312.3892 | -312.3892 | 0
2019-11-15 05:00 | 668.0559 | 0 | 286.6667 | 2724.3726 | -381.3892 | -381.3892 | 0
2019-11-15 06:00 | 870.1093 | 0 | 873.3333 | 2342.9834 | 3.224 | 3.224 | 0
2019-11-15 07:00 | 1143.9865 | 2106.7459 | 873.3333 | 2346.2075 | 1836.0928 | 1836.0928 | 0
2019-11-15 08:00 | 1097.0734 | 4463.5134 | 286.6667 | 4182.3002 | 3653.1067 | 3653.1067 | 0
2019-11-15 09:00 | 955.8056 | 6105.5788 | 873.3333 | 7835.4069 | 6023.1066 | 2164.5931 | 0
2019-11-15 10:00 | 960.9472 | 7055.5179 | 286.6667 | 10000 | 6381.2374 | 0 | 0
2019-11-15 11:00 | 944.4006 | 7325.5356 | 873.3333 | 10000 | 7254.4683 | 0 | 0
2019-11-15 12:00 | 917.6089 | 6941.5541 | 873.3333 | 10000 | 6897.2786 | 0 | 0
2019-11-15 13:00 | 889.3609 | 5893.0163 | 286.6667 | 10000 | 5290.3221 | 0 | 0
2019-11-15 14:00 | 903.1834 | 4265.0487 | 286.6667 | 10000 | 3648.532 | 0 | 0
2019-11-15 15:00 | 1014.928 | 1960.3659 | 286.6667 | 10000 | 1232.1046 | 0 | 0
2019-11-15 16:00 | 1342.5942 | 0 | 286.6667 | 10000 | -1055.9275 | -1055.9275 | 0
2019-11-15 17:00 | 1897.0145 | 0 | 286.6667 | 8944.0725 | -1610.3478 | -1610.3478 | 0
2019-11-15 18:00 | 2191.9222 | 0 | 286.6667 | 7333.7247 | -1905.2555 | -1905.2555 | 0
2019-11-15 19:00 | 2090.781 | 0 | 286.6667 | 5428.4692 | -1804.1144 | -1804.1144 | 0
2019-11-15 20:00 | 1998.0205 | 0 | 0 | 3624.3548 | -1998.0205 | -1998.0205 | 0
2019-11-15 21:00 | 1824.1636 | 0 | 0 | 1626.3343 | -1824.1636 | -1626.3343 | -197.8293
2019-11-15 22:00 | 1484.6871 | 0 | 0 | 0 | -1484.6871 | 0 | -1682.5164
2019-11-15 23:00 | 1164.6631 | 0 | 0 | 0 | -1164.6631 | 0 | -2847.1796
2019-11-16 | 840.8008 | 0 | 0 | 0 | -840.8008 | 0 | -3687.9804
2019-11-16 01:00 | 719.5056 | 0 | 0 | 0 | -719.5056 | 0 | -4407.4859
2019-11-16 02:00 | 664.5863 | 0 | 1666.6667 | 0 | 1002.0804 | 1002.0804 | -3405.4055
2019-11-16 03:00 | 660.1365 | 0 | 286.6667 | 1002.0804 | -373.4698 | -373.4698 | -2776.7949
2019-11-16 04:00 | 662.7497 | 0 | 873.3333 | 628.6106 | 210.5836 | 210.5836 | -1937.6007
2019-11-16 05:00 | 722.8043 | 0 | 2773.3333 | 839.1942 | 2050.529 | 2050.529 | 0
2019-11-16 06:00 | 904.5351 | 0 | 873.3333 | 2889.7232 | -31.2017 | -31.2017 | 0
2019-11-16 07:00 | 1185.0606 | 1986.9895 | 873.3333 | 2858.5215 | 1675.2623 | 1675.2623 | 0
2019-11-16 08:00 | 1133.6238 | 4177.0863 | 1666.6667 | 4533.7838 | 4710.1292 | 4710.1292 | 0
2019-11-16 09:00 | 990.8665 | 5681.054 | 2773.3333 | 9243.913 | 7463.5209 | 756.087 | 0
2019-11-16 10:00 | 992.9561 | 6521.9938 | 2773.3333 | 10000 | 8302.3711 | 0 | 0
2019-11-16 11:00 | 972.4409 | 6766.8058 | 873.3333 | 10000 | 6667.6983 | 0 | 0
2019-11-16 12:00 | 939.9021 | 6389.1895 | 873.3333 | 10000 | 6322.6207 | 0 | 0
2019-11-16 13:00 | 906.525 | 5477.6742 | 0 | 10000 | 4571.1492 | 0 | 0
2019-11-16 14:00 | 919.4122 | 3888.8688 | 0 | 10000 | 2969.4566 | 0 | 0
2019-11-16 15:00 | 1033.0028 | 1760.566 | 0 | 10000 | 727.5632 | 0 | 0
2019-11-16 16:00 | 1364.9915 | 0 | 0 | 10000 | -1364.9915 | -1364.9915 | 0
2019-11-16 17:00 | 1930.2885 | 0 | 873.3333 | 8635.0085 | -1056.9551 | -1056.9551 | 0
2019-11-16 18:00 | 2217.1176 | 0 | 2773.3333 | 7578.0533 | 556.2157 | 556.2157 | 0
2019-11-16 19:00 | 2119.4072 | 0 | 2773.3333 | 8134.269 | 653.9262 | 653.9262 | 0
2019-11-16 20:00 | 2030.1102 | 0 | 4266.6667 | 8788.1952 | 2236.5564 | 1211.8048 | 0
2019-11-16 21:00 | 1861.8377 | 0 | 6160 | 10000 | 4298.1623 | 0 | 0
2019-11-16 22:00 | 1525.5677 | 0 | 7873.3333 | 10000 | 6347.7657 | 0 | 0
2019-11-16 23:00 | 1210.1289 | 0 | 2773.3333 | 10000 | 1563.2044 | 0 | 0
2019-11-17 | 884.1548 | 0 | 6160 | 10000 | 5275.8452 | 0 | 0
2019-11-17 01:00 | 759.2136 | 0 | 4266.6667 | 10000 | 3507.4531 | 0 | 0
2019-11-17 02:00 | 703.6094 | 0 | 1666.6667 | 10000 | 963.0573 | 0 | 0
2019-11-17 03:00 | 696.7676 | 0 | 2773.3333 | 10000 | 2076.5657 | 0 | 0
2019-11-17 04:00 | 699.9683 | 0 | 4266.6667 | 10000 | 3566.6984 | 0 | 0
2019-11-17 05:00 | 761.5546 | 0 | 9060 | 10000 | 8298.4454 | 0 | 0
2019-11-17 06:00 | 943.2025 | 0 | 6160 | 10000 | 5216.7975 | 0 | 0
2019-11-17 07:00 | 1212.1204 | 230.7544 | 6160 | 10000 | 5178.634 | 0 | 0
2019-11-17 08:00 | 1175.2361 | 916.6799 | 9573.3333 | 10000 | 9314.7772 | 0 | 0
2019-11-17 09:00 | 1041.9136 | 1459.9802 | 9573.3333 | 10000 | 9991.4 | 0 | 0
2019-11-17 10:00 | 1056.1708 | 1097.4795 | 9060 | 10000 | 9101.3087 | 0 | 0
2019-11-17 11:00 | 1044.0575 | 1741.6727 | 9060 | 10000 | 9757.6152 | 0 | 0
2019-11-17 12:00 | 1018.2179 | 51.4912 | 7873.3333 | 10000 | 6906.6067 | 0 | 0
2019-11-17 13:00 | 988.613 | 164.7605 | 7873.3333 | 10000 | 7049.4809 | 0 | 0
2019-11-17 14:00 | 994.8455 | 898.1741 | 7873.3333 | 10000 | 7776.6619 | 0 | 0
2019-11-17 15:00 | 1093.9927 | 1319.426 | 2773.3333 | 10000 | 2998.7667 | 0 | 0
2019-11-17 16:00 | 1407.5372 | 0 | 2773.3333 | 10000 | 1365.7961 | 0 | 0
2019-11-17 17:00 | 1956.5985 | 0 | 1666.6667 | 10000 | -289.9319 | -289.9319 | 0
2019-11-17 18:00 | 2237.5028 | 0 | 2773.3333 | 9710.0681 | 535.8306 | 289.9319 | 0
2019-11-17 19:00 | 2127.5374 | 0 | 2773.3333 | 10000 | 645.796 | 0 | 0
2019-11-17 20:00 | 2027.32 | 0 | 873.3333 | 10000 | -1153.9867 | -1153.9867 | 0
2019-11-17 21:00 | 1838.2894 | 0 | 2773.3333 | 8846.0133 | 935.0439 | 935.0439 | 0
2019-11-17 22:00 | 1486.3317 | 0 | 1666.6667 | 9781.0572 | 180.3349 | 180.3349 | 0
2019-11-17 23:00 | 1160.4494 | 0 | 2773.3333 | 9961.3922 | 1612.8839 | 38.6078 | 0
2019-11-18 | 829.0815 | 0 | 286.6667 | 10000 | -542.4148 | -542.4148 | 0
2019-11-18 01:00 | 685.9449 | 0 | 286.6667 | 9457.5852 | -399.2782 | -399.2782 | 0
2019-11-18 02:00 | 618.1814 | 0 | 286.6667 | 9058.307 | -331.5148 | -331.5148 | 0
2019-11-18 03:00 | 601.0459 | 0 | 0 | 8726.7923 | -601.0459 | -601.0459 | 0
2019-11-18 04:00 | 596.7788 | 0 | 0 | 8125.7463 | -596.7788 | -596.7788 | 0
2019-11-18 05:00 | 653.6725 | 0 | 0 | 7528.9676 | -653.6725 | -653.6725 | 0
2019-11-18 06:00 | 836.7231 | 0 | 0 | 6875.295 | -836.7231 | -836.7231 | 0
2019-11-18 07:00 | 1125.2146 | 1541.8222 | 0 | 6038.5719 | 416.6077 | 416.6077 | 0
2019-11-18 08:00 | 1091.0408 | 3588.4197 | 0 | 6455.1796 | 2497.379 | 2497.379 | 0
2019-11-18 09:00 | 959.1548 | 5105.3284 | 0 | 8952.5586 | 4146.1736 | 1047.4414 | 0
2019-11-18 10:00 | 951.2784 | 6181.442 | 0 | 10000 | 5230.1636 | 0 | 0
2019-11-18 11:00 | 968.6494 | 6422.919 | 286.6667 | 10000 | 5740.9363 | 0 | 0
2019-11-18 12:00 | 947.6048 | 6085.7632 | 873.3333 | 10000 | 6011.4917 | 0 | 0
2019-11-18 13:00 | 916.8597 | 5141.4844 | 873.3333 | 10000 | 5097.958 | 0 | 0
2019-11-18 14:00 | 920.746 | 3625.9005 | 286.6667 | 10000 | 2991.8212 | 0 | 0
2019-11-18 15:00 | 1019.8425 | 1578.2669 | 286.6667 | 10000 | 845.0911 | 0 | 0
2019-11-18 16:00 | 1345.9848 | 0 | 286.6667 | 10000 | -1059.3181 | -1059.3181 | 0
2019-11-18 17:00 | 1900.2573 | 0 | 286.6667 | 8940.6819 | -1613.5907 | -1613.5907 | 0
2019-11-18 18:00 | 2198.2453 | 0 | 0 | 7327.0912 | -2198.2453 | -2198.2453 | 0
2019-11-18 19:00 | 2103.7345 | 0 | 0 | 5128.8459 | -2103.7345 | -2103.7345 | 0
2019-11-18 20:00 | 2015.6739 | 0 | 286.6667 | 3025.1114 | -1729.0072 | -1729.0072 | 0
2019-11-18 21:00 | 1845.5208 | 0 | 873.3333 | 1296.1042 | -972.1875 | -972.1875 | 0
2019-11-18 22:00 | 1502.7871 | 0 | 286.6667 | 323.9167 | -1216.1204 | -323.9167 | -892.2037
2019-11-18 23:00 | 1172.0873 | 0 | 873.3333 | 0 | -298.754 | 0 | -1190.9577
2019-11-19 | 838.1753 | 0 | 0 | 0 | -838.1753 | 0 | -2029.1329
2019-11-19 01:00 | 713.2889 | 0 | 873.3333 | 0 | 160.0444 | 160.0444 | -1869.0885
2019-11-19 02:00 | 660.1109 | 0 | 2773.3333 | 160.0444 | 2113.2224 | 2113.2224 | 0
2019-11-19 03:00 | 651.0891 | 0 | 1666.6667 | 2273.2668 | 1015.5775 | 1015.5775 | 0
2019-11-19 04:00 | 655.094 | 0 | 2773.3333 | 3288.8444 | 2118.2393 | 2118.2393 | 0
2019-11-19 05:00 | 720.2223 | 0 | 2773.3333 | 5407.0837 | 2053.111 | 2053.111 | 0
2019-11-19 06:00 | 910.0178 | 0 | 6160 | 7460.1947 | 5249.9822 | 2539.8053 | 0
2019-11-19 07:00 | 1194.7717 | 113.3808 | 4266.6667 | 10000 | 3185.2758 | 0 | 0
2019-11-19 08:00 | 1152.1662 | 414.6359 | 4266.6667 | 10000 | 3529.1364 | 0 | 0
2019-11-19 09:00 | 1014.617 | 965.0478 | 4266.6667 | 10000 | 4217.0975 | 0 | 0
2019-11-19 10:00 | 1019.7199 | 1018.7884 | 7873.3333 | 10000 | 7872.4018 | 0 | 0
2019-11-19 11:00 | 1003.2592 | 1192.6811 | 9960 | 10000 | 10149.4219 | 0 | 0
2019-11-19 12:00 | 970.4534 | 1452.3971 | 9060 | 10000 | 9541.9437 | 0 | 0
2019-11-19 13:00 | 936.7432 | 1104.2449 | 9573.3333 | 10000 | 9740.835 | 0 | 0
2019-11-19 14:00 | 944.8229 | 236.6562 | 9873.3333 | 10000 | 9165.1666 | 0 | 0
2019-11-19 15:00 | 1054.3429 | 129.8649 | 9873.3333 | 10000 | 8948.8554 | 0 | 0
2019-11-19 16:00 | 1383.3295 | 0 | 9873.3333 | 10000 | 8490.0039 | 0 | 0
2019-11-19 17:00 | 1941.8109 | 0 | 9060 | 10000 | 7118.1891 | 0 | 0
2019-11-19 18:00 | 2233.3462 | 0 | 9573.3333 | 10000 | 7339.9872 | 0 | 0
2019-11-19 19:00 | 2134.3612 | 0 | 9060 | 10000 | 6925.6388 | 0 | 0
2019-11-19 20:00 | 2043.5216 | 0 | 9573.3333 | 10000 | 7529.8117 | 0 | 0
2019-11-19 21:00 | 1872.706 | 0 | 2773.3333 | 10000 | 900.6273 | 0 | 0
2019-11-19 22:00 | 1525.7266 | 0 | 4266.6667 | 10000 | 2740.9401 | 0 | 0
2019-11-19 23:00 | 1195.0936 | 0 | 6160 | 10000 | 4964.9064 | 0 | 0
2019-11-20 | 853.7657 | 0 | 6160 | 10000 | 5306.2343 | 0 | 0
2019-11-20 01:00 | 731.8482 | 0 | 4266.6667 | 10000 | 3534.8185 | 0 | 0
2019-11-20 02:00 | 678.6148 | 0 | 2773.3333 | 10000 | 2094.7186 | 0 | 0
2019-11-20 03:00 | 672.2065 | 0 | 2773.3333 | 10000 | 2101.1268 | 0 | 0
2019-11-20 04:00 | 676.0451 | 0 | 1666.6667 | 10000 | 990.6216 | 0 | 0
2019-11-20 05:00 | 736.9872 | 0 | 4266.6667 | 10000 | 3529.6795 | 0 | 0
2019-11-20 06:00 | 942.0498 | 0 | 7873.3333 | 10000 | 6931.2835 | 0 | 0
2019-11-20 07:00 | 1201.6066 | 0 | 7873.3333 | 10000 | 6671.7267 | 0 | 0
2019-11-20 08:00 | 1153.3357 | 11.3102 | 6160 | 10000 | 5017.9746 | 0 | 0
2019-11-20 09:00 | 1000.0117 | 1094.0617 | 9960 | 10000 | 10054.05 | 0 | 0
2019-11-20 10:00 | 1005.297 | 3749.1438 | 9873.3333 | 10000 | 12617.1801 | 0 | 0
2019-11-20 11:00 | 979.7502 | 1185.374 | 9873.3333 | 10000 | 10078.9572 | 0 | 0
2019-11-20 12:00 | 946.4639 | 698.9343 | 6160 | 10000 | 5912.4704 | 0 | 0
2019-11-20 13:00 | 915.4585 | 941.9431 | 7873.3333 | 10000 | 7899.818 | 0 | 0
2019-11-20 14:00 | 933.1373 | 3540.1013 | 7873.3333 | 10000 | 10480.2973 | 0 | 0
2019-11-20 15:00 | 1051.775 | 1484.3993 | 9060 | 10000 | 9492.6243 | 0 | 0
2019-11-20 16:00 | 1386.0839 | 0 | 6160 | 10000 | 4773.9161 | 0 | 0
2019-11-20 17:00 | 1955.5031 | 0 | 1666.6667 | 10000 | -288.8364 | -288.8364 | 0
2019-11-20 18:00 | 2242.0258 | 0 | 1666.6667 | 9711.1636 | -575.3591 | -575.3591 | 0
2019-11-20 19:00 | 2142.5243 | 0 | 1666.6667 | 9135.8045 | -475.8577 | -475.8577 | 0
2019-11-20 20:00 | 2050.5114 | 0 | 4266.6667 | 8659.9468 | 2216.1552 | 1340.0532 | 0
2019-11-20 21:00 | 1877.2773 | 0 | 2773.3333 | 10000 | 896.056 | 0 | 0
2019-11-20 22:00 | 1536.8565 | 0 | 1666.6667 | 10000 | 129.8102 | 0 | 0
2019-11-20 23:00 | 1218.8483 | 0 | 1666.6667 | 10000 | 447.8184 | 0 | 0
2019-11-21 | 898.9748 | 0 | 2773.3333 | 10000 | 1874.3585 | 0 | 0
2019-11-21 01:00 | 774.0968 | 0 | 1666.6667 | 10000 | 892.5699 | 0 | 0
2019-11-21 02:00 | 723.3135 | 0 | 286.6667 | 10000 | -436.6469 | -436.6469 | 0
2019-11-21 03:00 | 723.0123 | 0 | 286.6667 | 9563.3531 | -436.3457 | -436.3457 | 0
2019-11-21 04:00 | 726.8797 | 0 | 286.6667 | 9127.0075 | -440.213 | -440.213 | 0
2019-11-21 05:00 | 789.7783 | 0 | 0 | 8686.7945 | -789.7783 | -789.7783 | 0
2019-11-21 06:00 | 973.663 | 0 | 0 | 7897.0162 | -973.663 | -973.663 | 0
2019-11-21 07:00 | 1277.3755 | 0 | 286.6667 | 6923.3532 | -990.7089 | -990.7089 | 0
2019-11-21 08:00 | 1237.7622 | 439.5254 | 2773.3333 | 5932.6443 | 1975.0965 | 1975.0965 | 0
2019-11-21 09:00 | 1108.0845 | 697.3025 | 6160 | 7907.7408 | 5749.218 | 2092.2592 | 0
2019-11-21 10:00 | 1142.6554 | 1731.3365 | 9060 | 10000 | 9648.6811 | 0 | 0
2019-11-21 11:00 | 1120.9662 | 1547.3457 | 10000 | 10000 | 10426.3795 | 0 | 0
2019-11-21 12:00 | 1090.3935 | 922.2264 | 9573.3333 | 10000 | 9405.1663 | 0 | 0
2019-11-21 13:00 | 1058.3575 | 735.6332 | 9573.3333 | 10000 | 9250.609 | 0 | 0
2019-11-21 14:00 | 1072.0869 | 3619.441 | 9573.3333 | 10000 | 12120.6874 | 0 | 0
2019-11-21 15:00 | 1172.0327 | 1556.7906 | 4266.6667 | 10000 | 4651.4246 | 0 | 0
2019-11-21 16:00 | 1491.0445 | 0 | 4266.6667 | 10000 | 2775.6222 | 0 | 0
2019-11-21 17:00 | 2052.865 | 0 | 873.3333 | 10000 | -1179.5316 | -1179.5316 | 0
2019-11-21 18:00 | 2323.993 | 0 | 4266.6667 | 8820.4684 | 1942.6736 | 1179.5316 | 0
2019-11-21 19:00 | 2215.8609 | 0 | 2773.3333 | 10000 | 557.4724 | 0 | 0
2019-11-21 20:00 | 2122.0281 | 0 | 4266.6667 | 10000 | 2144.6386 | 0 | 0
2019-11-21 21:00 | 1943.9226 | 0 | 2773.3333 | 10000 | 829.4107 | 0 | 0
2019-11-21 22:00 | 1593.0726 | 0 | 1666.6667 | 10000 | 73.5941 | 0 | 0
2019-11-21 23:00 | 1273.7954 | 0 | 286.6667 | 10000 | -987.1287 | -987.1287 | 0
2019-11-22 | 941.228 | 0 | 286.6667 | 9012.8713 | -654.5613 | -654.5613 | 0
2019-11-22 01:00 | 815.4848 | 0 | 286.6667 | 8358.31 | -528.8181 | -528.8181 | 0
2019-11-22 02:00 | 757.0748 | 0 | 873.3333 | 7829.4919 | 116.2585 | 116.2585 | 0
2019-11-22 03:00 | 750.7683 | 0 | 873.3333 | 7945.7504 | 122.565 | 122.565 | 0
2019-11-22 04:00 | 746.8513 | 0 | 286.6667 | 8068.3154 | -460.1847 | -460.1847 | 0
2019-11-22 05:00 | 805.5992 | 0 | 873.3333 | 7608.1307 | 67.7342 | 67.7342 | 0
2019-11-22 06:00 | 987.5004 | 0 | 0 | 7675.8649 | -987.5004 | -987.5004 | 0
2019-11-22 07:00 | 1282.4163 | 1586.5779 | 0 | 6688.3645 | 304.1616 | 304.1616 | 0
2019-11-22 08:00 | 1240.2704 | 3753.6207 | 0 | 6992.5261 | 2513.3503 | 2513.3503 | 0
2019-11-22 09:00 | 1111.269 | 5374.1846 | 0 | 9505.8764 | 4262.9156 | 494.1236 | 0
2019-11-22 10:00 | 1141.2702 | 4648.6335 | 0 | 10000 | 3507.3633 | 0 | 0
2019-11-22 11:00 | 1120.6189 | 6582.3792 | 286.6667 | 10000 | 5748.427 | 0 | 0
2019-11-22 12:00 | 1093.3155 | 6211.595 | 286.6667 | 10000 | 5404.9462 | 0 | 0
2019-11-22 13:00 | 1061.3164 | 5318.9018 | 873.3333 | 10000 | 5130.9187 | 0 | 0
2019-11-22 14:00 | 1069.6146 | 3777.3774 | 1666.6667 | 10000 | 4374.4295 | 0 | 0
2019-11-22 15:00 | 1171.4388 | 1679.0506 | 4266.6667 | 10000 | 4774.2784 | 0 | 0
2019-11-22 16:00 | 1487.4958 | 0 | 2773.3333 | 10000 | 1285.8375 | 0 | 0
2019-11-22 17:00 | 2049.0382 | 0 | 9060 | 10000 | 7010.9618 | 0 | 0
2019-11-22 18:00 | 2319.4927 | 0 | 9573.3333 | 10000 | 7253.8407 | 0 | 0
2019-11-22 19:00 | 2208.429 | 0 | 9060 | 10000 | 6851.571 | 0 | 0
2019-11-22 20:00 | 2107.9521 | 0 | 4266.6667 | 10000 | 2158.7145 | 0 | 0
2019-11-22 21:00 | 1926.4101 | 0 | 4266.6667 | 10000 | 2340.2566 | 0 | 0
2019-11-22 22:00 | 1580.8514 | 0 | 6160 | 10000 | 4579.1486 | 0 | 0
2019-11-22 23:00 | 1255.3924 | 0 | 6160 | 10000 | 4904.6076 | 0 | 0
2019-11-23 | 930.9371 | 0 | 7873.3333 | 10000 | 6942.3962 | 0 | 0
2019-11-23 01:00 | 805.1646 | 0 | 6160 | 10000 | 5354.8354 | 0 | 0
2019-11-23 02:00 | 747.0065 | 0 | 4266.6667 | 10000 | 3519.6602 | 0 | 0
2019-11-23 03:00 | 738.4334 | 0 | 2773.3333 | 10000 | 2034.8999 | 0 | 0
2019-11-23 04:00 | 736.4408 | 0 | 873.3333 | 10000 | 136.8925 | 0 | 0
2019-11-23 05:00 | 798.1038 | 0 | 286.6667 | 10000 | -511.4371 | -511.4371 | 0
2019-11-23 06:00 | 976.6172 | 0 | 0 | 9488.5629 | -976.6172 | -976.6172 | 0
2019-11-23 07:00 | 1277.2718 | 1445.8846 | 873.3333 | 8511.9457 | 1041.9461 | 1041.9461 | 0
2019-11-23 08:00 | 1231.4304 | 3465.2536 | 2773.3333 | 9553.8918 | 5007.1565 | 446.1082 | 0
2019-11-23 09:00 | 1092.6253 | 4257.7048 | 1666.6667 | 10000 | 4831.7462 | 0 | 0
2019-11-23 10:00 | 1122.225 | 4928.5516 | 1666.6667 | 10000 | 5472.9932 | 0 | 0
2019-11-23 11:00 | 1096.7884 | 6551.0658 | 2773.3333 | 10000 | 8227.6108 | 0 | 0
2019-11-23 12:00 | 1065.7227 | 5077.1511 | 286.6667 | 10000 | 4298.0951 | 0 | 0
2019-11-23 13:00 | 1033.1323 | 5310.2285 | 286.6667 | 10000 | 4563.7629 | 0 | 0
2019-11-23 14:00 | 1038.0113 | 3719.0897 | 286.6667 | 10000 | 2967.745 | 0 | 0
2019-11-23 15:00 | 1138.1946 | 1629.5074 | 286.6667 | 10000 | 777.9796 | 0 | 0
2019-11-23 16:00 | 1456.2946 | 0 | 286.6667 | 10000 | -1169.628 | -1169.628 | 0
2019-11-23 17:00 | 2014.4665 | 0 | 286.6667 | 8830.372 | -1727.7998 | -1727.7998 | 0
2019-11-23 18:00 | 2288.4745 | 0 | 286.6667 | 7102.5722 | -2001.8078 | -2001.8078 | 0
2019-11-23 19:00 | 2178.2424 | 0 | 0 | 5100.7644 | -2178.2424 | -2178.2424 | 0
2019-11-23 20:00 | 2077.4627 | 0 | 286.6667 | 2922.522 | -1790.796 | -1790.796 | 0
2019-11-23 21:00 | 1904.8924 | 0 | 286.6667 | 1131.726 | -1618.2257 | -1131.726 | -486.4998
2019-11-23 22:00 | 1560.5854 | 0 | 0 | 0 | -1560.5854 | 0 | -2047.0852
2019-11-23 23:00 | 1232.4759 | 0 | 0 | 0 | -1232.4759 | 0 | -3279.5611
2019-11-24 | 900.5268 | 0 | 0 | 0 | -900.5268 | 0 | -4180.0878
2019-11-24 01:00 | 763.8431 | 0 | 0 | 0 | -763.8431 | 0 | -4943.9309
2019-11-24 02:00 | 701.8327 | 0 | 286.6667 | 0 | -415.166 | 0 | -5359.0969
2019-11-24 03:00 | 685.5278 | 0 | 0 | 0 | -685.5278 | 0 | -6044.6247
2019-11-24 04:00 | 679.9358 | 0 | 0 | 0 | -679.9358 | 0 | -6724.5605
2019-11-24 05:00 | 736.4834 | 0 | 873.3333 | 0 | 136.85 | 136.85 | -6587.7105
2019-11-24 06:00 | 910.4936 | 0 | 873.3333 | 136.85 | -37.1603 | -37.1603 | -6488.0208
2019-11-24 07:00 | 1202.8433 | 1517.6469 | 873.3333 | 99.6897 | 1188.137 | 1188.137 | -5200.1941
2019-11-24 08:00 | 1159.5317 | 1700.2451 | 873.3333 | 1287.8267 | 1414.0468 | 1414.0468 | -2498.3205
2019-11-24 09:00 | 1027.3036 | 2478.2293 | 0 | 2701.8735 | 1450.9257 | 1450.9257 | 0
2019-11-24 10:00 | 1048.2236 | 3011.191 | 0 | 4152.7992 | 1962.9674 | 1962.9674 | 0
2019-11-24 11:00 | 1039.3917 | 6571.7704 | 0 | 6115.7666 | 5532.3788 | 3884.2334 | 0
2019-11-24 12:00 | 1012.8777 | 6157.2541 | 873.3333 | 10000 | 6017.7098 | 0 | 0
2019-11-24 13:00 | 1000.1891 | 5205.5842 | 873.3333 | 10000 | 5078.7285 | 0 | 0
2019-11-24 14:00 | 1015.9563 | 3648.0771 | 873.3333 | 10000 | 3505.4542 | 0 | 0
2019-11-24 15:00 | 1113.9348 | 1573.9325 | 2773.3333 | 10000 | 3233.3311 | 0 | 0
2019-11-24 16:00 | 1428.5103 | 0 | 1666.6667 | 10000 | 238.1563 | 0 | 0
2019-11-24 17:00 | 1982.4565 | 0 | 2773.3333 | 10000 | 790.8769 | 0 | 0
2019-11-24 18:00 | 2257.3277 | 0 | 2773.3333 | 10000 | 516.0057 | 0 | 0
2019-11-24 19:00 | 2146.7324 | 0 | 1666.6667 | 10000 | -480.0657 | -480.0657 | 0
2019-11-24 20:00 | 2047.935 | 0 | 1666.6667 | 9519.9343 | -381.2684 | -381.2684 | 0
2019-11-24 21:00 | 1867.2526 | 0 | 286.6667 | 9138.6659 | -1580.586 | -1580.586 | 0
2019-11-24 22:00 | 1523.5596 | 0 | 873.3333 | 7558.08 | -650.2263 | -650.2263 | 0
2019-11-24 23:00 | 1202.953 | 0 | 873.3333 | 6907.8537 | -329.6196 | -329.6196 | 0
2019-11-25 | 879.9559 | 0 | 286.6667 | 6578.234 | -593.2892 | -593.2892 | 0
2019-11-25 01:00 | 748.7936 | 0 | 286.6667 | 5984.9449 | -462.1269 | -462.1269 | 0
2019-11-25 02:00 | 691.9956 | 0 | 286.6667 | 5522.8179 | -405.329 | -405.329 | 0
2019-11-25 03:00 | 683.1469 | 0 | 286.6667 | 5117.489 | -396.4802 | -396.4802 | 0
2019-11-25 04:00 | 685.4825 | 0 | 286.6667 | 4721.0088 | -398.8159 | -398.8159 | 0
2019-11-25 05:00 | 752.862 | 0 | 1666.6667 | 4322.1929 | 913.8047 | 913.8047 | 0
2019-11-25 06:00 | 966.8839 | 0 | 873.3333 | 5235.9976 | -93.5505 | -93.5505 | 0
2019-11-25 07:00 | 1257.0964 | 1559.4644 | 286.6667 | 5142.4471 | 589.0346 | 589.0346 | 0
2019-11-25 08:00 | 1221.0002 | 3801.7367 | 873.3333 | 5731.4817 | 3454.0698 | 3454.0698 | 0
2019-11-25 09:00 | 1098.4191 | 5425.2549 | 6160 | 9185.5515 | 10486.8359 | 814.4485 | 0
2019-11-25 10:00 | 1117.5805 | 6355.6521 | 6160 | 10000 | 11398.0716 | 0 | 0
2019-11-25 11:00 | 1098.1887 | 6630.4181 | 2773.3333 | 10000 | 8305.5628 | 0 | 0
2019-11-25 12:00 | 1075.3909 | 4002.6325 | 2773.3333 | 10000 | 5700.5749 | 0 | 0
2019-11-25 13:00 | 1035.0692 | 3261.776 | 2773.3333 | 10000 | 5000.0402 | 0 | 0
2019-11-25 14:00 | 1037.9634 | 3807.0152 | 2773.3333 | 10000 | 5542.3851 | 0 | 0
2019-11-25 15:00 | 1152.9055 | 1606.9755 | 2773.3333 | 10000 | 3227.4034 | 0 | 0
2019-11-25 16:00 | 1475.696 | 0 | 873.3333 | 10000 | -602.3627 | -602.3627 | 0
2019-11-25 17:00 | 2043.3379 | 0 | 873.3333 | 9397.6373 | -1170.0046 | -1170.0046 | 0
2019-11-25 18:00 | 2321.4379 | 0 | 1666.6667 | 8227.6327 | -654.7712 | -654.7712 | 0
2019-11-25 19:00 | 2226.8661 | 0 | 1666.6667 | 7572.8615 | -560.1994 | -560.1994 | 0
2019-11-25 20:00 | 2137.2823 | 0 | 873.3333 | 7012.6621 | -1263.949 | -1263.949 | 0
2019-11-25 21:00 | 1964.381 | 0 | 873.3333 | 5748.7132 | -1091.0477 | -1091.0477 | 0
2019-11-25 22:00 | 1619.8433 | 0 | 873.3333 | 4657.6655 | -746.51 | -746.51 | 0
2019-11-25 23:00 | 1300.5587 | 0 | 286.6667 | 3911.1555 | -1013.892 | -1013.892 | 0
2019-11-26 | 972.385 | 0 | 873.3333 | 2897.2635 | -99.0517 | -99.0517 | 0
2019-11-26 01:00 | 840.4281 | 0 | 873.3333 | 2798.2118 | 32.9052 | 32.9052 | 0
2019-11-26 02:00 | 791.7755 | 0 | 873.3333 | 2831.117 | 81.5578 | 81.5578 | 0
2019-11-26 03:00 | 795.5027 | 0 | 4266.6667 | 2912.6748 | 3471.1639 | 3471.1639 | 0
2019-11-26 04:00 | 804.5168 | 0 | 2773.3333 | 6383.8388 | 1968.8165 | 1968.8165 | 0
2019-11-26 05:00 | 858.743 | 0 | 4266.6667 | 8352.6553 | 3407.9237 | 1647.3447 | 0
2019-11-26 06:00 | 1069.3213 | 0 | 4266.6667 | 10000 | 3197.3453 | 0 | 0
2019-11-26 07:00 | 1339.6951 | 420.3135 | 4266.6667 | 10000 | 3347.285 | 0 | 0
2019-11-26 08:00 | 1298.1444 | 3698.147 | 6160 | 10000 | 8560.0026 | 0 | 0
2019-11-26 09:00 | 1156.1642 | 4264.1954 | 9060 | 10000 | 12168.0312 | 0 | 0
2019-11-26 10:00 | 1176.7064 | 4366.6535 | 9573.3333 | 10000 | 12763.2804 | 0 | 0
2019-11-26 11:00 | 1146.8676 | 1920.5862 | 9960 | 10000 | 10733.7186 | 0 | 0
2019-11-26 12:00 | 1105.2405 | 4392.663 | 7873.3333 | 10000 | 11160.7559 | 0 | 0
2019-11-26 13:00 | 1064.8944 | 1410.2887 | 9873.3333 | 10000 | 10218.7276 | 0 | 0
2019-11-26 14:00 | 1072.0313 | 2826.432 | 6160 | 10000 | 7914.4007 | 0 | 0
2019-11-26 15:00 | 1182.3207 | 1176.7892 | 4266.6667 | 10000 | 4261.1352 | 0 | 0
2019-11-26 16:00 | 1511.9556 | 0 | 2773.3333 | 10000 | 1261.3777 | 0 | 0
2019-11-26 17:00 | 2093.6872 | 0 | 1666.6667 | 10000 | -427.0205 | -427.0205 | 0
2019-11-26 18:00 | 2374.5589 | 0 | 4266.6667 | 9572.9795 | 1892.1077 | 427.0205 | 0
2019-11-26 19:00 | 2274.1858 | 0 | 2773.3333 | 10000 | 499.1475 | 0 | 0
2019-11-26 20:00 | 2192.1394 | 0 | 1666.6667 | 10000 | -525.4728 | -525.4728 | 0
2019-11-26 21:00 | 2021.2793 | 0 | 873.3333 | 9474.5272 | -1147.946 | -1147.946 | 0
2019-11-26 22:00 | 1677.4675 | 0 | 873.3333 | 8326.5812 | -804.1341 | -804.1341 | 0
2019-11-26 23:00 | 1343.7369 | 0 | 1666.6667 | 7522.4471 | 322.9298 | 322.9298 | 0
2019-11-27 | 1002.426 | 0 | 1666.6667 | 7845.3769 | 664.2407 | 664.2407 | 0
2019-11-27 01:00 | 876.9652 | 0 | 873.3333 | 8509.6176 | -3.6319 | -3.6319 | 0
2019-11-27 02:00 | 816.5255 | 0 | 1666.6667 | 8505.9857 | 850.1411 | 850.1411 | 0
2019-11-27 03:00 | 805.9847 | 0 | 1666.6667 | 9356.1268 | 860.6819 | 643.8732 | 0
2019-11-27 04:00 | 804.8855 | 0 | 2773.3333 | 10000 | 1968.4478 | 0 | 0
2019-11-27 05:00 | 861.7218 | 0 | 2773.3333 | 10000 | 1911.6115 | 0 | 0
2019-11-27 06:00 | 1041.2725 | 0 | 2773.3333 | 10000 | 1732.0608 | 0 | 0
2019-11-27 07:00 | 1343.6169 | 391.5117 | 4266.6667 | 10000 | 3314.5615 | 0 | 0
2019-11-27 08:00 | 1292.6397 | 3110.8753 | 2773.3333 | 10000 | 4591.5689 | 0 | 0
2019-11-27 09:00 | 1156.7923 | 3872.8136 | 2773.3333 | 10000 | 5489.3546 | 0 | 0
2019-11-27 10:00 | 1197.821 | 6015.6511 | 2773.3333 | 10000 | 7591.1635 | 0 | 0
2019-11-27 11:00 | 1170.4862 | 6282.5949 | 4266.6667 | 10000 | 9378.7753 | 0 | 0
2019-11-27 12:00 | 1137.3026 | 4363.0712 | 2773.3333 | 10000 | 5999.102 | 0 | 0
2019-11-27 13:00 | 1099.467 | 3428.0258 | 4266.6667 | 10000 | 6595.2255 | 0 | 0
2019-11-27 14:00 | 1099.6844 | 3527.1845 | 4266.6667 | 10000 | 6694.1668 | 0 | 0
2019-11-27 15:00 | 1196.7785 | 1413.6674 | 1666.6667 | 10000 | 1883.5556 | 0 | 0
2019-11-27 16:00 | 1511.7984 | 0 | 2773.3333 | 10000 | 1261.5349 | 0 | 0
2019-11-27 17:00 | 2076.531 | 0 | 4266.6667 | 10000 | 2190.1357 | 0 | 0
2019-11-27 18:00 | 2380.4275 | 0 | 2773.3333 | 10000 | 392.9058 | 0 | 0
2019-11-27 19:00 | 2244.6683 | 0 | 1666.6667 | 10000 | -578.0017 | -578.0017 | 0
2019-11-27 20:00 | 2127.297 | 0 | 873.3333 | 9421.9983 | -1253.9637 | -1253.9637 | 0
2019-11-27 21:00 | 1942.833 | 0 | 2773.3333 | 8168.0346 | 830.5003 | 830.5003 | 0
2019-11-27 22:00 | 1591.3294 | 0 | 1666.6667 | 8998.5349 | 75.3373 | 75.3373 | 0
2019-11-27 23:00 | 1249.3763 | 0 | 1666.6667 | 9073.8722 | 417.2904 | 417.2904 | 0
2019-11-28 | 915.5894 | 0 | 2773.3333 | 9491.1626 | 1857.7439 | 508.8374 | 0
2019-11-28 01:00 | 782.6461 | 0 | 1666.6667 | 10000 | 884.0206 | 0 | 0
2019-11-28 02:00 | 734.7876 | 0 | 286.6667 | 10000 | -448.121 | -448.121 | 0
2019-11-28 03:00 | 737.551 | 0 | 873.3333 | 9551.879 | 135.7824 | 135.7824 | 0
2019-11-28 04:00 | 739.2719 | 0 | 873.3333 | 9687.6614 | 134.0614 | 134.0614 | 0
2019-11-28 05:00 | 802.6673 | 0 | 0 | 9821.7228 | -802.6673 | -802.6673 | 0
2019-11-28 06:00 | 1005.0654 | 0 | 286.6667 | 9019.0555 | -718.3987 | -718.3987 | 0
2019-11-28 07:00 | 1275.9198 | 0 | 0 | 8300.6568 | -1275.9198 | -1275.9198 | 0
2019-11-28 08:00 | 1245.1046 | 124.2575 | 0 | 7024.737 | -1120.8471 | -1120.8471 | 0
2019-11-28 09:00 | 1118.9694 | 284.387 | 0 | 5903.8899 | -834.5824 | -834.5824 | 0
2019-11-28 10:00 | 1156.6676 | 364.213 | 0 | 5069.3074 | -792.4546 | -792.4546 | 0
2019-11-28 11:00 | 1134.983 | 411.8794 | 0 | 4276.8529 | -723.1036 | -723.1036 | 0
2019-11-28 12:00 | 1104.636 | 958.2409 | 873.3333 | 3553.7493 | 726.9383 | 726.9383 | 0
2019-11-28 13:00 | 1060.2596 | 289.3032 | 873.3333 | 4280.6876 | 102.377 | 102.377 | 0
2019-11-28 14:00 | 1055.9231 | 259.5768 | 1666.6667 | 4383.0645 | 870.3204 | 870.3204 | 0
2019-11-28 15:00 | 1151.7344 | 70.9745 | 4266.6667 | 5253.3849 | 3185.9069 | 3185.9069 | 0
2019-11-28 16:00 | 1466.3235 | 0 | 2773.3333 | 8439.2918 | 1307.0098 | 1307.0098 | 0
2019-11-28 17:00 | 1987.8032 | 0 | 2773.3333 | 9746.3016 | 785.5301 | 253.6984 | 0
2019-11-28 18:00 | 2316.7744 | 0 | 286.6667 | 10000 | -2030.1077 | -2030.1077 | 0
2019-11-28 19:00 | 2187.6226 | 0 | 286.6667 | 7969.8923 | -1900.9559 | -1900.9559 | 0
2019-11-28 20:00 | 2086.1416 | 0 | 1666.6667 | 6068.9364 | -419.475 | -419.475 | 0
2019-11-28 21:00 | 1906.2021 | 0 | 873.3333 | 5649.4614 | -1032.8687 | -1032.8687 | 0
2019-11-28 22:00 | 1561.0091 | 0 | 2773.3333 | 4616.5927 | 1212.3243 | 1212.3243 | 0
2019-11-28 23:00 | 1236.9489 | 0 | 2773.3333 | 5828.9169 | 1536.3844 | 1536.3844 | 0
2019-11-29 | 907.4432 | 0 | 6160 | 7365.3014 | 5252.5568 | 2634.6986 | 0
2019-11-29 01:00 | 773.555 | 0 | 7873.3333 | 10000 | 7099.7783 | 0 | 0
2019-11-29 02:00 | 715.7506 | 0 | 6160 | 10000 | 5444.2494 | 0 | 0
2019-11-29 03:00 | 711.9231 | 0 | 7873.3333 | 10000 | 7161.4102 | 0 | 0
2019-11-29 04:00 | 714.0546 | 0 | 7873.3333 | 10000 | 7159.2788 | 0 | 0
2019-11-29 05:00 | 773.764 | 0 | 4266.6667 | 10000 | 3492.9027 | 0 | 0
2019-11-29 06:00 | 953.8439 | 0 | 7873.3333 | 10000 | 6919.4894 | 0 | 0
2019-11-29 07:00 | 1225.3065 | 0 | 4266.6667 | 10000 | 3041.3601 | 0 | 0
2019-11-29 08:00 | 1168.6188 | 534.0473 | 6160 | 10000 | 5525.4285 | 0 | 0
2019-11-29 09:00 | 1011.9352 | 2496.673 | 4266.6667 | 10000 | 5751.4045 | 0 | 0
2019-11-29 10:00 | 1013.9912 | 2618.6914 | 1666.6667 | 10000 | 3271.3669 | 0 | 0
2019-11-29 11:00 | 984.9717 | 6230.777 | 6160 | 10000 | 11405.8053 | 0 | 0
2019-11-29 12:00 | 953.6309 | 2356.2108 | 9573.3333 | 10000 | 10975.9133 | 0 | 0
2019-11-29 13:00 | 922.7506 | 3404.1173 | 9873.3333 | 10000 | 12354.7 | 0 | 0
2019-11-29 14:00 | 941.3159 | 222.5422 | 9573.3333 | 10000 | 8854.5597 | 0 | 0
2019-11-29 15:00 | 1059.1187 | 281.8765 | 4266.6667 | 10000 | 3489.4245 | 0 | 0
2019-11-29 16:00 | 1393.4135 | 0 | 4266.6667 | 10000 | 2873.2531 | 0 | 0
2019-11-29 17:00 | 1958.5996 | 0 | 4266.6667 | 10000 | 2308.067 | 0 | 0
2019-11-29 18:00 | 2247.9739 | 0 | 4266.6667 | 10000 | 2018.6928 | 0 | 0
2019-11-29 19:00 | 2149.5794 | 0 | 4266.6667 | 10000 | 2117.0872 | 0 | 0
2019-11-29 20:00 | 2053.4533 | 0 | 873.3333 | 10000 | -1180.12 | -1180.12 | 0
2019-11-29 21:00 | 1870.3153 | 0 | 2773.3333 | 8819.88 | 903.018 | 903.018 | 0
2019-11-29 22:00 | 1525.0002 | 0 | 2773.3333 | 9722.898 | 1248.3331 | 277.102 | 0
2019-11-29 23:00 | 1202.0955 | 0 | 1666.6667 | 10000 | 464.5712 | 0 | 0
2019-11-30 | 873.155 | 0 | 4266.6667 | 10000 | 3393.5117 | 0 | 0
2019-11-30 01:00 | 745.8131 | 0 | 2773.3333 | 10000 | 2027.5203 | 0 | 0
2019-11-30 02:00 | 687.7836 | 0 | 286.6667 | 10000 | -401.1169 | -401.1169 | 0
2019-11-30 03:00 | 677.3122 | 0 | 0 | 9598.8831 | -677.3122 | -677.3122 | 0
2019-11-30 04:00 | 679.9995 | 0 | 0 | 8921.5709 | -679.9995 | -679.9995 | 0
2019-11-30 05:00 | 742.6247 | 0 | 0 | 8241.5714 | -742.6247 | -742.6247 | 0
2019-11-30 06:00 | 921.3115 | 0 | 1666.6667 | 7498.9467 | 745.3552 | 745.3552 | 0
2019-11-30 07:00 | 1203.2472 | 24.1316 | 873.3333 | 8244.3019 | -305.7823 | -305.7823 | 0
2019-11-30 08:00 | 1166.7344 | 2681.8644 | 286.6667 | 7938.5197 | 1801.7966 | 1801.7966 | 0
2019-11-30 09:00 | 1011.344 | 3798.2487 | 0 | 9740.3163 | 2786.9047 | 259.6837 | 0
2019-11-30 10:00 | 1007.322 | 3361.412 | 0 | 10000 | 2354.0901 | 0 | 0
2019-11-30 11:00 | 984.4644 | 6380.8037 | 0 | 10000 | 5396.3393 | 0 | 0
2019-11-30 12:00 | 958.3348 | 6006.7559 | 0 | 10000 | 5048.4211 | 0 | 0
2019-11-30 13:00 | 928.251 | 5081.9558 | 0 | 10000 | 4153.7048 | 0 | 0
2019-11-30 14:00 | 943.2534 | 3518.6642 | 2773.3333 | 10000 | 5348.7441 | 0 | 0
2019-11-30 15:00 | 1056.5015 | 774.579 | 286.6667 | 10000 | 4.7443 | 0 | 0
2019-11-30 16:00 | 1379.5389 | 0 | 286.6667 | 10000 | -1092.8723 | -1092.8723 | 0
2019-11-30 17:00 | 1935.8688 | 0 | 873.3333 | 8907.1277 | -1062.5355 | -1062.5355 | 0
2019-11-30 18:00 | 2222.4789 | 0 | 0 | 7844.5923 | -2222.4789 | -2222.4789 | 0
2019-11-30 19:00 | 2123.1389 | 0 | 286.6667 | 5622.1134 | -1836.4722 | -1836.4722 | 0
2019-11-30 20:00 | 2030.7096 | 0 | 286.6667 | 3785.6412 | -1744.043 | -1744.043 | 0
2019-11-30 21:00 | 1854.1117 | 0 | 873.3333 | 2041.5982 | -980.7784 | -980.7784 | 0
2019-11-30 22:00 | 1511.2445 | 0 | 286.6667 | 1060.8198 | -1224.5778 | -1060.8198 | -163.758
2019-11-30 23:00 | 1188.4945 | 0 | 286.6667 | 0 | -901.8278 | 0 | -1065.5858
2019-12-01 | 922.4524 | 0 | 286.6667 | 0 | -635.7857 | 0 | -1701.3715
2019-12-01 01:00 | 791.2664 | 0 | 286.6667 | 0 | -504.5998 | 0 | -2205.9713
2019-12-01 02:00 | 728.0241 | 0 | 0 | 0 | -728.0241 | 0 | -2933.9954
2019-12-01 03:00 | 714.413 | 0 | 0 | 0 | -714.413 | 0 | -3648.4083
2019-12-01 04:00 | 712.0727 | 0 | 0 | 0 | -712.0727 | 0 | -4360.4811
2019-12-01 05:00 | 777.9418 | 0 | 286.6667 | 0 | -491.2751 | 0 | -4851.7561
2019-12-01 06:00 | 1002.1635 | 0 | 873.3333 | 0 | -128.8302 | 0 | -4980.5863
2019-12-01 07:00 | 1348.032 | 219.3084 | 873.3333 | 0 | -255.3902 | 0 | -5235.9766
2019-12-01 08:00 | 1296.1733 | 469.9981 | 873.3333 | 0 | 47.1581 | 47.1581 | -5188.8184
2019-12-01 09:00 | 1120.0358 | 423.5002 | 873.3333 | 47.1581 | 176.7977 | 176.7977 | -4964.8627
2019-12-01 10:00 | 1126.8428 | 5555.3694 | 1666.6667 | 223.9558 | 6095.1932 | 6095.1932 | 0
2019-12-01 11:00 | 1098.2004 | 6524.2283 | 4266.6667 | 6319.149 | 9692.6945 | 3680.851 | 0
2019-12-01 12:00 | 1068.0672 | 6264.1753 | 4266.6667 | 10000 | 9462.7748 | 0 | 0
2019-12-01 13:00 | 1028.592 | 5351.2582 | 2773.3333 | 10000 | 7095.9996 | 0 | 0
2019-12-01 14:00 | 1063.0735 | 1686.8361 | 6160 | 10000 | 6783.7626 | 0 | 0
2019-12-01 15:00 | 1188.1481 | 1556.4756 | 873.3333 | 10000 | 1241.6608 | 0 | 0
2019-12-01 16:00 | 1547.8042 | 0 | 1666.6667 | 10000 | 118.8624 | 0 | 0
2019-12-01 17:00 | 2152.3946 | 0 | 1666.6667 | 10000 | -485.728 | -485.728 | 0
2019-12-01 18:00 | 2446.5125 | 0 | 286.6667 | 9514.272 | -2159.8458 | -2159.8458 | 0
2019-12-01 19:00 | 2276.8552 | 0 | 286.6667 | 7354.4262 | -1990.1885 | -1990.1885 | 0
2019-12-01 20:00 | 2170.8657 | 0 | 873.3333 | 5364.2376 | -1297.5323 | -1297.5323 | 0
2019-12-01 21:00 | 1994.6355 | 0 | 2773.3333 | 4066.7053 | 778.6979 | 778.6979 | 0
2019-12-01 22:00 | 1646.112 | 0 | 1666.6667 | 4845.4032 | 20.5546 | 20.5546 | 0
2019-12-01 23:00 | 1315.9059 | 0 | 1666.6667 | 4865.9578 | 350.7607 | 350.7607 | 0
2019-12-02 | 980.4709 | 0 | 2773.3333 | 5216.7185 | 1792.8625 | 1792.8625 | 0
2019-12-02 01:00 | 854.0456 | 0 | 1666.6667 | 7009.581 | 812.6211 | 812.6211 | 0
2019-12-02 02:00 | 792.7364 | 0 | 873.3333 | 7822.202 | 80.5969 | 80.5969 | 0
2019-12-02 03:00 | 782.3777 | 0 | 0 | 7902.799 | -782.3777 | -782.3777 | 0
2019-12-02 04:00 | 785.0487 | 0 | 286.6667 | 7120.4213 | -498.382 | -498.382 | 0
2019-12-02 05:00 | 862.5654 | 0 | 873.3333 | 6622.0393 | 10.7679 | 10.7679 | 0
2019-12-02 06:00 | 1113.5927 | 0 | 286.6667 | 6632.8073 | -826.926 | -826.926 | 0
2019-12-02 07:00 | 1446.5795 | 1110.9851 | 286.6667 | 5805.8812 | -48.9277 | -48.9277 | 0
2019-12-02 08:00 | 1380.7642 | 870.55 | 286.6667 | 5756.9536 | -223.5475 | -223.5475 | 0
2019-12-02 09:00 | 1224.1264 | 1162.6316 | 0 | 5533.406 | -61.4948 | -61.4948 | 0
2019-12-02 10:00 | 1242.6639 | 2997.3657 | 0 | 5471.9113 | 1754.7019 | 1754.7019 | 0
2019-12-02 11:00 | 1233.3116 | 4239.935 | 0 | 7226.6132 | 3006.6234 | 2773.3868 | 0
2019-12-02 12:00 | 1230.6154 | 42.7214 | 0 | 10000 | -1187.8941 | -1187.8941 | 0
2019-12-02 13:00 | 1203.771 | 3822.4033 | 0 | 8812.1059 | 2618.6324 | 1187.8941 | 0
2019-12-02 14:00 | 1218.7705 | 1723.3911 | 0 | 10000 | 504.6207 | 0 | 0
2019-12-02 15:00 | 1343.2999 | 0 | 0 | 10000 | -1343.2999 | -1343.2999 | 0
2019-12-02 16:00 | 1706.7513 | 0 | 0 | 8656.7001 | -1706.7513 | -1706.7513 | 0
2019-12-02 17:00 | 2330.4906 | 0 | 0 | 6949.9488 | -2330.4906 | -2330.4906 | 0
2019-12-02 18:00 | 2613.974 | 0 | 0 | 4619.4582 | -2613.974 | -2613.974 | 0
2019-12-02 19:00 | 2455.6864 | 0 | 0 | 2005.4842 | -2455.6864 | -2005.4842 | -450.2021
2019-12-02 20:00 | 2353.6035 | 0 | 0 | 0 | -2353.6035 | 0 | -2803.8056
2019-12-02 21:00 | 2163.6082 | 0 | 0 | 0 | -2163.6082 | 0 | -4967.4138
2019-12-02 22:00 | 1792.0049 | 0 | 0 | 0 | -1792.0049 | 0 | -6759.4187
2019-12-02 23:00 | 1450.6935 | 0 | 0 | 0 | -1450.6935 | 0 | -8210.1122
2019-12-03 | 1104.3722 | 0 | 0 | 0 | -1104.3722 | 0 | -9314.4843
2019-12-03 01:00 | 975.042 | 0 | 0 | 0 | -975.042 | 0 | -10289.5263
2019-12-03 02:00 | 916.9926 | 0 | 0 | 0 | -916.9926 | 0 | -11206.519
2019-12-03 03:00 | 908.7814 | 0 | 286.6667 | 0 | -622.1147 | 0 | -11828.6337
2019-12-03 04:00 | 903.4311 | 0 | 0 | 0 | -903.4311 | 0 | -12732.0648
2019-12-03 05:00 | 967.2531 | 0 | 0 | 0 | -967.2531 | 0 | -13699.318
2019-12-03 06:00 | 1196.5512 | 0 | 0 | 0 | -1196.5512 | 0 | -14895.8691
2019-12-03 07:00 | 1562.0779 | 1338.3412 | 0 | 0 | -223.7366 | 0 | -15119.6058
2019-12-03 08:00 | 1487.2808 | 3693.6436 | 0 | 0 | 2206.3628 | 2206.3628 | -12913.243
2019-12-03 09:00 | 1289.3387 | 5441.838 | 0 | 2206.3628 | 4152.4993 | 4152.4993 | -6554.3809
2019-12-03 10:00 | 1296.5087 | 6492.7114 | 0 | 6358.8621 | 5196.2027 | 3641.1379 | 0
2019-12-03 11:00 | 1259.2012 | 6786.1937 | 0 | 10000 | 5526.9925 | 0 | 0
2019-12-03 12:00 | 1207.429 | 6474.0756 | 0 | 10000 | 5266.6467 | 0 | 0
2019-12-03 13:00 | 1166.4435 | 5566.5175 | 0 | 10000 | 4400.074 | 0 | 0
2019-12-03 14:00 | 1177.3452 | 3937.301 | 286.6667 | 10000 | 3046.6225 | 0 | 0
2019-12-03 15:00 | 1296.6688 | 1692.8425 | 0 | 10000 | 396.1738 | 0 | 0
2019-12-03 16:00 | 1674.7817 | 0 | 0 | 10000 | -1674.7817 | -1674.7817 | 0
2019-12-03 17:00 | 2299.0989 | 0 | 0 | 8325.2183 | -2299.0989 | -2299.0989 | 0
2019-12-03 18:00 | 2564.7236 | 0 | 0 | 6026.1193 | -2564.7236 | -2564.7236 | 0
2019-12-03 19:00 | 2392.3802 | 0 | 0 | 3461.3958 | -2392.3802 | -2392.3802 | 0
2019-12-03 20:00 | 2292.2024 | 0 | 0 | 1069.0155 | -2292.2024 | -1069.0155 | -1223.1868
2019-12-03 21:00 | 2114.6979 | 0 | 0 | 0 | -2114.6979 | 0 | -3337.8848
2019-12-03 22:00 | 1751.4101 | 0 | 0 | 0 | -1751.4101 | 0 | -5089.2949
2019-12-03 23:00 | 1410.1008 | 0 | 0 | 0 | -1410.1008 | 0 | -6499.3957
2019-12-04 | 1048.9721 | 0 | 0 | 0 | -1048.9721 | 0 | -7548.3678
2019-12-04 01:00 | 919.5866 | 0 | 0 | 0 | -919.5866 | 0 | -8467.9544
2019-12-04 02:00 | 858.8576 | 0 | 0 | 0 | -858.8576 | 0 | -9326.812
2019-12-04 03:00 | 846.5819 | 0 | 286.6667 | 0 | -559.9152 | 0 | -9886.7272
2019-12-04 04:00 | 848.1376 | 0 | 286.6667 | 0 | -561.4709 | 0 | -10448.1981
2019-12-04 05:00 | 910.1025 | 0 | 286.6667 | 0 | -623.4358 | 0 | -11071.6339
2019-12-04 06:00 | 1132.3554 | 0 | 286.6667 | 0 | -845.6888 | 0 | -11917.3227
2019-12-04 07:00 | 1457.367 | 322.0425 | 286.6667 | 0 | -848.6578 | 0 | -12765.9805
2019-12-04 08:00 | 1381.2482 | 3144.0482 | 0 | 0 | 1762.8 | 1762.8 | -11003.1804
2019-12-04 09:00 | 1174.3332 | 4836.9609 | 0 | 1762.8 | 3662.6277 | 3662.6277 | -5577.7527
2019-12-04 10:00 | 1177.083 | 6046.9875 | 0 | 5425.4277 | 4869.9045 | 4574.5723 | 0
2019-12-04 11:00 | 1157.1685 | 1429.1142 | 286.6667 | 10000 | 558.6124 | 0 | 0
2019-12-04 12:00 | 1137.8233 | 3751.0389 | 873.3333 | 10000 | 3486.549 | 0 | 0
2019-12-04 13:00 | 1116.2493 | 4190.1871 | 286.6667 | 10000 | 3360.6045 | 0 | 0
2019-12-04 14:00 | 1132.592 | 2362.7348 | 873.3333 | 10000 | 2103.4761 | 0 | 0
2019-12-04 15:00 | 1253.0542 | 586.178 | 0 | 10000 | -666.8762 | -666.8762 | 0
2019-12-04 16:00 | 1614.2058 | 0 | 286.6667 | 9333.1238 | -1327.5391 | -1327.5391 | 0
2019-12-04 17:00 | 2234.9862 | 0 | 286.6667 | 8005.5847 | -1948.3195 | -1948.3195 | 0
2019-12-04 18:00 | 2510.6029 | 0 | 286.6667 | 6057.2652 | -2223.9363 | -2223.9363 | 0
2019-12-04 19:00 | 2335.7663 | 0 | 286.6667 | 3833.3289 | -2049.0996 | -2049.0996 | 0
2019-12-04 20:00 | 2229.0989 | 0 | 873.3333 | 1784.2293 | -1355.7656 | -1355.7656 | 0
2019-12-04 21:00 | 2052.5902 | 0 | 873.3333 | 428.4638 | -1179.2569 | -428.4638 | -750.7931
2019-12-04 22:00 | 1707.6858 | 0 | 0 | 0 | -1707.6858 | 0 | -2458.479
2019-12-04 23:00 | 1382.2925 | 0 | 0 | 0 | -1382.2925 | 0 | -3840.7715
2019-12-05 | 1041.1098 | 0 | 286.6667 | 0 | -754.4431 | 0 | -4595.2146
2019-12-05 01:00 | 915.6449 | 0 | 0 | 0 | -915.6449 | 0 | -5510.8595
2019-12-05 02:00 | 860.3805 | 0 | 873.3333 | 0 | 12.9528 | 12.9528 | -5497.9067
2019-12-05 03:00 | 853.1304 | 0 | 2773.3333 | 12.9528 | 1920.203 | 1920.203 | -3564.7509
2019-12-05 04:00 | 853.3578 | 0 | 2773.3333 | 1933.1558 | 1919.9756 | 1919.9756 | 0
2019-12-05 05:00 | 925.6475 | 0 | 1666.6667 | 3853.1313 | 741.0191 | 741.0191 | 0
2019-12-05 06:00 | 1154.7785 | 0 | 2773.3333 | 4594.1505 | 1618.5548 | 1618.5548 | 0
2019-12-05 07:00 | 1511.1506 | 762.1084 | 1666.6667 | 6212.7052 | 917.6245 | 917.6245 | 0
2019-12-05 08:00 | 1435.3573 | 2360.6395 | 2773.3333 | 7130.3297 | 3698.6155 | 2869.6703 | 0
2019-12-05 09:00 | 1230.5129 | 4203.6812 | 4266.6667 | 10000 | 7239.8351 | 0 | 0
2019-12-05 10:00 | 1237.5657 | 4460.3118 | 2773.3333 | 10000 | 5996.0794 | 0 | 0
2019-12-05 11:00 | 1193.5983 | 4865.3878 | 6160 | 10000 | 9831.7895 | 0 | 0
2019-12-05 12:00 | 1159.8184 | 2996.2019 | 2773.3333 | 10000 | 4609.7169 | 0 | 0
2019-12-05 13:00 | 1131.0538 | 1875.6454 | 2773.3333 | 10000 | 3517.9249 | 0 | 0
2019-12-05 14:00 | 1149.737 | 1964.0827 | 1666.6667 | 10000 | 2481.0124 | 0 | 0
2019-12-05 15:00 | 1263.9649 | 710.0077 | 2773.3333 | 10000 | 2219.3762 | 0 | 0
2019-12-05 16:00 | 1620.5967 | 0 | 1666.6667 | 10000 | 46.0699 | 0 | 0
2019-12-05 17:00 | 2241.7092 | 0 | 2773.3333 | 10000 | 531.6241 | 0 | 0
2019-12-05 18:00 | 2527.4865 | 0 | 4266.6667 | 10000 | 1739.1801 | 0 | 0
2019-12-05 19:00 | 2347.7467 | 0 | 9060 | 10000 | 6712.2533 | 0 | 0
2019-12-05 20:00 | 2230.661 | 0 | 9873.3333 | 10000 | 7642.6723 | 0 | 0
2019-12-05 21:00 | 2049.1146 | 0 | 10000 | 10000 | 7950.8854 | 0 | 0
2019-12-05 22:00 | 1705.9928 | 0 | 10000 | 10000 | 8294.0072 | 0 | 0
2019-12-05 23:00 | 1375.177 | 0 | 9960 | 10000 | 8584.823 | 0 | 0
2019-12-06 | 1025.1964 | 0 | 9573.3333 | 10000 | 8548.1369 | 0 | 0
2019-12-06 01:00 | 909.0228 | 0 | 7873.3333 | 10000 | 6964.3105 | 0 | 0
2019-12-06 02:00 | 839.2298 | 0 | 873.3333 | 10000 | 34.1036 | 0 | 0
2019-12-06 03:00 | 825.9854 | 0 | 2773.3333 | 10000 | 1947.3479 | 0 | 0
2019-12-06 04:00 | 819.4423 | 0 | 2773.3333 | 10000 | 1953.891 | 0 | 0
2019-12-06 05:00 | 910.6095 | 0 | 9873.3333 | 10000 | 8962.7239 | 0 | 0
2019-12-06 06:00 | 1128.4966 | 0 | 6160 | 10000 | 5031.5034 | 0 | 0
2019-12-06 07:00 | 1470.4934 | 538.9417 | 4266.6667 | 10000 | 3335.115 | 0 | 0
2019-12-06 08:00 | 1406.0706 | 1117.6942 | 9060 | 10000 | 8771.6236 | 0 | 0
2019-12-06 09:00 | 1222.9622 | 2594.0009 | 7873.3333 | 10000 | 9244.3721 | 0 | 0
2019-12-06 10:00 | 1218.1617 | 1474.3678 | 4266.6667 | 10000 | 4522.8728 | 0 | 0
2019-12-06 11:00 | 1285.7228 | 2542.2705 | 2773.3333 | 10000 | 4029.881 | 0 | 0
2019-12-06 12:00 | 1230.7804 | 2204.8398 | 1666.6667 | 10000 | 2640.7261 | 0 | 0
2019-12-06 13:00 | 1213.7822 | 270.7238 | 1666.6667 | 10000 | 723.6083 | 0 | 0
2019-12-06 14:00 | 1221.93 | 689.7815 | 1666.6667 | 10000 | 1134.5182 | 0 | 0
2019-12-06 15:00 | 1344.3023 | 148.3362 | 2773.3333 | 10000 | 1577.3673 | 0 | 0
2019-12-06 16:00 | 1703.0283 | 0 | 2773.3333 | 10000 | 1070.305 | 0 | 0
2019-12-06 17:00 | 2280.3839 | 0 | 2773.3333 | 10000 | 492.9494 | 0 | 0
2019-12-06 18:00 | 2565.3701 | 0 | 873.3333 | 10000 | -1692.0368 | -1692.0368 | 0
2019-12-06 19:00 | 2378.1976 | 0 | 286.6667 | 8307.9632 | -2091.531 | -2091.531 | 0
2019-12-06 20:00 | 2264.1811 | 0 | 873.3333 | 6216.4323 | -1390.8478 | -1390.8478 | 0
2019-12-06 21:00 | 2085.4675 | 0 | 873.3333 | 4825.5845 | -1212.1342 | -1212.1342 | 0
2019-12-06 22:00 | 1730.1695 | 0 | 873.3333 | 3613.4503 | -856.8362 | -856.8362 | 0
2019-12-06 23:00 | 1400.1033 | 0 | 1666.6667 | 2756.6142 | 266.5634 | 266.5634 | 0
2019-12-07 | 1052.9477 | 0 | 2773.3333 | 3023.1776 | 1720.3857 | 1720.3857 | 0
2019-12-07 01:00 | 925.3325 | 0 | 2773.3333 | 4743.5632 | 1848.0008 | 1848.0008 | 0
2019-12-07 02:00 | 858.1319 | 0 | 2773.3333 | 6591.5641 | 1915.2014 | 1915.2014 | 0
2019-12-07 03:00 | 845.785 | 0 | 2773.3333 | 8506.7655 | 1927.5483 | 1493.2345 | 0
2019-12-07 04:00 | 843.9804 | 0 | 2773.3333 | 10000 | 1929.3529 | 0 | 0
2019-12-07 05:00 | 913.8709 | 0 | 1666.6667 | 10000 | 752.7957 | 0 | 0
2019-12-07 06:00 | 1133.4078 | 0 | 873.3333 | 10000 | -260.0745 | -260.0745 | 0
2019-12-07 07:00 | 1477.7877 | 161.8499 | 873.3333 | 9739.9255 | -442.6046 | -442.6046 | 0
2019-12-07 08:00 | 1420.4066 | 441.6437 | 1666.6667 | 9297.321 | 687.9038 | 687.9038 | 0
2019-12-07 09:00 | 1239.189 | 294.2677 | 1666.6667 | 9985.2248 | 721.7454 | 14.7752 | 0
2019-12-07 10:00 | 1258.8931 | 490.6912 | 1666.6667 | 10000 | 898.4648 | 0 | 0
2019-12-07 11:00 | 1210.6446 | 1618.6135 | 4266.6667 | 10000 | 4674.6356 | 0 | 0
2019-12-07 12:00 | 1183.7164 | 1486.8488 | 873.3333 | 10000 | 1176.4658 | 0 | 0
2019-12-07 13:00 | 1172.877 | 2476.0328 | 1666.6667 | 10000 | 2969.8225 | 0 | 0
2019-12-07 14:00 | 1186.3329 | 457.033 | 2773.3333 | 10000 | 2044.0334 | 0 | 0
2019-12-07 15:00 | 1298.7108 | 1135.1454 | 286.6667 | 10000 | 123.1013 | 0 | 0
2019-12-07 16:00 | 1655.6646 | 0 | 286.6667 | 10000 | -1368.9979 | -1368.9979 | 0
2019-12-07 17:00 | 2270.7347 | 0 | 286.6667 | 8631.0021 | -1984.068 | -1984.068 | 0
2019-12-07 18:00 | 2538.8736 | 0 | 0 | 6646.934 | -2538.8736 | -2538.8736 | 0
2019-12-07 19:00 | 2357.9756 | 0 | 0 | 4108.0605 | -2357.9756 | -2357.9756 | 0
2019-12-07 20:00 | 2245.863 | 0 | 2773.3333 | 1750.0848 | 527.4704 | 527.4704 | 0
2019-12-07 21:00 | 2069.6024 | 0 | 2773.3333 | 2277.5552 | 703.731 | 703.731 | 0
2019-12-07 22:00 | 1709.5202 | 0 | 4266.6667 | 2981.2862 | 2557.1465 | 2557.1465 | 0
2019-12-07 23:00 | 1379.2841 | 0 | 4266.6667 | 5538.4326 | 2887.3825 | 2887.3825 | 0
2019-12-08 | 1027.1854 | 0 | 1666.6667 | 8425.8152 | 639.4812 | 639.4812 | 0
2019-12-08 01:00 | 897.7242 | 0 | 1666.6667 | 9065.2964 | 768.9424 | 768.9424 | 0
2019-12-08 02:00 | 836.479 | 0 | 873.3333 | 9834.2388 | 36.8544 | 36.8544 | 0
2019-12-08 03:00 | 828.0482 | 0 | 1666.6667 | 9871.0932 | 838.6184 | 128.9068 | 0
2019-12-08 04:00 | 826.8804 | 0 | 873.3333 | 10000 | 46.453 | 0 | 0
2019-12-08 05:00 | 897.6825 | 0 | 873.3333 | 10000 | -24.3492 | -24.3492 | 0
2019-12-08 06:00 | 1123.8463 | 0 | 2773.3333 | 9975.6508 | 1649.487 | 24.3492 | 0
2019-12-08 07:00 | 1476.6511 | 1088.5762 | 1666.6667 | 10000 | 1278.5918 | 0 | 0
2019-12-08 08:00 | 1387.4261 | 3394.7218 | 873.3333 | 10000 | 2880.629 | 0 | 0
2019-12-08 09:00 | 1175.6435 | 5156.6563 | 1666.6667 | 10000 | 5647.6795 | 0 | 0
2019-12-08 10:00 | 1174.6305 | 6228.4506 | 873.3333 | 10000 | 5927.1534 | 0 | 0
2019-12-08 11:00 | 1156.1605 | 6621.1549 | 286.6667 | 10000 | 5751.6611 | 0 | 0
2019-12-08 12:00 | 1109.3358 | 6383.3625 | 873.3333 | 10000 | 6147.36 | 0 | 0
2019-12-08 13:00 | 1073.192 | 5475.5387 | 1666.6667 | 10000 | 6069.0133 | 0 | 0
2019-12-08 14:00 | 1085.9145 | 3855.8603 | 873.3333 | 10000 | 3643.2791 | 0 | 0
2019-12-08 15:00 | 1210.3288 | 1616.149 | 1666.6667 | 10000 | 2072.487 | 0 | 0
2019-12-08 16:00 | 1578.4465 | 0 | 873.3333 | 10000 | -705.1132 | -705.1132 | 0
2019-12-08 17:00 | 2204.5493 | 0 | 286.6667 | 9294.8868 | -1917.8827 | -1917.8827 | 0
2019-12-08 18:00 | 2487.6819 | 0 | 873.3333 | 7377.0041 | -1614.3486 | -1614.3486 | 0
2019-12-08 19:00 | 2312.6003 | 0 | 873.3333 | 5762.6555 | -1439.267 | -1439.267 | 0
2019-12-08 20:00 | 2210.9275 | 0 | 286.6667 | 4323.3885 | -1924.2609 | -1924.2609 | 0
2019-12-08 21:00 | 2034.3911 | 0 | 0 | 2399.1276 | -2034.3911 | -2034.3911 | 0
2019-12-08 22:00 | 1681.8323 | 0 | 0 | 364.7365 | -1681.8323 | -364.7365 | -1317.0958
2019-12-08 23:00 | 1353.8458 | 0 | 0 | 0 | -1353.8458 | 0 | -2670.9416
2019-12-09 | 1018.0738 | 0 | 0 | 0 | -1018.0738 | 0 | -3689.0154
2019-12-09 01:00 | 892.8012 | 0 | 0 | 0 | -892.8012 | 0 | -4581.8167
2019-12-09 02:00 | 832.8448 | 0 | 0 | 0 | -832.8448 | 0 | -5414.6615
2019-12-09 03:00 | 826.2831 | 0 | 0 | 0 | -826.2831 | 0 | -6240.9446
2019-12-09 04:00 | 828.9873 | 0 | 0 | 0 | -828.9873 | 0 | -7069.9319
2019-12-09 05:00 | 900.344 | 0 | 0 | 0 | -900.344 | 0 | -7970.2759
2019-12-09 06:00 | 1134.3934 | 0 | 0 | 0 | -1134.3934 | 0 | -9104.6693
2019-12-09 07:00 | 1502.5982 | 1147.4309 | 0 | 0 | -355.1673 | 0 | -9459.8367
2019-12-09 08:00 | 1423.6622 | 3470.0732 | 0 | 0 | 2046.411 | 2046.411 | -7413.4257
2019-12-09 09:00 | 1225.2572 | 5188.5252 | 286.6667 | 2046.411 | 4249.9347 | 4249.9347 | -1117.08
2019-12-09 10:00 | 1228.0436 | 6240.6762 | 0 | 6296.3457 | 5012.6327 | 3703.6543 | 0
2019-12-09 11:00 | 1207.3978 | 6600.2306 | 0 | 10000 | 5392.8328 | 0 | 0
2019-12-09 12:00 | 1159.0978 | 6301.7872 | 0 | 10000 | 5142.6894 | 0 | 0
2019-12-09 13:00 | 1117.9499 | 5351.5284 | 286.6667 | 10000 | 4520.2453 | 0 | 0
2019-12-09 14:00 | 1127.5012 | 3735.622 | 873.3333 | 10000 | 3481.4542 | 0 | 0
2019-12-09 15:00 | 1250.426 | 1522.002 | 286.6667 | 10000 | 558.2427 | 0 | 0
2019-12-09 16:00 | 1611.7463 | 0 | 873.3333 | 10000 | -738.4129 | -738.4129 | 0
2019-12-09 17:00 | 2237.426 | 0 | 1666.6667 | 9261.5871 | -570.7593 | -570.7593 | 0
2019-12-09 18:00 | 2512.5607 | 0 | 1666.6667 | 8690.8277 | -845.894 | -845.894 | 0
2019-12-09 19:00 | 2335.503 | 0 | 1666.6667 | 7844.9337 | -668.8363 | -668.8363 | 0
2019-12-09 20:00 | 2232.5076 | 0 | 873.3333 | 7176.0974 | -1359.1743 | -1359.1743 | 0
2019-12-09 21:00 | 2051.7838 | 0 | 2773.3333 | 5816.9231 | 721.5495 | 721.5495 | 0
2019-12-09 22:00 | 1692.1482 | 0 | 1666.6667 | 6538.4726 | -25.4815 | -25.4815 | 0
2019-12-09 23:00 | 1347.1554 | 0 | 873.3333 | 6512.9911 | -473.822 | -473.822 | 0
2019-12-10 | 990.7381 | 0 | 2773.3333 | 6039.169 | 1782.5952 | 1782.5952 | 0
2019-12-10 01:00 | 860.1529 | 0 | 1666.6667 | 7821.7642 | 806.5138 | 806.5138 | 0
2019-12-10 02:00 | 796.0594 | 0 | 2773.3333 | 8628.2781 | 1977.2739 | 1371.7219 | 0
2019-12-10 03:00 | 789.589 | 0 | 873.3333 | 10000 | 83.7443 | 0 | 0
2019-12-10 04:00 | 787.4443 | 0 | 873.3333 | 10000 | 85.8891 | 0 | 0
2019-12-10 05:00 | 852.1583 | 0 | 873.3333 | 10000 | 21.175 | 0 | 0
2019-12-10 06:00 | 1100.8303 | 0 | 2773.3333 | 10000 | 1672.503 | 0 | 0
2019-12-10 07:00 | 1431.918 | 901.8127 | 4266.6667 | 10000 | 3736.5614 | 0 | 0
2019-12-10 08:00 | 1391.0144 | 3099.4167 | 1666.6667 | 10000 | 3375.069 | 0 | 0
2019-12-10 09:00 | 1229.1396 | 765.7953 | 4266.6667 | 10000 | 3803.3224 | 0 | 0
2019-12-10 10:00 | 1258.1195 | 1410.2162 | 2773.3333 | 10000 | 2925.43 | 0 | 0
2019-12-10 11:00 | 1245.9153 | 1626.5588 | 1666.6667 | 10000 | 2047.3102 | 0 | 0
2019-12-10 12:00 | 1213.1445 | 1292.5724 | 2773.3333 | 10000 | 2852.7613 | 0 | 0
2019-12-10 13:00 | 1178.4417 | 1296.5744 | 6160 | 10000 | 6278.1327 | 0 | 0
2019-12-10 14:00 | 1180.9778 | 1521.8329 | 4266.6667 | 10000 | 4607.5219 | 0 | 0
2019-12-10 15:00 | 1284.9539 | 407.974 | 286.6667 | 10000 | -590.3132 | -590.3132 | 0
2019-12-10 16:00 | 1634.5524 | 0 | 873.3333 | 9409.6868 | -761.2191 | -761.2191 | 0
2019-12-10 17:00 | 2241.5991 | 0 | 873.3333 | 8648.4677 | -1368.2657 | -1368.2657 | 0
2019-12-10 18:00 | 2510.1238 | 0 | 2773.3333 | 7280.202 | 263.2095 | 263.2095 | 0
2019-12-10 19:00 | 2329.8649 | 0 | 1666.6667 | 7543.4115 | -663.1982 | -663.1982 | 0
2019-12-10 20:00 | 2217.1776 | 0 | 873.3333 | 6880.2132 | -1343.8443 | -1343.8443 | 0
2019-12-10 21:00 | 2032.3435 | 0 | 2773.3333 | 5536.369 | 740.9898 | 740.9898 | 0
2019-12-10 22:00 | 1668.3946 | 0 | 1666.6667 | 6277.3588 | -1.7279 | -1.7279 | 0
2019-12-10 23:00 | 1322.4068 | 0 | 873.3333 | 6275.6309 | -449.0735 | -449.0735 | 0
2019-12-11 | 953.5425 | 0 | 2773.3333 | 5826.5574 | 1819.7908 | 1819.7908 | 0
2019-12-11 01:00 | 824.6764 | 0 | 1666.6667 | 7646.3482 | 841.9903 | 841.9903 | 0
2019-12-11 02:00 | 761.9579 | 0 | 873.3333 | 8488.3385 | 111.3754 | 111.3754 | 0
2019-12-11 03:00 | 750.1047 | 0 | 873.3333 | 8599.7139 | 123.2286 | 123.2286 | 0
2019-12-11 04:00 | 746.7527 | 0 | 873.3333 | 8722.9426 | 126.5806 | 126.5806 | 0
2019-12-11 05:00 | 813.6381 | 0 | 873.3333 | 8849.5232 | 59.6952 | 59.6952 | 0
2019-12-11 06:00 | 1035.1127 | 0 | 4266.6667 | 8909.2183 | 3231.554 | 1090.7817 | 0
2019-12-11 07:00 | 1380.814 | 52.9909 | 2773.3333 | 10000 | 1445.5102 | 0 | 0
2019-12-11 08:00 | 1322.0818 | 408.6111 | 2773.3333 | 10000 | 1859.8626 | 0 | 0
2019-12-11 09:00 | 1146.698 | 1109.0105 | 2773.3333 | 10000 | 2735.6459 | 0 | 0
2019-12-11 10:00 | 1163.9654 | 2008.6164 | 1666.6667 | 10000 | 2511.3178 | 0 | 0
2019-12-11 11:00 | 1187.0044 | 707.1327 | 6160 | 10000 | 5680.1283 | 0 | 0
2019-12-11 12:00 | 1144.4172 | 597.755 | 4266.6667 | 10000 | 3720.0045 | 0 | 0
2019-12-11 13:00 | 1117.178 | 934.6188 | 1666.6667 | 10000 | 1484.1074 | 0 | 0
2019-12-11 14:00 | 1121.548 | 50.7426 | 873.3333 | 10000 | -197.4721 | -197.4721 | 0
2019-12-11 15:00 | 1220.498 | 0 | 286.6667 | 9802.5279 | -933.8313 | -933.8313 | 0
2019-12-11 16:00 | 1571.6936 | 0 | 286.6667 | 8868.6966 | -1285.0269 | -1285.0269 | 0
2019-12-11 17:00 | 2161.7862 | 0 | 286.6667 | 7583.6697 | -1875.1196 | -1875.1196 | 0
2019-12-11 18:00 | 2441.0782 | 0 | 0 | 5708.5501 | -2441.0782 | -2441.0782 | 0
2019-12-11 19:00 | 2260.148 | 0 | 0 | 3267.4719 | -2260.148 | -2260.148 | 0
2019-12-11 20:00 | 2147.6541 | 0 | 0 | 1007.3239 | -2147.6541 | -1007.3239 | -1140.3302
2019-12-11 21:00 | 1960.2323 | 0 | 0 | 0 | -1960.2323 | 0 | -3100.5625
2019-12-11 22:00 | 1605.9326 | 0 | 0 | 0 | -1605.9326 | 0 | -4706.4952
2019-12-11 23:00 | 1288.9767 | 0 | 0 | 0 | -1288.9767 | 0 | -5995.4719
2019-12-12 | 964.7843 | 0 | 0 | 0 | -964.7843 | 0 | -6960.2561
2019-12-12 01:00 | 845.7224 | 0 | 0 | 0 | -845.7224 | 0 | -7805.9785
2019-12-12 02:00 | 774.384 | 0 | 0 | 0 | -774.384 | 0 | -8580.3625
2019-12-12 03:00 | 761.7593 | 0 | 0 | 0 | -761.7593 | 0 | -9342.1218
2019-12-12 04:00 | 763.4402 | 0 | 286.6667 | 0 | -476.7735 | 0 | -9818.8953
2019-12-12 05:00 | 854.1756 | 0 | 286.6667 | 0 | -567.5089 | 0 | -10386.4042
2019-12-12 06:00 | 1084.719 | 0 | 4266.6667 | 0 | 3181.9477 | 3181.9477 | -7204.4566
2019-12-12 07:00 | 1410.8597 | 849.1117 | 4266.6667 | 3181.9477 | 3704.9187 | 3704.9187 | -317.5902
2019-12-12 08:00 | 1335.0807 | 3154.266 | 2773.3333 | 6886.8664 | 4592.5187 | 3113.1336 | 0
2019-12-12 09:00 | 1134.8051 | 5004.7195 | 4266.6667 | 10000 | 8136.581 | 0 | 0
2019-12-12 10:00 | 1127.4304 | 6180.2978 | 4266.6667 | 10000 | 9319.5341 | 0 | 0
2019-12-12 11:00 | 1112.7902 | 6611.6432 | 873.3333 | 10000 | 6372.1864 | 0 | 0
2019-12-12 12:00 | 1084.0921 | 6366.9037 | 2773.3333 | 10000 | 8056.1449 | 0 | 0
2019-12-12 13:00 | 1055.8402 | 5299.9532 | 4266.6667 | 10000 | 8510.7798 | 0 | 0
2019-12-12 14:00 | 1073.6514 | 3747.4544 | 2773.3333 | 10000 | 5447.1364 | 0 | 0
2019-12-12 15:00 | 1190.67 | 1573.5243 | 1666.6667 | 10000 | 2049.521 | 0 | 0
2019-12-12 16:00 | 1565.7945 | 0 | 1666.6667 | 10000 | 100.8722 | 0 | 0
2019-12-12 17:00 | 2182.9018 | 0 | 0 | 10000 | -2182.9018 | -2182.9018 | 0
2019-12-12 18:00 | 2470.4548 | 0 | 1666.6667 | 7817.0982 | -803.7881 | -803.7881 | 0
2019-12-12 19:00 | 2298.9305 | 0 | 2773.3333 | 7013.3101 | 474.4028 | 474.4028 | 0
2019-12-12 20:00 | 2195.7546 | 0 | 1666.6667 | 7487.7129 | -529.0879 | -529.0879 | 0
2019-12-12 21:00 | 2021.1927 | 0 | 1666.6667 | 6958.625 | -354.5261 | -354.5261 | 0
2019-12-12 22:00 | 1670.5913 | 0 | 1666.6667 | 6604.0989 | -3.9246 | -3.9246 | 0
2019-12-12 23:00 | 1341.6919 | 0 | 1666.6667 | 6600.1743 | 324.9748 | 324.9748 | 0
2019-12-13 | 1000.2329 | 0 | 4266.6667 | 6925.1491 | 3266.4338 | 3074.8509 | 0
2019-12-13 01:00 | 870.5787 | 0 | 4266.6667 | 10000 | 3396.088 | 0 | 0
2019-12-13 02:00 | 813.1121 | 0 | 6160 | 10000 | 5346.8879 | 0 | 0
2019-12-13 03:00 | 804.2921 | 0 | 9060 | 10000 | 8255.7079 | 0 | 0
2019-12-13 04:00 | 810.3987 | 0 | 9060 | 10000 | 8249.6013 | 0 | 0
2019-12-13 05:00 | 879.5417 | 0 | 6160 | 10000 | 5280.4583 | 0 | 0
2019-12-13 06:00 | 1106.4323 | 0 | 9573.3333 | 10000 | 8466.9011 | 0 | 0
2019-12-13 07:00 | 1465.2171 | 1112.1524 | 9573.3333 | 10000 | 9220.2686 | 0 | 0
2019-12-13 08:00 | 1389.0515 | 3498.4886 | 9060 | 10000 | 11169.4371 | 0 | 0
2019-12-13 09:00 | 1191.3686 | 5370.807 | 6160 | 10000 | 10339.4385 | 0 | 0
2019-12-13 10:00 | 1191.5149 | 6486.1495 | 2773.3333 | 10000 | 8067.968 | 0 | 0
2019-12-13 11:00 | 1173.9768 | 6884.7349 | 9060 | 10000 | 14770.7581 | 0 | 0
2019-12-13 12:00 | 1131.1965 | 6450.2649 | 9573.3333 | 10000 | 14892.4018 | 0 | 0
2019-12-13 13:00 | 1095.1477 | 5568.6852 | 9873.3333 | 10000 | 14346.8708 | 0 | 0
2019-12-13 14:00 | 1117.4953 | 3962.1709 | 9060 | 10000 | 11904.6756 | 0 | 0
2019-12-13 15:00 | 1247.8813 | 1725.7705 | 9573.3333 | 10000 | 10051.2225 | 0 | 0
2019-12-13 16:00 | 1612.1527 | 0 | 9573.3333 | 10000 | 7961.1807 | 0 | 0
2019-12-13 17:00 | 2247.2692 | 0 | 9060 | 10000 | 6812.7308 | 0 | 0
2019-12-13 18:00 | 2526.2954 | 0 | 9060 | 10000 | 6533.7046 | 0 | 0
2019-12-13 19:00 | 2352.279 | 0 | 9060 | 10000 | 6707.721 | 0 | 0
2019-12-13 20:00 | 2250.0105 | 0 | 9060 | 10000 | 6809.9895 | 0 | 0
2019-12-13 21:00 | 2076.6235 | 0 | 9060 | 10000 | 6983.3765 | 0 | 0
2019-12-13 22:00 | 1728.9749 | 0 | 9060 | 10000 | 7331.0251 | 0 | 0
2019-12-13 23:00 | 1404.0982 | 0 | 7873.3333 | 10000 | 6469.2352 | 0 | 0
2019-12-14 | 1061.9358 | 0 | 7873.3333 | 10000 | 6811.3976 | 0 | 0
2019-12-14 01:00 | 935.7787 | 0 | 7873.3333 | 10000 | 6937.5546 | 0 | 0
2019-12-14 02:00 | 880.6149 | 0 | 4266.6667 | 10000 | 3386.0518 | 0 | 0
2019-12-14 03:00 | 877.7457 | 0 | 4266.6667 | 10000 | 3388.921 | 0 | 0
2019-12-14 04:00 | 877.8652 | 0 | 2773.3333 | 10000 | 1895.4681 | 0 | 0
2019-12-14 05:00 | 945.7087 | 0 | 873.3333 | 10000 | -72.3753 | -72.3753 | 0
2019-12-14 06:00 | 1170.9851 | 0 | 286.6667 | 9927.6247 | -884.3184 | -884.3184 | 0
2019-12-14 07:00 | 1528.7585 | 47.9515 | 873.3333 | 9043.3063 | -607.4736 | -607.4736 | 0
2019-12-14 08:00 | 1465.3224 | 454.963 | 286.6667 | 8435.8327 | -723.6927 | -723.6927 | 0
2019-12-14 09:00 | 1277.1783 | 806.3788 | 873.3333 | 7712.1399 | 402.5338 | 402.5338 | 0
2019-12-14 10:00 | 1303.7382 | 1602.7906 | 1666.6667 | 8114.6738 | 1965.7192 | 1885.3262 | 0
2019-12-14 11:00 | 1274.7716 | 558.2491 | 4266.6667 | 10000 | 3550.1442 | 0 | 0
2019-12-14 12:00 | 1235.3963 | 604.4871 | 2773.3333 | 10000 | 2142.4242 | 0 | 0
2019-12-14 13:00 | 1201.4072 | 735.1249 | 6160 | 10000 | 5693.7177 | 0 | 0
2019-12-14 14:00 | 1210.7538 | 284.7101 | 4266.6667 | 10000 | 3340.623 | 0 | 0
2019-12-14 15:00 | 1320.4291 | 45.9781 | 4266.6667 | 10000 | 2992.2157 | 0 | 0
2019-12-14 16:00 | 1678.688 | 0 | 4266.6667 | 10000 | 2587.9786 | 0 | 0
2019-12-14 17:00 | 2247.0533 | 0 | 4266.6667 | 10000 | 2019.6134 | 0 | 0
2019-12-14 18:00 | 2552.6327 | 0 | 7873.3333 | 10000 | 5320.7007 | 0 | 0
2019-12-14 19:00 | 2370.7386 | 0 | 7873.3333 | 10000 | 5502.5948 | 0 | 0
2019-12-14 20:00 | 2268.7612 | 0 | 4266.6667 | 10000 | 1997.9055 | 0 | 0
2019-12-14 21:00 | 2066.0872 | 0 | 4266.6667 | 10000 | 2200.5794 | 0 | 0
2019-12-14 22:00 | 1699.2141 | 0 | 4266.6667 | 10000 | 2567.4526 | 0 | 0
2019-12-14 23:00 | 1370.7945 | 0 | 6160 | 10000 | 4789.2055 | 0 | 0
2019-12-15 | 998.8117 | 0 | 2773.3333 | 10000 | 1774.5216 | 0 | 0
2019-12-15 01:00 | 854.8344 | 0 | 1666.6667 | 10000 | 811.8322 | 0 | 0
2019-12-15 02:00 | 783.0461 | 0 | 286.6667 | 10000 | -496.3795 | -496.3795 | 0
2019-12-15 03:00 | 769.7001 | 0 | 1666.6667 | 9503.6205 | 896.9666 | 496.3795 | 0
2019-12-15 04:00 | 768.9545 | 0 | 873.3333 | 10000 | 104.3789 | 0 | 0
2019-12-15 05:00 | 837.7035 | 0 | 873.3333 | 10000 | 35.6299 | 0 | 0
2019-12-15 06:00 | 1067.7384 | 0 | 286.6667 | 10000 | -781.0718 | -781.0718 | 0
2019-12-15 07:00 | 1412.5422 | 495.7535 | 286.6667 | 9218.9282 | -630.122 | -630.122 | 0
2019-12-15 08:00 | 1373.8425 | 2815.0528 | 0 | 8588.8063 | 1441.2103 | 1411.1937 | 0
2019-12-15 09:00 | 1213.6673 | 645.4869 | 0 | 10000 | -568.1804 | -568.1804 | 0
2019-12-15 10:00 | 1206.269 | 304.4935 | 0 | 9431.8196 | -901.7755 | -901.7755 | 0
2019-12-15 11:00 | 1207.7363 | 3151.3047 | 0 | 8530.0442 | 1943.5684 | 1469.9558 | 0
2019-12-15 12:00 | 1187.1573 | 1765.7675 | 0 | 10000 | 578.6102 | 0 | 0
2019-12-15 13:00 | 1162.7722 | 4549.0147 | 0 | 10000 | 3386.2425 | 0 | 0
2019-12-15 14:00 | 1181.6648 | 3868.2504 | 286.6667 | 10000 | 2973.2523 | 0 | 0
2019-12-15 15:00 | 1307.6983 | 1584.7701 | 0 | 10000 | 277.0719 | 0 | 0
2019-12-15 16:00 | 1649.0421 | 0 | 0 | 10000 | -1649.0421 | -1649.0421 | 0
2019-12-15 17:00 | 2267.4822 | 0 | 0 | 8350.9579 | -2267.4822 | -2267.4822 | 0
2019-12-15 18:00 | 2554.3981 | 0 | 0 | 6083.4757 | -2554.3981 | -2554.3981 | 0
2019-12-15 19:00 | 2368.9657 | 0 | 286.6667 | 3529.0776 | -2082.299 | -2082.299 | 0
2019-12-15 20:00 | 2258.2906 | 0 | 873.3333 | 1446.7786 | -1384.9572 | -1384.9572 | 0
2019-12-15 21:00 | 2078.1974 | 0 | 1666.6667 | 61.8213 | -411.5308 | -61.8213 | -349.7094
2019-12-15 22:00 | 1712.5047 | 0 | 286.6667 | 0 | -1425.8381 | 0 | -1775.5475
2019-12-15 23:00 | 1380.0597 | 0 | 2773.3333 | 0 | 1393.2736 | 1393.2736 | -382.2739
2019-12-16 | 1029.0532 | 0 | 1666.6667 | 1393.2736 | 637.6135 | 637.6135 | 0
2019-12-16 01:00 | 891.6313 | 0 | 1666.6667 | 2030.887 | 775.0354 | 775.0354 | 0
2019-12-16 02:00 | 828.2337 | 0 | 2773.3333 | 2805.9224 | 1945.0997 | 1945.0997 | 0
2019-12-16 03:00 | 817.0776 | 0 | 2773.3333 | 4751.0221 | 1956.2557 | 1956.2557 | 0
2019-12-16 04:00 | 816.6155 | 0 | 2773.3333 | 6707.2778 | 1956.7179 | 1956.7179 | 0
2019-12-16 05:00 | 885.7595 | 0 | 2773.3333 | 8663.9957 | 1887.5738 | 1336.0043 | 0
2019-12-16 06:00 | 1118.9561 | 0 | 873.3333 | 10000 | -245.6228 | -245.6228 | 0
2019-12-16 07:00 | 1472.5184 | 229.3595 | 873.3333 | 9754.3772 | -369.8256 | -369.8256 | 0
2019-12-16 08:00 | 1414.6992 | 2406.9937 | 4266.6667 | 9384.5516 | 5258.9612 | 615.4484 | 0
2019-12-16 09:00 | 1225.6507 | 5041.8346 | 2773.3333 | 10000 | 6589.5172 | 0 | 0
2019-12-16 10:00 | 1226.3526 | 6104.591 | 6160 | 10000 | 11038.2384 | 0 | 0
2019-12-16 11:00 | 1197.0276 | 6504.8255 | 6160 | 10000 | 11467.7979 | 0 | 0
2019-12-16 12:00 | 1143.3478 | 6214.7506 | 4266.6667 | 10000 | 9338.0696 | 0 | 0
2019-12-16 13:00 | 1097.1849 | 5272.3302 | 4266.6667 | 10000 | 8441.812 | 0 | 0
2019-12-16 14:00 | 1100.6068 | 3697.9434 | 4266.6667 | 10000 | 6864.0033 | 0 | 0
2019-12-16 15:00 | 1220.4153 | 1565.4317 | 1666.6667 | 10000 | 2011.6831 | 0 | 0
2019-12-16 16:00 | 1585.6996 | 0 | 2773.3333 | 10000 | 1187.6337 | 0 | 0
2019-12-16 17:00 | 2211.7058 | 0 | 4266.6667 | 10000 | 2054.9609 | 0 | 0
2019-12-16 18:00 | 2492.4729 | 0 | 6160 | 10000 | 3667.5271 | 0 | 0
2019-12-16 19:00 | 2318.911 | 0 | 4266.6667 | 10000 | 1947.7557 | 0 | 0
2019-12-16 20:00 | 2220.2511 | 0 | 286.6667 | 10000 | -1933.5844 | -1933.5844 | 0
2019-12-16 21:00 | 2041.8341 | 0 | 1666.6667 | 8066.4156 | -375.1674 | -375.1674 | 0
2019-12-16 22:00 | 1679.6501 | 0 | 873.3333 | 7691.2482 | -806.3167 | -806.3167 | 0
2019-12-16 23:00 | 1337.856 | 0 | 1666.6667 | 6884.9315 | 328.8107 | 328.8107 | 0
2019-12-17 | 989.3752 | 0 | 873.3333 | 7213.7421 | -116.0419 | -116.0419 | 0
2019-12-17 01:00 | 855.2736 | 0 | 873.3333 | 7097.7002 | 18.0597 | 18.0597 | 0
2019-12-17 02:00 | 791.358 | 0 | 2773.3333 | 7115.7599 | 1981.9753 | 1981.9753 | 0
2019-12-17 03:00 | 774.2303 | 0 | 1666.6667 | 9097.7352 | 892.4364 | 892.4364 | 0
2019-12-17 04:00 | 769.1935 | 0 | 1666.6667 | 9990.1716 | 897.4731 | 9.8284 | 0
2019-12-17 05:00 | 835.4622 | 0 | 2773.3333 | 10000 | 1937.8711 | 0 | 0
2019-12-17 06:00 | 1077.4004 | 0 | 2773.3333 | 10000 | 1695.9329 | 0 | 0
2019-12-17 07:00 | 1424.4227 | 588.0536 | 1666.6667 | 10000 | 830.2976 | 0 | 0
2019-12-17 08:00 | 1359.6552 | 1435.7324 | 1666.6667 | 10000 | 1742.7439 | 0 | 0
2019-12-17 09:00 | 1184.6372 | 2228.8989 | 2773.3333 | 10000 | 3817.5951 | 0 | 0
2019-12-17 10:00 | 1196.9011 | 3021.5238 | 2773.3333 | 10000 | 4597.9561 | 0 | 0
2019-12-17 11:00 | 1188.1316 | 1378.0542 | 1666.6667 | 10000 | 1856.5893 | 0 | 0
2019-12-17 12:00 | 1159.8185 | 1501.3308 | 873.3333 | 10000 | 1214.8456 | 0 | 0
2019-12-17 13:00 | 1121.0561 | 1214.9267 | 873.3333 | 10000 | 967.204 | 0 | 0
2019-12-17 14:00 | 1126.7303 | 469.7819 | 286.6667 | 10000 | -370.2818 | -370.2818 | 0
2019-12-17 15:00 | 1238.8576 | 101.3656 | 873.3333 | 9629.7182 | -264.1587 | -264.1587 | 0
2019-12-17 16:00 | 1591.9406 | 0 | 873.3333 | 9365.5595 | -718.6073 | -718.6073 | 0
2019-12-17 17:00 | 2162.7395 | 0 | 286.6667 | 8646.9523 | -1876.0728 | -1876.0728 | 0
2019-12-17 18:00 | 2478.26 | 0 | 0 | 6770.8794 | -2478.26 | -2478.26 | 0
2019-12-17 19:00 | 2285.9781 | 0 | 0 | 4292.6194 | -2285.9781 | -2285.9781 | 0
2019-12-17 20:00 | 2163.4932 | 0 | 0 | 2006.6414 | -2163.4932 | -2006.6414 | -156.8519
2019-12-17 21:00 | 1981.0078 | 0 | 286.6667 | 0 | -1694.3412 | 0 | -1851.193
2019-12-17 22:00 | 1610.4404 | 0 | 286.6667 | 0 | -1323.7738 | 0 | -3174.9668
2019-12-17 23:00 | 1288.6055 | 0 | 0 | 0 | -1288.6055 | 0 | -4463.5723
2019-12-18 | 935.6818 | 0 | 0 | 0 | -935.6818 | 0 | -5399.2541
2019-12-18 01:00 | 817.1551 | 0 | 0 | 0 | -817.1551 | 0 | -6216.4093
2019-12-18 02:00 | 786.4788 | 0 | 0 | 0 | -786.4788 | 0 | -7002.8881
2019-12-18 03:00 | 767.8402 | 0 | 0 | 0 | -767.8402 | 0 | -7770.7283
2019-12-18 04:00 | 777.8814 | 0 | 0 | 0 | -777.8814 | 0 | -8548.6097
2019-12-18 05:00 | 856.7806 | 0 | 0 | 0 | -856.7806 | 0 | -9405.3903
2019-12-18 06:00 | 1087.3519 | 0 | 0 | 0 | -1087.3519 | 0 | -10492.7423
2019-12-18 07:00 | 1434.1083 | 117.7508 | 0 | 0 | -1316.3575 | 0 | -11809.0998
2019-12-18 08:00 | 1368.3337 | 2869.6605 | 0 | 0 | 1501.3268 | 1501.3268 | -10307.773
2019-12-18 09:00 | 1157.9793 | 4742.8679 | 0 | 1501.3268 | 3584.8887 | 3584.8887 | -5221.5575
2019-12-18 10:00 | 1156.6967 | 5894.9011 | 0 | 5086.2155 | 4738.2045 | 4738.2045 | 0
2019-12-18 11:00 | 1130.8803 | 6297.7726 | 0 | 9824.42 | 5166.8923 | 175.58 | 0
2019-12-18 12:00 | 1101.2517 | 6009.3388 | 0 | 10000 | 4908.0871 | 0 | 0
2019-12-18 13:00 | 1072.4011 | 5242.0565 | 0 | 10000 | 4169.6554 | 0 | 0
2019-12-18 14:00 | 1095.343 | 3609.9432 | 0 | 10000 | 2514.6001 | 0 | 0
2019-12-18 15:00 | 1214.4182 | 1419.6692 | 0 | 10000 | 205.2511 | 0 | 0
2019-12-18 16:00 | 1579.2256 | 0 | 0 | 10000 | -1579.2256 | -1579.2256 | 0
2019-12-18 17:00 | 2193.8987 | 0 | 0 | 8420.7744 | -2193.8987 | -2193.8987 | 0
2019-12-18 18:00 | 2481.8304 | 0 | 0 | 6226.8757 | -2481.8304 | -2481.8304 | 0
2019-12-18 19:00 | 2300.4355 | 0 | 0 | 3745.0453 | -2300.4355 | -2300.4355 | 0
2019-12-18 20:00 | 2201.3263 | 0 | 286.6667 | 1444.6098 | -1914.6596 | -1444.6098 | -470.0498
2019-12-18 21:00 | 2021.4606 | 0 | 0 | 0 | -2021.4606 | 0 | -2491.5104
2019-12-18 22:00 | 1665.0456 | 0 | 0 | 0 | -1665.0456 | 0 | -4156.556
2019-12-18 23:00 | 1337.8921 | 0 | 286.6667 | 0 | -1051.2255 | 0 | -5207.7815
2019-12-19 | 996.7912 | 0 | 286.6667 | 0 | -710.1245 | 0 | -5917.906
2019-12-19 01:00 | 867.8189 | 0 | 0 | 0 | -867.8189 | 0 | -6785.7249
2019-12-19 02:00 | 811.4729 | 0 | 0 | 0 | -811.4729 | 0 | -7597.1978
2019-12-19 03:00 | 804.4593 | 0 | 873.3333 | 0 | 68.8741 | 68.8741 | -7528.3237
2019-12-19 04:00 | 803.5443 | 0 | 873.3333 | 68.8741 | 69.789 | 69.789 | -7389.6607
2019-12-19 05:00 | 867.6762 | 0 | 286.6667 | 138.6631 | -581.0095 | -138.6631 | -7832.0071
2019-12-19 06:00 | 1095.7278 | 0 | 0 | 0 | -1095.7278 | 0 | -8927.7349
2019-12-19 07:00 | 1451.2845 | 910.7034 | 0 | 0 | -540.5811 | 0 | -9468.316
2019-12-19 08:00 | 1363.6723 | 3187.5746 | 873.3333 | 0 | 2697.2356 | 2697.2356 | -6771.0804
2019-12-19 09:00 | 1158.5606 | 4993.7531 | 6160 | 2697.2356 | 9995.1925 | 7302.7644 | 0
2019-12-19 10:00 | 1154.1023 | 6034.3133 | 4266.6667 | 10000 | 9146.8777 | 0 | 0
2019-12-19 11:00 | 1120.5991 | 6426.6784 | 4266.6667 | 10000 | 9572.746 | 0 | 0
2019-12-19 12:00 | 1077.3698 | 6159.0343 | 2773.3333 | 10000 | 7854.9978 | 0 | 0
2019-12-19 13:00 | 1041.9041 | 5326.3227 | 2773.3333 | 10000 | 7057.752 | 0 | 0
2019-12-19 14:00 | 1056.378 | 3798.6202 | 873.3333 | 10000 | 3615.5755 | 0 | 0
2019-12-19 15:00 | 1179.8654 | 1660.2101 | 4266.6667 | 10000 | 4747.0114 | 0 | 0
2019-12-19 16:00 | 1550.5334 | 0 | 2773.3333 | 10000 | 1222.8 | 0 | 0
2019-12-19 17:00 | 2170.393 | 0 | 873.3333 | 10000 | -1297.0596 | -1297.0596 | 0
2019-12-19 18:00 | 2454.3121 | 0 | 4266.6667 | 8702.9404 | 1812.3546 | 1297.0596 | 0
2019-12-19 19:00 | 2282.934 | 0 | 7873.3333 | 10000 | 5590.3993 | 0 | 0
2019-12-19 20:00 | 2181.799 | 0 | 6160 | 10000 | 3978.201 | 0 | 0
2019-12-19 21:00 | 2004.8843 | 0 | 6160 | 10000 | 4155.1157 | 0 | 0
2019-12-19 22:00 | 1654.6177 | 0 | 4266.6667 | 10000 | 2612.0489 | 0 | 0
2019-12-19 23:00 | 1327.6726 | 0 | 4266.6667 | 10000 | 2938.9941 | 0 | 0
2019-12-20 | 983.6759 | 0 | 2773.3333 | 10000 | 1789.6574 | 0 | 0
2019-12-20 01:00 | 855.18 | 0 | 6160 | 10000 | 5304.82 | 0 | 0
2019-12-20 02:00 | 797.7447 | 0 | 4266.6667 | 10000 | 3468.922 | 0 | 0
2019-12-20 03:00 | 790.504 | 0 | 6160 | 10000 | 5369.496 | 0 | 0
2019-12-20 04:00 | 789.7223 | 0 | 4266.6667 | 10000 | 3476.9444 | 0 | 0
2019-12-20 05:00 | 859.8243 | 0 | 1666.6667 | 10000 | 806.8423 | 0 | 0
2019-12-20 06:00 | 1106.0162 | 0 | 2773.3333 | 10000 | 1667.3171 | 0 | 0
2019-12-20 07:00 | 1444.9925 | 77.1144 | 2773.3333 | 10000 | 1405.4552 | 0 | 0
2019-12-20 08:00 | 1363.4227 | 1269.5551 | 7873.3333 | 10000 | 7779.4657 | 0 | 0
2019-12-20 09:00 | 1156.0676 | 4582.2831 | 9873.3333 | 10000 | 13299.5488 | 0 | 0
2019-12-20 10:00 | 1154.3904 | 5634.0041 | 9573.3333 | 10000 | 14052.947 | 0 | 0
2019-12-20 11:00 | 1123.1133 | 4467.8489 | 9573.3333 | 10000 | 12918.069 | 0 | 0
2019-12-20 12:00 | 1098.1863 | 3269.5914 | 4266.6667 | 10000 | 6438.0718 | 0 | 0
2019-12-20 13:00 | 1078.9965 | 2464.0486 | 6160 | 10000 | 7545.0521 | 0 | 0
2019-12-20 14:00 | 1104.1817 | 1589.7002 | 1666.6667 | 10000 | 2152.1852 | 0 | 0
2019-12-20 15:00 | 1222.3077 | 466.6849 | 6160 | 10000 | 5404.3773 | 0 | 0
2019-12-20 16:00 | 1584.495 | 0 | 4266.6667 | 10000 | 2682.1716 | 0 | 0
2019-12-20 17:00 | 2203.5515 | 0 | 2773.3333 | 10000 | 569.7818 | 0 | 0
2019-12-20 18:00 | 2486.3731 | 0 | 873.3333 | 10000 | -1613.0398 | -1613.0398 | 0
2019-12-20 19:00 | 2314.6337 | 0 | 873.3333 | 8386.9602 | -1441.3004 | -1441.3004 | 0
2019-12-20 20:00 | 2210.9543 | 0 | 1666.6667 | 6945.6598 | -544.2877 | -544.2877 | 0
2019-12-20 21:00 | 2033.3799 | 0 | 873.3333 | 6401.3721 | -1160.0466 | -1160.0466 | 0
2019-12-20 22:00 | 1686.2104 | 0 | 873.3333 | 5241.3255 | -812.8771 | -812.8771 | 0
2019-12-20 23:00 | 1359.855 | 0 | 2773.3333 | 4428.4485 | 1413.4783 | 1413.4783 | 0
2019-12-21 | 1016.2806 | 0 | 873.3333 | 5841.9268 | -142.9472 | -142.9472 | 0
2019-12-21 01:00 | 891.996 | 0 | 873.3333 | 5698.9795 | -18.6627 | -18.6627 | 0
2019-12-21 02:00 | 836.6301 | 0 | 1666.6667 | 5680.3169 | 830.0365 | 830.0365 | 0
2019-12-21 03:00 | 831.1679 | 0 | 873.3333 | 6510.3534 | 42.1654 | 42.1654 | 0
2019-12-21 04:00 | 844.7086 | 0 | 1666.6667 | 6552.5188 | 821.9581 | 821.9581 | 0
2019-12-21 05:00 | 914.5983 | 0 | 873.3333 | 7374.4769 | -41.265 | -41.265 | 0
2019-12-21 06:00 | 1139.4196 | 0 | 6160 | 7333.2119 | 5020.5804 | 2666.7881 | 0
2019-12-21 07:00 | 1496.2477 | 825.7644 | 6160 | 10000 | 5489.5167 | 0 | 0
2019-12-21 08:00 | 1419.4602 | 3107.0527 | 2773.3333 | 10000 | 4460.9259 | 0 | 0
2019-12-21 09:00 | 1201.3346 | 3293.738 | 2773.3333 | 10000 | 4865.7367 | 0 | 0
2019-12-21 10:00 | 1204.2423 | 5860.5656 | 2773.3333 | 10000 | 7429.6567 | 0 | 0
2019-12-21 11:00 | 1180.7509 | 6202.7987 | 873.3333 | 10000 | 5895.3811 | 0 | 0
2019-12-21 12:00 | 1139.9982 | 3152.6974 | 2773.3333 | 10000 | 4786.0325 | 0 | 0
2019-12-21 13:00 | 1124.2344 | 3871.8694 | 873.3333 | 10000 | 3620.9684 | 0 | 0
2019-12-21 14:00 | 1143.3821 | 1563.3272 | 286.6667 | 10000 | 706.6118 | 0 | 0
2019-12-21 15:00 | 1253.3657 | 1325.0771 | 286.6667 | 10000 | 358.3781 | 0 | 0
2019-12-21 16:00 | 1613.8787 | 0 | 286.6667 | 10000 | -1327.212 | -1327.212 | 0
2019-12-21 17:00 | 2226.449 | 0 | 0 | 8672.788 | -2226.449 | -2226.449 | 0
2019-12-21 18:00 | 2504.6169 | 0 | 0 | 6446.339 | -2504.6169 | -2504.6169 | 0
2019-12-21 19:00 | 2322.0645 | 0 | 0 | 3941.7221 | -2322.0645 | -2322.0645 | 0
2019-12-21 20:00 | 2207.9483 | 0 | 286.6667 | 1619.6576 | -1921.2816 | -1619.6576 | -301.624
2019-12-21 21:00 | 2024.5966 | 0 | 286.6667 | 0 | -1737.9299 | 0 | -2039.5539
2019-12-21 22:00 | 1671.0368 | 0 | 286.6667 | 0 | -1384.3701 | 0 | -3423.924
2019-12-21 23:00 | 1337.6187 | 0 | 0 | 0 | -1337.6187 | 0 | -4761.5427
2019-12-22 | 959.297 | 0 | 286.6667 | 0 | -672.6304 | 0 | -5434.173
2019-12-22 01:00 | 844.1603 | 0 | 286.6667 | 0 | -557.4937 | 0 | -5991.6667
2019-12-22 02:00 | 789.1871 | 0 | 286.6667 | 0 | -502.5204 | 0 | -6494.1871
2019-12-22 03:00 | 783.5253 | 0 | 286.6667 | 0 | -496.8586 | 0 | -6991.0457
2019-12-22 04:00 | 772.396 | 0 | 286.6667 | 0 | -485.7294 | 0 | -7476.7751
2019-12-22 05:00 | 831.8461 | 0 | 286.6667 | 0 | -545.1794 | 0 | -8021.9545
2019-12-22 06:00 | 1024.5726 | 0 | 286.6667 | 0 | -737.906 | 0 | -8759.8605
2019-12-22 07:00 | 1305.9188 | 184.0046 | 286.6667 | 0 | -835.2476 | 0 | -9595.1081
2019-12-22 08:00 | 1171.7677 | 2792.2115 | 0 | 0 | 1620.4438 | 1620.4438 | -7974.6643
2019-12-22 09:00 | 890.2383 | 4520.7236 | 0 | 1620.4438 | 3630.4853 | 3630.4853 | -2723.7352
2019-12-22 10:00 | 854.9071 | 3603.1605 | 0 | 5250.9291 | 2748.2533 | 2748.2533 | 0
2019-12-22 11:00 | 839.3005 | 3715.6431 | 286.6667 | 7999.1824 | 3163.0093 | 2000.8176 | 0
2019-12-22 12:00 | 833.3249 | 3451.2983 | 873.3333 | 10000 | 3491.3068 | 0 | 0
2019-12-22 13:00 | 809.5926 | 3110.7695 | 873.3333 | 10000 | 3174.5103 | 0 | 0
2019-12-22 14:00 | 846.9749 | 1044.4185 | 2773.3333 | 10000 | 2970.7769 | 0 | 0
2019-12-22 15:00 | 973.0514 | 283.1806 | 2773.3333 | 10000 | 2083.4625 | 0 | 0
2019-12-22 16:00 | 1344.5484 | 0 | 1666.6667 | 10000 | 322.1183 | 0 | 0
2019-12-22 17:00 | 1956.7929 | 0 | 873.3333 | 10000 | -1083.4595 | -1083.4595 | 0
2019-12-22 18:00 | 2247.5101 | 0 | 4266.6667 | 8916.5405 | 2019.1566 | 1083.4595 | 0
2019-12-22 19:00 | 2072.7751 | 0 | 2773.3333 | 10000 | 700.5582 | 0 | 0
2019-12-22 20:00 | 1964.6714 | 0 | 873.3333 | 10000 | -1091.3381 | -1091.3381 | 0
2019-12-22 21:00 | 1787.2742 | 0 | 286.6667 | 8908.6619 | -1500.6075 | -1500.6075 | 0
2019-12-22 22:00 | 1474.5499 | 0 | 286.6667 | 7408.0544 | -1187.8832 | -1187.8832 | 0
2019-12-22 23:00 | 1209.6601 | 0 | 873.3333 | 6220.1712 | -336.3268 | -336.3268 | 0
2019-12-23 | 908.676 | 0 | 1666.6667 | 5883.8444 | 757.9906 | 757.9906 | 0
2019-12-23 01:00 | 799.1148 | 0 | 286.6667 | 6641.8351 | -512.4481 | -512.4481 | 0
2019-12-23 02:00 | 744.4635 | 0 | 286.6667 | 6129.3869 | -457.7968 | -457.7968 | 0
2019-12-23 03:00 | 742.0339 | 0 | 873.3333 | 5671.5901 | 131.2994 | 131.2994 | 0
2019-12-23 04:00 | 734.9626 | 0 | 873.3333 | 5802.8895 | 138.3707 | 138.3707 | 0
2019-12-23 05:00 | 796.6426 | 0 | 286.6667 | 5941.2602 | -509.9759 | -509.9759 | 0
2019-12-23 06:00 | 989.8134 | 0 | 286.6667 | 5431.2843 | -703.1468 | -703.1468 | 0
2019-12-23 07:00 | 1267.4861 | 0 | 286.6667 | 4728.1375 | -980.8194 | -980.8194 | 0
2019-12-23 08:00 | 1158.3346 | 86.1683 | 0 | 3747.3181 | -1072.1663 | -1072.1663 | 0
2019-12-23 09:00 | 913.2021 | 777.9646 | 0 | 2675.1518 | -135.2374 | -135.2374 | 0
2019-12-23 10:00 | 891.162 | 2004.3522 | 0 | 2539.9144 | 1113.1903 | 1113.1903 | 0
2019-12-23 11:00 | 857.6426 | 2688.3193 | 0 | 3653.1047 | 1830.6767 | 1830.6767 | 0
2019-12-23 12:00 | 827.1378 | 4073.3541 | 0 | 5483.7814 | 3246.2162 | 3246.2162 | 0
2019-12-23 13:00 | 797.6932 | 3112.2737 | 0 | 8729.9976 | 2314.5805 | 1270.0024 | 0
2019-12-23 14:00 | 825.7088 | 3324.3809 | 286.6667 | 10000 | 2785.3387 | 0 | 0
2019-12-23 15:00 | 959.7052 | 1396.2138 | 286.6667 | 10000 | 723.1753 | 0 | 0
2019-12-23 16:00 | 1333.6141 | 0 | 286.6667 | 10000 | -1046.9475 | -1046.9475 | 0
2019-12-23 17:00 | 1950.1253 | 0 | 286.6667 | 8953.0525 | -1663.4586 | -1663.4586 | 0
2019-12-23 18:00 | 2235.4662 | 0 | 1666.6667 | 7289.5939 | -568.7995 | -568.7995 | 0
2019-12-23 19:00 | 2057.7173 | 0 | 286.6667 | 6720.7944 | -1771.0506 | -1771.0506 | 0
2019-12-23 20:00 | 1951.401 | 0 | 4266.6667 | 4949.7437 | 2315.2656 | 2315.2656 | 0
2019-12-23 21:00 | 1770.5256 | 0 | 2773.3333 | 7265.0094 | 1002.8078 | 1002.8078 | 0
2019-12-23 22:00 | 1456.2004 | 0 | 2773.3333 | 8267.8171 | 1317.1329 | 1317.1329 | 0
2019-12-23 23:00 | 1190.1775 | 0 | 2773.3333 | 9584.95 | 1583.1558 | 415.05 | 0
2019-12-24 | 890.0418 | 0 | 873.3333 | 10000 | -16.7084 | -16.7084 | 0
2019-12-24 01:00 | 771.3441 | 0 | 1666.6667 | 9983.2916 | 895.3226 | 16.7084 | 0
2019-12-24 02:00 | 719.027 | 0 | 1666.6667 | 10000 | 947.6397 | 0 | 0
2019-12-24 03:00 | 712.928 | 0 | 873.3333 | 10000 | 160.4054 | 0 | 0
2019-12-24 04:00 | 706.9468 | 0 | 286.6667 | 10000 | -420.2801 | -420.2801 | 0
2019-12-24 05:00 | 769.2764 | 0 | 1666.6667 | 9579.7199 | 897.3903 | 420.2801 | 0
2019-12-24 06:00 | 967.7586 | 0 | 286.6667 | 10000 | -681.0919 | -681.0919 | 0
2019-12-24 07:00 | 1239.0849 | 2.1091 | 286.6667 | 9318.9081 | -950.3091 | -950.3091 | 0
2019-12-24 08:00 | 1119.0201 | 553.1051 | 286.6667 | 8368.599 | -279.2483 | -279.2483 | 0
2019-12-24 09:00 | 863.7549 | 708.9152 | 873.3333 | 8089.3506 | 718.4936 | 718.4936 | 0
2019-12-24 10:00 | 839.3568 | 1163.0548 | 873.3333 | 8807.8443 | 1197.0313 | 1192.1557 | 0
2019-12-24 11:00 | 832.7205 | 1305.649 | 286.6667 | 10000 | 759.5952 | 0 | 0
2019-12-24 12:00 | 837.1726 | 869.3827 | 873.3333 | 10000 | 905.5434 | 0 | 0
2019-12-24 13:00 | 831.0421 | 422.9447 | 873.3333 | 10000 | 465.236 | 0 | 0
2019-12-24 14:00 | 864.2016 | 465.0531 | 873.3333 | 10000 | 474.1849 | 0 | 0
2019-12-24 15:00 | 985.2321 | 169.2501 | 286.6667 | 10000 | -529.3154 | -529.3154 | 0
2019-12-24 16:00 | 1343.3134 | 0 | 286.6667 | 9470.6846 | -1056.6467 | -1056.6467 | 0
2019-12-24 17:00 | 1938.3746 | 0 | 286.6667 | 8414.0379 | -1651.7079 | -1651.7079 | 0
2019-12-24 18:00 | 2240.566 | 0 | 286.6667 | 6762.33 | -1953.8993 | -1953.8993 | 0
2019-12-24 19:00 | 2039.7044 | 0 | 1666.6667 | 4808.4307 | -373.0377 | -373.0377 | 0
2019-12-24 20:00 | 1929.235 | 0 | 6160 | 4435.393 | 4230.765 | 4230.765 | 0
2019-12-24 21:00 | 1744.7511 | 0 | 7873.3333 | 8666.158 | 6128.5822 | 1333.842 | 0
2019-12-24 22:00 | 1428.2169 | 0 | 7873.3333 | 10000 | 6445.1164 | 0 | 0
2019-12-24 23:00 | 1159.3671 | 0 | 7873.3333 | 10000 | 6713.9662 | 0 | 0
2019-12-25 | 856.9134 | 0 | 9573.3333 | 10000 | 8716.4199 | 0 | 0
2019-12-25 01:00 | 740.9994 | 0 | 9060 | 10000 | 8319.0006 | 0 | 0
2019-12-25 02:00 | 687.9479 | 0 | 9060 | 10000 | 8372.0521 | 0 | 0
2019-12-25 03:00 | 685.5097 | 0 | 9060 | 10000 | 8374.4903 | 0 | 0
2019-12-25 04:00 | 682.9166 | 0 | 9060 | 10000 | 8377.0834 | 0 | 0
2019-12-25 05:00 | 747.3056 | 0 | 9573.3333 | 10000 | 8826.0278 | 0 | 0
2019-12-25 06:00 | 954.1329 | 0 | 6160 | 10000 | 5205.8671 | 0 | 0
2019-12-25 07:00 | 1231.211 | 22.6998 | 4266.6667 | 10000 | 3058.1555 | 0 | 0
2019-12-25 08:00 | 1110.0432 | 356.8726 | 6160 | 10000 | 5406.8294 | 0 | 0
2019-12-25 09:00 | 871.4753 | 94.1896 | 9873.3333 | 10000 | 9096.0476 | 0 | 0
2019-12-25 10:00 | 857.8475 | 63.9216 | 9060 | 10000 | 8266.0741 | 0 | 0
2019-12-25 11:00 | 848.5421 | 620.0604 | 6160 | 10000 | 5931.5183 | 0 | 0
2019-12-25 12:00 | 821.002 | 224.5708 | 1666.6667 | 10000 | 1070.2355 | 0 | 0
2019-12-25 13:00 | 830.115 | 344.2744 | 1666.6667 | 10000 | 1180.826 | 0 | 0
2019-12-25 14:00 | 871.2629 | 1965.5478 | 9873.3333 | 10000 | 10967.6182 | 0 | 0
2019-12-25 15:00 | 995.2744 | 1514.3361 | 7873.3333 | 10000 | 8392.395 | 0 | 0
2019-12-25 16:00 | 1360.1382 | 0 | 7873.3333 | 10000 | 6513.1951 | 0 | 0
2019-12-25 17:00 | 1975.6393 | 0 | 4266.6667 | 10000 | 2291.0274 | 0 | 0
2019-12-25 18:00 | 2266.783 | 0 | 9060 | 10000 | 6793.217 | 0 | 0
2019-12-25 19:00 | 2100.8383 | 0 | 7873.3333 | 10000 | 5772.4951 | 0 | 0
2019-12-25 20:00 | 2003.4265 | 0 | 6160 | 10000 | 4156.5735 | 0 | 0
2019-12-25 21:00 | 1822.0852 | 0 | 9573.3333 | 10000 | 7751.2482 | 0 | 0
2019-12-25 22:00 | 1510.6829 | 0 | 9060 | 10000 | 7549.3171 | 0 | 0
2019-12-25 23:00 | 1249.7882 | 0 | 4266.6667 | 10000 | 3016.8785 | 0 | 0
2019-12-26 | 983.856 | 0 | 4266.6667 | 10000 | 3282.8107 | 0 | 0
2019-12-26 01:00 | 853.7022 | 0 | 4266.6667 | 10000 | 3412.9645 | 0 | 0
2019-12-26 02:00 | 796.547 | 0 | 4266.6667 | 10000 | 3470.1196 | 0 | 0
2019-12-26 03:00 | 791.5531 | 0 | 4266.6667 | 10000 | 3475.1136 | 0 | 0
2019-12-26 04:00 | 791.9425 | 0 | 4266.6667 | 10000 | 3474.7242 | 0 | 0
2019-12-26 05:00 | 867.3302 | 0 | 2773.3333 | 10000 | 1906.0031 | 0 | 0
2019-12-26 06:00 | 1089.8176 | 0 | 873.3333 | 10000 | -216.4843 | -216.4843 | 0
2019-12-26 07:00 | 1437.2697 | 24.288 | 873.3333 | 9783.5157 | -539.6484 | -539.6484 | 0
2019-12-26 08:00 | 1360.9143 | 652.9803 | 4266.6667 | 9243.8673 | 3558.7327 | 756.1327 | 0
2019-12-26 09:00 | 1165.8576 | 1739.3577 | 6160 | 10000 | 6733.5001 | 0 | 0
2019-12-26 10:00 | 1198.3306 | 1460.9979 | 6160 | 10000 | 6422.6673 | 0 | 0
2019-12-26 11:00 | 1155.0285 | 623.998 | 9873.3333 | 10000 | 9342.3029 | 0 | 0
2019-12-26 12:00 | 1141.2916 | 2460.2697 | 7873.3333 | 10000 | 9192.3115 | 0 | 0
2019-12-26 13:00 | 1121.0218 | 2131.3893 | 7873.3333 | 10000 | 8883.7009 | 0 | 0
2019-12-26 14:00 | 1132.8962 | 427.6907 | 4266.6667 | 10000 | 3561.4612 | 0 | 0
2019-12-26 15:00 | 1240.7314 | 23.8935 | 2773.3333 | 10000 | 1556.4955 | 0 | 0
2019-12-26 16:00 | 1594.4373 | 0 | 2773.3333 | 10000 | 1178.896 | 0 | 0
2019-12-26 17:00 | 2200.7266 | 0 | 1666.6667 | 10000 | -534.0599 | -534.0599 | 0
2019-12-26 18:00 | 2476.5861 | 0 | 6160 | 9465.9401 | 3683.4139 | 534.0599 | 0
2019-12-26 19:00 | 2294.4449 | 0 | 4266.6667 | 10000 | 1972.2217 | 0 | 0
2019-12-26 20:00 | 2185.6834 | 0 | 4266.6667 | 10000 | 2080.9833 | 0 | 0
2019-12-26 21:00 | 2009.1535 | 0 | 6160 | 10000 | 4150.8465 | 0 | 0
2019-12-26 22:00 | 1653.164 | 0 | 2773.3333 | 10000 | 1120.1693 | 0 | 0
2019-12-26 23:00 | 1319.818 | 0 | 6160 | 10000 | 4840.182 | 0 | 0
2019-12-27 | 972.5841 | 0 | 2773.3333 | 10000 | 1800.7492 | 0 | 0
2019-12-27 01:00 | 846.5192 | 0 | 2773.3333 | 10000 | 1926.8141 | 0 | 0
2019-12-27 02:00 | 786.4091 | 0 | 873.3333 | 10000 | 86.9242 | 0 | 0
2019-12-27 03:00 | 776.9402 | 0 | 2773.3333 | 10000 | 1996.3932 | 0 | 0
2019-12-27 04:00 | 771.1563 | 0 | 4266.6667 | 10000 | 3495.5104 | 0 | 0
2019-12-27 05:00 | 839.3793 | 0 | 4266.6667 | 10000 | 3427.2874 | 0 | 0
2019-12-27 06:00 | 1087.9396 | 0 | 2773.3333 | 10000 | 1685.3937 | 0 | 0
2019-12-27 07:00 | 1426.72 | 822.4961 | 2773.3333 | 10000 | 2169.1095 | 0 | 0
2019-12-27 08:00 | 1344.8764 | 3101.0049 | 2773.3333 | 10000 | 4529.4618 | 0 | 0
2019-12-27 09:00 | 1137.5226 | 4876.8372 | 1666.6667 | 10000 | 5405.9813 | 0 | 0
2019-12-27 10:00 | 1123.3911 | 5997.8871 | 1666.6667 | 10000 | 6541.1626 | 0 | 0
2019-12-27 11:00 | 1090.5299 | 6454.9868 | 2773.3333 | 10000 | 8137.7902 | 0 | 0
2019-12-27 12:00 | 1050.9047 | 6269.3952 | 2773.3333 | 10000 | 7991.8238 | 0 | 0
2019-12-27 13:00 | 1015.2546 | 5447.006 | 1666.6667 | 10000 | 6098.4181 | 0 | 0
2019-12-27 14:00 | 1029.1253 | 4009.6026 | 2773.3333 | 10000 | 5753.8107 | 0 | 0
2019-12-27 15:00 | 1157.401 | 1982.3056 | 2773.3333 | 10000 | 3598.2379 | 0 | 0
2019-12-27 16:00 | 1530.0553 | 0 | 2773.3333 | 10000 | 1243.278 | 0 | 0
2019-12-27 17:00 | 2151.1562 | 0 | 1666.6667 | 10000 | -484.4895 | -484.4895 | 0
2019-12-27 18:00 | 2441.7314 | 0 | 4266.6667 | 9515.5105 | 1824.9353 | 484.4895 | 0
2019-12-27 19:00 | 2268.9597 | 0 | 4266.6667 | 10000 | 1997.707 | 0 | 0
2019-12-27 20:00 | 2168.438 | 0 | 2773.3333 | 10000 | 604.8953 | 0 | 0
2019-12-27 21:00 | 1993.8596 | 0 | 1666.6667 | 10000 | -327.1929 | -327.1929 | 0
2019-12-27 22:00 | 1644.5651 | 0 | 1666.6667 | 9672.8071 | 22.1015 | 22.1015 | 0
2019-12-27 23:00 | 1321.3529 | 0 | 4266.6667 | 9694.9086 | 2945.3138 | 305.0914 | 0
2019-12-28 | 978.0225 | 0 | 4266.6667 | 10000 | 3288.6441 | 0 | 0
2019-12-28 01:00 | 851.394 | 0 | 4266.6667 | 10000 | 3415.2727 | 0 | 0
2019-12-28 02:00 | 792.9021 | 0 | 2773.3333 | 10000 | 1980.4313 | 0 | 0
2019-12-28 03:00 | 785.247 | 0 | 1666.6667 | 10000 | 881.4196 | 0 | 0
2019-12-28 04:00 | 787.5087 | 0 | 1666.6667 | 10000 | 879.158 | 0 | 0
2019-12-28 05:00 | 856.9309 | 0 | 6160 | 10000 | 5303.0691 | 0 | 0
2019-12-28 06:00 | 1102.0745 | 0 | 4266.6667 | 10000 | 3164.5922 | 0 | 0
2019-12-28 07:00 | 1423.8519 | 778.3027 | 4266.6667 | 10000 | 3621.1175 | 0 | 0
2019-12-28 08:00 | 1347.3864 | 3057.4475 | 6160 | 10000 | 7870.0611 | 0 | 0
2019-12-28 09:00 | 1132.4081 | 4867.452 | 9060 | 10000 | 12795.044 | 0 | 0
2019-12-28 10:00 | 1110.8142 | 5917.7344 | 9873.3333 | 10000 | 14680.2536 | 0 | 0
2019-12-28 11:00 | 1074.2629 | 6319.6421 | 9873.3333 | 10000 | 15118.7126 | 0 | 0
2019-12-28 12:00 | 1032.6464 | 6113.7415 | 9060 | 10000 | 14141.0951 | 0 | 0
2019-12-28 13:00 | 994.8609 | 5345.2897 | 9573.3333 | 10000 | 13923.7621 | 0 | 0
2019-12-28 14:00 | 1008.5046 | 2120.5781 | 9060 | 10000 | 10172.0735 | 0 | 0
2019-12-28 15:00 | 1131.3189 | 813.3134 | 6160 | 10000 | 5841.9945 | 0 | 0
2019-12-28 16:00 | 1501.6211 | 0 | 6160 | 10000 | 4658.3789 | 0 | 0
2019-12-28 17:00 | 2115.7195 | 0 | 6160 | 10000 | 4044.2805 | 0 | 0
2019-12-28 18:00 | 2407.849 | 0 | 4266.6667 | 10000 | 1858.8177 | 0 | 0
2019-12-28 19:00 | 2241.4393 | 0 | 4266.6667 | 10000 | 2025.2273 | 0 | 0
2019-12-28 20:00 | 2136.9373 | 0 | 4266.6667 | 10000 | 2129.7294 | 0 | 0
2019-12-28 21:00 | 1966.3963 | 0 | 2773.3333 | 10000 | 806.937 | 0 | 0
2019-12-28 22:00 | 1615.6304 | 0 | 1666.6667 | 10000 | 51.0363 | 0 | 0
2019-12-28 23:00 | 1292.5709 | 0 | 4266.6667 | 10000 | 2974.0957 | 0 | 0
2019-12-29 | 952.0277 | 0 | 1666.6667 | 10000 | 714.6389 | 0 | 0
2019-12-29 01:00 | 824.0716 | 0 | 873.3333 | 10000 | 49.2617 | 0 | 0
2019-12-29 02:00 | 766.5224 | 0 | 1666.6667 | 10000 | 900.1442 | 0 | 0
2019-12-29 03:00 | 760.2523 | 0 | 2773.3333 | 10000 | 2013.081 | 0 | 0
2019-12-29 04:00 | 758.2559 | 0 | 1666.6667 | 10000 | 908.4108 | 0 | 0
2019-12-29 05:00 | 826.7052 | 0 | 0 | 10000 | -826.7052 | -826.7052 | 0
2019-12-29 06:00 | 1052.0355 | 0 | 873.3333 | 9173.2948 | -178.7022 | -178.7022 | 0
2019-12-29 07:00 | 1405.7062 | 597.9459 | 873.3333 | 8994.5926 | 65.5731 | 65.5731 | 0
2019-12-29 08:00 | 1320.9934 | 2810.7288 | 286.6667 | 9060.1656 | 1776.4021 | 939.8344 | 0
2019-12-29 09:00 | 1106.1997 | 4587.6202 | 286.6667 | 10000 | 3768.0873 | 0 | 0
2019-12-29 10:00 | 1084.2384 | 5653.9945 | 286.6667 | 10000 | 4856.4228 | 0 | 0
2019-12-29 11:00 | 1056.526 | 6090.3471 | 873.3333 | 10000 | 5907.1545 | 0 | 0
2019-12-29 12:00 | 1014.5175 | 5912.6778 | 873.3333 | 10000 | 5771.4937 | 0 | 0
2019-12-29 13:00 | 974.4519 | 5147.4276 | 873.3333 | 10000 | 5046.309 | 0 | 0
2019-12-29 14:00 | 989.2283 | 3763.674 | 873.3333 | 10000 | 3647.779 | 0 | 0
2019-12-29 15:00 | 1111.8733 | 1751.0636 | 6160 | 10000 | 6799.1903 | 0 | 0
2019-12-29 16:00 | 1482.0476 | 0 | 4266.6667 | 10000 | 2784.619 | 0 | 0
2019-12-29 17:00 | 2092.2238 | 0 | 6160 | 10000 | 4067.7762 | 0 | 0
2019-12-29 18:00 | 2387.1308 | 0 | 6160 | 10000 | 3772.8692 | 0 | 0
2019-12-29 19:00 | 2217.9738 | 0 | 4266.6667 | 10000 | 2048.6929 | 0 | 0
2019-12-29 20:00 | 2122.4183 | 0 | 2773.3333 | 10000 | 650.915 | 0 | 0
2019-12-29 21:00 | 1949.3404 | 0 | 2773.3333 | 10000 | 823.993 | 0 | 0
2019-12-29 22:00 | 1601.4387 | 0 | 2773.3333 | 10000 | 1171.8946 | 0 | 0
2019-12-29 23:00 | 1275.0221 | 0 | 4266.6667 | 10000 | 2991.6446 | 0 | 0
2019-12-30 | 941.7561 | 0 | 6160 | 10000 | 5218.2439 | 0 | 0
2019-12-30 01:00 | 814.1064 | 0 | 4266.6667 | 10000 | 3452.5602 | 0 | 0
2019-12-30 02:00 | 757.4177 | 0 | 873.3333 | 10000 | 115.9157 | 0 | 0
2019-12-30 03:00 | 745.4181 | 0 | 873.3333 | 10000 | 127.9152 | 0 | 0
2019-12-30 04:00 | 742.3981 | 0 | 1666.6667 | 10000 | 924.2685 | 0 | 0
2019-12-30 05:00 | 809.8128 | 0 | 873.3333 | 10000 | 63.5205 | 0 | 0
2019-12-30 06:00 | 1044.4199 | 0 | 873.3333 | 10000 | -171.0866 | -171.0866 | 0
2019-12-30 07:00 | 1383.5509 | 2.3725 | 873.3333 | 9828.9134 | -507.8451 | -507.8451 | 0
2019-12-30 08:00 | 1338.6066 | 874.2449 | 286.6667 | 9321.0683 | -177.695 | -177.695 | 0
2019-12-30 09:00 | 1148.8733 | 380.305 | 2773.3333 | 9143.3733 | 2004.7651 | 856.6267 | 0
2019-12-30 10:00 | 1163.5223 | 1093.0428 | 873.3333 | 10000 | 802.8538 | 0 | 0
2019-12-30 11:00 | 1162.259 | 1993.4491 | 0 | 10000 | 831.1901 | 0 | 0
2019-12-30 12:00 | 1136.6712 | 5773.1437 | 0 | 10000 | 4636.4726 | 0 | 0
2019-12-30 13:00 | 1088.5527 | 3280.3416 | 0 | 10000 | 2191.789 | 0 | 0
2019-12-30 14:00 | 1121.9946 | 829.7572 | 286.6667 | 10000 | -5.5707 | -5.5707 | 0
2019-12-30 15:00 | 1238.1955 | 1697.3241 | 0 | 9994.4293 | 459.1286 | 5.5707 | 0
2019-12-30 16:00 | 1589.4482 | 0 | 0 | 10000 | -1589.4482 | -1589.4482 | 0
2019-12-30 17:00 | 2197.132 | 0 | 0 | 8410.5518 | -2197.132 | -2197.132 | 0
2019-12-30 18:00 | 2485.7782 | 0 | 286.6667 | 6213.4198 | -2199.1115 | -2199.1115 | 0
2019-12-30 19:00 | 2310.2677 | 0 | 286.6667 | 4014.3083 | -2023.601 | -2023.601 | 0
2019-12-30 20:00 | 2202.6537 | 0 | 286.6667 | 1990.7072 | -1915.9871 | -1915.9871 | 0
2019-12-30 21:00 | 2021.8252 | 0 | 873.3333 | 74.7202 | -1148.4919 | -74.7202 | -1073.7717
2019-12-30 22:00 | 1665.4579 | 0 | 873.3333 | 0 | -792.1246 | 0 | -1865.8963
2019-12-30 23:00 | 1323.4655 | 0 | 873.3333 | 0 | -450.1322 | 0 | -2316.0285
2019-12-31 | 962.9862 | 0 | 873.3333 | 0 | -89.6529 | 0 | -2405.6814
2019-12-31 01:00 | 832.7887 | 0 | 873.3333 | 0 | 40.5447 | 40.5447 | -2365.1367
2019-12-31 02:00 | 776.2655 | 0 | 2773.3333 | 40.5447 | 1997.0679 | 1997.0679 | -327.5242
2019-12-31 03:00 | 768.8323 | 0 | 2773.3333 | 2037.6125 | 2004.501 | 2004.501 | 0
2019-12-31 04:00 | 761.8973 | 0 | 2773.3333 | 4042.1135 | 2011.436 | 2011.436 | 0
2019-12-31 05:00 | 830.9797 | 0 | 4266.6667 | 6053.5495 | 3435.687 | 3435.687 | 0
2019-12-31 06:00 | 1080.5204 | 0 | 4266.6667 | 9489.2365 | 3186.1462 | 510.7635 | 0
2019-12-31 07:00 | 1429.6876 | 565.9311 | 2773.3333 | 10000 | 1909.5768 | 0 | 0
2019-12-31 08:00 | 1383.2873 | 2797.6395 | 6160 | 10000 | 7574.3522 | 0 | 0
2019-12-31 09:00 | 1209.2188 | 3887.1713 | 9060 | 10000 | 11737.9525 | 0 | 0
2019-12-31 10:00 | 1218.7692 | 2820.9523 | 7873.3333 | 10000 | 9475.5165 | 0 | 0
2019-12-31 11:00 | 1212.4748 | 1156.8839 | 6160 | 10000 | 6104.4091 | 0 | 0
2019-12-31 12:00 | 1171.4391 | 4115.8258 | 7873.3333 | 10000 | 10817.7201 | 0 | 0
2019-12-31 13:00 | 1113.4676 | 5343.2691 | 7873.3333 | 10000 | 12103.1349 | 0 | 0
2019-12-31 14:00 | 1112.6698 | 3930.9771 | 6160 | 10000 | 8978.3074 | 0 | 0
2019-12-31 15:00 | 1225.5424 | 1886.046 | 6160 | 10000 | 6820.5036 | 0 | 0
2019-12-31 16:00 | 1590.8318 | 0 | 4266.6667 | 10000 | 2675.8348 | 0 | 0
2019-12-31 17:00 | 2208.595 | 0 | 2773.3333 | 10000 | 564.7383 | 0 | 0
2019-12-31 18:00 | 2491.3203 | 0 | 4266.6667 | 10000 | 1775.3464 | 0 | 0
2019-12-31 19:00 | 2309.8063 | 0 | 4266.6667 | 10000 | 1956.8604 | 0 | 0
2019-12-31 20:00 | 2212.1394 | 0 | 2773.3333 | 10000 | 561.1939 | 0 | 0
2019-12-31 21:00 | 2034.1153 | 0 | 6160 | 10000 | 4125.8847 | 0 | 0
2019-12-31 22:00 | 1669.1476 | 0 | 1666.6667 | 10000 | -2.4809 | -2.4809 | 0
2019-12-31 23:00 | 1322.8506 | 0 | 6160 | 9997.5191 | 4837.1494 | 2.4809 | 0
Formulas:
Date-Hour = [Date-Hour, row above]+1/24

## Load Profile
https://openei.org/datasets/files/961/pub/RESIDENTIAL_LOAD_DATA_E_PLUS_OUTPUT/BASE/
USA_MA_Boston-Logan.Intl.AP.725090_TMY3_BASE
|  |  | Annual Load | 10000000
Date | Month | Hour | Electricity:Facility [kW](Hourly) | Load
2017-01-01 | 1 | 0 | 0.93893 | 1042.0208
2017-01-01 01:00 | 1 | 1 | 0.80494 | 893.3192
2017-01-01 02:00 | 1 | 2 | 0.75671 | 839.8014
2017-01-01 03:00 | 1 | 3 | 0.74024 | 821.5169
2017-01-01 04:00 | 1 | 4 | 0.73539 | 816.1413
2017-01-01 05:00 | 1 | 5 | 0.78681 | 873.2033
2017-01-01 06:00 | 1 | 6 | 1.0116 | 1122.6479
2017-01-01 07:00 | 1 | 7 | 1.3515 | 1499.8922
2017-01-01 08:00 | 1 | 8 | 1.3051 | 1448.3726
2017-01-01 09:00 | 1 | 9 | 1.1142 | 1236.4919
2017-01-01 10:00 | 1 | 10 | 1.1284 | 1252.2673
2017-01-01 11:00 | 1 | 11 | 1.0952 | 1215.4377
2017-01-01 12:00 | 1 | 12 | 1.0527 | 1168.2547
2017-01-01 13:00 | 1 | 13 | 1.0238 | 1136.2649
2017-01-01 14:00 | 1 | 14 | 1.0262 | 1138.8866
2017-01-01 15:00 | 1 | 15 | 1.105 | 1226.292
2017-01-01 16:00 | 1 | 16 | 1.3845 | 1536.5213
2017-01-01 17:00 | 1 | 17 | 1.9157 | 2126.095
2017-01-01 18:00 | 1 | 18 | 2.2421 | 2488.3215
2017-01-01 19:00 | 1 | 19 | 2.2121 | 2454.9812
2017-01-01 20:00 | 1 | 20 | 2.0722 | 2299.757
2017-01-01 21:00 | 1 | 21 | 1.9194 | 2130.1209
2017-01-01 22:00 | 1 | 22 | 1.6075 | 1783.9856
2017-01-01 23:00 | 1 | 23 | 1.2918 | 1433.6875
2017-01-02 | 1 | 0 | 0.97261 | 1079.4076
2017-01-02 01:00 | 1 | 1 | 0.85793 | 952.1266
2017-01-02 02:00 | 1 | 2 | 0.82111 | 911.2734
2017-01-02 03:00 | 1 | 3 | 0.80476 | 893.1193
2017-01-02 04:00 | 1 | 4 | 0.80863 | 897.4218
2017-01-02 05:00 | 1 | 5 | 0.86624 | 961.3495
2017-01-02 06:00 | 1 | 6 | 1.0861 | 1205.3234
2017-01-02 07:00 | 1 | 7 | 1.4156 | 1571.0671
2017-01-02 08:00 | 1 | 8 | 1.33 | 1476.0105
2017-01-02 09:00 | 1 | 9 | 1.1156 | 1238.1063
2017-01-02 10:00 | 1 | 10 | 1.1382 | 1263.1562
2017-01-02 11:00 | 1 | 11 | 1.118 | 1240.8118
2017-01-02 12:00 | 1 | 12 | 1.0806 | 1199.2196
2017-01-02 13:00 | 1 | 13 | 1.032 | 1145.3117
2017-01-02 14:00 | 1 | 14 | 1.0331 | 1146.5493
2017-01-02 15:00 | 1 | 15 | 1.1104 | 1232.2918
2017-01-02 16:00 | 1 | 16 | 1.379 | 1530.4
2017-01-02 17:00 | 1 | 17 | 1.9035 | 2112.549
2017-01-02 18:00 | 1 | 18 | 2.2129 | 2455.9215
2017-01-02 19:00 | 1 | 19 | 2.1746 | 2413.3347
2017-01-02 20:00 | 1 | 20 | 2.0209 | 2242.7475
2017-01-02 21:00 | 1 | 21 | 1.8518 | 2055.1301
2017-01-02 22:00 | 1 | 22 | 1.537 | 1705.7544
2017-01-02 23:00 | 1 | 23 | 1.2275 | 1362.2701
2017-01-03 | 1 | 0 | 0.91828 | 1019.1125
2017-01-03 01:00 | 1 | 1 | 0.795 | 882.2924
2017-01-03 02:00 | 1 | 2 | 0.74587 | 827.7665
2017-01-03 03:00 | 1 | 3 | 0.73517 | 815.8933
2017-01-03 04:00 | 1 | 4 | 0.72938 | 809.4685
2017-01-03 05:00 | 1 | 5 | 0.77704 | 862.3635
2017-01-03 06:00 | 1 | 6 | 0.99054 | 1099.3037
2017-01-03 07:00 | 1 | 7 | 1.3189 | 1463.6729
2017-01-03 08:00 | 1 | 8 | 1.259 | 1397.2756
2017-01-03 09:00 | 1 | 9 | 1.0756 | 1193.6693
2017-01-03 10:00 | 1 | 10 | 1.0905 | 1210.2789
2017-01-03 11:00 | 1 | 11 | 1.0782 | 1196.5668
2017-01-03 12:00 | 1 | 12 | 1.0541 | 1169.7933
2017-01-03 13:00 | 1 | 13 | 1.0284 | 1141.3569
2017-01-03 14:00 | 1 | 14 | 1.0271 | 1139.9138
2017-01-03 15:00 | 1 | 15 | 1.0978 | 1218.3248
2017-01-03 16:00 | 1 | 16 | 1.3579 | 1506.9759
2017-01-03 17:00 | 1 | 17 | 1.8359 | 2037.4872
2017-01-03 18:00 | 1 | 18 | 2.1955 | 2436.5917
2017-01-03 19:00 | 1 | 19 | 2.1351 | 2369.5303
2017-01-03 20:00 | 1 | 20 | 1.9837 | 2201.5219
2017-01-03 21:00 | 1 | 21 | 1.8115 | 2010.361
2017-01-03 22:00 | 1 | 22 | 1.4982 | 1662.7543
2017-01-03 23:00 | 1 | 23 | 1.1946 | 1325.8165
2017-01-04 | 1 | 0 | 0.8925 | 990.4983
2017-01-04 01:00 | 1 | 1 | 0.77607 | 861.2787
2017-01-04 02:00 | 1 | 2 | 0.73111 | 811.391
2017-01-04 03:00 | 1 | 3 | 0.72259 | 801.9284
2017-01-04 04:00 | 1 | 4 | 0.72462 | 804.1801
2017-01-04 05:00 | 1 | 5 | 0.78162 | 867.4404
2017-01-04 06:00 | 1 | 6 | 1.0089 | 1119.6275
2017-01-04 07:00 | 1 | 7 | 1.3036 | 1446.7352
2017-01-04 08:00 | 1 | 8 | 1.2636 | 1402.3409
2017-01-04 09:00 | 1 | 9 | 1.1011 | 1221.9481
2017-01-04 10:00 | 1 | 10 | 1.0899 | 1209.5577
2017-01-04 11:00 | 1 | 11 | 1.085 | 1204.1012
2017-01-04 12:00 | 1 | 12 | 1.0534 | 1169.0455
2017-01-04 13:00 | 1 | 13 | 1.0198 | 1131.7361
2017-01-04 14:00 | 1 | 14 | 1.0262 | 1138.8976
2017-01-04 15:00 | 1 | 15 | 1.1066 | 1228.0748
2017-01-04 16:00 | 1 | 16 | 1.3983 | 1551.8261
2017-01-04 17:00 | 1 | 17 | 1.9267 | 2138.284
2017-01-04 18:00 | 1 | 18 | 2.2443 | 2490.7181
2017-01-04 19:00 | 1 | 19 | 2.2114 | 2454.1603
2017-01-04 20:00 | 1 | 20 | 2.0707 | 2298.0408
2017-01-04 21:00 | 1 | 21 | 1.9064 | 2115.7759
2017-01-04 22:00 | 1 | 22 | 1.5955 | 1770.7263
2017-01-04 23:00 | 1 | 23 | 1.2933 | 1435.3098
2017-01-05 | 1 | 0 | 0.99849 | 1108.1231
2017-01-05 01:00 | 1 | 1 | 0.88096 | 977.69
2017-01-05 02:00 | 1 | 2 | 0.8417 | 934.1205
2017-01-05 03:00 | 1 | 3 | 0.83068 | 921.89
2017-01-05 04:00 | 1 | 4 | 0.84553 | 938.3732
2017-01-05 05:00 | 1 | 5 | 0.9011 | 1000.0422
2017-01-05 06:00 | 1 | 6 | 1.1273 | 1251.0793
2017-01-05 07:00 | 1 | 7 | 1.4362 | 1593.9334
2017-01-05 08:00 | 1 | 8 | 1.362 | 1511.5761
2017-01-05 09:00 | 1 | 9 | 1.1586 | 1285.8132
2017-01-05 10:00 | 1 | 10 | 1.1687 | 1296.9823
2017-01-05 11:00 | 1 | 11 | 1.1291 | 1253.0589
2017-01-05 12:00 | 1 | 12 | 1.0839 | 1202.8901
2017-01-05 13:00 | 1 | 13 | 1.0458 | 1160.6337
2017-01-05 14:00 | 1 | 14 | 1.0515 | 1166.9031
2017-01-05 15:00 | 1 | 15 | 1.1399 | 1265.0815
2017-01-05 16:00 | 1 | 16 | 1.4179 | 1573.6313
2017-01-05 17:00 | 1 | 17 | 1.9569 | 2171.8176
2017-01-05 18:00 | 1 | 18 | 2.2726 | 2522.1304
2017-01-05 19:00 | 1 | 19 | 2.2415 | 2487.6218
2017-01-05 20:00 | 1 | 20 | 2.0952 | 2325.2633
2017-01-05 21:00 | 1 | 21 | 1.9335 | 2145.8022
2017-01-05 22:00 | 1 | 22 | 1.6237 | 1802.0216
2017-01-05 23:00 | 1 | 23 | 1.3168 | 1461.3819
2017-01-06 | 1 | 0 | 1.018 | 1129.743
2017-01-06 01:00 | 1 | 1 | 0.89209 | 990.0455
2017-01-06 02:00 | 1 | 2 | 0.84709 | 940.1069
2017-01-06 03:00 | 1 | 3 | 0.8415 | 933.8959
2017-01-06 04:00 | 1 | 4 | 0.83912 | 931.2571
2017-01-06 05:00 | 1 | 5 | 0.89411 | 992.2818
2017-01-06 06:00 | 1 | 6 | 1.1124 | 1234.5975
2017-01-06 07:00 | 1 | 7 | 1.4183 | 1574.0274
2017-01-06 08:00 | 1 | 8 | 1.3474 | 1495.3606
2017-01-06 09:00 | 1 | 9 | 1.1302 | 1254.2489
2017-01-06 10:00 | 1 | 10 | 1.1323 | 1256.5931
2017-01-06 11:00 | 1 | 11 | 1.0945 | 1214.7196
2017-01-06 12:00 | 1 | 12 | 1.0562 | 1172.1534
2017-01-06 13:00 | 1 | 13 | 1.0192 | 1131.0846
2017-01-06 14:00 | 1 | 14 | 1.0287 | 1141.6182
2017-01-06 15:00 | 1 | 15 | 1.1051 | 1226.4254
2017-01-06 16:00 | 1 | 16 | 1.3796 | 1531.0673
2017-01-06 17:00 | 1 | 17 | 1.9033 | 2112.311
2017-01-06 18:00 | 1 | 18 | 2.2178 | 2461.3628
2017-01-06 19:00 | 1 | 19 | 2.1821 | 2421.6762
2017-01-06 20:00 | 1 | 20 | 2.0319 | 2254.9516
2017-01-06 21:00 | 1 | 21 | 1.8682 | 2073.3565
2017-01-06 22:00 | 1 | 22 | 1.5556 | 1726.4627
2017-01-06 23:00 | 1 | 23 | 1.2495 | 1386.7211
2017-01-07 | 1 | 0 | 0.94948 | 1053.7304
2017-01-07 01:00 | 1 | 1 | 0.82378 | 914.2289
2017-01-07 02:00 | 1 | 2 | 0.77462 | 859.6796
2017-01-07 03:00 | 1 | 3 | 0.75738 | 840.5408
2017-01-07 04:00 | 1 | 4 | 0.75289 | 835.563
2017-01-07 05:00 | 1 | 5 | 0.8056 | 894.051
2017-01-07 06:00 | 1 | 6 | 1.0263 | 1139.0025
2017-01-07 07:00 | 1 | 7 | 1.35 | 1498.2187
2017-01-07 08:00 | 1 | 8 | 1.3036 | 1446.7904
2017-01-07 09:00 | 1 | 9 | 1.1147 | 1237.1264
2017-01-07 10:00 | 1 | 10 | 1.1264 | 1250.1037
2017-01-07 11:00 | 1 | 11 | 1.1106 | 1232.5755
2017-01-07 12:00 | 1 | 12 | 1.0772 | 1195.4708
2017-01-07 13:00 | 1 | 13 | 1.0384 | 1152.4164
2017-01-07 14:00 | 1 | 14 | 1.0395 | 1153.606
2017-01-07 15:00 | 1 | 15 | 1.1106 | 1232.5736
2017-01-07 16:00 | 1 | 16 | 1.3732 | 1523.9281
2017-01-07 17:00 | 1 | 17 | 1.8855 | 2092.4904
2017-01-07 18:00 | 1 | 18 | 2.1983 | 2439.7012
2017-01-07 19:00 | 1 | 19 | 2.1563 | 2393.0598
2017-01-07 20:00 | 1 | 20 | 2.0016 | 2221.3541
2017-01-07 21:00 | 1 | 21 | 1.8342 | 2035.6386
2017-01-07 22:00 | 1 | 22 | 1.5117 | 1677.6564
2017-01-07 23:00 | 1 | 23 | 1.1901 | 1320.8098
2017-01-08 | 1 | 0 | 0.87564 | 971.7899
2017-01-08 01:00 | 1 | 1 | 0.75002 | 832.3694
2017-01-08 02:00 | 1 | 2 | 0.70317 | 780.3847
2017-01-08 03:00 | 1 | 3 | 0.6997 | 776.5227
2017-01-08 04:00 | 1 | 4 | 0.70247 | 779.5976
2017-01-08 05:00 | 1 | 5 | 0.7602 | 843.6749
2017-01-08 06:00 | 1 | 6 | 0.98459 | 1092.6993
2017-01-08 07:00 | 1 | 7 | 1.3233 | 1468.5789
2017-01-08 08:00 | 1 | 8 | 1.2773 | 1417.516
2017-01-08 09:00 | 1 | 9 | 1.1124 | 1234.5601
2017-01-08 10:00 | 1 | 10 | 1.1394 | 1264.5128
2017-01-08 11:00 | 1 | 11 | 1.1304 | 1254.5346
2017-01-08 12:00 | 1 | 12 | 1.1035 | 1224.6702
2017-01-08 13:00 | 1 | 13 | 1.0769 | 1195.1458
2017-01-08 14:00 | 1 | 14 | 1.0819 | 1200.6413
2017-01-08 15:00 | 1 | 15 | 1.1586 | 1285.8584
2017-01-08 16:00 | 1 | 16 | 1.4317 | 1588.8933
2017-01-08 17:00 | 1 | 17 | 1.9588 | 2173.9246
2017-01-08 18:00 | 1 | 18 | 2.2806 | 2531.0058
2017-01-08 19:00 | 1 | 19 | 2.2471 | 2493.8456
2017-01-08 20:00 | 1 | 20 | 2.106 | 2337.2326
2017-01-08 21:00 | 1 | 21 | 1.9403 | 2153.3967
2017-01-08 22:00 | 1 | 22 | 1.6258 | 1804.3532
2017-01-08 23:00 | 1 | 23 | 1.3096 | 1453.3781
2017-01-09 | 1 | 0 | 0.99127 | 1100.1168
2017-01-09 01:00 | 1 | 1 | 0.8731 | 968.9644
2017-01-09 02:00 | 1 | 2 | 0.83977 | 931.9764
2017-01-09 03:00 | 1 | 3 | 0.84043 | 932.7078
2017-01-09 04:00 | 1 | 4 | 0.83939 | 931.5577
2017-01-09 05:00 | 1 | 5 | 0.89532 | 993.6304
2017-01-09 06:00 | 1 | 6 | 1.1368 | 1261.6405
2017-01-09 07:00 | 1 | 7 | 1.4545 | 1614.2213
2017-01-09 08:00 | 1 | 8 | 1.3673 | 1517.4772
2017-01-09 09:00 | 1 | 9 | 1.1583 | 1285.4932
2017-01-09 10:00 | 1 | 10 | 1.163 | 1290.7479
2017-01-09 11:00 | 1 | 11 | 1.1155 | 1238.0291
2017-01-09 12:00 | 1 | 12 | 1.0728 | 1190.6351
2017-01-09 13:00 | 1 | 13 | 1.0346 | 1148.2085
2017-01-09 14:00 | 1 | 14 | 1.0468 | 1161.7449
2017-01-09 15:00 | 1 | 15 | 1.1335 | 1257.9821
2017-01-09 16:00 | 1 | 16 | 1.41 | 1564.8568
2017-01-09 17:00 | 1 | 17 | 1.942 | 2155.2275
2017-01-09 18:00 | 1 | 18 | 2.2513 | 2498.5406
2017-01-09 19:00 | 1 | 19 | 2.2177 | 2461.1569
2017-01-09 20:00 | 1 | 20 | 2.0676 | 2294.6091
2017-01-09 21:00 | 1 | 21 | 1.9113 | 2121.1985
2017-01-09 22:00 | 1 | 22 | 1.6012 | 1776.9825
2017-01-09 23:00 | 1 | 23 | 1.2956 | 1437.8816
2017-01-10 | 1 | 0 | 0.9904 | 1099.1459
2017-01-10 01:00 | 1 | 1 | 0.87214 | 967.9049
2017-01-10 02:00 | 1 | 2 | 0.82831 | 919.2615
2017-01-10 03:00 | 1 | 3 | 0.82115 | 911.3138
2017-01-10 04:00 | 1 | 4 | 0.82171 | 911.9384
2017-01-10 05:00 | 1 | 5 | 0.87439 | 970.4012
2017-01-10 06:00 | 1 | 6 | 1.1152 | 1237.6796
2017-01-10 07:00 | 1 | 7 | 1.427 | 1583.6504
2017-01-10 08:00 | 1 | 8 | 1.3399 | 1486.9945
2017-01-10 09:00 | 1 | 9 | 1.1291 | 1253.0934
2017-01-10 10:00 | 1 | 10 | 1.1298 | 1253.8638
2017-01-10 11:00 | 1 | 11 | 1.0958 | 1216.162
2017-01-10 12:00 | 1 | 12 | 1.0695 | 1186.9317
2017-01-10 13:00 | 1 | 13 | 1.0417 | 1156.0461
2017-01-10 14:00 | 1 | 14 | 1.0518 | 1167.2865
2017-01-10 15:00 | 1 | 15 | 1.1342 | 1258.7129
2017-01-10 16:00 | 1 | 16 | 1.4101 | 1564.9035
2017-01-10 17:00 | 1 | 17 | 1.9456 | 2159.2321
2017-01-10 18:00 | 1 | 18 | 2.2566 | 2504.3254
2017-01-10 19:00 | 1 | 19 | 2.2232 | 2467.3409
2017-01-10 20:00 | 1 | 20 | 2.0845 | 2313.3317
2017-01-10 21:00 | 1 | 21 | 1.9262 | 2137.6896
2017-01-10 22:00 | 1 | 22 | 1.627 | 1805.6335
2017-01-10 23:00 | 1 | 23 | 1.3235 | 1468.8726
2017-01-11 | 1 | 0 | 1.0227 | 1134.9702
2017-01-11 01:00 | 1 | 1 | 0.90966 | 1009.5438
2017-01-11 02:00 | 1 | 2 | 0.86279 | 957.5205
2017-01-11 03:00 | 1 | 3 | 0.85852 | 952.7863
2017-01-11 04:00 | 1 | 4 | 0.85721 | 951.3375
2017-01-11 05:00 | 1 | 5 | 0.91368 | 1014.0059
2017-01-11 06:00 | 1 | 6 | 1.1552 | 1282.0857
2017-01-11 07:00 | 1 | 7 | 1.4692 | 1630.5214
2017-01-11 08:00 | 1 | 8 | 1.3854 | 1537.4837
2017-01-11 09:00 | 1 | 9 | 1.1745 | 1303.4911
2017-01-11 10:00 | 1 | 10 | 1.1939 | 1324.9925
2017-01-11 11:00 | 1 | 11 | 1.1656 | 1293.5942
2017-01-11 12:00 | 1 | 12 | 1.1385 | 1263.5404
2017-01-11 13:00 | 1 | 13 | 1.1069 | 1228.4431
2017-01-11 14:00 | 1 | 14 | 1.1115 | 1233.5561
2017-01-11 15:00 | 1 | 15 | 1.1859 | 1316.1137
2017-01-11 16:00 | 1 | 16 | 1.4461 | 1604.9263
2017-01-11 17:00 | 1 | 17 | 1.9245 | 2135.7964
2017-01-11 18:00 | 1 | 18 | 2.3004 | 2553.0007
2017-01-11 19:00 | 1 | 19 | 2.2285 | 2473.1916
2017-01-11 20:00 | 1 | 20 | 2.0675 | 2294.4682
2017-01-11 21:00 | 1 | 21 | 1.9021 | 2111.0057
2017-01-11 22:00 | 1 | 22 | 1.5886 | 1762.9842
2017-01-11 23:00 | 1 | 23 | 1.2803 | 1420.9287
2017-01-12 | 1 | 0 | 0.98313 | 1091.0769
2017-01-12 01:00 | 1 | 1 | 0.87363 | 969.5585
2017-01-12 02:00 | 1 | 2 | 0.83157 | 922.8738
2017-01-12 03:00 | 1 | 3 | 0.8258 | 916.4785
2017-01-12 04:00 | 1 | 4 | 0.82581 | 916.4849
2017-01-12 05:00 | 1 | 5 | 0.893 | 991.0524
2017-01-12 06:00 | 1 | 6 | 1.1122 | 1234.3075
2017-01-12 07:00 | 1 | 7 | 1.4416 | 1599.9252
2017-01-12 08:00 | 1 | 8 | 1.3843 | 1536.2566
2017-01-12 09:00 | 1 | 9 | 1.1972 | 1328.6617
2017-01-12 10:00 | 1 | 10 | 1.2285 | 1363.3813
2017-01-12 11:00 | 1 | 11 | 1.191 | 1321.792
2017-01-12 12:00 | 1 | 12 | 1.158 | 1285.1337
2017-01-12 13:00 | 1 | 13 | 1.1227 | 1245.9316
2017-01-12 14:00 | 1 | 14 | 1.1199 | 1242.9141
2017-01-12 15:00 | 1 | 15 | 1.1956 | 1326.9046
2017-01-12 16:00 | 1 | 16 | 1.4599 | 1620.2033
2017-01-12 17:00 | 1 | 17 | 1.986 | 2204.0909
2017-01-12 18:00 | 1 | 18 | 2.2887 | 2539.9982
2017-01-12 19:00 | 1 | 19 | 2.2432 | 2489.553
2017-01-12 20:00 | 1 | 20 | 2.088 | 2317.242
2017-01-12 21:00 | 1 | 21 | 1.9222 | 2133.2084
2017-01-12 22:00 | 1 | 22 | 1.6057 | 1782.0521
2017-01-12 23:00 | 1 | 23 | 1.2994 | 1442.1133
2017-01-13 | 1 | 0 | 0.99707 | 1106.5453
2017-01-13 01:00 | 1 | 1 | 0.87136 | 967.0336
2017-01-13 02:00 | 1 | 2 | 0.83649 | 928.3393
2017-01-13 03:00 | 1 | 3 | 0.83481 | 926.4689
2017-01-13 04:00 | 1 | 4 | 0.82674 | 917.5191
2017-01-13 05:00 | 1 | 5 | 0.87847 | 974.9294
2017-01-13 06:00 | 1 | 6 | 1.1225 | 1245.7623
2017-01-13 07:00 | 1 | 7 | 1.4359 | 1593.6157
2017-01-13 08:00 | 1 | 8 | 1.3503 | 1498.5987
2017-01-13 09:00 | 1 | 9 | 1.138 | 1262.9549
2017-01-13 10:00 | 1 | 10 | 1.1306 | 1254.7644
2017-01-13 11:00 | 1 | 11 | 1.0853 | 1204.4716
2017-01-13 12:00 | 1 | 12 | 1.04 | 1154.2388
2017-01-13 13:00 | 1 | 13 | 1.0013 | 1111.2412
2017-01-13 14:00 | 1 | 14 | 1.0055 | 1115.894
2017-01-13 15:00 | 1 | 15 | 1.0835 | 1202.5254
2017-01-13 16:00 | 1 | 16 | 1.3503 | 1498.5686
2017-01-13 17:00 | 1 | 17 | 1.8728 | 2078.403
2017-01-13 18:00 | 1 | 18 | 2.1872 | 2427.3876
2017-01-13 19:00 | 1 | 19 | 2.1456 | 2381.2042
2017-01-13 20:00 | 1 | 20 | 1.9931 | 2211.9885
2017-01-13 21:00 | 1 | 21 | 1.8203 | 2020.156
2017-01-13 22:00 | 1 | 22 | 1.5106 | 1676.4262
2017-01-13 23:00 | 1 | 23 | 1.1911 | 1321.8451
2017-01-14 | 1 | 0 | 0.88367 | 980.7033
2017-01-14 01:00 | 1 | 1 | 0.75388 | 836.6575
2017-01-14 02:00 | 1 | 2 | 0.71257 | 790.8116
2017-01-14 03:00 | 1 | 3 | 0.68442 | 759.5663
2017-01-14 04:00 | 1 | 4 | 0.67685 | 751.1711
2017-01-14 05:00 | 1 | 5 | 0.7204 | 799.5044
2017-01-14 06:00 | 1 | 6 | 0.94732 | 1051.333
2017-01-14 07:00 | 1 | 7 | 1.2902 | 1431.8255
2017-01-14 08:00 | 1 | 8 | 1.2521 | 1389.5915
2017-01-14 09:00 | 1 | 9 | 1.0618 | 1178.3947
2017-01-14 10:00 | 1 | 10 | 1.0594 | 1175.7576
2017-01-14 11:00 | 1 | 11 | 1.0666 | 1183.7616
2017-01-14 12:00 | 1 | 12 | 1.0321 | 1145.4295
2017-01-14 13:00 | 1 | 13 | 1.0118 | 1122.9399
2017-01-14 14:00 | 1 | 14 | 0.98917 | 1097.7804
2017-01-14 15:00 | 1 | 15 | 1.0731 | 1190.9402
2017-01-14 16:00 | 1 | 16 | 1.3543 | 1502.9951
2017-01-14 17:00 | 1 | 17 | 1.883 | 2089.7165
2017-01-14 18:00 | 1 | 18 | 2.2033 | 2445.2593
2017-01-14 19:00 | 1 | 19 | 2.1755 | 2414.326
2017-01-14 20:00 | 1 | 20 | 2.0272 | 2249.8169
2017-01-14 21:00 | 1 | 21 | 1.868 | 2073.1239
2017-01-14 22:00 | 1 | 22 | 1.5501 | 1720.3067
2017-01-14 23:00 | 1 | 23 | 1.2403 | 1376.5154
2017-01-15 | 1 | 0 | 0.92023 | 1021.2685
2017-01-15 01:00 | 1 | 1 | 0.79733 | 884.8755
2017-01-15 02:00 | 1 | 2 | 0.76277 | 846.5273
2017-01-15 03:00 | 1 | 3 | 0.75522 | 838.1416
2017-01-15 04:00 | 1 | 4 | 0.75419 | 837.0028
2017-01-15 05:00 | 1 | 5 | 0.80842 | 897.1803
2017-01-15 06:00 | 1 | 6 | 1.0389 | 1152.9911
2017-01-15 07:00 | 1 | 7 | 1.3669 | 1516.9659
2017-01-15 08:00 | 1 | 8 | 1.3035 | 1446.6477
2017-01-15 09:00 | 1 | 9 | 1.1176 | 1240.2874
2017-01-15 10:00 | 1 | 10 | 1.1531 | 1279.727
2017-01-15 11:00 | 1 | 11 | 1.1328 | 1257.1741
2017-01-15 12:00 | 1 | 12 | 1.1156 | 1238.0586
2017-01-15 13:00 | 1 | 13 | 1.0806 | 1199.1964
2017-01-15 14:00 | 1 | 14 | 1.0787 | 1197.1765
2017-01-15 15:00 | 1 | 15 | 1.157 | 1284.0345
2017-01-15 16:00 | 1 | 16 | 1.4331 | 1590.4354
2017-01-15 17:00 | 1 | 17 | 1.9555 | 2170.2063
2017-01-15 18:00 | 1 | 18 | 2.2752 | 2524.9814
2017-01-15 19:00 | 1 | 19 | 2.2396 | 2485.5055
2017-01-15 20:00 | 1 | 20 | 2.0848 | 2313.7149
2017-01-15 21:00 | 1 | 21 | 1.9205 | 2131.4109
2017-01-15 22:00 | 1 | 22 | 1.6046 | 1780.8071
2017-01-15 23:00 | 1 | 23 | 1.2854 | 1426.4938
2017-01-16 | 1 | 0 | 0.9589 | 1064.1937
2017-01-16 01:00 | 1 | 1 | 0.83379 | 925.3398
2017-01-16 02:00 | 1 | 2 | 0.78801 | 874.5328
2017-01-16 03:00 | 1 | 3 | 0.77812 | 863.5571
2017-01-16 04:00 | 1 | 4 | 0.77601 | 861.2195
2017-01-16 05:00 | 1 | 5 | 0.82959 | 920.675
2017-01-16 06:00 | 1 | 6 | 1.0465 | 1161.3779
2017-01-16 07:00 | 1 | 7 | 1.3577 | 1506.7941
2017-01-16 08:00 | 1 | 8 | 1.3091 | 1452.801
2017-01-16 09:00 | 1 | 9 | 1.1241 | 1247.5783
2017-01-16 10:00 | 1 | 10 | 1.1365 | 1261.3221
2017-01-16 11:00 | 1 | 11 | 1.1151 | 1237.4988
2017-01-16 12:00 | 1 | 12 | 1.0841 | 1203.0897
2017-01-16 13:00 | 1 | 13 | 1.046 | 1160.826
2017-01-16 14:00 | 1 | 14 | 1.0419 | 1156.3318
2017-01-16 15:00 | 1 | 15 | 1.1109 | 1232.9217
2017-01-16 16:00 | 1 | 16 | 1.3735 | 1524.3101
2017-01-16 17:00 | 1 | 17 | 1.8811 | 2087.6373
2017-01-16 18:00 | 1 | 18 | 2.2184 | 2462.035
2017-01-16 19:00 | 1 | 19 | 2.1478 | 2383.6495
2017-01-16 20:00 | 1 | 20 | 1.9881 | 2206.3424
2017-01-16 21:00 | 1 | 21 | 1.8161 | 2015.4962
2017-01-16 22:00 | 1 | 22 | 1.5025 | 1667.4942
2017-01-16 23:00 | 1 | 23 | 1.1979 | 1329.3998
2017-01-17 | 1 | 0 | 0.8958 | 994.1555
2017-01-17 01:00 | 1 | 1 | 0.77969 | 865.2969
2017-01-17 02:00 | 1 | 2 | 0.73862 | 819.7261
2017-01-17 03:00 | 1 | 3 | 0.7344 | 815.039
2017-01-17 04:00 | 1 | 4 | 0.73553 | 816.2918
2017-01-17 05:00 | 1 | 5 | 0.79378 | 880.9404
2017-01-17 06:00 | 1 | 6 | 1.0276 | 1140.3784
2017-01-17 07:00 | 1 | 7 | 1.3446 | 1492.1999
2017-01-17 08:00 | 1 | 8 | 1.2932 | 1435.1415
2017-01-17 09:00 | 1 | 9 | 1.0997 | 1220.4165
2017-01-17 10:00 | 1 | 10 | 1.1185 | 1241.3648
2017-01-17 11:00 | 1 | 11 | 1.0778 | 1196.13
2017-01-17 12:00 | 1 | 12 | 1.0476 | 1162.6076
2017-01-17 13:00 | 1 | 13 | 1.0221 | 1134.351
2017-01-17 14:00 | 1 | 14 | 1.0304 | 1143.5175
2017-01-17 15:00 | 1 | 15 | 1.1261 | 1249.7695
2017-01-17 16:00 | 1 | 16 | 1.4074 | 1561.9174
2017-01-17 17:00 | 1 | 17 | 1.9535 | 2167.9562
2017-01-17 18:00 | 1 | 18 | 2.2789 | 2529.1432
2017-01-17 19:00 | 1 | 19 | 2.2338 | 2479.0587
2017-01-17 20:00 | 1 | 20 | 2.0972 | 2327.4386
2017-01-17 21:00 | 1 | 21 | 1.934 | 2146.3039
2017-01-17 22:00 | 1 | 22 | 1.6266 | 1805.2376
2017-01-17 23:00 | 1 | 23 | 1.3303 | 1476.4142
2017-01-18 | 1 | 0 | 1.0293 | 1142.3495
2017-01-18 01:00 | 1 | 1 | 0.9112 | 1011.2487
2017-01-18 02:00 | 1 | 2 | 0.87003 | 965.5616
2017-01-18 03:00 | 1 | 3 | 0.86823 | 963.567
2017-01-18 04:00 | 1 | 4 | 0.87151 | 967.1993
2017-01-18 05:00 | 1 | 5 | 0.93055 | 1032.7226
2017-01-18 06:00 | 1 | 6 | 1.1736 | 1302.4447
2017-01-18 07:00 | 1 | 7 | 1.4895 | 1653.0783
2017-01-18 08:00 | 1 | 8 | 1.4119 | 1566.9229
2017-01-18 09:00 | 1 | 9 | 1.1964 | 1327.7309
2017-01-18 10:00 | 1 | 10 | 1.2051 | 1337.411
2017-01-18 11:00 | 1 | 11 | 1.1508 | 1277.2035
2017-01-18 12:00 | 1 | 12 | 1.1123 | 1234.4014
2017-01-18 13:00 | 1 | 13 | 1.0661 | 1183.1775
2017-01-18 14:00 | 1 | 14 | 1.0666 | 1183.6735
2017-01-18 15:00 | 1 | 15 | 1.1592 | 1286.4846
2017-01-18 16:00 | 1 | 16 | 1.4398 | 1597.853
2017-01-18 17:00 | 1 | 17 | 1.9909 | 2209.4723
2017-01-18 18:00 | 1 | 18 | 2.3082 | 2561.6335
2017-01-18 19:00 | 1 | 19 | 2.2723 | 2521.7886
2017-01-18 20:00 | 1 | 20 | 2.1327 | 2366.897
2017-01-18 21:00 | 1 | 21 | 1.9739 | 2190.6705
2017-01-18 22:00 | 1 | 22 | 1.6633 | 1845.9155
2017-01-18 23:00 | 1 | 23 | 1.3663 | 1516.2844
2017-01-19 | 1 | 0 | 1.058 | 1174.1528
2017-01-19 01:00 | 1 | 1 | 0.93586 | 1038.6212
2017-01-19 02:00 | 1 | 2 | 0.8921 | 990.0507
2017-01-19 03:00 | 1 | 3 | 0.88538 | 982.597
2017-01-19 04:00 | 1 | 4 | 0.88055 | 977.2347
2017-01-19 05:00 | 1 | 5 | 0.93627 | 1039.0727
2017-01-19 06:00 | 1 | 6 | 1.1553 | 1282.1593
2017-01-19 07:00 | 1 | 7 | 1.4912 | 1654.9666
2017-01-19 08:00 | 1 | 8 | 1.4032 | 1557.2568
2017-01-19 09:00 | 1 | 9 | 1.1745 | 1303.4426
2017-01-19 10:00 | 1 | 10 | 1.174 | 1302.9389
2017-01-19 11:00 | 1 | 11 | 1.1146 | 1237.0056
2017-01-19 12:00 | 1 | 12 | 1.0704 | 1187.972
2017-01-19 13:00 | 1 | 13 | 1.0336 | 1147.105
2017-01-19 14:00 | 1 | 14 | 1.0323 | 1145.6303
2017-01-19 15:00 | 1 | 15 | 1.1137 | 1236.0177
2017-01-19 16:00 | 1 | 16 | 1.3927 | 1545.6045
2017-01-19 17:00 | 1 | 17 | 1.9339 | 2146.225
2017-01-19 18:00 | 1 | 18 | 2.2462 | 2492.804
2017-01-19 19:00 | 1 | 19 | 2.2105 | 2453.2607
2017-01-19 20:00 | 1 | 20 | 2.0594 | 2285.5781
2017-01-19 21:00 | 1 | 21 | 1.8953 | 2103.3648
2017-01-19 22:00 | 1 | 22 | 1.5887 | 1763.1147
2017-01-19 23:00 | 1 | 23 | 1.2827 | 1423.5258
2017-01-20 | 1 | 0 | 0.97618 | 1083.3644
2017-01-20 01:00 | 1 | 1 | 0.855 | 948.8806
2017-01-20 02:00 | 1 | 2 | 0.80868 | 897.4717
2017-01-20 03:00 | 1 | 3 | 0.79561 | 882.9725
2017-01-20 04:00 | 1 | 4 | 0.79176 | 878.691
2017-01-20 05:00 | 1 | 5 | 0.84129 | 933.6678
2017-01-20 06:00 | 1 | 6 | 1.0642 | 1181.0944
2017-01-20 07:00 | 1 | 7 | 1.361 | 1510.473
2017-01-20 08:00 | 1 | 8 | 1.3057 | 1449.0384
2017-01-20 09:00 | 1 | 9 | 1.1174 | 1240.1077
2017-01-20 10:00 | 1 | 10 | 1.1196 | 1242.5125
2017-01-20 11:00 | 1 | 11 | 1.1026 | 1223.68
2017-01-20 12:00 | 1 | 12 | 1.0829 | 1201.76
2017-01-20 13:00 | 1 | 13 | 1.0517 | 1167.2337
2017-01-20 14:00 | 1 | 14 | 1.0555 | 1171.4244
2017-01-20 15:00 | 1 | 15 | 1.1299 | 1253.9191
2017-01-20 16:00 | 1 | 16 | 1.3878 | 1540.1594
2017-01-20 17:00 | 1 | 17 | 1.9048 | 2113.9344
2017-01-20 18:00 | 1 | 18 | 2.2172 | 2460.6605
2017-01-20 19:00 | 1 | 19 | 2.1752 | 2414.062
2017-01-20 20:00 | 1 | 20 | 2.0277 | 2250.3254
2017-01-20 21:00 | 1 | 21 | 1.8596 | 2063.7319
2017-01-20 22:00 | 1 | 22 | 1.546 | 1715.8068
2017-01-20 23:00 | 1 | 23 | 1.2402 | 1376.4285
2017-01-21 | 1 | 0 | 0.94118 | 1044.5197
2017-01-21 01:00 | 1 | 1 | 0.81793 | 907.7362
2017-01-21 02:00 | 1 | 2 | 0.77179 | 856.5391
2017-01-21 03:00 | 1 | 3 | 0.76114 | 844.718
2017-01-21 04:00 | 1 | 4 | 0.76884 | 853.2605
2017-01-21 05:00 | 1 | 5 | 0.82072 | 910.8369
2017-01-21 06:00 | 1 | 6 | 1.0477 | 1162.7189
2017-01-21 07:00 | 1 | 7 | 1.3875 | 1539.8908
2017-01-21 08:00 | 1 | 8 | 1.3115 | 1455.4819
2017-01-21 09:00 | 1 | 9 | 1.1131 | 1235.2849
2017-01-21 10:00 | 1 | 10 | 1.1201 | 1243.062
2017-01-21 11:00 | 1 | 11 | 1.0975 | 1217.9629
2017-01-21 12:00 | 1 | 12 | 1.0793 | 1197.8194
2017-01-21 13:00 | 1 | 13 | 1.0505 | 1165.8059
2017-01-21 14:00 | 1 | 14 | 1.0512 | 1166.6776
2017-01-21 15:00 | 1 | 15 | 1.1225 | 1245.7464
2017-01-21 16:00 | 1 | 16 | 1.389 | 1541.5534
2017-01-21 17:00 | 1 | 17 | 1.909 | 2118.6245
2017-01-21 18:00 | 1 | 18 | 2.2217 | 2465.5942
2017-01-21 19:00 | 1 | 19 | 2.1814 | 2420.9017
2017-01-21 20:00 | 1 | 20 | 2.0299 | 2252.8064
2017-01-21 21:00 | 1 | 21 | 1.8637 | 2068.3448
2017-01-21 22:00 | 1 | 22 | 1.5414 | 1710.6804
2017-01-21 23:00 | 1 | 23 | 1.2262 | 1360.8709
2017-01-22 | 1 | 0 | 0.91224 | 1012.4045
2017-01-22 01:00 | 1 | 1 | 0.79024 | 877.0126
2017-01-22 02:00 | 1 | 2 | 0.74464 | 826.4
2017-01-22 03:00 | 1 | 3 | 0.73601 | 816.8215
2017-01-22 04:00 | 1 | 4 | 0.73815 | 819.2013
2017-01-22 05:00 | 1 | 5 | 0.79761 | 885.1944
2017-01-22 06:00 | 1 | 6 | 1.0245 | 1136.96
2017-01-22 07:00 | 1 | 7 | 1.3651 | 1514.9863
2017-01-22 08:00 | 1 | 8 | 1.3216 | 1466.688
2017-01-22 09:00 | 1 | 9 | 1.1412 | 1266.5131
2017-01-22 10:00 | 1 | 10 | 1.1479 | 1273.9204
2017-01-22 11:00 | 1 | 11 | 1.1187 | 1241.5184
2017-01-22 12:00 | 1 | 12 | 1.123 | 1246.3218
2017-01-22 13:00 | 1 | 13 | 1.1195 | 1242.4496
2017-01-22 14:00 | 1 | 14 | 1.1428 | 1268.2631
2017-01-22 15:00 | 1 | 15 | 1.2176 | 1351.2652
2017-01-22 16:00 | 1 | 16 | 1.5087 | 1674.3772
2017-01-22 17:00 | 1 | 17 | 2.0477 | 2272.5749
2017-01-22 18:00 | 1 | 18 | 2.3835 | 2645.158
2017-01-22 19:00 | 1 | 19 | 2.3908 | 2653.2846
2017-01-22 20:00 | 1 | 20 | 2.231 | 2475.9969
2017-01-22 21:00 | 1 | 21 | 2.0832 | 2311.9676
2017-01-22 22:00 | 1 | 22 | 1.777 | 1972.1364
2017-01-22 23:00 | 1 | 23 | 1.4757 | 1637.7704
2017-01-23 | 1 | 0 | 1.1596 | 1286.8751
2017-01-23 01:00 | 1 | 1 | 1.028 | 1140.9131
2017-01-23 02:00 | 1 | 2 | 0.98001 | 1087.6222
2017-01-23 03:00 | 1 | 3 | 0.97197 | 1078.6953
2017-01-23 04:00 | 1 | 4 | 0.95943 | 1064.7714
2017-01-23 05:00 | 1 | 5 | 1.0211 | 1133.2132
2017-01-23 06:00 | 1 | 6 | 1.2566 | 1394.5648
2017-01-23 07:00 | 1 | 7 | 1.5307 | 1698.7745
2017-01-23 08:00 | 1 | 8 | 1.459 | 1619.1588
2017-01-23 09:00 | 1 | 9 | 1.2341 | 1369.6154
2017-01-23 10:00 | 1 | 10 | 1.2417 | 1378.0664
2017-01-23 11:00 | 1 | 11 | 1.1944 | 1325.5733
2017-01-23 12:00 | 1 | 12 | 1.145 | 1270.673
2017-01-23 13:00 | 1 | 13 | 1.1104 | 1232.3321
2017-01-23 14:00 | 1 | 14 | 1.1043 | 1225.5876
2017-01-23 15:00 | 1 | 15 | 1.1832 | 1313.1156
2017-01-23 16:00 | 1 | 16 | 1.4624 | 1623.0013
2017-01-23 17:00 | 1 | 17 | 2.0001 | 2219.6949
2017-01-23 18:00 | 1 | 18 | 2.3105 | 2564.2211
2017-01-23 19:00 | 1 | 19 | 2.273 | 2522.6271
2017-01-23 20:00 | 1 | 20 | 2.1246 | 2357.8716
2017-01-23 21:00 | 1 | 21 | 1.9614 | 2176.7949
2017-01-23 22:00 | 1 | 22 | 1.6448 | 1825.4166
2017-01-23 23:00 | 1 | 23 | 1.3345 | 1481.0469
2017-01-24 | 1 | 0 | 1.0333 | 1146.775
2017-01-24 01:00 | 1 | 1 | 0.912 | 1012.1422
2017-01-24 02:00 | 1 | 2 | 0.86338 | 958.178
2017-01-24 03:00 | 1 | 3 | 0.85026 | 943.623
2017-01-24 04:00 | 1 | 4 | 0.84763 | 940.696
2017-01-24 05:00 | 1 | 5 | 0.89863 | 997.3008
2017-01-24 06:00 | 1 | 6 | 1.1139 | 1236.1758
2017-01-24 07:00 | 1 | 7 | 1.4481 | 1607.1438
2017-01-24 08:00 | 1 | 8 | 1.3807 | 1532.2539
2017-01-24 09:00 | 1 | 9 | 1.1942 | 1325.324
2017-01-24 10:00 | 1 | 10 | 1.2278 | 1362.5857
2017-01-24 11:00 | 1 | 11 | 1.1957 | 1326.9383
2017-01-24 12:00 | 1 | 12 | 1.164 | 1291.7765
2017-01-24 13:00 | 1 | 13 | 1.1346 | 1259.1784
2017-01-24 14:00 | 1 | 14 | 1.1348 | 1259.3985
2017-01-24 15:00 | 1 | 15 | 1.2028 | 1334.8979
2017-01-24 16:00 | 1 | 16 | 1.4664 | 1627.3925
2017-01-24 17:00 | 1 | 17 | 1.9903 | 2208.8502
2017-01-24 18:00 | 1 | 18 | 2.2894 | 2540.7739
2017-01-24 19:00 | 1 | 19 | 2.2439 | 2490.2724
2017-01-24 20:00 | 1 | 20 | 2.0891 | 2318.4458
2017-01-24 21:00 | 1 | 21 | 1.9262 | 2137.7022
2017-01-24 22:00 | 1 | 22 | 1.6102 | 1786.957
2017-01-24 23:00 | 1 | 23 | 1.3004 | 1443.1652
2017-01-25 | 1 | 0 | 0.99339 | 1102.4695
2017-01-25 01:00 | 1 | 1 | 0.87225 | 968.0245
2017-01-25 02:00 | 1 | 2 | 0.82403 | 914.5121
2017-01-25 03:00 | 1 | 3 | 0.81035 | 899.3305
2017-01-25 04:00 | 1 | 4 | 0.80766 | 896.3437
2017-01-25 05:00 | 1 | 5 | 0.86224 | 956.9103
2017-01-25 06:00 | 1 | 6 | 1.0951 | 1215.3361
2017-01-25 07:00 | 1 | 7 | 1.3854 | 1537.4715
2017-01-25 08:00 | 1 | 8 | 1.3194 | 1464.2614
2017-01-25 09:00 | 1 | 9 | 1.1135 | 1235.7892
2017-01-25 10:00 | 1 | 10 | 1.1295 | 1253.5029
2017-01-25 11:00 | 1 | 11 | 1.1089 | 1230.6477
2017-01-25 12:00 | 1 | 12 | 1.0775 | 1195.7628
2017-01-25 13:00 | 1 | 13 | 1.0475 | 1162.4777
2017-01-25 14:00 | 1 | 14 | 1.0413 | 1155.6555
2017-01-25 15:00 | 1 | 15 | 1.1166 | 1239.1712
2017-01-25 16:00 | 1 | 16 | 1.3844 | 1536.3834
2017-01-25 17:00 | 1 | 17 | 1.9071 | 2116.4573
2017-01-25 18:00 | 1 | 18 | 2.2149 | 2458.0514
2017-01-25 19:00 | 1 | 19 | 2.1683 | 2406.4321
2017-01-25 20:00 | 1 | 20 | 2.0122 | 2233.1742
2017-01-25 21:00 | 1 | 21 | 1.8415 | 2043.6667
2017-01-25 22:00 | 1 | 22 | 1.5276 | 1695.2938
2017-01-25 23:00 | 1 | 23 | 1.2143 | 1347.5914
2017-01-26 | 1 | 0 | 0.90497 | 1004.3397
2017-01-26 01:00 | 1 | 1 | 0.77776 | 863.1574
2017-01-26 02:00 | 1 | 2 | 0.72973 | 809.8609
2017-01-26 03:00 | 1 | 3 | 0.7172 | 795.9519
2017-01-26 04:00 | 1 | 4 | 0.70911 | 786.9748
2017-01-26 05:00 | 1 | 5 | 0.76068 | 844.2034
2017-01-26 06:00 | 1 | 6 | 0.97522 | 1082.3061
2017-01-26 07:00 | 1 | 7 | 1.3022 | 1445.1917
2017-01-26 08:00 | 1 | 8 | 1.2376 | 1373.4371
2017-01-26 09:00 | 1 | 9 | 1.0604 | 1176.8673
2017-01-26 10:00 | 1 | 10 | 1.0755 | 1193.6198
2017-01-26 11:00 | 1 | 11 | 1.0575 | 1173.5659
2017-01-26 12:00 | 1 | 12 | 1.0308 | 1143.9622
2017-01-26 13:00 | 1 | 13 | 1.0028 | 1112.9298
2017-01-26 14:00 | 1 | 14 | 1.0003 | 1110.1004
2017-01-26 15:00 | 1 | 15 | 1.0696 | 1187.069
2017-01-26 16:00 | 1 | 16 | 1.3345 | 1481.0084
2017-01-26 17:00 | 1 | 17 | 1.8501 | 2053.1912
2017-01-26 18:00 | 1 | 18 | 2.1618 | 2399.1319
2017-01-26 19:00 | 1 | 19 | 2.1242 | 2357.4158
2017-01-26 20:00 | 1 | 20 | 1.9717 | 2188.2032
2017-01-26 21:00 | 1 | 21 | 1.8045 | 2002.5932
2017-01-26 22:00 | 1 | 22 | 1.4897 | 1653.2331
2017-01-26 23:00 | 1 | 23 | 1.1785 | 1307.8693
2017-01-27 | 1 | 0 | 0.86867 | 964.0521
2017-01-27 01:00 | 1 | 1 | 0.73251 | 812.9373
2017-01-27 02:00 | 1 | 2 | 0.67681 | 751.122
2017-01-27 03:00 | 1 | 3 | 0.66318 | 735.998
2017-01-27 04:00 | 1 | 4 | 0.6565 | 728.5807
2017-01-27 05:00 | 1 | 5 | 0.70258 | 779.7277
2017-01-27 06:00 | 1 | 6 | 0.91688 | 1017.552
2017-01-27 07:00 | 1 | 7 | 1.2338 | 1369.2532
2017-01-27 08:00 | 1 | 8 | 1.1774 | 1306.6954
2017-01-27 09:00 | 1 | 9 | 0.99631 | 1105.7016
2017-01-27 10:00 | 1 | 10 | 0.99714 | 1106.6311
2017-01-27 11:00 | 1 | 11 | 0.99914 | 1108.8422
2017-01-27 12:00 | 1 | 12 | 0.97572 | 1082.8504
2017-01-27 13:00 | 1 | 13 | 0.95566 | 1060.5898
2017-01-27 14:00 | 1 | 14 | 0.95697 | 1062.0479
2017-01-27 15:00 | 1 | 15 | 1.0291 | 1142.0533
2017-01-27 16:00 | 1 | 16 | 1.2914 | 1433.1679
2017-01-27 17:00 | 1 | 17 | 1.7934 | 1990.3296
2017-01-27 18:00 | 1 | 18 | 2.1315 | 2365.4897
2017-01-27 19:00 | 1 | 19 | 2.0749 | 2302.7784
2017-01-27 20:00 | 1 | 20 | 1.9179 | 2128.5062
2017-01-27 21:00 | 1 | 21 | 1.7465 | 1938.3175
2017-01-27 22:00 | 1 | 22 | 1.4285 | 1585.3487
2017-01-27 23:00 | 1 | 23 | 1.1187 | 1241.4877
2017-01-28 | 1 | 0 | 0.82683 | 917.6138
2017-01-28 01:00 | 1 | 1 | 0.7031 | 780.2961
2017-01-28 02:00 | 1 | 2 | 0.66388 | 736.7804
2017-01-28 03:00 | 1 | 3 | 0.65954 | 731.9534
2017-01-28 04:00 | 1 | 4 | 0.66291 | 735.6987
2017-01-28 05:00 | 1 | 5 | 0.71642 | 795.0888
2017-01-28 06:00 | 1 | 6 | 0.95564 | 1060.5679
2017-01-28 07:00 | 1 | 7 | 1.2739 | 1413.7599
2017-01-28 08:00 | 1 | 8 | 1.2418 | 1378.1132
2017-01-28 09:00 | 1 | 9 | 1.0793 | 1197.819
2017-01-28 10:00 | 1 | 10 | 1.1028 | 1223.886
2017-01-28 11:00 | 1 | 11 | 1.1297 | 1253.7416
2017-01-28 12:00 | 1 | 12 | 1.084 | 1203.0159
2017-01-28 13:00 | 1 | 13 | 1.0403 | 1154.5071
2017-01-28 14:00 | 1 | 14 | 1.0452 | 1159.9189
2017-01-28 15:00 | 1 | 15 | 1.1106 | 1232.5716
2017-01-28 16:00 | 1 | 16 | 1.385 | 1537.1242
2017-01-28 17:00 | 1 | 17 | 1.9103 | 2120.1088
2017-01-28 18:00 | 1 | 18 | 2.2338 | 2479.0492
2017-01-28 19:00 | 1 | 19 | 2.1971 | 2438.347
2017-01-28 20:00 | 1 | 20 | 2.0501 | 2275.1822
2017-01-28 21:00 | 1 | 21 | 1.8884 | 2095.7377
2017-01-28 22:00 | 1 | 22 | 1.5673 | 1739.3605
2017-01-28 23:00 | 1 | 23 | 1.2481 | 1385.1879
2017-01-29 | 1 | 0 | 0.93377 | 1036.3004
2017-01-29 01:00 | 1 | 1 | 0.808 | 896.7224
2017-01-29 02:00 | 1 | 2 | 0.76009 | 843.5519
2017-01-29 03:00 | 1 | 3 | 0.74957 | 831.8732
2017-01-29 04:00 | 1 | 4 | 0.74755 | 829.6349
2017-01-29 05:00 | 1 | 5 | 0.79919 | 886.9388
2017-01-29 06:00 | 1 | 6 | 1.018 | 1129.8136
2017-01-29 07:00 | 1 | 7 | 1.3587 | 1507.9069
2017-01-29 08:00 | 1 | 8 | 1.3054 | 1448.6848
2017-01-29 09:00 | 1 | 9 | 1.1236 | 1246.9369
2017-01-29 10:00 | 1 | 10 | 1.1189 | 1241.8035
2017-01-29 11:00 | 1 | 11 | 1.0871 | 1206.4906
2017-01-29 12:00 | 1 | 12 | 1.0611 | 1177.6434
2017-01-29 13:00 | 1 | 13 | 1.0307 | 1143.8723
2017-01-29 14:00 | 1 | 14 | 1.0319 | 1145.2487
2017-01-29 15:00 | 1 | 15 | 1.1127 | 1234.9285
2017-01-29 16:00 | 1 | 16 | 1.3733 | 1524.0564
2017-01-29 17:00 | 1 | 17 | 1.89 | 2097.5615
2017-01-29 18:00 | 1 | 18 | 2.2074 | 2449.7931
2017-01-29 19:00 | 1 | 19 | 2.166 | 2403.8072
2017-01-29 20:00 | 1 | 20 | 2.0139 | 2234.9994
2017-01-29 21:00 | 1 | 21 | 1.847 | 2049.7907
2017-01-29 22:00 | 1 | 22 | 1.5243 | 1691.7112
2017-01-29 23:00 | 1 | 23 | 1.2085 | 1341.183
2017-01-30 | 1 | 0 | 0.89116 | 989.0102
2017-01-30 01:00 | 1 | 1 | 0.77583 | 861.0135
2017-01-30 02:00 | 1 | 2 | 0.73739 | 818.3529
2017-01-30 03:00 | 1 | 3 | 0.72978 | 809.9062
2017-01-30 04:00 | 1 | 4 | 0.7327 | 813.1561
2017-01-30 05:00 | 1 | 5 | 0.79105 | 877.9137
2017-01-30 06:00 | 1 | 6 | 1.0245 | 1136.9463
2017-01-30 07:00 | 1 | 7 | 1.3389 | 1485.9642
2017-01-30 08:00 | 1 | 8 | 1.2611 | 1399.612
2017-01-30 09:00 | 1 | 9 | 1.0542 | 1169.9742
2017-01-30 10:00 | 1 | 10 | 1.0576 | 1173.7355
2017-01-30 11:00 | 1 | 11 | 1.0407 | 1154.9907
2017-01-30 12:00 | 1 | 12 | 1.0169 | 1128.5623
2017-01-30 13:00 | 1 | 13 | 0.99539 | 1104.6879
2017-01-30 14:00 | 1 | 14 | 1.0024 | 1112.4942
2017-01-30 15:00 | 1 | 15 | 1.0876 | 1207.002
2017-01-30 16:00 | 1 | 16 | 1.3589 | 1508.1507
2017-01-30 17:00 | 1 | 17 | 1.8851 | 2092.0525
2017-01-30 18:00 | 1 | 18 | 2.1997 | 2441.2049
2017-01-30 19:00 | 1 | 19 | 2.1646 | 2402.3179
2017-01-30 20:00 | 1 | 20 | 2.0186 | 2240.2838
2017-01-30 21:00 | 1 | 21 | 1.8576 | 2061.5464
2017-01-30 22:00 | 1 | 22 | 1.5502 | 1720.4238
2017-01-30 23:00 | 1 | 23 | 1.2481 | 1385.1798
2017-01-31 | 1 | 0 | 0.94975 | 1054.0378
2017-01-31 01:00 | 1 | 1 | 0.83027 | 921.4298
2017-01-31 02:00 | 1 | 2 | 0.7901 | 876.8591
2017-01-31 03:00 | 1 | 3 | 0.78536 | 871.5935
2017-01-31 04:00 | 1 | 4 | 0.78833 | 874.8927
2017-01-31 05:00 | 1 | 5 | 0.84763 | 940.7039
2017-01-31 06:00 | 1 | 6 | 1.0861 | 1205.3787
2017-01-31 07:00 | 1 | 7 | 1.399 | 1552.6316
2017-01-31 08:00 | 1 | 8 | 1.312 | 1456.0062
2017-01-31 09:00 | 1 | 9 | 1.1038 | 1225.0165
2017-01-31 10:00 | 1 | 10 | 1.1039 | 1225.0856
2017-01-31 11:00 | 1 | 11 | 1.0645 | 1181.3611
2017-01-31 12:00 | 1 | 12 | 1.0269 | 1139.69
2017-01-31 13:00 | 1 | 13 | 0.99892 | 1108.6061
2017-01-31 14:00 | 1 | 14 | 1.0053 | 1115.7237
2017-01-31 15:00 | 1 | 15 | 1.0858 | 1205.0264
2017-01-31 16:00 | 1 | 16 | 1.3596 | 1508.9029
2017-01-31 17:00 | 1 | 17 | 1.8849 | 2091.8662
2017-01-31 18:00 | 1 | 18 | 2.202 | 2443.7305
2017-01-31 19:00 | 1 | 19 | 2.1662 | 2404.0791
2017-01-31 20:00 | 1 | 20 | 2.0156 | 2236.941
2017-01-31 21:00 | 1 | 21 | 1.8545 | 2058.18
2017-01-31 22:00 | 1 | 22 | 1.5484 | 1718.4208
2017-01-31 23:00 | 1 | 23 | 1.249 | 1386.1312
2017-02-01 | 2 | 0 | 0.95108 | 1055.5094
2017-02-01 01:00 | 2 | 1 | 0.84182 | 934.2521
2017-02-01 02:00 | 2 | 2 | 0.80477 | 893.139
2017-02-01 03:00 | 2 | 3 | 0.80752 | 896.1835
2017-02-01 04:00 | 2 | 4 | 0.81324 | 902.5338
2017-02-01 05:00 | 2 | 5 | 0.87601 | 972.1991
2017-02-01 06:00 | 2 | 6 | 1.0761 | 1194.229
2017-02-01 07:00 | 2 | 7 | 1.3501 | 1498.3768
2017-02-01 08:00 | 2 | 8 | 1.2815 | 1422.2581
2017-02-01 09:00 | 2 | 9 | 1.1038 | 1224.9464
2017-02-01 10:00 | 2 | 10 | 1.1119 | 1233.9941
2017-02-01 11:00 | 2 | 11 | 1.0742 | 1192.1004
2017-02-01 12:00 | 2 | 12 | 1.0287 | 1141.6891
2017-02-01 13:00 | 2 | 13 | 1.0202 | 1132.2413
2017-02-01 14:00 | 2 | 14 | 1.0274 | 1140.1556
2017-02-01 15:00 | 2 | 15 | 1.0948 | 1215.0334
2017-02-01 16:00 | 2 | 16 | 1.304 | 1447.1433
2017-02-01 17:00 | 2 | 17 | 1.7405 | 1931.6224
2017-02-01 18:00 | 2 | 18 | 2.0503 | 2275.4567
2017-02-01 19:00 | 2 | 19 | 2.1661 | 2403.9234
2017-02-01 20:00 | 2 | 20 | 2.0971 | 2327.3621
2017-02-01 21:00 | 2 | 21 | 1.9223 | 2133.3777
2017-02-01 22:00 | 2 | 22 | 1.6079 | 1784.4004
2017-02-01 23:00 | 2 | 23 | 1.3151 | 1459.4457
2017-02-02 | 2 | 0 | 1.0108 | 1121.7581
2017-02-02 01:00 | 2 | 1 | 0.88823 | 985.7646
2017-02-02 02:00 | 2 | 2 | 0.83825 | 930.2966
2017-02-02 03:00 | 2 | 3 | 0.82977 | 920.8762
2017-02-02 04:00 | 2 | 4 | 0.83921 | 931.3621
2017-02-02 05:00 | 2 | 5 | 0.90619 | 1005.6866
2017-02-02 06:00 | 2 | 6 | 1.0982 | 1218.7982
2017-02-02 07:00 | 2 | 7 | 1.3723 | 1522.9691
2017-02-02 08:00 | 2 | 8 | 1.2791 | 1419.5629
2017-02-02 09:00 | 2 | 9 | 1.1067 | 1228.2721
2017-02-02 10:00 | 2 | 10 | 1.1215 | 1244.6626
2017-02-02 11:00 | 2 | 11 | 1.0826 | 1201.521
2017-02-02 12:00 | 2 | 12 | 1.0379 | 1151.8455
2017-02-02 13:00 | 2 | 13 | 1.0068 | 1117.3109
2017-02-02 14:00 | 2 | 14 | 0.99881 | 1108.484
2017-02-02 15:00 | 2 | 15 | 1.0594 | 1175.6783
2017-02-02 16:00 | 2 | 16 | 1.2741 | 1413.9492
2017-02-02 17:00 | 2 | 17 | 1.7183 | 1906.9693
2017-02-02 18:00 | 2 | 18 | 2.0357 | 2259.1901
2017-02-02 19:00 | 2 | 19 | 2.1504 | 2386.5173
2017-02-02 20:00 | 2 | 20 | 2.0782 | 2306.3588
2017-02-02 21:00 | 2 | 21 | 1.9022 | 2111.061
2017-02-02 22:00 | 2 | 22 | 1.5846 | 1758.5457
2017-02-02 23:00 | 2 | 23 | 1.289 | 1430.5059
2017-02-03 | 2 | 0 | 0.97796 | 1085.3408
2017-02-03 01:00 | 2 | 1 | 0.86283 | 957.5744
2017-02-03 02:00 | 2 | 2 | 0.81424 | 903.644
2017-02-03 03:00 | 2 | 3 | 0.80435 | 892.6671
2017-02-03 04:00 | 2 | 4 | 0.80052 | 888.4193
2017-02-03 05:00 | 2 | 5 | 0.85673 | 950.8042
2017-02-03 06:00 | 2 | 6 | 1.0649 | 1181.8825
2017-02-03 07:00 | 2 | 7 | 1.3285 | 1474.3566
2017-02-03 08:00 | 2 | 8 | 1.2597 | 1398.0474
2017-02-03 09:00 | 2 | 9 | 1.0968 | 1217.2482
2017-02-03 10:00 | 2 | 10 | 1.1084 | 1230.0507
2017-02-03 11:00 | 2 | 11 | 1.0785 | 1196.9201
2017-02-03 12:00 | 2 | 12 | 1.0475 | 1162.5654
2017-02-03 13:00 | 2 | 13 | 1.0129 | 1124.1689
2017-02-03 14:00 | 2 | 14 | 1.0103 | 1121.1999
2017-02-03 15:00 | 2 | 15 | 1.063 | 1179.6905
2017-02-03 16:00 | 2 | 16 | 1.2653 | 1404.1803
2017-02-03 17:00 | 2 | 17 | 1.6913 | 1876.9881
2017-02-03 18:00 | 2 | 18 | 2.0049 | 2225.0194
2017-02-03 19:00 | 2 | 19 | 2.1136 | 2345.6264
2017-02-03 20:00 | 2 | 20 | 2.0326 | 2255.8228
2017-02-03 21:00 | 2 | 21 | 1.8531 | 2056.5892
2017-02-03 22:00 | 2 | 22 | 1.5341 | 1702.4944
2017-02-03 23:00 | 2 | 23 | 1.2368 | 1372.6557
2017-02-04 | 2 | 0 | 0.93221 | 1034.5651
2017-02-04 01:00 | 2 | 1 | 0.81142 | 900.5178
2017-02-04 02:00 | 2 | 2 | 0.76294 | 846.7175
2017-02-04 03:00 | 2 | 3 | 0.75492 | 837.8158
2017-02-04 04:00 | 2 | 4 | 0.75406 | 836.8607
2017-02-04 05:00 | 2 | 5 | 0.82672 | 917.4926
2017-02-04 06:00 | 2 | 6 | 1.0342 | 1147.775
2017-02-04 07:00 | 2 | 7 | 1.3259 | 1471.4783
2017-02-04 08:00 | 2 | 8 | 1.2473 | 1384.2196
2017-02-04 09:00 | 2 | 9 | 1.0877 | 1207.1536
2017-02-04 10:00 | 2 | 10 | 1.1132 | 1235.3853
2017-02-04 11:00 | 2 | 11 | 1.0792 | 1197.6932
2017-02-04 12:00 | 2 | 12 | 1.0311 | 1144.3476
2017-02-04 13:00 | 2 | 13 | 0.99536 | 1104.6534
2017-02-04 14:00 | 2 | 14 | 0.98501 | 1093.165
2017-02-04 15:00 | 2 | 15 | 1.047 | 1161.9819
2017-02-04 16:00 | 2 | 16 | 1.2643 | 1403.0768
2017-02-04 17:00 | 2 | 17 | 1.701 | 1887.8124
2017-02-04 18:00 | 2 | 18 | 2.0176 | 2239.1647
2017-02-04 19:00 | 2 | 19 | 2.1312 | 2365.2082
2017-02-04 20:00 | 2 | 20 | 2.0551 | 2280.741
2017-02-04 21:00 | 2 | 21 | 1.8786 | 2084.8919
2017-02-04 22:00 | 2 | 22 | 1.5563 | 1727.1724
2017-02-04 23:00 | 2 | 23 | 1.2437 | 1380.2824
2017-02-05 | 2 | 0 | 0.92277 | 1024.0888
2017-02-05 01:00 | 2 | 1 | 0.805 | 893.3937
2017-02-05 02:00 | 2 | 2 | 0.75885 | 842.1718
2017-02-05 03:00 | 2 | 3 | 0.75321 | 835.9096
2017-02-05 04:00 | 2 | 4 | 0.75257 | 835.1986
2017-02-05 05:00 | 2 | 5 | 0.81512 | 904.6218
2017-02-05 06:00 | 2 | 6 | 1.0105 | 1121.4366
2017-02-05 07:00 | 2 | 7 | 1.3226 | 1467.8013
2017-02-05 08:00 | 2 | 8 | 1.2482 | 1385.3015
2017-02-05 09:00 | 2 | 9 | 1.1044 | 1225.7037
2017-02-05 10:00 | 2 | 10 | 1.1365 | 1261.2833
2017-02-05 11:00 | 2 | 11 | 1.1213 | 1244.4624
2017-02-05 12:00 | 2 | 12 | 1.0846 | 1203.7138
2017-02-05 13:00 | 2 | 13 | 1.055 | 1170.8142
2017-02-05 14:00 | 2 | 14 | 1.0517 | 1167.1409
2017-02-05 15:00 | 2 | 15 | 1.1046 | 1225.9146
2017-02-05 16:00 | 2 | 16 | 1.3068 | 1450.3137
2017-02-05 17:00 | 2 | 17 | 1.7395 | 1930.4843
2017-02-05 18:00 | 2 | 18 | 2.0515 | 2276.7038
2017-02-05 19:00 | 2 | 19 | 2.1645 | 2402.1959
2017-02-05 20:00 | 2 | 20 | 2.0859 | 2314.8956
2017-02-05 21:00 | 2 | 21 | 1.9121 | 2122.0012
2017-02-05 22:00 | 2 | 22 | 1.5836 | 1757.526
2017-02-05 23:00 | 2 | 23 | 1.2708 | 1410.3548
2017-02-06 | 2 | 0 | 0.94286 | 1046.3835
2017-02-06 01:00 | 2 | 1 | 0.82494 | 915.5226
2017-02-06 02:00 | 2 | 2 | 0.7912 | 878.0776
2017-02-06 03:00 | 2 | 3 | 0.79112 | 877.9834
2017-02-06 04:00 | 2 | 4 | 0.79128 | 878.1645
2017-02-06 05:00 | 2 | 5 | 0.86423 | 959.1211
2017-02-06 06:00 | 2 | 6 | 1.0768 | 1195.0335
2017-02-06 07:00 | 2 | 7 | 1.3631 | 1512.7444
2017-02-06 08:00 | 2 | 8 | 1.2618 | 1400.3941
2017-02-06 09:00 | 2 | 9 | 1.0837 | 1202.7233
2017-02-06 10:00 | 2 | 10 | 1.1035 | 1224.697
2017-02-06 11:00 | 2 | 11 | 1.0683 | 1185.5683
2017-02-06 12:00 | 2 | 12 | 1.0354 | 1149.0696
2017-02-06 13:00 | 2 | 13 | 0.99873 | 1108.3898
2017-02-06 14:00 | 2 | 14 | 1.0013 | 1111.2533
2017-02-06 15:00 | 2 | 15 | 1.0792 | 1197.7056
2017-02-06 16:00 | 2 | 16 | 1.3157 | 1460.1168
2017-02-06 17:00 | 2 | 17 | 1.755 | 1947.6574
2017-02-06 18:00 | 2 | 18 | 2.0726 | 2300.2165
2017-02-06 19:00 | 2 | 19 | 2.1906 | 2431.1841
2017-02-06 20:00 | 2 | 20 | 2.1124 | 2344.4003
2017-02-06 21:00 | 2 | 21 | 1.9379 | 2150.6771
2017-02-06 22:00 | 2 | 22 | 1.6167 | 1794.2546
2017-02-06 23:00 | 2 | 23 | 1.3221 | 1467.2426
2017-02-07 | 2 | 0 | 1.011 | 1121.9813
2017-02-07 01:00 | 2 | 1 | 0.89219 | 990.1545
2017-02-07 02:00 | 2 | 2 | 0.83912 | 931.2572
2017-02-07 03:00 | 2 | 3 | 0.82283 | 913.1829
2017-02-07 04:00 | 2 | 4 | 0.81828 | 908.1286
2017-02-07 05:00 | 2 | 5 | 0.88143 | 978.2115
2017-02-07 06:00 | 2 | 6 | 1.0667 | 1183.8257
2017-02-07 07:00 | 2 | 7 | 1.3511 | 1499.469
2017-02-07 08:00 | 2 | 8 | 1.28 | 1420.5609
2017-02-07 09:00 | 2 | 9 | 1.1165 | 1239.1387
2017-02-07 10:00 | 2 | 10 | 1.1254 | 1248.977
2017-02-07 11:00 | 2 | 11 | 1.0811 | 1199.7724
2017-02-07 12:00 | 2 | 12 | 1.0323 | 1145.6492
2017-02-07 13:00 | 2 | 13 | 1.0017 | 1111.7321
2017-02-07 14:00 | 2 | 14 | 0.99259 | 1101.5788
2017-02-07 15:00 | 2 | 15 | 1.0537 | 1169.4173
2017-02-07 16:00 | 2 | 16 | 1.275 | 1415.0306
2017-02-07 17:00 | 2 | 17 | 1.7212 | 1910.2258
2017-02-07 18:00 | 2 | 18 | 2.035 | 2258.4332
2017-02-07 19:00 | 2 | 19 | 2.1508 | 2386.9919
2017-02-07 20:00 | 2 | 20 | 2.0834 | 2312.2123
2017-02-07 21:00 | 2 | 21 | 1.9114 | 2121.2702
2017-02-07 22:00 | 2 | 22 | 1.5986 | 1774.0893
2017-02-07 23:00 | 2 | 23 | 1.3048 | 1448.0762
2017-02-08 | 2 | 0 | 0.99456 | 1103.7621
2017-02-08 01:00 | 2 | 1 | 0.87852 | 974.9776
2017-02-08 02:00 | 2 | 2 | 0.82732 | 918.1642
2017-02-08 03:00 | 2 | 3 | 0.81571 | 905.2781
2017-02-08 04:00 | 2 | 4 | 0.81587 | 905.4545
2017-02-08 05:00 | 2 | 5 | 0.88159 | 978.3876
2017-02-08 06:00 | 2 | 6 | 1.0691 | 1186.529
2017-02-08 07:00 | 2 | 7 | 1.3485 | 1496.5129
2017-02-08 08:00 | 2 | 8 | 1.2603 | 1398.6873
2017-02-08 09:00 | 2 | 9 | 1.0843 | 1203.3583
2017-02-08 10:00 | 2 | 10 | 1.0819 | 1200.6879
2017-02-08 11:00 | 2 | 11 | 1.0445 | 1159.1954
2017-02-08 12:00 | 2 | 12 | 1.0021 | 1112.1168
2017-02-08 13:00 | 2 | 13 | 0.9582 | 1063.4142
2017-02-08 14:00 | 2 | 14 | 0.95976 | 1065.1474
2017-02-08 15:00 | 2 | 15 | 1.0207 | 1132.8047
2017-02-08 16:00 | 2 | 16 | 1.2397 | 1375.8112
2017-02-08 17:00 | 2 | 17 | 1.6842 | 1869.1186
2017-02-08 18:00 | 2 | 18 | 2.0015 | 2221.2972
2017-02-08 19:00 | 2 | 19 | 2.1192 | 2351.8793
2017-02-08 20:00 | 2 | 20 | 2.0487 | 2273.7047
2017-02-08 21:00 | 2 | 21 | 1.8745 | 2080.2912
2017-02-08 22:00 | 2 | 22 | 1.5575 | 1728.5405
2017-02-08 23:00 | 2 | 23 | 1.2642 | 1403.002
2017-02-09 | 2 | 0 | 0.95183 | 1056.337
2017-02-09 01:00 | 2 | 1 | 0.83713 | 929.0471
2017-02-09 02:00 | 2 | 2 | 0.79513 | 882.4319
2017-02-09 03:00 | 2 | 3 | 0.78538 | 871.6107
2017-02-09 04:00 | 2 | 4 | 0.78391 | 869.9804
2017-02-09 05:00 | 2 | 5 | 0.8462 | 939.1171
2017-02-09 06:00 | 2 | 6 | 1.038 | 1151.9589
2017-02-09 07:00 | 2 | 7 | 1.3394 | 1486.5177
2017-02-09 08:00 | 2 | 8 | 1.2354 | 1371.0583
2017-02-09 09:00 | 2 | 9 | 1.0604 | 1176.8748
2017-02-09 10:00 | 2 | 10 | 1.0619 | 1178.4835
2017-02-09 11:00 | 2 | 11 | 1.0275 | 1140.273
2017-02-09 12:00 | 2 | 12 | 0.99568 | 1105.0125
2017-02-09 13:00 | 2 | 13 | 0.97262 | 1079.4192
2017-02-09 14:00 | 2 | 14 | 0.97097 | 1077.5839
2017-02-09 15:00 | 2 | 15 | 1.0279 | 1140.8091
2017-02-09 16:00 | 2 | 16 | 1.24 | 1376.1466
2017-02-09 17:00 | 2 | 17 | 1.6834 | 1868.2515
2017-02-09 18:00 | 2 | 18 | 2.0015 | 2221.2512
2017-02-09 19:00 | 2 | 19 | 2.1149 | 2347.0838
2017-02-09 20:00 | 2 | 20 | 2.0424 | 2266.6082
2017-02-09 21:00 | 2 | 21 | 1.8629 | 2067.4598
2017-02-09 22:00 | 2 | 22 | 1.5399 | 1709.0378
2017-02-09 23:00 | 2 | 23 | 1.2358 | 1371.5345
2017-02-10 | 2 | 0 | 0.91627 | 1016.8805
2017-02-10 01:00 | 2 | 1 | 0.79497 | 882.2621
2017-02-10 02:00 | 2 | 2 | 0.74448 | 826.2228
2017-02-10 03:00 | 2 | 3 | 0.73381 | 814.3819
2017-02-10 04:00 | 2 | 4 | 0.73007 | 810.2316
2017-02-10 05:00 | 2 | 5 | 0.79225 | 879.2419
2017-02-10 06:00 | 2 | 6 | 0.98122 | 1088.9558
2017-02-10 07:00 | 2 | 7 | 1.2652 | 1404.0988
2017-02-10 08:00 | 2 | 8 | 1.2036 | 1335.7395
2017-02-10 09:00 | 2 | 9 | 1.0191 | 1131.0008
2017-02-10 10:00 | 2 | 10 | 1.0134 | 1124.7009
2017-02-10 11:00 | 2 | 11 | 0.99445 | 1103.6447
2017-02-10 12:00 | 2 | 12 | 0.95809 | 1063.2943
2017-02-10 13:00 | 2 | 13 | 0.92626 | 1027.9692
2017-02-10 14:00 | 2 | 14 | 0.92322 | 1024.5947
2017-02-10 15:00 | 2 | 15 | 0.98302 | 1090.9604
2017-02-10 16:00 | 2 | 16 | 1.1952 | 1326.4499
2017-02-10 17:00 | 2 | 17 | 1.6336 | 1812.9692
2017-02-10 18:00 | 2 | 18 | 1.9566 | 2171.4769
2017-02-10 19:00 | 2 | 19 | 2.0772 | 2305.2961
2017-02-10 20:00 | 2 | 20 | 2.0041 | 2224.1282
2017-02-10 21:00 | 2 | 21 | 1.8298 | 2030.7227
2017-02-10 22:00 | 2 | 22 | 1.518 | 1684.6774
2017-02-10 23:00 | 2 | 23 | 1.2279 | 1362.6762
2017-02-11 | 2 | 0 | 0.92649 | 1028.2172
2017-02-11 01:00 | 2 | 1 | 0.8059 | 894.3859
2017-02-11 02:00 | 2 | 2 | 0.75464 | 837.5045
2017-02-11 03:00 | 2 | 3 | 0.74527 | 827.1001
2017-02-11 04:00 | 2 | 4 | 0.74708 | 829.1063
2017-02-11 05:00 | 2 | 5 | 0.81132 | 900.3992
2017-02-11 06:00 | 2 | 6 | 1.0285 | 1141.4599
2017-02-11 07:00 | 2 | 7 | 1.3035 | 1446.6522
2017-02-11 08:00 | 2 | 8 | 1.244 | 1380.611
2017-02-11 09:00 | 2 | 9 | 1.0714 | 1189.0488
2017-02-11 10:00 | 2 | 10 | 1.0765 | 1194.7559
2017-02-11 11:00 | 2 | 11 | 1.0668 | 1183.9867
2017-02-11 12:00 | 2 | 12 | 1.018 | 1129.815
2017-02-11 13:00 | 2 | 13 | 0.9747 | 1081.7201
2017-02-11 14:00 | 2 | 14 | 0.9681 | 1074.3941
2017-02-11 15:00 | 2 | 15 | 1.0235 | 1135.8461
2017-02-11 16:00 | 2 | 16 | 1.231 | 1366.1768
2017-02-11 17:00 | 2 | 17 | 1.6687 | 1851.9696
2017-02-11 18:00 | 2 | 18 | 1.9891 | 2207.5523
2017-02-11 19:00 | 2 | 19 | 2.0982 | 2328.6182
2017-02-11 20:00 | 2 | 20 | 2.0192 | 2240.9199
2017-02-11 21:00 | 2 | 21 | 1.8399 | 2041.8803
2017-02-11 22:00 | 2 | 22 | 1.5105 | 1676.3132
2017-02-11 23:00 | 2 | 23 | 1.1885 | 1318.9587
2017-02-12 | 2 | 0 | 0.86911 | 964.5416
2017-02-12 01:00 | 2 | 1 | 0.75371 | 836.4689
2017-02-12 02:00 | 2 | 2 | 0.70641 | 783.9719
2017-02-12 03:00 | 2 | 3 | 0.69754 | 774.1326
2017-02-12 04:00 | 2 | 4 | 0.69845 | 775.1458
2017-02-12 05:00 | 2 | 5 | 0.75962 | 843.0295
2017-02-12 06:00 | 2 | 6 | 0.96857 | 1074.9257
2017-02-12 07:00 | 2 | 7 | 1.2465 | 1383.4114
2017-02-12 08:00 | 2 | 8 | 1.1911 | 1321.8876
2017-02-12 09:00 | 2 | 9 | 1.0444 | 1159.1162
2017-02-12 10:00 | 2 | 10 | 1.0597 | 1176.0516
2017-02-12 11:00 | 2 | 11 | 1.0255 | 1138.0798
2017-02-12 12:00 | 2 | 12 | 0.98621 | 1094.492
2017-02-12 13:00 | 2 | 13 | 0.95534 | 1060.2426
2017-02-12 14:00 | 2 | 14 | 0.96212 | 1067.7617
2017-02-12 15:00 | 2 | 15 | 1.018 | 1129.821
2017-02-12 16:00 | 2 | 16 | 1.2239 | 1358.2761
2017-02-12 17:00 | 2 | 17 | 1.6569 | 1838.8149
2017-02-12 18:00 | 2 | 18 | 1.981 | 2198.542
2017-02-12 19:00 | 2 | 19 | 2.0965 | 2326.7486
2017-02-12 20:00 | 2 | 20 | 2.0222 | 2244.2241
2017-02-12 21:00 | 2 | 21 | 1.8501 | 2053.2475
2017-02-12 22:00 | 2 | 22 | 1.5243 | 1691.6667
2017-02-12 23:00 | 2 | 23 | 1.2148 | 1348.164
2017-02-13 | 2 | 0 | 0.88821 | 985.7325
2017-02-13 01:00 | 2 | 1 | 0.76968 | 854.1892
2017-02-13 02:00 | 2 | 2 | 0.7241 | 803.6126
2017-02-13 03:00 | 2 | 3 | 0.71605 | 794.673
2017-02-13 04:00 | 2 | 4 | 0.71808 | 796.9295
2017-02-13 05:00 | 2 | 5 | 0.77839 | 863.8534
2017-02-13 06:00 | 2 | 6 | 0.96763 | 1073.8728
2017-02-13 07:00 | 2 | 7 | 1.2652 | 1404.1233
2017-02-13 08:00 | 2 | 8 | 1.183 | 1312.9262
2017-02-13 09:00 | 2 | 9 | 1.0312 | 1144.4439
2017-02-13 10:00 | 2 | 10 | 1.0453 | 1160.1108
2017-02-13 11:00 | 2 | 11 | 1.0319 | 1145.244
2017-02-13 12:00 | 2 | 12 | 1.0095 | 1120.3832
2017-02-13 13:00 | 2 | 13 | 0.98139 | 1089.15
2017-02-13 14:00 | 2 | 14 | 0.97637 | 1083.574
2017-02-13 15:00 | 2 | 15 | 1.0277 | 1140.5004
2017-02-13 16:00 | 2 | 16 | 1.2333 | 1368.6876
2017-02-13 17:00 | 2 | 17 | 1.6643 | 1847.0118
2017-02-13 18:00 | 2 | 18 | 1.9749 | 2191.7617
2017-02-13 19:00 | 2 | 19 | 2.0826 | 2311.2348
2017-02-13 20:00 | 2 | 20 | 2.0019 | 2221.7468
2017-02-13 21:00 | 2 | 21 | 1.8219 | 2021.9593
2017-02-13 22:00 | 2 | 22 | 1.4987 | 1663.3131
2017-02-13 23:00 | 2 | 23 | 1.197 | 1328.4263
2017-02-14 | 2 | 0 | 0.88734 | 984.7724
2017-02-14 01:00 | 2 | 1 | 0.76975 | 854.2666
2017-02-14 02:00 | 2 | 2 | 0.72403 | 803.5312
2017-02-14 03:00 | 2 | 3 | 0.71631 | 794.9667
2017-02-14 04:00 | 2 | 4 | 0.72002 | 799.0806
2017-02-14 05:00 | 2 | 5 | 0.78281 | 868.7637
2017-02-14 06:00 | 2 | 6 | 0.97353 | 1080.4264
2017-02-14 07:00 | 2 | 7 | 1.2537 | 1391.404
2017-02-14 08:00 | 2 | 8 | 1.1701 | 1298.599
2017-02-14 09:00 | 2 | 9 | 0.99429 | 1103.4694
2017-02-14 10:00 | 2 | 10 | 1 | 1109.8291
2017-02-14 11:00 | 2 | 11 | 0.99507 | 1104.335
2017-02-14 12:00 | 2 | 12 | 0.94954 | 1053.8017
2017-02-14 13:00 | 2 | 13 | 0.9115 | 1011.5796
2017-02-14 14:00 | 2 | 14 | 0.91347 | 1013.771
2017-02-14 15:00 | 2 | 15 | 0.97538 | 1082.4806
2017-02-14 16:00 | 2 | 16 | 1.1864 | 1316.668
2017-02-14 17:00 | 2 | 17 | 1.6175 | 1795.0562
2017-02-14 18:00 | 2 | 18 | 1.943 | 2156.2907
2017-02-14 19:00 | 2 | 19 | 2.0659 | 2292.6892
2017-02-14 20:00 | 2 | 20 | 1.9939 | 2212.7911
2017-02-14 21:00 | 2 | 21 | 1.8193 | 2019.0114
2017-02-14 22:00 | 2 | 22 | 1.5024 | 1667.3974
2017-02-14 23:00 | 2 | 23 | 1.2054 | 1337.7263
2017-02-15 | 2 | 0 | 0.89396 | 992.1156
2017-02-15 01:00 | 2 | 1 | 0.77639 | 861.6387
2017-02-15 02:00 | 2 | 2 | 0.72778 | 807.6888
2017-02-15 03:00 | 2 | 3 | 0.71858 | 797.4795
2017-02-15 04:00 | 2 | 4 | 0.71913 | 798.0958
2017-02-15 05:00 | 2 | 5 | 0.77928 | 864.841
2017-02-15 06:00 | 2 | 6 | 0.96967 | 1076.143
2017-02-15 07:00 | 2 | 7 | 1.2656 | 1404.5294
2017-02-15 08:00 | 2 | 8 | 1.1858 | 1315.9888
2017-02-15 09:00 | 2 | 9 | 1.0318 | 1145.0434
2017-02-15 10:00 | 2 | 10 | 1.059 | 1175.3167
2017-02-15 11:00 | 2 | 11 | 1.0389 | 1152.9893
2017-02-15 12:00 | 2 | 12 | 1.0119 | 1123.0198
2017-02-15 13:00 | 2 | 13 | 0.98527 | 1093.4553
2017-02-15 14:00 | 2 | 14 | 0.99112 | 1099.9492
2017-02-15 15:00 | 2 | 15 | 1.0464 | 1161.2567
2017-02-15 16:00 | 2 | 16 | 1.2522 | 1389.6616
2017-02-15 17:00 | 2 | 17 | 1.6914 | 1877.075
2017-02-15 18:00 | 2 | 18 | 2.0158 | 2237.1616
2017-02-15 19:00 | 2 | 19 | 2.1266 | 2360.0773
2017-02-15 20:00 | 2 | 20 | 2.0538 | 2279.3492
2017-02-15 21:00 | 2 | 21 | 1.8748 | 2080.6297
2017-02-15 22:00 | 2 | 22 | 1.5669 | 1738.9273
2017-02-15 23:00 | 2 | 23 | 1.2682 | 1407.4522
2017-02-16 | 2 | 0 | 0.96246 | 1068.1351
2017-02-16 01:00 | 2 | 1 | 0.84747 | 940.5236
2017-02-16 02:00 | 2 | 2 | 0.80442 | 892.7496
2017-02-16 03:00 | 2 | 3 | 0.80017 | 888.0249
2017-02-16 04:00 | 2 | 4 | 0.79819 | 885.8277
2017-02-16 05:00 | 2 | 5 | 0.86192 | 956.5563
2017-02-16 06:00 | 2 | 6 | 1.0707 | 1188.3196
2017-02-16 07:00 | 2 | 7 | 1.3321 | 1478.3373
2017-02-16 08:00 | 2 | 8 | 1.2429 | 1379.3351
2017-02-16 09:00 | 2 | 9 | 1.0658 | 1182.8217
2017-02-16 10:00 | 2 | 10 | 1.0853 | 1204.4851
2017-02-16 11:00 | 2 | 11 | 1.0484 | 1163.4882
2017-02-16 12:00 | 2 | 12 | 1.0125 | 1123.7152
2017-02-16 13:00 | 2 | 13 | 0.97981 | 1087.3898
2017-02-16 14:00 | 2 | 14 | 0.97771 | 1085.0627
2017-02-16 15:00 | 2 | 15 | 1.0449 | 1159.6008
2017-02-16 16:00 | 2 | 16 | 1.2584 | 1396.5276
2017-02-16 17:00 | 2 | 17 | 1.7082 | 1895.809
2017-02-16 18:00 | 2 | 18 | 2.0265 | 2248.9788
2017-02-16 19:00 | 2 | 19 | 2.1501 | 2386.2017
2017-02-16 20:00 | 2 | 20 | 2.0806 | 2309.0029
2017-02-16 21:00 | 2 | 21 | 1.9101 | 2119.8312
2017-02-16 22:00 | 2 | 22 | 1.598 | 1773.5053
2017-02-16 23:00 | 2 | 23 | 1.3028 | 1445.8384
2017-02-17 | 2 | 0 | 0.99569 | 1105.0146
2017-02-17 01:00 | 2 | 1 | 0.88983 | 987.5338
2017-02-17 02:00 | 2 | 2 | 0.8543 | 948.1033
2017-02-17 03:00 | 2 | 3 | 0.85354 | 947.2589
2017-02-17 04:00 | 2 | 4 | 0.85532 | 949.2302
2017-02-17 05:00 | 2 | 5 | 0.92234 | 1023.6148
2017-02-17 06:00 | 2 | 6 | 1.1367 | 1261.4749
2017-02-17 07:00 | 2 | 7 | 1.3947 | 1547.8297
2017-02-17 08:00 | 2 | 8 | 1.3032 | 1446.2703
2017-02-17 09:00 | 2 | 9 | 1.1274 | 1251.1595
2017-02-17 10:00 | 2 | 10 | 1.1403 | 1265.4673
2017-02-17 11:00 | 2 | 11 | 1.0969 | 1217.3209
2017-02-17 12:00 | 2 | 12 | 1.0561 | 1172.0512
2017-02-17 13:00 | 2 | 13 | 1.0176 | 1129.2908
2017-02-17 14:00 | 2 | 14 | 1.0128 | 1124.0574
2017-02-17 15:00 | 2 | 15 | 1.0759 | 1194.087
2017-02-17 16:00 | 2 | 16 | 1.2876 | 1428.9417
2017-02-17 17:00 | 2 | 17 | 1.7366 | 1927.3274
2017-02-17 18:00 | 2 | 18 | 2.05 | 2275.1252
2017-02-17 19:00 | 2 | 19 | 2.1653 | 2403.009
2017-02-17 20:00 | 2 | 20 | 2.0888 | 2318.1552
2017-02-17 21:00 | 2 | 21 | 1.9154 | 2125.723
2017-02-17 22:00 | 2 | 22 | 1.6014 | 1777.2
2017-02-17 23:00 | 2 | 23 | 1.3056 | 1448.9987
2017-02-18 | 2 | 0 | 1.003 | 1113.17
2017-02-18 01:00 | 2 | 1 | 0.88566 | 982.9078
2017-02-18 02:00 | 2 | 2 | 0.83567 | 927.4296
2017-02-18 03:00 | 2 | 3 | 0.82687 | 917.657
2017-02-18 04:00 | 2 | 4 | 0.82673 | 917.5026
2017-02-18 05:00 | 2 | 5 | 0.88819 | 985.7114
2017-02-18 06:00 | 2 | 6 | 1.0833 | 1202.2062
2017-02-18 07:00 | 2 | 7 | 1.3634 | 1513.1335
2017-02-18 08:00 | 2 | 8 | 1.2849 | 1425.9594
2017-02-18 09:00 | 2 | 9 | 1.1144 | 1236.7546
2017-02-18 10:00 | 2 | 10 | 1.1179 | 1240.6269
2017-02-18 11:00 | 2 | 11 | 1.0849 | 1204.0601
2017-02-18 12:00 | 2 | 12 | 1.0406 | 1154.816
2017-02-18 13:00 | 2 | 13 | 1 | 1109.802
2017-02-18 14:00 | 2 | 14 | 0.99247 | 1101.4454
2017-02-18 15:00 | 2 | 15 | 1.0498 | 1165.0715
2017-02-18 16:00 | 2 | 16 | 1.2779 | 1418.2608
2017-02-18 17:00 | 2 | 17 | 1.7278 | 1917.5699
2017-02-18 18:00 | 2 | 18 | 2.0406 | 2264.6169
2017-02-18 19:00 | 2 | 19 | 2.1577 | 2394.622
2017-02-18 20:00 | 2 | 20 | 2.0868 | 2315.9424
2017-02-18 21:00 | 2 | 21 | 1.9108 | 2120.6632
2017-02-18 22:00 | 2 | 22 | 1.5917 | 1766.443
2017-02-18 23:00 | 2 | 23 | 1.2824 | 1423.2324
2017-02-19 | 2 | 0 | 0.96216 | 1067.8058
2017-02-19 01:00 | 2 | 1 | 0.84281 | 935.3464
2017-02-19 02:00 | 2 | 2 | 0.79731 | 884.861
2017-02-19 03:00 | 2 | 3 | 0.78781 | 874.3151
2017-02-19 04:00 | 2 | 4 | 0.78398 | 870.0568
2017-02-19 05:00 | 2 | 5 | 0.84383 | 936.4786
2017-02-19 06:00 | 2 | 6 | 1.0516 | 1167.0637
2017-02-19 07:00 | 2 | 7 | 1.3243 | 1469.6576
2017-02-19 08:00 | 2 | 8 | 1.2583 | 1396.4509
2017-02-19 09:00 | 2 | 9 | 1.1124 | 1234.555
2017-02-19 10:00 | 2 | 10 | 1.1283 | 1252.2254
2017-02-19 11:00 | 2 | 11 | 1.1064 | 1227.8876
2017-02-19 12:00 | 2 | 12 | 1.0746 | 1192.5418
2017-02-19 13:00 | 2 | 13 | 1.0371 | 1151.023
2017-02-19 14:00 | 2 | 14 | 1.0323 | 1145.6231
2017-02-19 15:00 | 2 | 15 | 1.0853 | 1204.4618
2017-02-19 16:00 | 2 | 16 | 1.284 | 1424.9824
2017-02-19 17:00 | 2 | 17 | 1.7121 | 1900.0891
2017-02-19 18:00 | 2 | 18 | 2.0218 | 2243.7938
2017-02-19 19:00 | 2 | 19 | 2.1353 | 2369.7194
2017-02-19 20:00 | 2 | 20 | 2.0597 | 2285.8245
2017-02-19 21:00 | 2 | 21 | 1.8873 | 2094.5076
2017-02-19 22:00 | 2 | 22 | 1.559 | 1730.1678
2017-02-19 23:00 | 2 | 23 | 1.2458 | 1382.5971
2017-02-20 | 2 | 0 | 0.9192 | 1020.1327
2017-02-20 01:00 | 2 | 1 | 0.81219 | 901.3676
2017-02-20 02:00 | 2 | 2 | 0.75983 | 843.2639
2017-02-20 03:00 | 2 | 3 | 0.75249 | 835.1149
2017-02-20 04:00 | 2 | 4 | 0.75206 | 834.6369
2017-02-20 05:00 | 2 | 5 | 0.81382 | 903.1749
2017-02-20 06:00 | 2 | 6 | 1.0034 | 1113.5258
2017-02-20 07:00 | 2 | 7 | 1.2816 | 1422.3596
2017-02-20 08:00 | 2 | 8 | 1.2091 | 1341.8636
2017-02-20 09:00 | 2 | 9 | 1.054 | 1169.7194
2017-02-20 10:00 | 2 | 10 | 1.0656 | 1182.6419
2017-02-20 11:00 | 2 | 11 | 1.0576 | 1173.7149
2017-02-20 12:00 | 2 | 12 | 1.0348 | 1148.4179
2017-02-20 13:00 | 2 | 13 | 1.0091 | 1119.8665
2017-02-20 14:00 | 2 | 14 | 1.0118 | 1122.893
2017-02-20 15:00 | 2 | 15 | 1.0673 | 1184.4491
2017-02-20 16:00 | 2 | 16 | 1.2638 | 1402.5478
2017-02-20 17:00 | 2 | 17 | 1.6976 | 1883.9797
2017-02-20 18:00 | 2 | 18 | 2.021 | 2242.8959
2017-02-20 19:00 | 2 | 19 | 2.1231 | 2356.2264
2017-02-20 20:00 | 2 | 20 | 2.043 | 2267.328
2017-02-20 21:00 | 2 | 21 | 1.8632 | 2067.7832
2017-02-20 22:00 | 2 | 22 | 1.5429 | 1712.28
2017-02-20 23:00 | 2 | 23 | 1.2407 | 1376.8812
2017-02-21 | 2 | 0 | 0.92609 | 1027.7779
2017-02-21 01:00 | 2 | 1 | 0.80669 | 895.2698
2017-02-21 02:00 | 2 | 2 | 0.76025 | 843.7302
2017-02-21 03:00 | 2 | 3 | 0.75096 | 833.4174
2017-02-21 04:00 | 2 | 4 | 0.74733 | 829.3902
2017-02-21 05:00 | 2 | 5 | 0.80652 | 895.0808
2017-02-21 06:00 | 2 | 6 | 0.9959 | 1105.2494
2017-02-21 07:00 | 2 | 7 | 1.2917 | 1433.514
2017-02-21 08:00 | 2 | 8 | 1.1952 | 1326.4802
2017-02-21 09:00 | 2 | 9 | 1.026 | 1138.6682
2017-02-21 10:00 | 2 | 10 | 1.0367 | 1150.5138
2017-02-21 11:00 | 2 | 11 | 1.0153 | 1126.7433
2017-02-21 12:00 | 2 | 12 | 0.98992 | 1098.619
2017-02-21 13:00 | 2 | 13 | 0.96912 | 1075.535
2017-02-21 14:00 | 2 | 14 | 0.97303 | 1079.8653
2017-02-21 15:00 | 2 | 15 | 1.0348 | 1148.3755
2017-02-21 16:00 | 2 | 16 | 1.2594 | 1397.6754
2017-02-21 17:00 | 2 | 17 | 1.6903 | 1875.9175
2017-02-21 18:00 | 2 | 18 | 2.023 | 2245.107
2017-02-21 19:00 | 2 | 19 | 2.1322 | 2366.2726
2017-02-21 20:00 | 2 | 20 | 2.0749 | 2302.764
2017-02-21 21:00 | 2 | 21 | 1.9114 | 2121.3239
2017-02-21 22:00 | 2 | 22 | 1.597 | 1772.3662
2017-02-21 23:00 | 2 | 23 | 1.2897 | 1431.311
2017-02-22 | 2 | 0 | 0.97525 | 1082.339
2017-02-22 01:00 | 2 | 1 | 0.86882 | 964.2137
2017-02-22 02:00 | 2 | 2 | 0.81738 | 907.1309
2017-02-22 03:00 | 2 | 3 | 0.81458 | 904.0244
2017-02-22 04:00 | 2 | 4 | 0.81058 | 899.5784
2017-02-22 05:00 | 2 | 5 | 0.87606 | 972.2513
2017-02-22 06:00 | 2 | 6 | 1.0888 | 1208.3748
2017-02-22 07:00 | 2 | 7 | 1.3471 | 1495.0602
2017-02-22 08:00 | 2 | 8 | 1.2539 | 1391.5535
2017-02-22 09:00 | 2 | 9 | 1.0943 | 1214.416
2017-02-22 10:00 | 2 | 10 | 1.099 | 1219.7067
2017-02-22 11:00 | 2 | 11 | 1.0757 | 1193.7871
2017-02-22 12:00 | 2 | 12 | 1.0456 | 1160.3678
2017-02-22 13:00 | 2 | 13 | 1.0169 | 1128.6125
2017-02-22 14:00 | 2 | 14 | 1.0093 | 1120.132
2017-02-22 15:00 | 2 | 15 | 1.051 | 1166.4567
2017-02-22 16:00 | 2 | 16 | 1.249 | 1386.1751
2017-02-22 17:00 | 2 | 17 | 1.6838 | 1868.6449
2017-02-22 18:00 | 2 | 18 | 2.0012 | 2220.9807
2017-02-22 19:00 | 2 | 19 | 2.1099 | 2341.5662
2017-02-22 20:00 | 2 | 20 | 2.0285 | 2251.279
2017-02-22 21:00 | 2 | 21 | 1.8506 | 2053.7532
2017-02-22 22:00 | 2 | 22 | 1.5372 | 1706.0125
2017-02-22 23:00 | 2 | 23 | 1.2326 | 1367.9103
2017-02-23 | 2 | 0 | 0.91644 | 1017.0657
2017-02-23 01:00 | 2 | 1 | 0.79521 | 882.5261
2017-02-23 02:00 | 2 | 2 | 0.74553 | 827.3953
2017-02-23 03:00 | 2 | 3 | 0.73501 | 815.7154
2017-02-23 04:00 | 2 | 4 | 0.73305 | 813.5452
2017-02-23 05:00 | 2 | 5 | 0.7961 | 883.5141
2017-02-23 06:00 | 2 | 6 | 0.98772 | 1096.1741
2017-02-23 07:00 | 2 | 7 | 1.2673 | 1406.4393
2017-02-23 08:00 | 2 | 8 | 1.1892 | 1319.7867
2017-02-23 09:00 | 2 | 9 | 1.0171 | 1128.7277
2017-02-23 10:00 | 2 | 10 | 1.0258 | 1138.4534
2017-02-23 11:00 | 2 | 11 | 1.0054 | 1115.8111
2017-02-23 12:00 | 2 | 12 | 0.98462 | 1092.7292
2017-02-23 13:00 | 2 | 13 | 0.96218 | 1067.8252
2017-02-23 14:00 | 2 | 14 | 0.96989 | 1076.3868
2017-02-23 15:00 | 2 | 15 | 1.0277 | 1140.564
2017-02-23 16:00 | 2 | 16 | 1.2362 | 1371.8901
2017-02-23 17:00 | 2 | 17 | 1.6753 | 1859.2868
2017-02-23 18:00 | 2 | 18 | 1.9897 | 2208.2207
2017-02-23 19:00 | 2 | 19 | 2.1002 | 2330.8284
2017-02-23 20:00 | 2 | 20 | 2.0212 | 2243.1014
2017-02-23 21:00 | 2 | 21 | 1.8448 | 2047.3071
2017-02-23 22:00 | 2 | 22 | 1.5226 | 1689.7644
2017-02-23 23:00 | 2 | 23 | 1.2233 | 1357.5855
2017-02-24 | 2 | 0 | 0.91555 | 1016.0778
2017-02-24 01:00 | 2 | 1 | 0.79812 | 885.7536
2017-02-24 02:00 | 2 | 2 | 0.75045 | 832.8554
2017-02-24 03:00 | 2 | 3 | 0.74128 | 822.6774
2017-02-24 04:00 | 2 | 4 | 0.73693 | 817.8406
2017-02-24 05:00 | 2 | 5 | 0.79764 | 885.2275
2017-02-24 06:00 | 2 | 6 | 0.98636 | 1094.6676
2017-02-24 07:00 | 2 | 7 | 1.2648 | 1403.629
2017-02-24 08:00 | 2 | 8 | 1.2008 | 1332.6872
2017-02-24 09:00 | 2 | 9 | 1.0604 | 1176.8519
2017-02-24 10:00 | 2 | 10 | 1.0817 | 1200.4678
2017-02-24 11:00 | 2 | 11 | 1.0686 | 1185.9434
2017-02-24 12:00 | 2 | 12 | 1.0429 | 1157.4011
2017-02-24 13:00 | 2 | 13 | 1.0122 | 1123.3111
2017-02-24 14:00 | 2 | 14 | 1.0118 | 1122.9062
2017-02-24 15:00 | 2 | 15 | 1.0649 | 1181.7866
2017-02-24 16:00 | 2 | 16 | 1.2655 | 1404.4931
2017-02-24 17:00 | 2 | 17 | 1.6977 | 1884.1222
2017-02-24 18:00 | 2 | 18 | 2.0385 | 2262.2874
2017-02-24 19:00 | 2 | 19 | 2.1191 | 2351.7706
2017-02-24 20:00 | 2 | 20 | 2.0274 | 2249.9789
2017-02-24 21:00 | 2 | 21 | 1.8367 | 2038.359
2017-02-24 22:00 | 2 | 22 | 1.5102 | 1676.0176
2017-02-24 23:00 | 2 | 23 | 1.2077 | 1340.3596
2017-02-25 | 2 | 0 | 0.89598 | 994.3558
2017-02-25 01:00 | 2 | 1 | 0.78808 | 874.6147
2017-02-25 02:00 | 2 | 2 | 0.74032 | 821.6119
2017-02-25 03:00 | 2 | 3 | 0.73 | 810.1552
2017-02-25 04:00 | 2 | 4 | 0.70874 | 786.5605
2017-02-25 05:00 | 2 | 5 | 0.76335 | 847.1689
2017-02-25 06:00 | 2 | 6 | 0.9949 | 1104.1411
2017-02-25 07:00 | 2 | 7 | 1.2858 | 1426.949
2017-02-25 08:00 | 2 | 8 | 1.2101 | 1343.0065
2017-02-25 09:00 | 2 | 9 | 1.0535 | 1169.1801
2017-02-25 10:00 | 2 | 10 | 1.0605 | 1176.9271
2017-02-25 11:00 | 2 | 11 | 1.0481 | 1163.1349
2017-02-25 12:00 | 2 | 12 | 1.0172 | 1128.9263
2017-02-25 13:00 | 2 | 13 | 0.98518 | 1093.3544
2017-02-25 14:00 | 2 | 14 | 0.97636 | 1083.5654
2017-02-25 15:00 | 2 | 15 | 1.033 | 1146.4203
2017-02-25 16:00 | 2 | 16 | 1.2373 | 1373.2122
2017-02-25 17:00 | 2 | 17 | 1.6593 | 1841.4519
2017-02-25 18:00 | 2 | 18 | 1.9798 | 2197.1825
2017-02-25 19:00 | 2 | 19 | 2.1018 | 2332.6186
2017-02-25 20:00 | 2 | 20 | 2.0219 | 2243.8531
2017-02-25 21:00 | 2 | 21 | 1.8452 | 2047.8272
2017-02-25 22:00 | 2 | 22 | 1.5176 | 1684.2791
2017-02-25 23:00 | 2 | 23 | 1.2052 | 1337.4856
2017-02-26 | 2 | 0 | 0.87877 | 975.2552
2017-02-26 01:00 | 2 | 1 | 0.7578 | 841.0063
2017-02-26 02:00 | 2 | 2 | 0.70876 | 786.5796
2017-02-26 03:00 | 2 | 3 | 0.69668 | 773.1768
2017-02-26 04:00 | 2 | 4 | 0.69904 | 775.8002
2017-02-26 05:00 | 2 | 5 | 0.75806 | 841.3008
2017-02-26 06:00 | 2 | 6 | 0.96799 | 1074.2782
2017-02-26 07:00 | 2 | 7 | 1.2453 | 1382.0529
2017-02-26 08:00 | 2 | 8 | 1.1719 | 1300.5499
2017-02-26 09:00 | 2 | 9 | 1.0222 | 1134.4113
2017-02-26 10:00 | 2 | 10 | 1.0472 | 1162.1938
2017-02-26 11:00 | 2 | 11 | 1.039 | 1153.0999
2017-02-26 12:00 | 2 | 12 | 1.0008 | 1110.6455
2017-02-26 13:00 | 2 | 13 | 0.95547 | 1060.3776
2017-02-26 14:00 | 2 | 14 | 0.9492 | 1053.4291
2017-02-26 15:00 | 2 | 15 | 1.0074 | 1118.01
2017-02-26 16:00 | 2 | 16 | 1.2209 | 1354.9028
2017-02-26 17:00 | 2 | 17 | 1.6527 | 1834.2145
2017-02-26 18:00 | 2 | 18 | 1.9757 | 2192.5797
2017-02-26 19:00 | 2 | 19 | 2.0938 | 2323.7074
2017-02-26 20:00 | 2 | 20 | 2.0202 | 2242.0222
2017-02-26 21:00 | 2 | 21 | 1.8438 | 2046.2873
2017-02-26 22:00 | 2 | 22 | 1.5214 | 1688.4475
2017-02-26 23:00 | 2 | 23 | 1.2142 | 1347.5649
2017-02-27 | 2 | 0 | 0.88788 | 985.3666
2017-02-27 01:00 | 2 | 1 | 0.76757 | 851.8539
2017-02-27 02:00 | 2 | 2 | 0.72324 | 802.6537
2017-02-27 03:00 | 2 | 3 | 0.71777 | 796.5829
2017-02-27 04:00 | 2 | 4 | 0.71624 | 794.8828
2017-02-27 05:00 | 2 | 5 | 0.77969 | 865.2988
2017-02-27 06:00 | 2 | 6 | 0.96971 | 1076.182
2017-02-27 07:00 | 2 | 7 | 1.2435 | 1380.0091
2017-02-27 08:00 | 2 | 8 | 1.1588 | 1285.9836
2017-02-27 09:00 | 2 | 9 | 1.0123 | 1123.4791
2017-02-27 10:00 | 2 | 10 | 1.0304 | 1143.5581
2017-02-27 11:00 | 2 | 11 | 1.0225 | 1134.8232
2017-02-27 12:00 | 2 | 12 | 0.99815 | 1107.7535
2017-02-27 13:00 | 2 | 13 | 0.97502 | 1082.074
2017-02-27 14:00 | 2 | 14 | 0.97589 | 1083.0425
2017-02-27 15:00 | 2 | 15 | 1.0302 | 1143.3443
2017-02-27 16:00 | 2 | 16 | 1.236 | 1371.7498
2017-02-27 17:00 | 2 | 17 | 1.6652 | 1848.0596
2017-02-27 18:00 | 2 | 18 | 1.9776 | 2194.7935
2017-02-27 19:00 | 2 | 19 | 2.0839 | 2312.7158
2017-02-27 20:00 | 2 | 20 | 2.0023 | 2222.1174
2017-02-27 21:00 | 2 | 21 | 1.8204 | 2020.3038
2017-02-27 22:00 | 2 | 22 | 1.4981 | 1662.605
2017-02-27 23:00 | 2 | 23 | 1.192 | 1322.8724
2017-02-28 | 2 | 0 | 0.87883 | 975.3234
2017-02-28 01:00 | 2 | 1 | 0.76014 | 843.6096
2017-02-28 02:00 | 2 | 2 | 0.71352 | 791.8669
2017-02-28 03:00 | 2 | 3 | 0.7016 | 778.6324
2017-02-28 04:00 | 2 | 4 | 0.69875 | 775.4775
2017-02-28 05:00 | 2 | 5 | 0.75764 | 840.8306
2017-02-28 06:00 | 2 | 6 | 0.94741 | 1051.4324
2017-02-28 07:00 | 2 | 7 | 1.2443 | 1380.8756
2017-02-28 08:00 | 2 | 8 | 1.1548 | 1281.6092
2017-02-28 09:00 | 2 | 9 | 0.98701 | 1095.3877
2017-02-28 10:00 | 2 | 10 | 0.98907 | 1097.6747
2017-02-28 11:00 | 2 | 11 | 0.96954 | 1076.0005
2017-02-28 12:00 | 2 | 12 | 0.93971 | 1042.8947
2017-02-28 13:00 | 2 | 13 | 0.90861 | 1008.3718
2017-02-28 14:00 | 2 | 14 | 0.91145 | 1011.5324
2017-02-28 15:00 | 2 | 15 | 0.97615 | 1083.3383
2017-02-28 16:00 | 2 | 16 | 1.1962 | 1327.4933
2017-02-28 17:00 | 2 | 17 | 1.6392 | 1819.2384
2017-02-28 18:00 | 2 | 18 | 1.9648 | 2180.5381
2017-02-28 19:00 | 2 | 19 | 2.0886 | 2317.9788
2017-02-28 20:00 | 2 | 20 | 2.0181 | 2239.6388
2017-02-28 21:00 | 2 | 21 | 1.8421 | 2044.3892
2017-02-28 22:00 | 2 | 22 | 1.5231 | 1690.3217
2017-02-28 23:00 | 2 | 23 | 1.2212 | 1355.317
2017-03-01 | 3 | 0 | 0.86326 | 958.0488
2017-03-01 01:00 | 3 | 1 | 0.74506 | 826.864
2017-03-01 02:00 | 3 | 2 | 0.69353 | 769.678
2017-03-01 03:00 | 3 | 3 | 0.68046 | 755.1802
2017-03-01 04:00 | 3 | 4 | 0.67755 | 751.9414
2017-03-01 05:00 | 3 | 5 | 0.7296 | 809.7061
2017-03-01 06:00 | 3 | 6 | 0.87607 | 972.26
2017-03-01 07:00 | 3 | 7 | 1.0813 | 1200.0219
2017-03-01 08:00 | 3 | 8 | 0.99924 | 1108.963
2017-03-01 09:00 | 3 | 9 | 0.91486 | 1015.3083
2017-03-01 10:00 | 3 | 10 | 0.93327 | 1035.7423
2017-03-01 11:00 | 3 | 11 | 0.91931 | 1020.2572
2017-03-01 12:00 | 3 | 12 | 0.88274 | 979.6636
2017-03-01 13:00 | 3 | 13 | 0.842 | 934.4509
2017-03-01 14:00 | 3 | 14 | 0.83137 | 922.6531
2017-03-01 15:00 | 3 | 15 | 0.87415 | 970.1345
2017-03-01 16:00 | 3 | 16 | 1.0427 | 1157.1991
2017-03-01 17:00 | 3 | 17 | 1.3872 | 1539.5626
2017-03-01 18:00 | 3 | 18 | 1.661 | 1843.348
2017-03-01 19:00 | 3 | 19 | 1.8412 | 2043.3776
2017-03-01 20:00 | 3 | 20 | 1.8923 | 2100.0646
2017-03-01 21:00 | 3 | 21 | 1.7361 | 1926.6909
2017-03-01 22:00 | 3 | 22 | 1.4373 | 1595.1349
2017-03-01 23:00 | 3 | 23 | 1.1496 | 1275.8202
2017-03-02 | 3 | 0 | 0.8464 | 939.332
2017-03-02 01:00 | 3 | 1 | 0.73589 | 816.6882
2017-03-02 02:00 | 3 | 2 | 0.69175 | 767.7008
2017-03-02 03:00 | 3 | 3 | 0.68372 | 758.7987
2017-03-02 04:00 | 3 | 4 | 0.68432 | 759.4543
2017-03-02 05:00 | 3 | 5 | 0.7388 | 819.9219
2017-03-02 06:00 | 3 | 6 | 0.88807 | 985.5835
2017-03-02 07:00 | 3 | 7 | 1.0992 | 1219.9024
2017-03-02 08:00 | 3 | 8 | 1.0192 | 1131.1237
2017-03-02 09:00 | 3 | 9 | 0.90974 | 1009.6326
2017-03-02 10:00 | 3 | 10 | 0.92064 | 1021.7244
2017-03-02 11:00 | 3 | 11 | 0.90985 | 1009.7512
2017-03-02 12:00 | 3 | 12 | 0.8914 | 989.2784
2017-03-02 13:00 | 3 | 13 | 0.868 | 963.3063
2017-03-02 14:00 | 3 | 14 | 0.86209 | 956.7481
2017-03-02 15:00 | 3 | 15 | 0.9096 | 1009.4749
2017-03-02 16:00 | 3 | 16 | 1.0705 | 1188.0838
2017-03-02 17:00 | 3 | 17 | 1.4116 | 1566.6161
2017-03-02 18:00 | 3 | 18 | 1.6807 | 1865.2946
2017-03-02 19:00 | 3 | 19 | 1.8601 | 2064.2887
2017-03-02 20:00 | 3 | 20 | 1.9069 | 2116.2725
2017-03-02 21:00 | 3 | 21 | 1.7486 | 1940.5563
2017-03-02 22:00 | 3 | 22 | 1.4434 | 1601.8626
2017-03-02 23:00 | 3 | 23 | 1.1599 | 1287.2609
2017-03-03 | 3 | 0 | 0.86191 | 956.5491
2017-03-03 01:00 | 3 | 1 | 0.75116 | 833.6411
2017-03-03 02:00 | 3 | 2 | 0.70596 | 783.4787
2017-03-03 03:00 | 3 | 3 | 0.70064 | 777.5675
2017-03-03 04:00 | 3 | 4 | 0.70413 | 781.448
2017-03-03 05:00 | 3 | 5 | 0.76164 | 845.2655
2017-03-03 06:00 | 3 | 6 | 0.91272 | 1012.9372
2017-03-03 07:00 | 3 | 7 | 1.1191 | 1241.9306
2017-03-03 08:00 | 3 | 8 | 1.0434 | 1157.9753
2017-03-03 09:00 | 3 | 9 | 0.94075 | 1044.0404
2017-03-03 10:00 | 3 | 10 | 0.95609 | 1061.0734
2017-03-03 11:00 | 3 | 11 | 0.92769 | 1029.5488
2017-03-03 12:00 | 3 | 12 | 0.90509 | 1004.4662
2017-03-03 13:00 | 3 | 13 | 0.87753 | 973.8864
2017-03-03 14:00 | 3 | 14 | 0.87556 | 971.6957
2017-03-03 15:00 | 3 | 15 | 0.93044 | 1032.6059
2017-03-03 16:00 | 3 | 16 | 1.098 | 1218.5772
2017-03-03 17:00 | 3 | 17 | 1.4543 | 1613.9293
2017-03-03 18:00 | 3 | 18 | 1.7325 | 1922.6885
2017-03-03 19:00 | 3 | 19 | 1.9169 | 2127.3493
2017-03-03 20:00 | 3 | 20 | 1.9648 | 2180.5508
2017-03-03 21:00 | 3 | 21 | 1.8187 | 2018.343
2017-03-03 22:00 | 3 | 22 | 1.5141 | 1680.3139
2017-03-03 23:00 | 3 | 23 | 1.2305 | 1365.594
2017-03-04 | 3 | 0 | 0.9379 | 1040.8873
2017-03-04 01:00 | 3 | 1 | 0.82393 | 914.398
2017-03-04 02:00 | 3 | 2 | 0.77708 | 862.4089
2017-03-04 03:00 | 3 | 3 | 0.76397 | 847.8498
2017-03-04 04:00 | 3 | 4 | 0.76542 | 849.4686
2017-03-04 05:00 | 3 | 5 | 0.82251 | 912.8229
2017-03-04 06:00 | 3 | 6 | 0.97876 | 1086.2319
2017-03-04 07:00 | 3 | 7 | 1.2 | 1331.7782
2017-03-04 08:00 | 3 | 8 | 1.1138 | 1236.1175
2017-03-04 09:00 | 3 | 9 | 1.0172 | 1128.8436
2017-03-04 10:00 | 3 | 10 | 1.0314 | 1144.6612
2017-03-04 11:00 | 3 | 11 | 0.9956 | 1104.9167
2017-03-04 12:00 | 3 | 12 | 0.95034 | 1054.688
2017-03-04 13:00 | 3 | 13 | 0.9066 | 1006.1442
2017-03-04 14:00 | 3 | 14 | 0.89136 | 989.2379
2017-03-04 15:00 | 3 | 15 | 0.93036 | 1032.5143
2017-03-04 16:00 | 3 | 16 | 1.0946 | 1214.778
2017-03-04 17:00 | 3 | 17 | 1.4399 | 1597.9705
2017-03-04 18:00 | 3 | 18 | 1.7127 | 1900.7189
2017-03-04 19:00 | 3 | 19 | 1.893 | 2100.8642
2017-03-04 20:00 | 3 | 20 | 1.9434 | 2156.7911
2017-03-04 21:00 | 3 | 21 | 1.7839 | 1979.7665
2017-03-04 22:00 | 3 | 22 | 1.4789 | 1641.2587
2017-03-04 23:00 | 3 | 23 | 1.1807 | 1310.3075
2017-03-05 | 3 | 0 | 0.87325 | 969.1305
2017-03-05 01:00 | 3 | 1 | 0.76184 | 845.4868
2017-03-05 02:00 | 3 | 2 | 0.71897 | 797.9097
2017-03-05 03:00 | 3 | 3 | 0.71374 | 792.113
2017-03-05 04:00 | 3 | 4 | 0.71838 | 797.2586
2017-03-05 05:00 | 3 | 5 | 0.77613 | 861.3515
2017-03-05 06:00 | 3 | 6 | 0.93613 | 1038.9237
2017-03-05 07:00 | 3 | 7 | 1.1566 | 1283.5997
2017-03-05 08:00 | 3 | 8 | 1.0791 | 1197.6417
2017-03-05 09:00 | 3 | 9 | 0.99134 | 1100.1924
2017-03-05 10:00 | 3 | 10 | 1.0171 | 1128.765
2017-03-05 11:00 | 3 | 11 | 1 | 1109.8552
2017-03-05 12:00 | 3 | 12 | 0.97274 | 1079.5446
2017-03-05 13:00 | 3 | 13 | 0.9367 | 1039.5473
2017-03-05 14:00 | 3 | 14 | 0.9265 | 1028.2295
2017-03-05 15:00 | 3 | 15 | 0.97052 | 1077.0823
2017-03-05 16:00 | 3 | 16 | 1.1374 | 1262.2984
2017-03-05 17:00 | 3 | 17 | 1.487 | 1650.2919
2017-03-05 18:00 | 3 | 18 | 1.7553 | 1948.0271
2017-03-05 19:00 | 3 | 19 | 1.9302 | 2142.1662
2017-03-05 20:00 | 3 | 20 | 1.9792 | 2196.5137
2017-03-05 21:00 | 3 | 21 | 1.8174 | 2016.9215
2017-03-05 22:00 | 3 | 22 | 1.5046 | 1669.8304
2017-03-05 23:00 | 3 | 23 | 1.1987 | 1330.346
2017-03-06 | 3 | 0 | 0.87819 | 974.6215
2017-03-06 01:00 | 3 | 1 | 0.76401 | 847.8996
2017-03-06 02:00 | 3 | 2 | 0.71508 | 793.5957
2017-03-06 03:00 | 3 | 3 | 0.70456 | 781.9186
2017-03-06 04:00 | 3 | 4 | 0.70123 | 778.2309
2017-03-06 05:00 | 3 | 5 | 0.75071 | 833.1355
2017-03-06 06:00 | 3 | 6 | 0.89903 | 997.7395
2017-03-06 07:00 | 3 | 7 | 1.1283 | 1252.2199
2017-03-06 08:00 | 3 | 8 | 1.0478 | 1162.8176
2017-03-06 09:00 | 3 | 9 | 0.95779 | 1062.9528
2017-03-06 10:00 | 3 | 10 | 0.98634 | 1094.6419
2017-03-06 11:00 | 3 | 11 | 0.96988 | 1076.3766
2017-03-06 12:00 | 3 | 12 | 0.94315 | 1046.7088
2017-03-06 13:00 | 3 | 13 | 0.91765 | 1018.4048
2017-03-06 14:00 | 3 | 14 | 0.91403 | 1014.3874
2017-03-06 15:00 | 3 | 15 | 0.95078 | 1055.1773
2017-03-06 16:00 | 3 | 16 | 1.1051 | 1226.4156
2017-03-06 17:00 | 3 | 17 | 1.4482 | 1607.1934
2017-03-06 18:00 | 3 | 18 | 1.718 | 1906.6181
2017-03-06 19:00 | 3 | 19 | 1.8896 | 2097.0978
2017-03-06 20:00 | 3 | 20 | 1.9344 | 2146.7495
2017-03-06 21:00 | 3 | 21 | 1.7716 | 1966.1737
2017-03-06 22:00 | 3 | 22 | 1.4669 | 1627.9873
2017-03-06 23:00 | 3 | 23 | 1.1712 | 1299.7919
2017-03-07 | 3 | 0 | 0.8639 | 958.7558
2017-03-07 01:00 | 3 | 1 | 0.74938 | 831.6674
2017-03-07 02:00 | 3 | 2 | 0.70032 | 777.217
2017-03-07 03:00 | 3 | 3 | 0.69043 | 766.2449
2017-03-07 04:00 | 3 | 4 | 0.68953 | 765.2387
2017-03-07 05:00 | 3 | 5 | 0.74496 | 826.7604
2017-03-07 06:00 | 3 | 6 | 0.89566 | 994.0012
2017-03-07 07:00 | 3 | 7 | 1.1237 | 1247.092
2017-03-07 08:00 | 3 | 8 | 1.0461 | 1160.9117
2017-03-07 09:00 | 3 | 9 | 0.96088 | 1066.3842
2017-03-07 10:00 | 3 | 10 | 0.99067 | 1099.4435
2017-03-07 11:00 | 3 | 11 | 0.97892 | 1086.4105
2017-03-07 12:00 | 3 | 12 | 0.95258 | 1057.1703
2017-03-07 13:00 | 3 | 13 | 0.92987 | 1031.9749
2017-03-07 14:00 | 3 | 14 | 0.92092 | 1022.043
2017-03-07 15:00 | 3 | 15 | 0.96354 | 1069.3412
2017-03-07 16:00 | 3 | 16 | 1.1255 | 1249.0691
2017-03-07 17:00 | 3 | 17 | 1.4647 | 1625.5038
2017-03-07 18:00 | 3 | 18 | 1.7265 | 1916.056
2017-03-07 19:00 | 3 | 19 | 1.8965 | 2104.7413
2017-03-07 20:00 | 3 | 20 | 1.9412 | 2154.3291
2017-03-07 21:00 | 3 | 21 | 1.774 | 1968.8211
2017-03-07 22:00 | 3 | 22 | 1.4677 | 1628.8587
2017-03-07 23:00 | 3 | 23 | 1.1737 | 1302.5465
2017-03-08 | 3 | 0 | 0.86706 | 962.2615
2017-03-08 01:00 | 3 | 1 | 0.74827 | 830.4283
2017-03-08 02:00 | 3 | 2 | 0.7004 | 777.3047
2017-03-08 03:00 | 3 | 3 | 0.69117 | 767.0574
2017-03-08 04:00 | 3 | 4 | 0.69222 | 768.228
2017-03-08 05:00 | 3 | 5 | 0.74544 | 827.2949
2017-03-08 06:00 | 3 | 6 | 0.89047 | 988.2455
2017-03-08 07:00 | 3 | 7 | 1.1083 | 1229.9701
2017-03-08 08:00 | 3 | 8 | 1.0341 | 1147.6105
2017-03-08 09:00 | 3 | 9 | 0.95458 | 1059.398
2017-03-08 10:00 | 3 | 10 | 0.98417 | 1092.2298
2017-03-08 11:00 | 3 | 11 | 0.96008 | 1065.497
2017-03-08 12:00 | 3 | 12 | 0.93748 | 1040.4139
2017-03-08 13:00 | 3 | 13 | 0.90931 | 1009.158
2017-03-08 14:00 | 3 | 14 | 0.90036 | 999.2259
2017-03-08 15:00 | 3 | 15 | 0.94019 | 1043.4292
2017-03-08 16:00 | 3 | 16 | 1.0998 | 1220.5531
2017-03-08 17:00 | 3 | 17 | 1.4465 | 1605.2871
2017-03-08 18:00 | 3 | 18 | 1.7108 | 1898.6288
2017-03-08 19:00 | 3 | 19 | 1.8843 | 2091.2209
2017-03-08 20:00 | 3 | 20 | 1.9314 | 2143.508
2017-03-08 21:00 | 3 | 21 | 1.7647 | 1958.4845
2017-03-08 22:00 | 3 | 22 | 1.4602 | 1620.5265
2017-03-08 23:00 | 3 | 23 | 1.1695 | 1297.8767
2017-03-09 | 3 | 0 | 0.86439 | 959.3068
2017-03-09 01:00 | 3 | 1 | 0.7484 | 830.5748
2017-03-09 02:00 | 3 | 2 | 0.70015 | 777.0241
2017-03-09 03:00 | 3 | 3 | 0.69072 | 766.567
2017-03-09 04:00 | 3 | 4 | 0.68902 | 764.6741
2017-03-09 05:00 | 3 | 5 | 0.74254 | 824.0727
2017-03-09 06:00 | 3 | 6 | 0.89503 | 993.3088
2017-03-09 07:00 | 3 | 7 | 1.0999 | 1220.665
2017-03-09 08:00 | 3 | 8 | 1.0237 | 1136.1549
2017-03-09 09:00 | 3 | 9 | 0.93295 | 1035.3872
2017-03-09 10:00 | 3 | 10 | 0.95805 | 1063.2493
2017-03-09 11:00 | 3 | 11 | 0.94014 | 1043.3717
2017-03-09 12:00 | 3 | 12 | 0.90794 | 1007.6346
2017-03-09 13:00 | 3 | 13 | 0.87216 | 967.927
2017-03-09 14:00 | 3 | 14 | 0.86318 | 957.9531
2017-03-09 15:00 | 3 | 15 | 0.90357 | 1002.7821
2017-03-09 16:00 | 3 | 16 | 1.0632 | 1179.9819
2017-03-09 17:00 | 3 | 17 | 1.4059 | 1560.241
2017-03-09 18:00 | 3 | 18 | 1.6784 | 1862.7441
2017-03-09 19:00 | 3 | 19 | 1.857 | 2060.8885
2017-03-09 20:00 | 3 | 20 | 1.9042 | 2113.3059
2017-03-09 21:00 | 3 | 21 | 1.7416 | 1932.8819
2017-03-09 22:00 | 3 | 22 | 1.4373 | 1595.0655
2017-03-09 23:00 | 3 | 23 | 1.149 | 1275.1324
2017-03-10 | 3 | 0 | 0.84553 | 938.3697
2017-03-10 01:00 | 3 | 1 | 0.73064 | 810.8701
2017-03-10 02:00 | 3 | 2 | 0.6842 | 759.3318
2017-03-10 03:00 | 3 | 3 | 0.67559 | 749.7701
2017-03-10 04:00 | 3 | 4 | 0.67598 | 750.2035
2017-03-10 05:00 | 3 | 5 | 0.73087 | 811.1254
2017-03-10 06:00 | 3 | 6 | 0.88323 | 980.2069
2017-03-10 07:00 | 3 | 7 | 1.0869 | 1206.1935
2017-03-10 08:00 | 3 | 8 | 1.0138 | 1125.1662
2017-03-10 09:00 | 3 | 9 | 0.9245 | 1026.0156
2017-03-10 10:00 | 3 | 10 | 0.94503 | 1048.7925
2017-03-10 11:00 | 3 | 11 | 0.92889 | 1030.8849
2017-03-10 12:00 | 3 | 12 | 0.90388 | 1003.1266
2017-03-10 13:00 | 3 | 13 | 0.87696 | 973.2526
2017-03-10 14:00 | 3 | 14 | 0.86905 | 964.4722
2017-03-10 15:00 | 3 | 15 | 0.90669 | 1006.2454
2017-03-10 16:00 | 3 | 16 | 1.0693 | 1186.666
2017-03-10 17:00 | 3 | 17 | 1.4083 | 1562.984
2017-03-10 18:00 | 3 | 18 | 1.6784 | 1862.644
2017-03-10 19:00 | 3 | 19 | 1.8548 | 2058.443
2017-03-10 20:00 | 3 | 20 | 1.9001 | 2108.73
2017-03-10 21:00 | 3 | 21 | 1.7392 | 1930.1291
2017-03-10 22:00 | 3 | 22 | 1.4399 | 1598.0107
2017-03-10 23:00 | 3 | 23 | 1.1517 | 1278.1876
2017-03-11 | 3 | 0 | 0.8589 | 953.209
2017-03-11 01:00 | 3 | 1 | 0.74495 | 826.7487
2017-03-11 02:00 | 3 | 2 | 0.69838 | 775.0608
2017-03-11 03:00 | 3 | 3 | 0.69012 | 765.8966
2017-03-11 04:00 | 3 | 4 | 0.69509 | 771.4159
2017-03-11 05:00 | 3 | 5 | 0.75091 | 833.3665
2017-03-11 06:00 | 3 | 6 | 0.91913 | 1020.0516
2017-03-11 07:00 | 3 | 7 | 1.1307 | 1254.8985
2017-03-11 08:00 | 3 | 8 | 1.0588 | 1175.0983
2017-03-11 09:00 | 3 | 9 | 0.97551 | 1082.6226
2017-03-11 10:00 | 3 | 10 | 1.0038 | 1114.034
2017-03-11 11:00 | 3 | 11 | 0.99733 | 1106.8396
2017-03-11 12:00 | 3 | 12 | 0.97118 | 1077.8169
2017-03-11 13:00 | 3 | 13 | 0.93267 | 1035.078
2017-03-11 14:00 | 3 | 14 | 0.91877 | 1019.6578
2017-03-11 15:00 | 3 | 15 | 0.95552 | 1060.4388
2017-03-11 16:00 | 3 | 16 | 1.1153 | 1237.716
2017-03-11 17:00 | 3 | 17 | 1.4563 | 1616.2522
2017-03-11 18:00 | 3 | 18 | 1.7247 | 1914.1059
2017-03-11 19:00 | 3 | 19 | 1.8998 | 2108.387
2017-03-11 20:00 | 3 | 20 | 1.9532 | 2167.6451
2017-03-11 21:00 | 3 | 21 | 1.7907 | 1987.2862
2017-03-11 22:00 | 3 | 22 | 1.4836 | 1646.4861
2017-03-11 23:00 | 3 | 23 | 1.1843 | 1314.3226
2017-03-12 | 3 | 0 | 0.88052 | 977.206
2017-03-12 01:00 | 3 | 1 | 0.76504 | 849.04
2017-03-12 02:00 | 3 | 2 | 0.72289 | 802.2684
2017-03-12 03:00 | 3 | 3 | 0.71292 | 791.2036
2017-03-12 04:00 | 3 | 4 | 0.71713 | 795.8746
2017-03-12 05:00 | 3 | 5 | 0.77179 | 856.5381
2017-03-12 06:00 | 3 | 6 | 0.93892 | 1042.0129
2017-03-12 07:00 | 3 | 7 | 1.1464 | 1272.3076
2017-03-12 08:00 | 3 | 8 | 1.0732 | 1191.0327
2017-03-12 09:00 | 3 | 9 | 0.97749 | 1084.8248
2017-03-12 10:00 | 3 | 10 | 0.9988 | 1108.471
2017-03-12 11:00 | 3 | 11 | 0.98418 | 1092.2413
2017-03-12 12:00 | 3 | 12 | 0.95851 | 1063.7614
2017-03-12 13:00 | 3 | 13 | 0.92481 | 1026.353
2017-03-12 14:00 | 3 | 14 | 0.9134 | 1013.6932
2017-03-12 15:00 | 3 | 15 | 0.95172 | 1056.2169
2017-03-12 16:00 | 3 | 16 | 1.1154 | 1237.8388
2017-03-12 17:00 | 3 | 17 | 1.4605 | 1620.9005
2017-03-12 18:00 | 3 | 18 | 1.7265 | 1916.084
2017-03-12 19:00 | 3 | 19 | 1.903 | 2111.903
2017-03-12 20:00 | 3 | 20 | 1.9483 | 2162.2229
2017-03-12 21:00 | 3 | 21 | 1.7866 | 1982.7296
2017-03-12 22:00 | 3 | 22 | 1.475 | 1636.9628
2017-03-12 23:00 | 3 | 23 | 1.1719 | 1300.5828
2017-03-13 | 3 | 0 | 0.85442 | 948.2416
2017-03-13 01:00 | 3 | 1 | 0.74399 | 825.6764
2017-03-13 02:00 | 3 | 2 | 0.6969 | 773.4204
2017-03-13 03:00 | 3 | 3 | 0.69387 | 770.053
2017-03-13 04:00 | 3 | 4 | 0.69267 | 768.7212
2017-03-13 05:00 | 3 | 5 | 0.74095 | 822.3041
2017-03-13 06:00 | 3 | 6 | 0.8886 | 986.1657
2017-03-13 07:00 | 3 | 7 | 1.0936 | 1213.6426
2017-03-13 08:00 | 3 | 8 | 0.99872 | 1108.3834
2017-03-13 09:00 | 3 | 9 | 0.88775 | 985.221
2017-03-13 10:00 | 3 | 10 | 0.88276 | 979.6857
2017-03-13 11:00 | 3 | 11 | 0.86183 | 956.4655
2017-03-13 12:00 | 3 | 12 | 0.83252 | 923.9331
2017-03-13 13:00 | 3 | 13 | 0.8184 | 908.2583
2017-03-13 14:00 | 3 | 14 | 0.807 | 895.6154
2017-03-13 15:00 | 3 | 15 | 0.85185 | 945.3883
2017-03-13 16:00 | 3 | 16 | 1.017 | 1128.6567
2017-03-13 17:00 | 3 | 17 | 1.3534 | 1501.9692
2017-03-13 18:00 | 3 | 18 | 1.6376 | 1817.3965
2017-03-13 19:00 | 3 | 19 | 1.8155 | 2014.8473
2017-03-13 20:00 | 3 | 20 | 1.8746 | 2080.4764
2017-03-13 21:00 | 3 | 21 | 1.716 | 1904.4634
2017-03-13 22:00 | 3 | 22 | 1.4158 | 1571.2993
2017-03-13 23:00 | 3 | 23 | 1.1281 | 1251.965
2017-03-14 | 3 | 0 | 0.82509 | 915.6857
2017-03-14 01:00 | 3 | 1 | 0.71862 | 797.5291
2017-03-14 02:00 | 3 | 2 | 0.67369 | 747.6673
2017-03-14 03:00 | 3 | 3 | 0.67251 | 746.3524
2017-03-14 04:00 | 3 | 4 | 0.67923 | 753.8149
2017-03-14 05:00 | 3 | 5 | 0.73896 | 820.1023
2017-03-14 06:00 | 3 | 6 | 0.90796 | 1007.658
2017-03-14 07:00 | 3 | 7 | 1.1164 | 1238.9668
2017-03-14 08:00 | 3 | 8 | 1.0268 | 1139.5429
2017-03-14 09:00 | 3 | 9 | 0.92508 | 1026.6524
2017-03-14 10:00 | 3 | 10 | 0.9503 | 1054.64
2017-03-14 11:00 | 3 | 11 | 0.95178 | 1056.2858
2017-03-14 12:00 | 3 | 12 | 0.92194 | 1023.1751
2017-03-14 13:00 | 3 | 13 | 0.91209 | 1012.2371
2017-03-14 14:00 | 3 | 14 | 0.91637 | 1016.9915
2017-03-14 15:00 | 3 | 15 | 0.96953 | 1075.9817
2017-03-14 16:00 | 3 | 16 | 1.1409 | 1266.2266
2017-03-14 17:00 | 3 | 17 | 1.4894 | 1652.9441
2017-03-14 18:00 | 3 | 18 | 1.7649 | 1958.7169
2017-03-14 19:00 | 3 | 19 | 1.9517 | 2165.9949
2017-03-14 20:00 | 3 | 20 | 2.0107 | 2231.481
2017-03-14 21:00 | 3 | 21 | 1.8469 | 2049.6413
2017-03-14 22:00 | 3 | 22 | 1.5393 | 1708.2892
2017-03-14 23:00 | 3 | 23 | 1.2472 | 1384.1291
2017-03-15 | 3 | 0 | 0.9549 | 1059.7507
2017-03-15 01:00 | 3 | 1 | 0.83789 | 929.8903
2017-03-15 02:00 | 3 | 2 | 0.77263 | 857.4676
2017-03-15 03:00 | 3 | 3 | 0.75921 | 842.5747
2017-03-15 04:00 | 3 | 4 | 0.75061 | 833.0251
2017-03-15 05:00 | 3 | 5 | 0.79468 | 881.9376
2017-03-15 06:00 | 3 | 6 | 0.94198 | 1045.4082
2017-03-15 07:00 | 3 | 7 | 1.133 | 1257.3842
2017-03-15 08:00 | 3 | 8 | 1.0354 | 1149.0777
2017-03-15 09:00 | 3 | 9 | 0.9203 | 1021.3553
2017-03-15 10:00 | 3 | 10 | 0.92093 | 1022.0488
2017-03-15 11:00 | 3 | 11 | 0.89184 | 989.7649
2017-03-15 12:00 | 3 | 12 | 0.85157 | 945.0784
2017-03-15 13:00 | 3 | 13 | 0.8133 | 902.5971
2017-03-15 14:00 | 3 | 14 | 0.80195 | 890.0037
2017-03-15 15:00 | 3 | 15 | 0.84515 | 937.9468
2017-03-15 16:00 | 3 | 16 | 1.0094 | 1120.2881
2017-03-15 17:00 | 3 | 17 | 1.3491 | 1497.211
2017-03-15 18:00 | 3 | 18 | 1.6343 | 1813.704
2017-03-15 19:00 | 3 | 19 | 1.82 | 2019.8364
2017-03-15 20:00 | 3 | 20 | 1.871 | 2076.4359
2017-03-15 21:00 | 3 | 21 | 1.709 | 1896.6327
2017-03-15 22:00 | 3 | 22 | 1.4113 | 1566.2489
2017-03-15 23:00 | 3 | 23 | 1.1257 | 1249.29
2017-03-16 | 3 | 0 | 0.82651 | 917.262
2017-03-16 01:00 | 3 | 1 | 0.71616 | 794.7957
2017-03-16 02:00 | 3 | 2 | 0.66669 | 739.8903
2017-03-16 03:00 | 3 | 3 | 0.66077 | 733.3201
2017-03-16 04:00 | 3 | 4 | 0.6632 | 736.023
2017-03-16 05:00 | 3 | 5 | 0.71862 | 797.5294
2017-03-16 06:00 | 3 | 6 | 0.88046 | 977.1413
2017-03-16 07:00 | 3 | 7 | 1.0765 | 1194.7385
2017-03-16 08:00 | 3 | 8 | 0.9976 | 1107.1403
2017-03-16 09:00 | 3 | 9 | 0.90339 | 1002.5785
2017-03-16 10:00 | 3 | 10 | 0.91695 | 1017.6289
2017-03-16 11:00 | 3 | 11 | 0.90231 | 1001.3811
2017-03-16 12:00 | 3 | 12 | 0.88177 | 978.5911
2017-03-16 13:00 | 3 | 13 | 0.86464 | 959.5756
2017-03-16 14:00 | 3 | 14 | 0.86452 | 959.4418
2017-03-16 15:00 | 3 | 15 | 0.90551 | 1004.9333
2017-03-16 16:00 | 3 | 16 | 1.0767 | 1194.9671
2017-03-16 17:00 | 3 | 17 | 1.4425 | 1600.9058
2017-03-16 18:00 | 3 | 18 | 1.7106 | 1898.4355
2017-03-16 19:00 | 3 | 19 | 1.8905 | 2098.0949
2017-03-16 20:00 | 3 | 20 | 1.9515 | 2165.8233
2017-03-16 21:00 | 3 | 21 | 1.7923 | 1989.0578
2017-03-16 22:00 | 3 | 22 | 1.4982 | 1662.7364
2017-03-16 23:00 | 3 | 23 | 1.2165 | 1350.0791
2017-03-17 | 3 | 0 | 0.91988 | 1020.8884
2017-03-17 01:00 | 3 | 1 | 0.81526 | 904.7743
2017-03-17 02:00 | 3 | 2 | 0.7745 | 859.5447
2017-03-17 03:00 | 3 | 3 | 0.77991 | 865.5476
2017-03-17 04:00 | 3 | 4 | 0.77253 | 857.3537
2017-03-17 05:00 | 3 | 5 | 0.83471 | 926.3649
2017-03-17 06:00 | 3 | 6 | 0.98626 | 1094.5528
2017-03-17 07:00 | 3 | 7 | 1.1932 | 1324.2701
2017-03-17 08:00 | 3 | 8 | 1.1051 | 1226.4185
2017-03-17 09:00 | 3 | 9 | 0.99254 | 1101.523
2017-03-17 10:00 | 3 | 10 | 0.99422 | 1103.388
2017-03-17 11:00 | 3 | 11 | 0.96192 | 1067.5411
2017-03-17 12:00 | 3 | 12 | 0.9263 | 1028.0108
2017-03-17 13:00 | 3 | 13 | 0.89111 | 988.9534
2017-03-17 14:00 | 3 | 14 | 0.87659 | 972.8359
2017-03-17 15:00 | 3 | 15 | 0.92085 | 1021.9649
2017-03-17 16:00 | 3 | 16 | 1.0847 | 1203.7938
2017-03-17 17:00 | 3 | 17 | 1.4211 | 1577.1257
2017-03-17 18:00 | 3 | 18 | 1.6927 | 1878.561
2017-03-17 19:00 | 3 | 19 | 1.8763 | 2082.2691
2017-03-17 20:00 | 3 | 20 | 1.9346 | 2146.9907
2017-03-17 21:00 | 3 | 21 | 1.7988 | 1996.2877
2017-03-17 22:00 | 3 | 22 | 1.5094 | 1675.1161
2017-03-17 23:00 | 3 | 23 | 1.2285 | 1363.4214
2017-03-18 | 3 | 0 | 0.95516 | 1060.0389
2017-03-18 01:00 | 3 | 1 | 0.83936 | 931.5217
2017-03-18 02:00 | 3 | 2 | 0.79936 | 887.1331
2017-03-18 03:00 | 3 | 3 | 0.80045 | 888.3453
2017-03-18 04:00 | 3 | 4 | 0.80557 | 894.0201
2017-03-18 05:00 | 3 | 5 | 0.86647 | 961.6114
2017-03-18 06:00 | 3 | 6 | 1.0293 | 1142.2809
2017-03-18 07:00 | 3 | 7 | 1.2282 | 1363.0656
2017-03-18 08:00 | 3 | 8 | 1.1518 | 1278.2613
2017-03-18 09:00 | 3 | 9 | 1.0452 | 1160.0161
2017-03-18 10:00 | 3 | 10 | 1.0486 | 1163.7823
2017-03-18 11:00 | 3 | 11 | 1.026 | 1138.625
2017-03-18 12:00 | 3 | 12 | 0.98763 | 1096.0744
2017-03-18 13:00 | 3 | 13 | 0.93757 | 1040.5219
2017-03-18 14:00 | 3 | 14 | 0.92707 | 1028.8599
2017-03-18 15:00 | 3 | 15 | 0.97702 | 1084.3014
2017-03-18 16:00 | 3 | 16 | 1.1419 | 1267.2466
2017-03-18 17:00 | 3 | 17 | 1.4864 | 1649.6602
2017-03-18 18:00 | 3 | 18 | 1.76 | 1953.2845
2017-03-18 19:00 | 3 | 19 | 1.9405 | 2153.5997
2017-03-18 20:00 | 3 | 20 | 1.9879 | 2206.1672
2017-03-18 21:00 | 3 | 21 | 1.8289 | 2029.7497
2017-03-18 22:00 | 3 | 22 | 1.5217 | 1688.7791
2017-03-18 23:00 | 3 | 23 | 1.2245 | 1358.9055
2017-03-19 | 3 | 0 | 0.91471 | 1015.146
2017-03-19 01:00 | 3 | 1 | 0.80362 | 891.862
2017-03-19 02:00 | 3 | 2 | 0.76161 | 845.2414
2017-03-19 03:00 | 3 | 3 | 0.75358 | 836.3199
2017-03-19 04:00 | 3 | 4 | 0.75885 | 842.172
2017-03-19 05:00 | 3 | 5 | 0.81676 | 906.4427
2017-03-19 06:00 | 3 | 6 | 0.9904 | 1099.1507
2017-03-19 07:00 | 3 | 7 | 1.1884 | 1318.9393
2017-03-19 08:00 | 3 | 8 | 1.1056 | 1227.0499
2017-03-19 09:00 | 3 | 9 | 1.0073 | 1117.874
2017-03-19 10:00 | 3 | 10 | 1.0241 | 1136.4993
2017-03-19 11:00 | 3 | 11 | 0.98579 | 1094.0341
2017-03-19 12:00 | 3 | 12 | 0.957 | 1062.0787
2017-03-19 13:00 | 3 | 13 | 0.91867 | 1019.5414
2017-03-19 14:00 | 3 | 14 | 0.91091 | 1010.9249
2017-03-19 15:00 | 3 | 15 | 0.95863 | 1063.8899
2017-03-19 16:00 | 3 | 16 | 1.1243 | 1247.7521
2017-03-19 17:00 | 3 | 17 | 1.486 | 1649.1156
2017-03-19 18:00 | 3 | 18 | 1.7576 | 1950.5764
2017-03-19 19:00 | 3 | 19 | 1.9357 | 2148.2131
2017-03-19 20:00 | 3 | 20 | 1.9932 | 2212.0713
2017-03-19 21:00 | 3 | 21 | 1.8272 | 2027.8258
2017-03-19 22:00 | 3 | 22 | 1.5172 | 1683.7571
2017-03-19 23:00 | 3 | 23 | 1.2152 | 1348.6299
2017-03-20 | 3 | 0 | 0.89714 | 995.6487
2017-03-20 01:00 | 3 | 1 | 0.78171 | 867.5482
2017-03-20 02:00 | 3 | 2 | 0.73305 | 813.5351
2017-03-20 03:00 | 3 | 3 | 0.72824 | 808.2069
2017-03-20 04:00 | 3 | 4 | 0.72952 | 809.6224
2017-03-20 05:00 | 3 | 5 | 0.78488 | 871.0616
2017-03-20 06:00 | 3 | 6 | 0.94339 | 1046.9767
2017-03-20 07:00 | 3 | 7 | 1.1329 | 1257.2996
2017-03-20 08:00 | 3 | 8 | 1.0368 | 1150.6901
2017-03-20 09:00 | 3 | 9 | 0.94787 | 1051.9473
2017-03-20 10:00 | 3 | 10 | 0.97091 | 1077.5196
2017-03-20 11:00 | 3 | 11 | 0.94256 | 1046.0568
2017-03-20 12:00 | 3 | 12 | 0.91088 | 1010.8908
2017-03-20 13:00 | 3 | 13 | 0.89034 | 988.0966
2017-03-20 14:00 | 3 | 14 | 0.8925 | 990.503
2017-03-20 15:00 | 3 | 15 | 0.93828 | 1041.3068
2017-03-20 16:00 | 3 | 16 | 1.0987 | 1219.3384
2017-03-20 17:00 | 3 | 17 | 1.4519 | 1611.3037
2017-03-20 18:00 | 3 | 18 | 1.7199 | 1908.7673
2017-03-20 19:00 | 3 | 19 | 1.8978 | 2106.1378
2017-03-20 20:00 | 3 | 20 | 1.9422 | 2155.4284
2017-03-20 21:00 | 3 | 21 | 1.7739 | 1968.6715
2017-03-20 22:00 | 3 | 22 | 1.4732 | 1634.9584
2017-03-20 23:00 | 3 | 23 | 1.186 | 1316.2307
2017-03-21 | 3 | 0 | 0.88123 | 977.9913
2017-03-21 01:00 | 3 | 1 | 0.76694 | 851.1498
2017-03-21 02:00 | 3 | 2 | 0.72161 | 800.8412
2017-03-21 03:00 | 3 | 3 | 0.71158 | 789.7089
2017-03-21 04:00 | 3 | 4 | 0.70888 | 786.7125
2017-03-21 05:00 | 3 | 5 | 0.76469 | 848.6543
2017-03-21 06:00 | 3 | 6 | 0.91301 | 1013.2574
2017-03-21 07:00 | 3 | 7 | 1.126 | 1249.6563
2017-03-21 08:00 | 3 | 8 | 1.0521 | 1167.5696
2017-03-21 09:00 | 3 | 9 | 0.9583 | 1063.528
2017-03-21 10:00 | 3 | 10 | 0.98845 | 1096.9881
2017-03-21 11:00 | 3 | 11 | 0.97291 | 1079.7409
2017-03-21 12:00 | 3 | 12 | 0.95135 | 1055.8066
2017-03-21 13:00 | 3 | 13 | 0.91787 | 1018.6513
2017-03-21 14:00 | 3 | 14 | 0.90719 | 1006.8018
2017-03-21 15:00 | 3 | 15 | 0.93551 | 1038.2282
2017-03-21 16:00 | 3 | 16 | 1.093 | 1213.017
2017-03-21 17:00 | 3 | 17 | 1.4395 | 1597.5238
2017-03-21 18:00 | 3 | 18 | 1.702 | 1888.9117
2017-03-21 19:00 | 3 | 19 | 1.8794 | 2085.808
2017-03-21 20:00 | 3 | 20 | 1.9263 | 2137.825
2017-03-21 21:00 | 3 | 21 | 1.7593 | 1952.5193
2017-03-21 22:00 | 3 | 22 | 1.4517 | 1611.1544
2017-03-21 23:00 | 3 | 23 | 1.162 | 1289.6365
2017-03-22 | 3 | 0 | 0.85672 | 950.7928
2017-03-22 01:00 | 3 | 1 | 0.74392 | 825.6078
2017-03-22 02:00 | 3 | 2 | 0.69584 | 772.244
2017-03-22 03:00 | 3 | 3 | 0.68747 | 762.9543
2017-03-22 04:00 | 3 | 4 | 0.69016 | 765.939
2017-03-22 05:00 | 3 | 5 | 0.74766 | 829.7488
2017-03-22 06:00 | 3 | 6 | 0.91135 | 1011.4199
2017-03-22 07:00 | 3 | 7 | 1.1037 | 1224.9301
2017-03-22 08:00 | 3 | 8 | 1.0145 | 1125.8593
2017-03-22 09:00 | 3 | 9 | 0.91178 | 1011.892
2017-03-22 10:00 | 3 | 10 | 0.93157 | 1033.8558
2017-03-22 11:00 | 3 | 11 | 0.91194 | 1012.0723
2017-03-22 12:00 | 3 | 12 | 0.88689 | 984.2772
2017-03-22 13:00 | 3 | 13 | 0.85209 | 945.6524
2017-03-22 14:00 | 3 | 14 | 0.8465 | 939.4524
2017-03-22 15:00 | 3 | 15 | 0.89226 | 990.2358
2017-03-22 16:00 | 3 | 16 | 1.0581 | 1174.2741
2017-03-22 17:00 | 3 | 17 | 1.4083 | 1562.9185
2017-03-22 18:00 | 3 | 18 | 1.6819 | 1866.6302
2017-03-22 19:00 | 3 | 19 | 1.864 | 2068.6548
2017-03-22 20:00 | 3 | 20 | 1.912 | 2121.8872
2017-03-22 21:00 | 3 | 21 | 1.7558 | 1948.5739
2017-03-22 22:00 | 3 | 22 | 1.4538 | 1613.4243
2017-03-22 23:00 | 3 | 23 | 1.1671 | 1295.2049
2017-03-23 | 3 | 0 | 0.86896 | 964.3729
2017-03-23 01:00 | 3 | 1 | 0.75992 | 843.3625
2017-03-23 02:00 | 3 | 2 | 0.71161 | 789.7438
2017-03-23 03:00 | 3 | 3 | 0.69862 | 775.3302
2017-03-23 04:00 | 3 | 4 | 0.6986 | 775.3057
2017-03-23 05:00 | 3 | 5 | 0.75255 | 835.1767
2017-03-23 06:00 | 3 | 6 | 0.90144 | 1000.4187
2017-03-23 07:00 | 3 | 7 | 1.107 | 1228.5064
2017-03-23 08:00 | 3 | 8 | 1.0229 | 1135.2107
2017-03-23 09:00 | 3 | 9 | 0.92387 | 1025.3174
2017-03-23 10:00 | 3 | 10 | 0.94701 | 1050.9942
2017-03-23 11:00 | 3 | 11 | 0.92302 | 1024.3719
2017-03-23 12:00 | 3 | 12 | 0.89113 | 988.9816
2017-03-23 13:00 | 3 | 13 | 0.8673 | 962.5336
2017-03-23 14:00 | 3 | 14 | 0.85836 | 952.612
2017-03-23 15:00 | 3 | 15 | 0.90233 | 1001.4088
2017-03-23 16:00 | 3 | 16 | 1.0682 | 1185.5381
2017-03-23 17:00 | 3 | 17 | 1.4209 | 1576.9098
2017-03-23 18:00 | 3 | 18 | 1.6929 | 1878.7567
2017-03-23 19:00 | 3 | 19 | 1.8734 | 2079.0717
2017-03-23 20:00 | 3 | 20 | 1.9225 | 2133.6398
2017-03-23 21:00 | 3 | 21 | 1.7583 | 1951.3866
2017-03-23 22:00 | 3 | 22 | 1.459 | 1619.1484
2017-03-23 23:00 | 3 | 23 | 1.1702 | 1298.661
2017-03-24 | 3 | 0 | 0.86656 | 961.7091
2017-03-24 01:00 | 3 | 1 | 0.754 | 836.7906
2017-03-24 02:00 | 3 | 2 | 0.70828 | 786.055
2017-03-24 03:00 | 3 | 3 | 0.6988 | 775.5322
2017-03-24 04:00 | 3 | 4 | 0.70001 | 776.8709
2017-03-24 05:00 | 3 | 5 | 0.75639 | 839.4459
2017-03-24 06:00 | 3 | 6 | 0.91676 | 1017.4259
2017-03-24 07:00 | 3 | 7 | 1.1085 | 1230.2615
2017-03-24 08:00 | 3 | 8 | 1.0143 | 1125.6342
2017-03-24 09:00 | 3 | 9 | 0.91144 | 1011.5225
2017-03-24 10:00 | 3 | 10 | 0.92264 | 1023.9427
2017-03-24 11:00 | 3 | 11 | 0.89562 | 993.9633
2017-03-24 12:00 | 3 | 12 | 0.85909 | 953.4201
2017-03-24 13:00 | 3 | 13 | 0.83071 | 921.9199
2017-03-24 14:00 | 3 | 14 | 0.82556 | 916.2117
2017-03-24 15:00 | 3 | 15 | 0.87377 | 969.7096
2017-03-24 16:00 | 3 | 16 | 1.04 | 1154.1728
2017-03-24 17:00 | 3 | 17 | 1.3938 | 1546.8739
2017-03-24 18:00 | 3 | 18 | 1.6643 | 1847.0673
2017-03-24 19:00 | 3 | 19 | 1.8471 | 2049.8809
2017-03-24 20:00 | 3 | 20 | 1.8946 | 2102.5977
2017-03-24 21:00 | 3 | 21 | 1.7311 | 1921.1465
2017-03-24 22:00 | 3 | 22 | 1.4314 | 1588.5153
2017-03-24 23:00 | 3 | 23 | 1.1404 | 1265.5919
2017-03-25 | 3 | 0 | 0.84507 | 937.8548
2017-03-25 01:00 | 3 | 1 | 0.72801 | 807.9516
2017-03-25 02:00 | 3 | 2 | 0.68376 | 758.8427
2017-03-25 03:00 | 3 | 3 | 0.67454 | 748.6029
2017-03-25 04:00 | 3 | 4 | 0.67895 | 753.4976
2017-03-25 05:00 | 3 | 5 | 0.7395 | 820.6931
2017-03-25 06:00 | 3 | 6 | 0.89379 | 991.9259
2017-03-25 07:00 | 3 | 7 | 1.105 | 1226.3258
2017-03-25 08:00 | 3 | 8 | 1.04 | 1154.1637
2017-03-25 09:00 | 3 | 9 | 0.96816 | 1074.4664
2017-03-25 10:00 | 3 | 10 | 0.99939 | 1109.126
2017-03-25 11:00 | 3 | 11 | 1.0009 | 1110.842
2017-03-25 12:00 | 3 | 12 | 0.98301 | 1090.9456
2017-03-25 13:00 | 3 | 13 | 0.96068 | 1066.1611
2017-03-25 14:00 | 3 | 14 | 0.94833 | 1052.4628
2017-03-25 15:00 | 3 | 15 | 0.98594 | 1094.1941
2017-03-25 16:00 | 3 | 16 | 1.1447 | 1270.3858
2017-03-25 17:00 | 3 | 17 | 1.489 | 1652.4863
2017-03-25 18:00 | 3 | 18 | 1.7503 | 1942.4946
2017-03-25 19:00 | 3 | 19 | 1.9217 | 2132.6935
2017-03-25 20:00 | 3 | 20 | 1.9659 | 2181.7536
2017-03-25 21:00 | 3 | 21 | 1.8033 | 2001.2632
2017-03-25 22:00 | 3 | 22 | 1.4918 | 1655.5722
2017-03-25 23:00 | 3 | 23 | 1.1882 | 1318.7131
2017-03-26 | 3 | 0 | 0.88208 | 978.934
2017-03-26 01:00 | 3 | 1 | 0.76565 | 849.7179
2017-03-26 02:00 | 3 | 2 | 0.71806 | 796.9043
2017-03-26 03:00 | 3 | 3 | 0.70329 | 780.5164
2017-03-26 04:00 | 3 | 4 | 0.70521 | 782.644
2017-03-26 05:00 | 3 | 5 | 0.76132 | 844.9109
2017-03-26 06:00 | 3 | 6 | 0.92773 | 1029.5957
2017-03-26 07:00 | 3 | 7 | 1.1306 | 1254.7085
2017-03-26 08:00 | 3 | 8 | 1.0464 | 1161.2784
2017-03-26 09:00 | 3 | 9 | 0.95422 | 1058.9946
2017-03-26 10:00 | 3 | 10 | 0.95532 | 1060.2113
2017-03-26 11:00 | 3 | 11 | 0.93782 | 1040.7908
2017-03-26 12:00 | 3 | 12 | 0.90745 | 1007.0935
2017-03-26 13:00 | 3 | 13 | 0.87 | 965.5327
2017-03-26 14:00 | 3 | 14 | 0.85682 | 950.9031
2017-03-26 15:00 | 3 | 15 | 0.88762 | 985.0871
2017-03-26 16:00 | 3 | 16 | 1.0527 | 1168.24
2017-03-26 17:00 | 3 | 17 | 1.4003 | 1554.0835
2017-03-26 18:00 | 3 | 18 | 1.6825 | 1867.1949
2017-03-26 19:00 | 3 | 19 | 1.8675 | 2072.5344
2017-03-26 20:00 | 3 | 20 | 1.9238 | 2135.0089
2017-03-26 21:00 | 3 | 21 | 1.769 | 1963.2123
2017-03-26 22:00 | 3 | 22 | 1.4622 | 1622.7369
2017-03-26 23:00 | 3 | 23 | 1.1659 | 1293.9228
2017-03-27 | 3 | 0 | 0.85474 | 948.5883
2017-03-27 01:00 | 3 | 1 | 0.73913 | 820.2894
2017-03-27 02:00 | 3 | 2 | 0.69238 | 768.4075
2017-03-27 03:00 | 3 | 3 | 0.68597 | 761.2942
2017-03-27 04:00 | 3 | 4 | 0.68565 | 760.9382
2017-03-27 05:00 | 3 | 5 | 0.73563 | 816.4041
2017-03-27 06:00 | 3 | 6 | 0.8933 | 991.3834
2017-03-27 07:00 | 3 | 7 | 1.0942 | 1214.3566
2017-03-27 08:00 | 3 | 8 | 1.0221 | 1134.3102
2017-03-27 09:00 | 3 | 9 | 0.93496 | 1037.6181
2017-03-27 10:00 | 3 | 10 | 0.96134 | 1066.8975
2017-03-27 11:00 | 3 | 11 | 0.95259 | 1057.1904
2017-03-27 12:00 | 3 | 12 | 0.93326 | 1035.7324
2017-03-27 13:00 | 3 | 13 | 0.90954 | 1009.4073
2017-03-27 14:00 | 3 | 14 | 0.89879 | 997.48
2017-03-27 15:00 | 3 | 15 | 0.92983 | 1031.927
2017-03-27 16:00 | 3 | 16 | 1.083 | 1201.9385
2017-03-27 17:00 | 3 | 17 | 1.4212 | 1577.2981
2017-03-27 18:00 | 3 | 18 | 1.6877 | 1873.0402
2017-03-27 19:00 | 3 | 19 | 1.859 | 2063.0791
2017-03-27 20:00 | 3 | 20 | 1.9036 | 2112.6464
2017-03-27 21:00 | 3 | 21 | 1.7396 | 1930.5862
2017-03-27 22:00 | 3 | 22 | 1.4372 | 1594.9869
2017-03-27 23:00 | 3 | 23 | 1.1484 | 1274.4882
2017-03-28 | 3 | 0 | 0.85067 | 944.0769
2017-03-28 01:00 | 3 | 1 | 0.73845 | 819.5321
2017-03-28 02:00 | 3 | 2 | 0.69268 | 768.7343
2017-03-28 03:00 | 3 | 3 | 0.68871 | 764.3308
2017-03-28 04:00 | 3 | 4 | 0.69034 | 766.142
2017-03-28 05:00 | 3 | 5 | 0.74767 | 829.7657
2017-03-28 06:00 | 3 | 6 | 0.9071 | 1006.701
2017-03-28 07:00 | 3 | 7 | 1.093 | 1212.9683
2017-03-28 08:00 | 3 | 8 | 1.0071 | 1117.6566
2017-03-28 09:00 | 3 | 9 | 0.90383 | 1003.0719
2017-03-28 10:00 | 3 | 10 | 0.91841 | 1019.2547
2017-03-28 11:00 | 3 | 11 | 0.89117 | 989.0261
2017-03-28 12:00 | 3 | 12 | 0.85323 | 946.9211
2017-03-28 13:00 | 3 | 13 | 0.82265 | 912.9774
2017-03-28 14:00 | 3 | 14 | 0.81562 | 905.178
2017-03-28 15:00 | 3 | 15 | 0.85936 | 953.7223
2017-03-28 16:00 | 3 | 16 | 1.0187 | 1130.5738
2017-03-28 17:00 | 3 | 17 | 1.3539 | 1502.5895
2017-03-28 18:00 | 3 | 18 | 1.6347 | 1814.2277
2017-03-28 19:00 | 3 | 19 | 1.8165 | 2015.9971
2017-03-28 20:00 | 3 | 20 | 1.8676 | 2072.6718
2017-03-28 21:00 | 3 | 21 | 1.7091 | 1896.8084
2017-03-28 22:00 | 3 | 22 | 1.408 | 1562.6397
2017-03-28 23:00 | 3 | 23 | 1.1196 | 1242.5675
2017-03-29 | 3 | 0 | 0.81775 | 907.5419
2017-03-29 01:00 | 3 | 1 | 0.70265 | 779.8043
2017-03-29 02:00 | 3 | 2 | 0.65977 | 732.2114
2017-03-29 03:00 | 3 | 3 | 0.65242 | 724.0539
2017-03-29 04:00 | 3 | 4 | 0.65317 | 724.8923
2017-03-29 05:00 | 3 | 5 | 0.70512 | 782.5426
2017-03-29 06:00 | 3 | 6 | 0.86205 | 956.7052
2017-03-29 07:00 | 3 | 7 | 1.0673 | 1184.4404
2017-03-29 08:00 | 3 | 8 | 0.98657 | 1094.8933
2017-03-29 09:00 | 3 | 9 | 0.88176 | 978.5799
2017-03-29 10:00 | 3 | 10 | 0.87417 | 970.1526
2017-03-29 11:00 | 3 | 11 | 0.85737 | 951.5103
2017-03-29 12:00 | 3 | 12 | 0.81136 | 900.4493
2017-03-29 13:00 | 3 | 13 | 0.76517 | 849.1813
2017-03-29 14:00 | 3 | 14 | 0.74713 | 829.1612
2017-03-29 15:00 | 3 | 15 | 0.78252 | 868.4395
2017-03-29 16:00 | 3 | 16 | 0.94077 | 1044.0694
2017-03-29 17:00 | 3 | 17 | 1.2578 | 1395.8735
2017-03-29 18:00 | 3 | 18 | 1.5511 | 1721.358
2017-03-29 19:00 | 3 | 19 | 1.7342 | 1924.6579
2017-03-29 20:00 | 3 | 20 | 1.7839 | 1979.8111
2017-03-29 21:00 | 3 | 21 | 1.6227 | 1800.9046
2017-03-29 22:00 | 3 | 22 | 1.3213 | 1466.4238
2017-03-29 23:00 | 3 | 23 | 1.0334 | 1146.8865
2017-03-30 | 3 | 0 | 0.73215 | 812.5412
2017-03-30 01:00 | 3 | 1 | 0.62287 | 691.2593
2017-03-30 02:00 | 3 | 2 | 0.57932 | 642.9315
2017-03-30 03:00 | 3 | 3 | 0.57501 | 638.148
2017-03-30 04:00 | 3 | 4 | 0.57917 | 642.7667
2017-03-30 05:00 | 3 | 5 | 0.63976 | 710.0113
2017-03-30 06:00 | 3 | 6 | 0.78982 | 876.5428
2017-03-30 07:00 | 3 | 7 | 1 | 1109.8103
2017-03-30 08:00 | 3 | 8 | 0.91272 | 1012.9356
2017-03-30 09:00 | 3 | 9 | 0.81144 | 900.5339
2017-03-30 10:00 | 3 | 10 | 0.79917 | 886.9243
2017-03-30 11:00 | 3 | 11 | 0.79849 | 886.1634
2017-03-30 12:00 | 3 | 12 | 0.77883 | 864.3453
2017-03-30 13:00 | 3 | 13 | 0.7563 | 839.3428
2017-03-30 14:00 | 3 | 14 | 0.75506 | 837.9684
2017-03-30 15:00 | 3 | 15 | 0.80249 | 890.6082
2017-03-30 16:00 | 3 | 16 | 0.9762 | 1083.3903
2017-03-30 17:00 | 3 | 17 | 1.3119 | 1455.9485
2017-03-30 18:00 | 3 | 18 | 1.6023 | 1778.2257
2017-03-30 19:00 | 3 | 19 | 1.7846 | 1980.5517
2017-03-30 20:00 | 3 | 20 | 1.8311 | 2032.1285
2017-03-30 21:00 | 3 | 21 | 1.6676 | 1850.6813
2017-03-30 22:00 | 3 | 22 | 1.3631 | 1512.7725
2017-03-30 23:00 | 3 | 23 | 1.0725 | 1190.24
2017-03-31 | 3 | 0 | 0.77031 | 854.8861
2017-03-31 01:00 | 3 | 1 | 0.65402 | 725.8337
2017-03-31 02:00 | 3 | 2 | 0.60495 | 671.3775
2017-03-31 03:00 | 3 | 3 | 0.60061 | 666.5549
2017-03-31 04:00 | 3 | 4 | 0.59728 | 662.8602
2017-03-31 05:00 | 3 | 5 | 0.6504 | 721.8097
2017-03-31 06:00 | 3 | 6 | 0.80476 | 893.1282
2017-03-31 07:00 | 3 | 7 | 1.0122 | 1123.2862
2017-03-31 08:00 | 3 | 8 | 0.92365 | 1025.07
2017-03-31 09:00 | 3 | 9 | 0.83717 | 929.0973
2017-03-31 10:00 | 3 | 10 | 0.82098 | 911.1264
2017-03-31 11:00 | 3 | 11 | 0.82647 | 917.2179
2017-03-31 12:00 | 3 | 12 | 0.79754 | 885.1141
2017-03-31 13:00 | 3 | 13 | 0.76133 | 844.9201
2017-03-31 14:00 | 3 | 14 | 0.75474 | 837.613
2017-03-31 15:00 | 3 | 15 | 0.79455 | 881.7927
2017-03-31 16:00 | 3 | 16 | 0.95577 | 1060.7139
2017-03-31 17:00 | 3 | 17 | 1.2781 | 1418.3876
2017-03-31 18:00 | 3 | 18 | 1.5851 | 1759.1867
2017-03-31 19:00 | 3 | 19 | 1.7696 | 1963.9133
2017-03-31 20:00 | 3 | 20 | 1.8221 | 2022.1345
2017-03-31 21:00 | 3 | 21 | 1.6668 | 1849.7816
2017-03-31 22:00 | 3 | 22 | 1.3723 | 1523.0334
2017-03-31 23:00 | 3 | 23 | 1.0912 | 1211.0383
2017-04-01 | 4 | 0 | 0.80224 | 890.3315
2017-04-01 01:00 | 4 | 1 | 0.69903 | 775.7832
2017-04-01 02:00 | 4 | 2 | 0.65742 | 729.6024
2017-04-01 03:00 | 4 | 3 | 0.65796 | 730.2055
2017-04-01 04:00 | 4 | 4 | 0.66749 | 740.7839
2017-04-01 05:00 | 4 | 5 | 0.72952 | 809.6262
2017-04-01 06:00 | 4 | 6 | 0.89432 | 992.5165
2017-04-01 07:00 | 4 | 7 | 1.1299 | 1253.9937
2017-04-01 08:00 | 4 | 8 | 1.07 | 1187.446
2017-04-01 09:00 | 4 | 9 | 0.97748 | 1084.8074
2017-04-01 10:00 | 4 | 10 | 1.01 | 1120.8507
2017-04-01 11:00 | 4 | 11 | 0.99484 | 1104.0757
2017-04-01 12:00 | 4 | 12 | 0.96368 | 1069.4951
2017-04-01 13:00 | 4 | 13 | 0.93138 | 1033.6441
2017-04-01 14:00 | 4 | 14 | 0.91494 | 1015.4021
2017-04-01 15:00 | 4 | 15 | 0.94181 | 1045.2219
2017-04-01 16:00 | 4 | 16 | 1.0572 | 1173.3086
2017-04-01 17:00 | 4 | 17 | 1.2926 | 1434.4963
2017-04-01 18:00 | 4 | 18 | 1.4012 | 1555.0798
2017-04-01 19:00 | 4 | 19 | 1.5155 | 1681.8952
2017-04-01 20:00 | 4 | 20 | 1.7615 | 1954.9647
2017-04-01 21:00 | 4 | 21 | 1.7869 | 1983.1151
2017-04-01 22:00 | 4 | 22 | 1.473 | 1634.793
2017-04-01 23:00 | 4 | 23 | 1.164 | 1291.783
2017-04-02 | 4 | 0 | 0.73702 | 817.9423
2017-04-02 01:00 | 4 | 1 | 0.68535 | 760.6067
2017-04-02 02:00 | 4 | 2 | 0.67448 | 748.5346
2017-04-02 03:00 | 4 | 3 | 0.67485 | 748.9497
2017-04-02 04:00 | 4 | 4 | 0.72854 | 808.5324
2017-04-02 05:00 | 4 | 5 | 0.89051 | 988.2949
2017-04-02 06:00 | 4 | 6 | 1.1307 | 1254.8446
2017-04-02 07:00 | 4 | 7 | 1.068 | 1185.2992
2017-04-02 08:00 | 4 | 8 | 0.97763 | 1084.9766
2017-04-02 09:00 | 4 | 9 | 1.0115 | 1122.5757
2017-04-02 10:00 | 4 | 10 | 0.99362 | 1102.7205
2017-04-02 11:00 | 4 | 11 | 0.96134 | 1066.9015
2017-04-02 12:00 | 4 | 12 | 0.93014 | 1032.2675
2017-04-02 13:00 | 4 | 13 | 0.91387 | 1014.2118
2017-04-02 14:00 | 4 | 14 | 0.9392 | 1042.3225
2017-04-02 15:00 | 4 | 15 | 1.054 | 1169.7847
2017-04-02 16:00 | 4 | 16 | 1.2852 | 1426.2994
2017-04-02 17:00 | 4 | 17 | 1.387 | 1539.3242
2017-04-02 18:00 | 4 | 18 | 1.5022 | 1667.09
2017-04-02 19:00 | 4 | 19 | 1.7487 | 1940.7643
2017-04-02 20:00 | 4 | 20 | 1.7741 | 1968.88
2017-04-02 21:00 | 4 | 21 | 1.4595 | 1619.7482
2017-04-02 22:00 | 4 | 22 | 1.15 | 1276.2911
2017-04-02 23:00 | 4 | 23 | 0.84221 | 934.691
2017-04-03 | 4 | 0 | 0.72768 | 807.5843
2017-04-03 01:00 | 4 | 1 | 0.67879 | 753.3187
2017-04-03 02:00 | 4 | 2 | 0.67144 | 745.1627
2017-04-03 03:00 | 4 | 3 | 0.66964 | 743.1673
2017-04-03 04:00 | 4 | 4 | 0.72573 | 805.4168
2017-04-03 05:00 | 4 | 5 | 0.87933 | 975.8791
2017-04-03 06:00 | 4 | 6 | 1.1244 | 1247.8247
2017-04-03 07:00 | 4 | 7 | 1.0443 | 1158.9708
2017-04-03 08:00 | 4 | 8 | 0.941 | 1044.3242
2017-04-03 09:00 | 4 | 9 | 0.96999 | 1076.4912
2017-04-03 10:00 | 4 | 10 | 0.96513 | 1071.1016
2017-04-03 11:00 | 4 | 11 | 0.94195 | 1045.3782
2017-04-03 12:00 | 4 | 12 | 0.91737 | 1018.0939
2017-04-03 13:00 | 4 | 13 | 0.91221 | 1012.3689
2017-04-03 14:00 | 4 | 14 | 0.93793 | 1040.9131
2017-04-03 15:00 | 4 | 15 | 1.0651 | 1182.0515
2017-04-03 16:00 | 4 | 16 | 1.2687 | 1408.0216
2017-04-03 17:00 | 4 | 17 | 1.3846 | 1536.5842
2017-04-03 18:00 | 4 | 18 | 1.5006 | 1665.4138
2017-04-03 19:00 | 4 | 19 | 1.7452 | 1936.7999
2017-04-03 20:00 | 4 | 20 | 1.7658 | 1959.6827
2017-04-03 21:00 | 4 | 21 | 1.4526 | 1612.0873
2017-04-03 22:00 | 4 | 22 | 1.1464 | 1272.2883
2017-04-03 23:00 | 4 | 23 | 0.84452 | 937.249
2017-04-04 | 4 | 0 | 0.74367 | 825.3243
2017-04-04 01:00 | 4 | 1 | 0.69556 | 771.9385
2017-04-04 02:00 | 4 | 2 | 0.68549 | 760.7634
2017-04-04 03:00 | 4 | 3 | 0.67112 | 744.8126
2017-04-04 04:00 | 4 | 4 | 0.71954 | 798.544
2017-04-04 05:00 | 4 | 5 | 0.86663 | 961.7831
2017-04-04 06:00 | 4 | 6 | 1.0887 | 1208.2911
2017-04-04 07:00 | 4 | 7 | 1.0142 | 1125.5978
2017-04-04 08:00 | 4 | 8 | 0.9029 | 1002.0371
2017-04-04 09:00 | 4 | 9 | 0.92116 | 1022.3031
2017-04-04 10:00 | 4 | 10 | 0.91814 | 1018.9577
2017-04-04 11:00 | 4 | 11 | 0.89482 | 993.0764
2017-04-04 12:00 | 4 | 12 | 0.86778 | 963.059
2017-04-04 13:00 | 4 | 13 | 0.86266 | 957.3778
2017-04-04 14:00 | 4 | 14 | 0.89026 | 988.012
2017-04-04 15:00 | 4 | 15 | 1.0041 | 1114.3019
2017-04-04 16:00 | 4 | 16 | 1.2281 | 1362.8962
2017-04-04 17:00 | 4 | 17 | 1.3387 | 1485.6928
2017-04-04 18:00 | 4 | 18 | 1.4589 | 1619.088
2017-04-04 19:00 | 4 | 19 | 1.7037 | 1890.7825
2017-04-04 20:00 | 4 | 20 | 1.7315 | 1921.6122
2017-04-04 21:00 | 4 | 21 | 1.4272 | 1583.8991
2017-04-04 22:00 | 4 | 22 | 1.132 | 1256.2565
2017-04-04 23:00 | 4 | 23 | 0.8331 | 924.5783
2017-04-05 | 4 | 0 | 0.72094 | 800.1032
2017-04-05 01:00 | 4 | 1 | 0.66959 | 743.1153
2017-04-05 02:00 | 4 | 2 | 0.6615 | 734.1314
2017-04-05 03:00 | 4 | 3 | 0.65936 | 731.7537
2017-04-05 04:00 | 4 | 4 | 0.71759 | 796.3801
2017-04-05 05:00 | 4 | 5 | 0.87421 | 970.2044
2017-04-05 06:00 | 4 | 6 | 1.1048 | 1226.1059
2017-04-05 07:00 | 4 | 7 | 1.0214 | 1133.5786
2017-04-05 08:00 | 4 | 8 | 0.90277 | 1001.8945
2017-04-05 09:00 | 4 | 9 | 0.90286 | 1001.9919
2017-04-05 10:00 | 4 | 10 | 0.8891 | 986.7214
2017-04-05 11:00 | 4 | 11 | 0.85788 | 952.0746
2017-04-05 12:00 | 4 | 12 | 0.82194 | 912.1892
2017-04-05 13:00 | 4 | 13 | 0.81268 | 901.9189
2017-04-05 14:00 | 4 | 14 | 0.83735 | 929.289
2017-04-05 15:00 | 4 | 15 | 0.95414 | 1058.9106
2017-04-05 16:00 | 4 | 16 | 1.1708 | 1299.3801
2017-04-05 17:00 | 4 | 17 | 1.2941 | 1436.2447
2017-04-05 18:00 | 4 | 18 | 1.4177 | 1573.4119
2017-04-05 19:00 | 4 | 19 | 1.6682 | 1851.4075
2017-04-05 20:00 | 4 | 20 | 1.6987 | 1885.2434
2017-04-05 21:00 | 4 | 21 | 1.3976 | 1551.0321
2017-04-05 22:00 | 4 | 22 | 1.1064 | 1227.8414
2017-04-05 23:00 | 4 | 23 | 0.82019 | 910.2527
2017-04-06 | 4 | 0 | 0.71602 | 794.6347
2017-04-06 01:00 | 4 | 1 | 0.66702 | 740.2601
2017-04-06 02:00 | 4 | 2 | 0.65692 | 729.0493
2017-04-06 03:00 | 4 | 3 | 0.65478 | 726.6772
2017-04-06 04:00 | 4 | 4 | 0.70682 | 784.4286
2017-04-06 05:00 | 4 | 5 | 0.86245 | 957.1512
2017-04-06 06:00 | 4 | 6 | 1.0901 | 1209.769
2017-04-06 07:00 | 4 | 7 | 1.0148 | 1126.183
2017-04-06 08:00 | 4 | 8 | 0.90261 | 1001.7224
2017-04-06 09:00 | 4 | 9 | 0.91731 | 1018.031
2017-04-06 10:00 | 4 | 10 | 0.89875 | 997.4338
2017-04-06 11:00 | 4 | 11 | 0.87095 | 966.5857
2017-04-06 12:00 | 4 | 12 | 0.83864 | 930.7265
2017-04-06 13:00 | 4 | 13 | 0.82234 | 912.6396
2017-04-06 14:00 | 4 | 14 | 0.85207 | 945.6298
2017-04-06 15:00 | 4 | 15 | 0.96894 | 1075.3315
2017-04-06 16:00 | 4 | 16 | 1.1914 | 1322.2624
2017-04-06 17:00 | 4 | 17 | 1.306 | 1449.4075
2017-04-06 18:00 | 4 | 18 | 1.4247 | 1581.1397
2017-04-06 19:00 | 4 | 19 | 1.6797 | 1864.1126
2017-04-06 20:00 | 4 | 20 | 1.7103 | 1898.1071
2017-04-06 21:00 | 4 | 21 | 1.4086 | 1563.2618
2017-04-06 22:00 | 4 | 22 | 1.1175 | 1240.2402
2017-04-06 23:00 | 4 | 23 | 0.82364 | 914.0772
2017-04-07 | 4 | 0 | 0.71372 | 792.0929
2017-04-07 01:00 | 4 | 1 | 0.66722 | 740.4777
2017-04-07 02:00 | 4 | 2 | 0.6631 | 735.912
2017-04-07 03:00 | 4 | 3 | 0.66447 | 737.4341
2017-04-07 04:00 | 4 | 4 | 0.73675 | 817.6408
2017-04-07 05:00 | 4 | 5 | 0.91042 | 1010.3899
2017-04-07 06:00 | 4 | 6 | 1.135 | 1259.6429
2017-04-07 07:00 | 4 | 7 | 1.0662 | 1183.3011
2017-04-07 08:00 | 4 | 8 | 0.96202 | 1067.6539
2017-04-07 09:00 | 4 | 9 | 0.98165 | 1089.4345
2017-04-07 10:00 | 4 | 10 | 0.96187 | 1067.4814
2017-04-07 11:00 | 4 | 11 | 0.92207 | 1023.3109
2017-04-07 12:00 | 4 | 12 | 0.8866 | 983.945
2017-04-07 13:00 | 4 | 13 | 0.86773 | 963.0057
2017-04-07 14:00 | 4 | 14 | 0.89093 | 988.7534
2017-04-07 15:00 | 4 | 15 | 1.0025 | 1112.536
2017-04-07 16:00 | 4 | 16 | 1.2256 | 1360.2258
2017-04-07 17:00 | 4 | 17 | 1.3285 | 1474.3376
2017-04-07 18:00 | 4 | 18 | 1.4475 | 1606.4193
2017-04-07 19:00 | 4 | 19 | 1.6994 | 1885.9704
2017-04-07 20:00 | 4 | 20 | 1.738 | 1928.8433
2017-04-07 21:00 | 4 | 21 | 1.4352 | 1592.8366
2017-04-07 22:00 | 4 | 22 | 1.1464 | 1272.3276
2017-04-07 23:00 | 4 | 23 | 0.85041 | 943.7851
2017-04-08 | 4 | 0 | 0.75153 | 834.0547
2017-04-08 01:00 | 4 | 1 | 0.69898 | 775.7316
2017-04-08 02:00 | 4 | 2 | 0.68905 | 764.7069
2017-04-08 03:00 | 4 | 3 | 0.69738 | 773.9559
2017-04-08 04:00 | 4 | 4 | 0.75622 | 839.2492
2017-04-08 05:00 | 4 | 5 | 0.91842 | 1019.2589
2017-04-08 06:00 | 4 | 6 | 1.1591 | 1286.3884
2017-04-08 07:00 | 4 | 7 | 1.0883 | 1207.8025
2017-04-08 08:00 | 4 | 8 | 0.98739 | 1095.8079
2017-04-08 09:00 | 4 | 9 | 1.0044 | 1114.6338
2017-04-08 10:00 | 4 | 10 | 0.98795 | 1096.4232
2017-04-08 11:00 | 4 | 11 | 0.94474 | 1048.4762
2017-04-08 12:00 | 4 | 12 | 0.91162 | 1011.7174
2017-04-08 13:00 | 4 | 13 | 0.89825 | 996.8745
2017-04-08 14:00 | 4 | 14 | 0.91872 | 1019.5918
2017-04-08 15:00 | 4 | 15 | 1.0331 | 1146.5235
2017-04-08 16:00 | 4 | 16 | 1.2586 | 1396.8449
2017-04-08 17:00 | 4 | 17 | 1.3669 | 1517.0332
2017-04-08 18:00 | 4 | 18 | 1.4844 | 1647.4027
2017-04-08 19:00 | 4 | 19 | 1.7374 | 1928.1722
2017-04-08 20:00 | 4 | 20 | 1.7646 | 1958.3297
2017-04-08 21:00 | 4 | 21 | 1.4577 | 1617.7598
2017-04-08 22:00 | 4 | 22 | 1.1523 | 1278.7875
2017-04-08 23:00 | 4 | 23 | 0.84897 | 942.1852
2017-04-09 | 4 | 0 | 0.73802 | 819.0579
2017-04-09 01:00 | 4 | 1 | 0.68758 | 763.0827
2017-04-09 02:00 | 4 | 2 | 0.67733 | 751.7073
2017-04-09 03:00 | 4 | 3 | 0.68162 | 756.4582
2017-04-09 04:00 | 4 | 4 | 0.73734 | 818.3034
2017-04-09 05:00 | 4 | 5 | 0.89963 | 998.4162
2017-04-09 06:00 | 4 | 6 | 1.1362 | 1260.9407
2017-04-09 07:00 | 4 | 7 | 1.0653 | 1182.2474
2017-04-09 08:00 | 4 | 8 | 0.95113 | 1055.564
2017-04-09 09:00 | 4 | 9 | 0.95445 | 1059.2499
2017-04-09 10:00 | 4 | 10 | 0.93213 | 1034.4841
2017-04-09 11:00 | 4 | 11 | 0.88975 | 987.4489
2017-04-09 12:00 | 4 | 12 | 0.84836 | 941.5076
2017-04-09 13:00 | 4 | 13 | 0.82593 | 916.6237
2017-04-09 14:00 | 4 | 14 | 0.84408 | 936.7577
2017-04-09 15:00 | 4 | 15 | 0.96035 | 1065.802
2017-04-09 16:00 | 4 | 16 | 1.1747 | 1303.6804
2017-04-09 17:00 | 4 | 17 | 1.2994 | 1442.0863
2017-04-09 18:00 | 4 | 18 | 1.4281 | 1584.9204
2017-04-09 19:00 | 4 | 19 | 1.6836 | 1868.482
2017-04-09 20:00 | 4 | 20 | 1.7203 | 1909.207
2017-04-09 21:00 | 4 | 21 | 1.4118 | 1566.8168
2017-04-09 22:00 | 4 | 22 | 1.106 | 1227.4809
2017-04-09 23:00 | 4 | 23 | 0.80459 | 892.9352
2017-04-10 | 4 | 0 | 0.68886 | 764.4979
2017-04-10 01:00 | 4 | 1 | 0.64028 | 710.5843
2017-04-10 02:00 | 4 | 2 | 0.63255 | 702.0005
2017-04-10 03:00 | 4 | 3 | 0.63675 | 706.6633
2017-04-10 04:00 | 4 | 4 | 0.68943 | 765.1309
2017-04-10 05:00 | 4 | 5 | 0.85198 | 945.5335
2017-04-10 06:00 | 4 | 6 | 1.0715 | 1189.1087
2017-04-10 07:00 | 4 | 7 | 0.99431 | 1103.4831
2017-04-10 08:00 | 4 | 8 | 0.8824 | 979.2929
2017-04-10 09:00 | 4 | 9 | 0.89875 | 997.4369
2017-04-10 10:00 | 4 | 10 | 0.88495 | 982.1153
2017-04-10 11:00 | 4 | 11 | 0.85161 | 945.1184
2017-04-10 12:00 | 4 | 12 | 0.82539 | 916.017
2017-04-10 13:00 | 4 | 13 | 0.807 | 895.612
2017-04-10 14:00 | 4 | 14 | 0.83024 | 921.4031
2017-04-10 15:00 | 4 | 15 | 0.94552 | 1049.3355
2017-04-10 16:00 | 4 | 16 | 1.1548 | 1281.6363
2017-04-10 17:00 | 4 | 17 | 1.2765 | 1416.6551
2017-04-10 18:00 | 4 | 18 | 1.3909 | 1543.5692
2017-04-10 19:00 | 4 | 19 | 1.6377 | 1817.5354
2017-04-10 20:00 | 4 | 20 | 1.6628 | 1845.4249
2017-04-10 21:00 | 4 | 21 | 1.3655 | 1515.4076
2017-04-10 22:00 | 4 | 22 | 1.0744 | 1192.3466
2017-04-10 23:00 | 4 | 23 | 0.7752 | 860.3137
2017-04-11 | 4 | 0 | 0.66357 | 736.4357
2017-04-11 01:00 | 4 | 1 | 0.61239 | 679.6358
2017-04-11 02:00 | 4 | 2 | 0.60707 | 673.7221
2017-04-11 03:00 | 4 | 3 | 0.60614 | 672.7001
2017-04-11 04:00 | 4 | 4 | 0.657 | 729.1384
2017-04-11 05:00 | 4 | 5 | 0.81689 | 906.5879
2017-04-11 06:00 | 4 | 6 | 1.0486 | 1163.7858
2017-04-11 07:00 | 4 | 7 | 0.96864 | 1074.9982
2017-04-11 08:00 | 4 | 8 | 0.85662 | 950.6752
2017-04-11 09:00 | 4 | 9 | 0.86811 | 963.4274
2017-04-11 10:00 | 4 | 10 | 0.86353 | 958.3458
2017-04-11 11:00 | 4 | 11 | 0.84581 | 938.6817
2017-04-11 12:00 | 4 | 12 | 0.82165 | 911.863
2017-04-11 13:00 | 4 | 13 | 0.81044 | 899.4267
2017-04-11 14:00 | 4 | 14 | 0.8385 | 930.5672
2017-04-11 15:00 | 4 | 15 | 0.95581 | 1060.7543
2017-04-11 16:00 | 4 | 16 | 1.1837 | 1313.6449
2017-04-11 17:00 | 4 | 17 | 1.301 | 1443.8379
2017-04-11 18:00 | 4 | 18 | 1.4277 | 1584.5072
2017-04-11 19:00 | 4 | 19 | 1.6808 | 1865.3619
2017-04-11 20:00 | 4 | 20 | 1.7207 | 1909.6381
2017-04-11 21:00 | 4 | 21 | 1.4195 | 1575.3565
2017-04-11 22:00 | 4 | 22 | 1.1276 | 1251.3686
2017-04-11 23:00 | 4 | 23 | 0.83905 | 931.1812
2017-04-12 | 4 | 0 | 0.72952 | 809.628
2017-04-12 01:00 | 4 | 1 | 0.68184 | 756.7098
2017-04-12 02:00 | 4 | 2 | 0.67493 | 749.0357
2017-04-12 03:00 | 4 | 3 | 0.68148 | 756.3121
2017-04-12 04:00 | 4 | 4 | 0.7408 | 822.1442
2017-04-12 05:00 | 4 | 5 | 0.89667 | 995.124
2017-04-12 06:00 | 4 | 6 | 1.1249 | 1248.4378
2017-04-12 07:00 | 4 | 7 | 1.0441 | 1158.7559
2017-04-12 08:00 | 4 | 8 | 0.93038 | 1032.5357
2017-04-12 09:00 | 4 | 9 | 0.93863 | 1041.697
2017-04-12 10:00 | 4 | 10 | 0.92546 | 1027.0721
2017-04-12 11:00 | 4 | 11 | 0.88902 | 986.6359
2017-04-12 12:00 | 4 | 12 | 0.85871 | 953.0026
2017-04-12 13:00 | 4 | 13 | 0.83825 | 930.2908
2017-04-12 14:00 | 4 | 14 | 0.8651 | 960.0916
2017-04-12 15:00 | 4 | 15 | 0.98611 | 1094.388
2017-04-12 16:00 | 4 | 16 | 1.214 | 1347.347
2017-04-12 17:00 | 4 | 17 | 1.3316 | 1477.8523
2017-04-12 18:00 | 4 | 18 | 1.4534 | 1612.9812
2017-04-12 19:00 | 4 | 19 | 1.7071 | 1894.5635
2017-04-12 20:00 | 4 | 20 | 1.743 | 1934.3799
2017-04-12 21:00 | 4 | 21 | 1.4426 | 1600.9903
2017-04-12 22:00 | 4 | 22 | 1.1552 | 1282.0915
2017-04-12 23:00 | 4 | 23 | 0.85723 | 951.3503
2017-04-13 | 4 | 0 | 0.75139 | 833.8936
2017-04-13 01:00 | 4 | 1 | 0.70524 | 782.676
2017-04-13 02:00 | 4 | 2 | 0.6992 | 775.9778
2017-04-13 03:00 | 4 | 3 | 0.69839 | 775.0705
2017-04-13 04:00 | 4 | 4 | 0.75768 | 840.8717
2017-04-13 05:00 | 4 | 5 | 0.9244 | 1025.9018
2017-04-13 06:00 | 4 | 6 | 1.1358 | 1260.5475
2017-04-13 07:00 | 4 | 7 | 1.0527 | 1168.2697
2017-04-13 08:00 | 4 | 8 | 0.93218 | 1034.5384
2017-04-13 09:00 | 4 | 9 | 0.9463 | 1050.2107
2017-04-13 10:00 | 4 | 10 | 0.92299 | 1024.3371
2017-04-13 11:00 | 4 | 11 | 0.88484 | 981.9918
2017-04-13 12:00 | 4 | 12 | 0.84953 | 942.8117
2017-04-13 13:00 | 4 | 13 | 0.84111 | 933.4642
2017-04-13 14:00 | 4 | 14 | 0.87127 | 966.9363
2017-04-13 15:00 | 4 | 15 | 0.98846 | 1096.9981
2017-04-13 16:00 | 4 | 16 | 1.2194 | 1353.2592
2017-04-13 17:00 | 4 | 17 | 1.3215 | 1466.6127
2017-04-13 18:00 | 4 | 18 | 1.4431 | 1601.5848
2017-04-13 19:00 | 4 | 19 | 1.6988 | 1885.3531
2017-04-13 20:00 | 4 | 20 | 1.7317 | 1921.7951
2017-04-13 21:00 | 4 | 21 | 1.4312 | 1588.3958
2017-04-13 22:00 | 4 | 22 | 1.144 | 1269.6056
2017-04-13 23:00 | 4 | 23 | 0.84821 | 941.3457
2017-04-14 | 4 | 0 | 0.74056 | 821.877
2017-04-14 01:00 | 4 | 1 | 0.69186 | 767.8275
2017-04-14 02:00 | 4 | 2 | 0.68464 | 759.8149
2017-04-14 03:00 | 4 | 3 | 0.68645 | 761.8287
2017-04-14 04:00 | 4 | 4 | 0.74182 | 823.2722
2017-04-14 05:00 | 4 | 5 | 0.90931 | 1009.1574
2017-04-14 06:00 | 4 | 6 | 1.1214 | 1244.56
2017-04-14 07:00 | 4 | 7 | 1.0355 | 1149.2439
2017-04-14 08:00 | 4 | 8 | 0.90982 | 1009.7182
2017-04-14 09:00 | 4 | 9 | 0.90978 | 1009.6798
2017-04-14 10:00 | 4 | 10 | 0.89381 | 991.9522
2017-04-14 11:00 | 4 | 11 | 0.85679 | 950.8626
2017-04-14 12:00 | 4 | 12 | 0.82134 | 911.5227
2017-04-14 13:00 | 4 | 13 | 0.80535 | 893.7813
2017-04-14 14:00 | 4 | 14 | 0.8308 | 922.0185
2017-04-14 15:00 | 4 | 15 | 0.94632 | 1050.2246
2017-04-14 16:00 | 4 | 16 | 1.1777 | 1307.0474
2017-04-14 17:00 | 4 | 17 | 1.3009 | 1443.7381
2017-04-14 18:00 | 4 | 18 | 1.425 | 1581.4508
2017-04-14 19:00 | 4 | 19 | 1.6784 | 1862.6611
2017-04-14 20:00 | 4 | 20 | 1.7152 | 1903.5798
2017-04-14 21:00 | 4 | 21 | 1.4138 | 1569.0317
2017-04-14 22:00 | 4 | 22 | 1.1175 | 1240.2537
2017-04-14 23:00 | 4 | 23 | 0.82281 | 913.1577
2017-04-15 | 4 | 0 | 0.71714 | 795.8853
2017-04-15 01:00 | 4 | 1 | 0.66106 | 733.6462
2017-04-15 02:00 | 4 | 2 | 0.6488 | 720.0367
2017-04-15 03:00 | 4 | 3 | 0.64868 | 719.9036
2017-04-15 04:00 | 4 | 4 | 0.70244 | 779.5673
2017-04-15 05:00 | 4 | 5 | 0.87527 | 971.3786
2017-04-15 06:00 | 4 | 6 | 1.1053 | 1226.6504
2017-04-15 07:00 | 4 | 7 | 1.0459 | 1160.7083
2017-04-15 08:00 | 4 | 8 | 0.95886 | 1064.1427
2017-04-15 09:00 | 4 | 9 | 0.9796 | 1087.1635
2017-04-15 10:00 | 4 | 10 | 0.968 | 1074.2933
2017-04-15 11:00 | 4 | 11 | 0.93426 | 1036.8422
2017-04-15 12:00 | 4 | 12 | 0.89945 | 998.2136
2017-04-15 13:00 | 4 | 13 | 0.88165 | 978.4553
2017-04-15 14:00 | 4 | 14 | 0.90332 | 1002.5083
2017-04-15 15:00 | 4 | 15 | 1.0143 | 1125.6542
2017-04-15 16:00 | 4 | 16 | 1.2115 | 1344.5669
2017-04-15 17:00 | 4 | 17 | 1.3322 | 1478.5001
2017-04-15 18:00 | 4 | 18 | 1.4485 | 1607.5555
2017-04-15 19:00 | 4 | 19 | 1.6971 | 1883.441
2017-04-15 20:00 | 4 | 20 | 1.7211 | 1910.1299
2017-04-15 21:00 | 4 | 21 | 1.4084 | 1563.0444
2017-04-15 22:00 | 4 | 22 | 1.1021 | 1223.1345
2017-04-15 23:00 | 4 | 23 | 0.79307 | 880.1493
2017-04-16 | 4 | 0 | 0.68278 | 757.7527
2017-04-16 01:00 | 4 | 1 | 0.62812 | 697.0939
2017-04-16 02:00 | 4 | 2 | 0.62019 | 688.2865
2017-04-16 03:00 | 4 | 3 | 0.62332 | 691.7659
2017-04-16 04:00 | 4 | 4 | 0.67845 | 752.9448
2017-04-16 05:00 | 4 | 5 | 0.84126 | 933.6278
2017-04-16 06:00 | 4 | 6 | 1.0815 | 1200.256
2017-04-16 07:00 | 4 | 7 | 1.0078 | 1118.4552
2017-04-16 08:00 | 4 | 8 | 0.9055 | 1004.9288
2017-04-16 09:00 | 4 | 9 | 0.91562 | 1016.1555
2017-04-16 10:00 | 4 | 10 | 0.90729 | 1006.9111
2017-04-16 11:00 | 4 | 11 | 0.87018 | 965.7216
2017-04-16 12:00 | 4 | 12 | 0.83076 | 921.9766
2017-04-16 13:00 | 4 | 13 | 0.80607 | 894.5771
2017-04-16 14:00 | 4 | 14 | 0.82499 | 915.5801
2017-04-16 15:00 | 4 | 15 | 0.9371 | 1039.9992
2017-04-16 16:00 | 4 | 16 | 1.1473 | 1273.2215
2017-04-16 17:00 | 4 | 17 | 1.2682 | 1407.4859
2017-04-16 18:00 | 4 | 18 | 1.3916 | 1544.4015
2017-04-16 19:00 | 4 | 19 | 1.645 | 1825.6326
2017-04-16 20:00 | 4 | 20 | 1.6803 | 1864.7767
2017-04-16 21:00 | 4 | 21 | 1.379 | 1530.418
2017-04-16 22:00 | 4 | 22 | 1.086 | 1205.2202
2017-04-16 23:00 | 4 | 23 | 0.78464 | 870.7968
2017-04-17 | 4 | 0 | 0.67468 | 748.7628
2017-04-17 01:00 | 4 | 1 | 0.63252 | 701.9743
2017-04-17 02:00 | 4 | 2 | 0.62773 | 696.6507
2017-04-17 03:00 | 4 | 3 | 0.63442 | 704.0856
2017-04-17 04:00 | 4 | 4 | 0.69043 | 766.2425
2017-04-17 05:00 | 4 | 5 | 0.84919 | 942.4286
2017-04-17 06:00 | 4 | 6 | 1.0762 | 1194.3633
2017-04-17 07:00 | 4 | 7 | 0.9985 | 1108.1393
2017-04-17 08:00 | 4 | 8 | 0.89379 | 991.9319
2017-04-17 09:00 | 4 | 9 | 0.90588 | 1005.3445
2017-04-17 10:00 | 4 | 10 | 0.92694 | 1028.7208
2017-04-17 11:00 | 4 | 11 | 0.8892 | 986.8374
2017-04-17 12:00 | 4 | 12 | 0.8583 | 952.5444
2017-04-17 13:00 | 4 | 13 | 0.84226 | 934.7398
2017-04-17 14:00 | 4 | 14 | 0.8596 | 953.9809
2017-04-17 15:00 | 4 | 15 | 0.98472 | 1092.8452
2017-04-17 16:00 | 4 | 16 | 1.219 | 1352.8312
2017-04-17 17:00 | 4 | 17 | 1.332 | 1478.2983
2017-04-17 18:00 | 4 | 18 | 1.4472 | 1606.0577
2017-04-17 19:00 | 4 | 19 | 1.6953 | 1881.4953
2017-04-17 20:00 | 4 | 20 | 1.725 | 1914.3646
2017-04-17 21:00 | 4 | 21 | 1.4262 | 1582.8259
2017-04-17 22:00 | 4 | 22 | 1.1324 | 1256.782
2017-04-17 23:00 | 4 | 23 | 0.83758 | 929.5465
2017-04-18 | 4 | 0 | 0.73226 | 812.6619
2017-04-18 01:00 | 4 | 1 | 0.68802 | 763.5673
2017-04-18 02:00 | 4 | 2 | 0.68449 | 759.6452
2017-04-18 03:00 | 4 | 3 | 0.68526 | 760.4993
2017-04-18 04:00 | 4 | 4 | 0.74069 | 822.0143
2017-04-18 05:00 | 4 | 5 | 0.89549 | 993.8145
2017-04-18 06:00 | 4 | 6 | 1.1165 | 1239.0904
2017-04-18 07:00 | 4 | 7 | 1.0375 | 1151.4188
2017-04-18 08:00 | 4 | 8 | 0.9163 | 1016.9159
2017-04-18 09:00 | 4 | 9 | 0.92564 | 1027.2778
2017-04-18 10:00 | 4 | 10 | 0.90752 | 1007.1661
2017-04-18 11:00 | 4 | 11 | 0.87644 | 972.6723
2017-04-18 12:00 | 4 | 12 | 0.85078 | 944.2007
2017-04-18 13:00 | 4 | 13 | 0.8429 | 935.4504
2017-04-18 14:00 | 4 | 14 | 0.87313 | 969.0001
2017-04-18 15:00 | 4 | 15 | 0.99613 | 1105.5095
2017-04-18 16:00 | 4 | 16 | 1.219 | 1352.8701
2017-04-18 17:00 | 4 | 17 | 1.3345 | 1481.0507
2017-04-18 18:00 | 4 | 18 | 1.4581 | 1618.1648
2017-04-18 19:00 | 4 | 19 | 1.7086 | 1896.2558
2017-04-18 20:00 | 4 | 20 | 1.7354 | 1925.9464
2017-04-18 21:00 | 4 | 21 | 1.4302 | 1587.2364
2017-04-18 22:00 | 4 | 22 | 1.1392 | 1264.3227
2017-04-18 23:00 | 4 | 23 | 0.84396 | 936.6313
2017-04-19 | 4 | 0 | 0.73939 | 820.5758
2017-04-19 01:00 | 4 | 1 | 0.69272 | 768.7767
2017-04-19 02:00 | 4 | 2 | 0.68464 | 759.8151
2017-04-19 03:00 | 4 | 3 | 0.68367 | 758.7395
2017-04-19 04:00 | 4 | 4 | 0.73612 | 816.9484
2017-04-19 05:00 | 4 | 5 | 0.905 | 1004.3698
2017-04-19 06:00 | 4 | 6 | 1.1158 | 1238.2621
2017-04-19 07:00 | 4 | 7 | 1.0208 | 1132.8648
2017-04-19 08:00 | 4 | 8 | 0.90186 | 1000.8839
2017-04-19 09:00 | 4 | 9 | 0.91352 | 1013.8217
2017-04-19 10:00 | 4 | 10 | 0.89621 | 994.615
2017-04-19 11:00 | 4 | 11 | 0.85807 | 952.2838
2017-04-19 12:00 | 4 | 12 | 0.82687 | 917.662
2017-04-19 13:00 | 4 | 13 | 0.82161 | 911.8212
2017-04-19 14:00 | 4 | 14 | 0.84543 | 938.2634
2017-04-19 15:00 | 4 | 15 | 0.94632 | 1050.2299
2017-04-19 16:00 | 4 | 16 | 1.1709 | 1299.4937
2017-04-19 17:00 | 4 | 17 | 1.2896 | 1431.2007
2017-04-19 18:00 | 4 | 18 | 1.4209 | 1576.9432
2017-04-19 19:00 | 4 | 19 | 1.6709 | 1854.3666
2017-04-19 20:00 | 4 | 20 | 1.7054 | 1892.6798
2017-04-19 21:00 | 4 | 21 | 1.4038 | 1557.8892
2017-04-19 22:00 | 4 | 22 | 1.1172 | 1239.922
2017-04-19 23:00 | 4 | 23 | 0.8214 | 911.5861
2017-04-20 | 4 | 0 | 0.71582 | 794.4146
2017-04-20 01:00 | 4 | 1 | 0.66541 | 738.4772
2017-04-20 02:00 | 4 | 2 | 0.65984 | 732.2863
2017-04-20 03:00 | 4 | 3 | 0.65689 | 729.0211
2017-04-20 04:00 | 4 | 4 | 0.70873 | 786.5484
2017-04-20 05:00 | 4 | 5 | 0.86748 | 962.7349
2017-04-20 06:00 | 4 | 6 | 1.089 | 1208.6253
2017-04-20 07:00 | 4 | 7 | 1.0082 | 1118.8924
2017-04-20 08:00 | 4 | 8 | 0.8955 | 993.8221
2017-04-20 09:00 | 4 | 9 | 0.89533 | 993.6349
2017-04-20 10:00 | 4 | 10 | 0.87748 | 973.8258
2017-04-20 11:00 | 4 | 11 | 0.84708 | 940.0865
2017-04-20 12:00 | 4 | 12 | 0.81313 | 902.4077
2017-04-20 13:00 | 4 | 13 | 0.79605 | 883.4617
2017-04-20 14:00 | 4 | 14 | 0.82143 | 911.6273
2017-04-20 15:00 | 4 | 15 | 0.93764 | 1040.5953
2017-04-20 16:00 | 4 | 16 | 1.1548 | 1281.5682
2017-04-20 17:00 | 4 | 17 | 1.2773 | 1417.5555
2017-04-20 18:00 | 4 | 18 | 1.3996 | 1553.239
2017-04-20 19:00 | 4 | 19 | 1.6516 | 1832.9499
2017-04-20 20:00 | 4 | 20 | 1.6842 | 1869.0827
2017-04-20 21:00 | 4 | 21 | 1.3792 | 1530.5912
2017-04-20 22:00 | 4 | 22 | 1.0839 | 1202.9046
2017-04-20 23:00 | 4 | 23 | 0.78427 | 870.3787
2017-04-21 | 4 | 0 | 0.67126 | 744.9629
2017-04-21 01:00 | 4 | 1 | 0.61904 | 687.008
2017-04-21 02:00 | 4 | 2 | 0.60984 | 676.7984
2017-04-21 03:00 | 4 | 3 | 0.60815 | 674.9283
2017-04-21 04:00 | 4 | 4 | 0.66048 | 732.9978
2017-04-21 05:00 | 4 | 5 | 0.8167 | 906.376
2017-04-21 06:00 | 4 | 6 | 1.0565 | 1172.5024
2017-04-21 07:00 | 4 | 7 | 0.97769 | 1085.0399
2017-04-21 08:00 | 4 | 8 | 0.87453 | 970.5592
2017-04-21 09:00 | 4 | 9 | 0.89102 | 988.8517
2017-04-21 10:00 | 4 | 10 | 0.88676 | 984.1325
2017-04-21 11:00 | 4 | 11 | 0.86261 | 957.323
2017-04-21 12:00 | 4 | 12 | 0.83454 | 926.1734
2017-04-21 13:00 | 4 | 13 | 0.82164 | 911.8556
2017-04-21 14:00 | 4 | 14 | 0.84278 | 935.3232
2017-04-21 15:00 | 4 | 15 | 0.96061 | 1066.0841
2017-04-21 16:00 | 4 | 16 | 1.182 | 1311.7469
2017-04-21 17:00 | 4 | 17 | 1.2941 | 1436.2447
2017-04-21 18:00 | 4 | 18 | 1.4097 | 1564.4857
2017-04-21 19:00 | 4 | 19 | 1.6575 | 1839.4948
2017-04-21 20:00 | 4 | 20 | 1.687 | 1872.2698
2017-04-21 21:00 | 4 | 21 | 1.3798 | 1531.2526
2017-04-21 22:00 | 4 | 22 | 1.0841 | 1203.1826
2017-04-21 23:00 | 4 | 23 | 0.78983 | 876.5545
2017-04-22 | 4 | 0 | 0.68376 | 758.8381
2017-04-22 01:00 | 4 | 1 | 0.62939 | 698.5011
2017-04-22 02:00 | 4 | 2 | 0.62013 | 688.2262
2017-04-22 03:00 | 4 | 3 | 0.62185 | 690.1338
2017-04-22 04:00 | 4 | 4 | 0.67898 | 753.5372
2017-04-22 05:00 | 4 | 5 | 0.83989 | 932.1081
2017-04-22 06:00 | 4 | 6 | 1.0759 | 1194.023
2017-04-22 07:00 | 4 | 7 | 1.0097 | 1120.5355
2017-04-22 08:00 | 4 | 8 | 0.91236 | 1012.5354
2017-04-22 09:00 | 4 | 9 | 0.92433 | 1025.8226
2017-04-22 10:00 | 4 | 10 | 0.91488 | 1015.3384
2017-04-22 11:00 | 4 | 11 | 0.88803 | 985.5417
2017-04-22 12:00 | 4 | 12 | 0.85221 | 945.7853
2017-04-22 13:00 | 4 | 13 | 0.83325 | 924.741
2017-04-22 14:00 | 4 | 14 | 0.85608 | 950.077
2017-04-22 15:00 | 4 | 15 | 0.97638 | 1083.5927
2017-04-22 16:00 | 4 | 16 | 1.1981 | 1329.6989
2017-04-22 17:00 | 4 | 17 | 1.3126 | 1456.7781
2017-04-22 18:00 | 4 | 18 | 1.4296 | 1586.6245
2017-04-22 19:00 | 4 | 19 | 1.6854 | 1870.4108
2017-04-22 20:00 | 4 | 20 | 1.7132 | 1901.2706
2017-04-22 21:00 | 4 | 21 | 1.4019 | 1555.8128
2017-04-22 22:00 | 4 | 22 | 1.0953 | 1215.5965
2017-04-22 23:00 | 4 | 23 | 0.79171 | 878.6409
2017-04-23 | 4 | 0 | 0.68086 | 755.6165
2017-04-23 01:00 | 4 | 1 | 0.63018 | 699.3738
2017-04-23 02:00 | 4 | 2 | 0.61689 | 684.6277
2017-04-23 03:00 | 4 | 3 | 0.61755 | 685.356
2017-04-23 04:00 | 4 | 4 | 0.67031 | 743.9138
2017-04-23 05:00 | 4 | 5 | 0.83311 | 924.5821
2017-04-23 06:00 | 4 | 6 | 1.0657 | 1182.7012
2017-04-23 07:00 | 4 | 7 | 1.0012 | 1111.123
2017-04-23 08:00 | 4 | 8 | 0.89552 | 993.8458
2017-04-23 09:00 | 4 | 9 | 0.90869 | 1008.4643
2017-04-23 10:00 | 4 | 10 | 0.89817 | 996.7851
2017-04-23 11:00 | 4 | 11 | 0.86894 | 964.3498
2017-04-23 12:00 | 4 | 12 | 0.84508 | 937.8735
2017-04-23 13:00 | 4 | 13 | 0.82604 | 916.7383
2017-04-23 14:00 | 4 | 14 | 0.85168 | 945.1973
2017-04-23 15:00 | 4 | 15 | 0.96871 | 1075.0724
2017-04-23 16:00 | 4 | 16 | 1.1967 | 1328.0735
2017-04-23 17:00 | 4 | 17 | 1.3134 | 1457.5774
2017-04-23 18:00 | 4 | 18 | 1.4362 | 1593.933
2017-04-23 19:00 | 4 | 19 | 1.6892 | 1874.6921
2017-04-23 20:00 | 4 | 20 | 1.7214 | 1910.3795
2017-04-23 21:00 | 4 | 21 | 1.4131 | 1568.2532
2017-04-23 22:00 | 4 | 22 | 1.1064 | 1227.8989
2017-04-23 23:00 | 4 | 23 | 0.80283 | 890.9819
2017-04-24 | 4 | 0 | 0.68961 | 765.3343
2017-04-24 01:00 | 4 | 1 | 0.63994 | 710.2082
2017-04-24 02:00 | 4 | 2 | 0.63339 | 702.9322
2017-04-24 03:00 | 4 | 3 | 0.63357 | 703.1349
2017-04-24 04:00 | 4 | 4 | 0.69377 | 769.949
2017-04-24 05:00 | 4 | 5 | 0.85478 | 948.6389
2017-04-24 06:00 | 4 | 6 | 1.0707 | 1188.2932
2017-04-24 07:00 | 4 | 7 | 0.98857 | 1097.1221
2017-04-24 08:00 | 4 | 8 | 0.8757 | 971.8489
2017-04-24 09:00 | 4 | 9 | 0.89019 | 987.9323
2017-04-24 10:00 | 4 | 10 | 0.88311 | 980.0717
2017-04-24 11:00 | 4 | 11 | 0.8547 | 948.5498
2017-04-24 12:00 | 4 | 12 | 0.82713 | 917.9484
2017-04-24 13:00 | 4 | 13 | 0.81113 | 900.1956
2017-04-24 14:00 | 4 | 14 | 0.84218 | 934.6526
2017-04-24 15:00 | 4 | 15 | 0.95712 | 1062.2125
2017-04-24 16:00 | 4 | 16 | 1.182 | 1311.7337
2017-04-24 17:00 | 4 | 17 | 1.2919 | 1433.73
2017-04-24 18:00 | 4 | 18 | 1.4097 | 1564.4344
2017-04-24 19:00 | 4 | 19 | 1.6598 | 1842.0882
2017-04-24 20:00 | 4 | 20 | 1.6925 | 1878.3057
2017-04-24 21:00 | 4 | 21 | 1.3915 | 1544.2719
2017-04-24 22:00 | 4 | 22 | 1.0988 | 1219.4356
2017-04-24 23:00 | 4 | 23 | 0.80172 | 889.7536
2017-04-25 | 4 | 0 | 0.69281 | 768.8868
2017-04-25 01:00 | 4 | 1 | 0.64429 | 715.0323
2017-04-25 02:00 | 4 | 2 | 0.6362 | 706.061
2017-04-25 03:00 | 4 | 3 | 0.6364 | 706.2807
2017-04-25 04:00 | 4 | 4 | 0.69104 | 766.9119
2017-04-25 05:00 | 4 | 5 | 0.85472 | 948.5713
2017-04-25 06:00 | 4 | 6 | 1.0728 | 1190.5578
2017-04-25 07:00 | 4 | 7 | 0.99801 | 1107.5944
2017-04-25 08:00 | 4 | 8 | 0.88964 | 987.3194
2017-04-25 09:00 | 4 | 9 | 0.90569 | 1005.14
2017-04-25 10:00 | 4 | 10 | 0.9028 | 1001.9265
2017-04-25 11:00 | 4 | 11 | 0.88081 | 977.5268
2017-04-25 12:00 | 4 | 12 | 0.8578 | 951.9901
2017-04-25 13:00 | 4 | 13 | 0.84949 | 942.7661
2017-04-25 14:00 | 4 | 14 | 0.87939 | 975.9502
2017-04-25 15:00 | 4 | 15 | 0.99512 | 1104.3823
2017-04-25 16:00 | 4 | 16 | 1.197 | 1328.4801
2017-04-25 17:00 | 4 | 17 | 1.3198 | 1464.6844
2017-04-25 18:00 | 4 | 18 | 1.4361 | 1593.817
2017-04-25 19:00 | 4 | 19 | 1.6813 | 1865.9311
2017-04-25 20:00 | 4 | 20 | 1.7063 | 1893.7019
2017-04-25 21:00 | 4 | 21 | 1.3972 | 1550.6459
2017-04-25 22:00 | 4 | 22 | 1.1014 | 1222.3861
2017-04-25 23:00 | 4 | 23 | 0.80186 | 889.9069
2017-04-26 | 4 | 0 | 0.69023 | 766.0194
2017-04-26 01:00 | 4 | 1 | 0.63761 | 707.6166
2017-04-26 02:00 | 4 | 2 | 0.62811 | 697.0749
2017-04-26 03:00 | 4 | 3 | 0.62487 | 693.4843
2017-04-26 04:00 | 4 | 4 | 0.67753 | 751.9198
2017-04-26 05:00 | 4 | 5 | 0.83214 | 923.5106
2017-04-26 06:00 | 4 | 6 | 1.0582 | 1174.4447
2017-04-26 07:00 | 4 | 7 | 0.98513 | 1093.3013
2017-04-26 08:00 | 4 | 8 | 0.87719 | 973.5119
2017-04-26 09:00 | 4 | 9 | 0.88944 | 987.1037
2017-04-26 10:00 | 4 | 10 | 0.8748 | 970.8502
2017-04-26 11:00 | 4 | 11 | 0.83865 | 930.7374
2017-04-26 12:00 | 4 | 12 | 0.81249 | 901.7049
2017-04-26 13:00 | 4 | 13 | 0.79758 | 885.1571
2017-04-26 14:00 | 4 | 14 | 0.82343 | 913.8418
2017-04-26 15:00 | 4 | 15 | 0.94043 | 1043.6872
2017-04-26 16:00 | 4 | 16 | 1.158 | 1285.1309
2017-04-26 17:00 | 4 | 17 | 1.2655 | 1404.4036
2017-04-26 18:00 | 4 | 18 | 1.3852 | 1537.3233
2017-04-26 19:00 | 4 | 19 | 1.6264 | 1805.0295
2017-04-26 20:00 | 4 | 20 | 1.6573 | 1839.3252
2017-04-26 21:00 | 4 | 21 | 1.3551 | 1503.8555
2017-04-26 22:00 | 4 | 22 | 1.0652 | 1182.1257
2017-04-26 23:00 | 4 | 23 | 0.77096 | 855.6089
2017-04-27 | 4 | 0 | 0.66373 | 736.604
2017-04-27 01:00 | 4 | 1 | 0.61567 | 683.2732
2017-04-27 02:00 | 4 | 2 | 0.60988 | 676.8462
2017-04-27 03:00 | 4 | 3 | 0.60821 | 674.9869
2017-04-27 04:00 | 4 | 4 | 0.66099 | 733.5733
2017-04-27 05:00 | 4 | 5 | 0.81967 | 909.6745
2017-04-27 06:00 | 4 | 6 | 1.0324 | 1145.7663
2017-04-27 07:00 | 4 | 7 | 0.94385 | 1047.482
2017-04-27 08:00 | 4 | 8 | 0.81747 | 907.2285
2017-04-27 09:00 | 4 | 9 | 0.78524 | 871.4652
2017-04-27 10:00 | 4 | 10 | 0.78246 | 868.3749
2017-04-27 11:00 | 4 | 11 | 0.76388 | 847.758
2017-04-27 12:00 | 4 | 12 | 0.74221 | 823.7088
2017-04-27 13:00 | 4 | 13 | 0.73523 | 815.9545
2017-04-27 14:00 | 4 | 14 | 0.76257 | 846.3013
2017-04-27 15:00 | 4 | 15 | 0.87928 | 975.826
2017-04-27 16:00 | 4 | 16 | 1.0841 | 1203.1223
2017-04-27 17:00 | 4 | 17 | 1.2112 | 1344.2348
2017-04-27 18:00 | 4 | 18 | 1.328 | 1473.8274
2017-04-27 19:00 | 4 | 19 | 1.5749 | 1747.839
2017-04-27 20:00 | 4 | 20 | 1.5994 | 1775.0343
2017-04-27 21:00 | 4 | 21 | 1.2855 | 1426.6169
2017-04-27 22:00 | 4 | 22 | 0.98039 | 1088.0352
2017-04-27 23:00 | 4 | 23 | 0.67139 | 745.1074
2017-04-28 | 4 | 0 | 0.55374 | 614.5462
2017-04-28 01:00 | 4 | 1 | 0.49787 | 552.5338
2017-04-28 02:00 | 4 | 2 | 0.48575 | 539.0912
2017-04-28 03:00 | 4 | 3 | 0.4833 | 536.3645
2017-04-28 04:00 | 4 | 4 | 0.54262 | 602.1987
2017-04-28 05:00 | 4 | 5 | 0.69782 | 774.4467
2017-04-28 06:00 | 4 | 6 | 0.9343 | 1036.8877
2017-04-28 07:00 | 4 | 7 | 0.86304 | 957.804
2017-04-28 08:00 | 4 | 8 | 0.761 | 844.563
2017-04-28 09:00 | 4 | 9 | 0.76362 | 847.4639
2017-04-28 10:00 | 4 | 10 | 0.77889 | 864.418
2017-04-28 11:00 | 4 | 11 | 0.76388 | 847.758
2017-04-28 12:00 | 4 | 12 | 0.74221 | 823.7088
2017-04-28 13:00 | 4 | 13 | 0.73523 | 815.9545
2017-04-28 14:00 | 4 | 14 | 0.76257 | 846.3013
2017-04-28 15:00 | 4 | 15 | 0.87928 | 975.826
2017-04-28 16:00 | 4 | 16 | 1.1023 | 1223.3895
2017-04-28 17:00 | 4 | 17 | 1.2343 | 1369.8071
2017-04-28 18:00 | 4 | 18 | 1.365 | 1514.8718
2017-04-28 19:00 | 4 | 19 | 1.6305 | 1809.5423
2017-04-28 20:00 | 4 | 20 | 1.6668 | 1849.7633
2017-04-28 21:00 | 4 | 21 | 1.3732 | 1523.9465
2017-04-28 22:00 | 4 | 22 | 1.087 | 1206.338
2017-04-28 23:00 | 4 | 23 | 0.7941 | 881.288
2017-04-29 | 4 | 0 | 0.689 | 764.6577
2017-04-29 01:00 | 4 | 1 | 0.64216 | 712.668
2017-04-29 02:00 | 4 | 2 | 0.63429 | 703.9409
2017-04-29 03:00 | 4 | 3 | 0.64069 | 711.0344
2017-04-29 04:00 | 4 | 4 | 0.69622 | 772.6618
2017-04-29 05:00 | 4 | 5 | 0.87198 | 967.7251
2017-04-29 06:00 | 4 | 6 | 1.1167 | 1239.3266
2017-04-29 07:00 | 4 | 7 | 1.0488 | 1163.9249
2017-04-29 08:00 | 4 | 8 | 0.95661 | 1061.645
2017-04-29 09:00 | 4 | 9 | 0.98636 | 1094.6673
2017-04-29 10:00 | 4 | 10 | 0.98124 | 1088.9868
2017-04-29 11:00 | 4 | 11 | 0.95767 | 1062.8188
2017-04-29 12:00 | 4 | 12 | 0.92538 | 1026.9885
2017-04-29 13:00 | 4 | 13 | 0.91097 | 1010.9955
2017-04-29 14:00 | 4 | 14 | 0.93618 | 1038.9717
2017-04-29 15:00 | 4 | 15 | 1.0505 | 1165.8015
2017-04-29 16:00 | 4 | 16 | 1.274 | 1413.8773
2017-04-29 17:00 | 4 | 17 | 1.3786 | 1529.927
2017-04-29 18:00 | 4 | 18 | 1.4928 | 1656.7376
2017-04-29 19:00 | 4 | 19 | 1.7364 | 1927.0907
2017-04-29 20:00 | 4 | 20 | 1.7621 | 1955.5349
2017-04-29 21:00 | 4 | 21 | 1.446 | 1604.7215
2017-04-29 22:00 | 4 | 22 | 1.1353 | 1259.9048
2017-04-29 23:00 | 4 | 23 | 0.82685 | 917.6447
2017-04-30 | 4 | 0 | 0.71175 | 789.9062
2017-04-30 01:00 | 4 | 1 | 0.6601 | 732.5754
2017-04-30 02:00 | 4 | 2 | 0.65206 | 723.6601
2017-04-30 03:00 | 4 | 3 | 0.64688 | 717.9109
2017-04-30 04:00 | 4 | 4 | 0.70091 | 777.8724
2017-04-30 05:00 | 4 | 5 | 0.8708 | 966.4157
2017-04-30 06:00 | 4 | 6 | 1.1045 | 1225.7409
2017-04-30 07:00 | 4 | 7 | 1.0402 | 1154.4378
2017-04-30 08:00 | 4 | 8 | 0.95072 | 1055.1071
2017-04-30 09:00 | 4 | 9 | 0.96977 | 1076.255
2017-04-30 10:00 | 4 | 10 | 0.96426 | 1070.1364
2017-04-30 11:00 | 4 | 11 | 0.93299 | 1035.4377
2017-04-30 12:00 | 4 | 12 | 0.89962 | 998.4029
2017-04-30 13:00 | 4 | 13 | 0.88507 | 982.2519
2017-04-30 14:00 | 4 | 14 | 0.90801 | 1007.7148
2017-04-30 15:00 | 4 | 15 | 1.019 | 1130.9068
2017-04-30 16:00 | 4 | 16 | 1.241 | 1377.281
2017-04-30 17:00 | 4 | 17 | 1.3479 | 1495.8592
2017-04-30 18:00 | 4 | 18 | 1.4652 | 1626.1109
2017-04-30 19:00 | 4 | 19 | 1.7123 | 1900.2785
2017-04-30 20:00 | 4 | 20 | 1.7411 | 1932.2671
2017-04-30 21:00 | 4 | 21 | 1.4309 | 1588.0282
2017-04-30 22:00 | 4 | 22 | 1.1263 | 1249.9527
2017-04-30 23:00 | 4 | 23 | 0.82274 | 913.0816
2017-05-01 | 5 | 0 | 0.70791 | 785.6385
2017-05-01 01:00 | 5 | 1 | 0.66268 | 735.4434
2017-05-01 02:00 | 5 | 2 | 0.65882 | 731.1585
2017-05-01 03:00 | 5 | 3 | 0.6639 | 736.8025
2017-05-01 04:00 | 5 | 4 | 0.72088 | 800.0309
2017-05-01 05:00 | 5 | 5 | 0.85799 | 952.2016
2017-05-01 06:00 | 5 | 6 | 1.0394 | 1153.5373
2017-05-01 07:00 | 5 | 7 | 0.95602 | 1060.9901
2017-05-01 08:00 | 5 | 8 | 0.87604 | 972.2357
2017-05-01 09:00 | 5 | 9 | 0.89504 | 993.3196
2017-05-01 10:00 | 5 | 10 | 0.87989 | 976.5085
2017-05-01 11:00 | 5 | 11 | 0.84615 | 939.0585
2017-05-01 12:00 | 5 | 12 | 0.81037 | 899.3522
2017-05-01 13:00 | 5 | 13 | 0.79316 | 880.2498
2017-05-01 14:00 | 5 | 14 | 0.8233 | 913.6965
2017-05-01 15:00 | 5 | 15 | 0.93381 | 1036.3432
2017-05-01 16:00 | 5 | 16 | 1.1495 | 1275.6933
2017-05-01 17:00 | 5 | 17 | 1.244 | 1380.5793
2017-05-01 18:00 | 5 | 18 | 1.3154 | 1459.8557
2017-05-01 19:00 | 5 | 19 | 1.531 | 1699.0642
2017-05-01 20:00 | 5 | 20 | 1.6697 | 1853.0032
2017-05-01 21:00 | 5 | 21 | 1.4002 | 1553.9772
2017-05-01 22:00 | 5 | 22 | 1.1199 | 1242.9218
2017-05-01 23:00 | 5 | 23 | 0.82164 | 911.8556
2017-05-02 | 5 | 0 | 0.71136 | 789.4635
2017-05-02 01:00 | 5 | 1 | 0.6666 | 739.7923
2017-05-02 02:00 | 5 | 2 | 0.65617 | 728.2151
2017-05-02 03:00 | 5 | 3 | 0.65957 | 731.9882
2017-05-02 04:00 | 5 | 4 | 0.71307 | 791.3667
2017-05-02 05:00 | 5 | 5 | 0.85738 | 951.5265
2017-05-02 06:00 | 5 | 6 | 1.0298 | 1142.838
2017-05-02 07:00 | 5 | 7 | 0.95226 | 1056.8212
2017-05-02 08:00 | 5 | 8 | 0.86951 | 964.9838
2017-05-02 09:00 | 5 | 9 | 0.88106 | 977.799
2017-05-02 10:00 | 5 | 10 | 0.86634 | 961.4683
2017-05-02 11:00 | 5 | 11 | 0.8322 | 923.5756
2017-05-02 12:00 | 5 | 12 | 0.79518 | 882.4962
2017-05-02 13:00 | 5 | 13 | 0.76806 | 852.3901
2017-05-02 14:00 | 5 | 14 | 0.78448 | 870.6201
2017-05-02 15:00 | 5 | 15 | 0.89452 | 992.7437
2017-05-02 16:00 | 5 | 16 | 1.0925 | 1212.4351
2017-05-02 17:00 | 5 | 17 | 1.182 | 1311.7426
2017-05-02 18:00 | 5 | 18 | 1.2558 | 1393.7441
2017-05-02 19:00 | 5 | 19 | 1.4762 | 1638.3356
2017-05-02 20:00 | 5 | 20 | 1.6195 | 1797.3185
2017-05-02 21:00 | 5 | 21 | 1.3549 | 1503.656
2017-05-02 22:00 | 5 | 22 | 1.0709 | 1188.4426
2017-05-02 23:00 | 5 | 23 | 0.77853 | 864.0112
2017-05-03 | 5 | 0 | 0.67051 | 744.1279
2017-05-03 01:00 | 5 | 1 | 0.62497 | 693.5906
2017-05-03 02:00 | 5 | 2 | 0.61792 | 685.7685
2017-05-03 03:00 | 5 | 3 | 0.62157 | 689.8232
2017-05-03 04:00 | 5 | 4 | 0.67281 | 746.6804
2017-05-03 05:00 | 5 | 5 | 0.81003 | 898.9754
2017-05-03 06:00 | 5 | 6 | 0.99614 | 1105.5222
2017-05-03 07:00 | 5 | 7 | 0.92232 | 1023.5925
2017-05-03 08:00 | 5 | 8 | 0.84332 | 935.9142
2017-05-03 09:00 | 5 | 9 | 0.85699 | 951.0835
2017-05-03 10:00 | 5 | 10 | 0.84614 | 939.0521
2017-05-03 11:00 | 5 | 11 | 0.81474 | 904.2028
2017-05-03 12:00 | 5 | 12 | 0.77884 | 864.3625
2017-05-03 13:00 | 5 | 13 | 0.7631 | 846.8867
2017-05-03 14:00 | 5 | 14 | 0.78699 | 873.4019
2017-05-03 15:00 | 5 | 15 | 0.90785 | 1007.5363
2017-05-03 16:00 | 5 | 16 | 1.1192 | 1242.116
2017-05-03 17:00 | 5 | 17 | 1.2041 | 1336.3412
2017-05-03 18:00 | 5 | 18 | 1.2711 | 1410.6563
2017-05-03 19:00 | 5 | 19 | 1.4926 | 1656.5358
2017-05-03 20:00 | 5 | 20 | 1.6363 | 1815.9459
2017-05-03 21:00 | 5 | 21 | 1.3662 | 1516.2402
2017-05-03 22:00 | 5 | 22 | 1.0783 | 1196.7419
2017-05-03 23:00 | 5 | 23 | 0.77923 | 864.7925
2017-05-04 | 5 | 0 | 0.67131 | 745.0156
2017-05-04 01:00 | 5 | 1 | 0.62676 | 695.5782
2017-05-04 02:00 | 5 | 2 | 0.62755 | 696.4565
2017-05-04 03:00 | 5 | 3 | 0.63144 | 700.7704
2017-05-04 04:00 | 5 | 4 | 0.68469 | 759.8714
2017-05-04 05:00 | 5 | 5 | 0.83516 | 926.8576
2017-05-04 06:00 | 5 | 6 | 1.0107 | 1121.6505
2017-05-04 07:00 | 5 | 7 | 0.92428 | 1025.7709
2017-05-04 08:00 | 5 | 8 | 0.84619 | 939.1018
2017-05-04 09:00 | 5 | 9 | 0.86037 | 954.8424
2017-05-04 10:00 | 5 | 10 | 0.85096 | 944.3991
2017-05-04 11:00 | 5 | 11 | 0.82441 | 914.936
2017-05-04 12:00 | 5 | 12 | 0.79524 | 882.5535
2017-05-04 13:00 | 5 | 13 | 0.7771 | 862.431
2017-05-04 14:00 | 5 | 14 | 0.79832 | 885.9762
2017-05-04 15:00 | 5 | 15 | 0.91199 | 1012.1227
2017-05-04 16:00 | 5 | 16 | 1.1199 | 1242.8191
2017-05-04 17:00 | 5 | 17 | 1.2047 | 1337.0225
2017-05-04 18:00 | 5 | 18 | 1.2719 | 1411.5738
2017-05-04 19:00 | 5 | 19 | 1.4891 | 1652.5941
2017-05-04 20:00 | 5 | 20 | 1.6278 | 1806.5436
2017-05-04 21:00 | 5 | 21 | 1.3556 | 1504.4574
2017-05-04 22:00 | 5 | 22 | 1.0683 | 1185.633
2017-05-04 23:00 | 5 | 23 | 0.77253 | 857.3594
2017-05-05 | 5 | 0 | 0.6628 | 735.5719
2017-05-05 01:00 | 5 | 1 | 0.6153 | 682.8616
2017-05-05 02:00 | 5 | 2 | 0.60809 | 674.8612
2017-05-05 03:00 | 5 | 3 | 0.61078 | 677.8412
2017-05-05 04:00 | 5 | 4 | 0.66659 | 739.7781
2017-05-05 05:00 | 5 | 5 | 0.80368 | 891.927
2017-05-05 06:00 | 5 | 6 | 1.0065 | 1117.0456
2017-05-05 07:00 | 5 | 7 | 0.93683 | 1039.693
2017-05-05 08:00 | 5 | 8 | 0.87339 | 969.2856
2017-05-05 09:00 | 5 | 9 | 0.90535 | 1004.7548
2017-05-05 10:00 | 5 | 10 | 0.92337 | 1024.7574
2017-05-05 11:00 | 5 | 11 | 0.88775 | 985.2284
2017-05-05 12:00 | 5 | 12 | 0.86067 | 955.1765
2017-05-05 13:00 | 5 | 13 | 0.84419 | 936.879
2017-05-05 14:00 | 5 | 14 | 0.86666 | 961.8192
2017-05-05 15:00 | 5 | 15 | 0.97962 | 1087.18
2017-05-05 16:00 | 5 | 16 | 1.1905 | 1321.2467
2017-05-05 17:00 | 5 | 17 | 1.2647 | 1403.5609
2017-05-05 18:00 | 5 | 18 | 1.3243 | 1469.7454
2017-05-05 19:00 | 5 | 19 | 1.534 | 1702.4387
2017-05-05 20:00 | 5 | 20 | 1.6674 | 1850.491
2017-05-05 21:00 | 5 | 21 | 1.3915 | 1544.269
2017-05-05 22:00 | 5 | 22 | 1.0993 | 1219.9652
2017-05-05 23:00 | 5 | 23 | 0.79834 | 886.0045
2017-05-06 | 5 | 0 | 0.68847 | 764.0611
2017-05-06 01:00 | 5 | 1 | 0.63698 | 706.9194
2017-05-06 02:00 | 5 | 2 | 0.62584 | 694.5533
2017-05-06 03:00 | 5 | 3 | 0.6267 | 695.5111
2017-05-06 04:00 | 5 | 4 | 0.67952 | 754.1329
2017-05-06 05:00 | 5 | 5 | 0.82822 | 919.1565
2017-05-06 06:00 | 5 | 6 | 1.0128 | 1123.9886
2017-05-06 07:00 | 5 | 7 | 0.93933 | 1042.4665
2017-05-06 08:00 | 5 | 8 | 0.86918 | 964.6223
2017-05-06 09:00 | 5 | 9 | 0.88483 | 981.9912
2017-05-06 10:00 | 5 | 10 | 0.87708 | 973.387
2017-05-06 11:00 | 5 | 11 | 0.84202 | 934.4796
2017-05-06 12:00 | 5 | 12 | 0.80443 | 892.761
2017-05-06 13:00 | 5 | 13 | 0.78179 | 867.635
2017-05-06 14:00 | 5 | 14 | 0.80208 | 890.1469
2017-05-06 15:00 | 5 | 15 | 0.91473 | 1015.17
2017-05-06 16:00 | 5 | 16 | 1.1151 | 1237.5129
2017-05-06 17:00 | 5 | 17 | 1.2068 | 1339.3461
2017-05-06 18:00 | 5 | 18 | 1.2749 | 1414.835
2017-05-06 19:00 | 5 | 19 | 1.4954 | 1659.5599
2017-05-06 20:00 | 5 | 20 | 1.6404 | 1820.4852
2017-05-06 21:00 | 5 | 21 | 1.3636 | 1513.2969
2017-05-06 22:00 | 5 | 22 | 1.0637 | 1180.5042
2017-05-06 23:00 | 5 | 23 | 0.75916 | 842.5191
2017-05-07 | 5 | 0 | 0.64348 | 714.1359
2017-05-07 01:00 | 5 | 1 | 0.5933 | 658.444
2017-05-07 02:00 | 5 | 2 | 0.58413 | 648.2723
2017-05-07 03:00 | 5 | 3 | 0.58656 | 650.9706
2017-05-07 04:00 | 5 | 4 | 0.64009 | 710.3781
2017-05-07 05:00 | 5 | 5 | 0.78684 | 873.2318
2017-05-07 06:00 | 5 | 6 | 0.97797 | 1085.3552
2017-05-07 07:00 | 5 | 7 | 0.90888 | 1008.6788
2017-05-07 08:00 | 5 | 8 | 0.84484 | 937.6029
2017-05-07 09:00 | 5 | 9 | 0.85741 | 951.5523
2017-05-07 10:00 | 5 | 10 | 0.85968 | 954.0698
2017-05-07 11:00 | 5 | 11 | 0.83427 | 925.8698
2017-05-07 12:00 | 5 | 12 | 0.79957 | 887.3647
2017-05-07 13:00 | 5 | 13 | 0.77872 | 864.2239
2017-05-07 14:00 | 5 | 14 | 0.79609 | 883.5061
2017-05-07 15:00 | 5 | 15 | 0.9067 | 1006.2554
2017-05-07 16:00 | 5 | 16 | 1.1053 | 1226.6609
2017-05-07 17:00 | 5 | 17 | 1.1978 | 1329.3443
2017-05-07 18:00 | 5 | 18 | 1.2671 | 1406.2199
2017-05-07 19:00 | 5 | 19 | 1.4877 | 1651.058
2017-05-07 20:00 | 5 | 20 | 1.6295 | 1808.4082
2017-05-07 21:00 | 5 | 21 | 1.3521 | 1500.5145
2017-05-07 22:00 | 5 | 22 | 1.0526 | 1168.1774
2017-05-07 23:00 | 5 | 23 | 0.74839 | 830.5674
2017-05-08 | 5 | 0 | 0.63311 | 702.6296
2017-05-08 01:00 | 5 | 1 | 0.58487 | 649.0888
2017-05-08 02:00 | 5 | 2 | 0.58085 | 644.6295
2017-05-08 03:00 | 5 | 3 | 0.58291 | 646.9191
2017-05-08 04:00 | 5 | 4 | 0.63892 | 709.075
2017-05-08 05:00 | 5 | 5 | 0.78154 | 867.3513
2017-05-08 06:00 | 5 | 6 | 0.95779 | 1062.9565
2017-05-08 07:00 | 5 | 7 | 0.8762 | 972.4081
2017-05-08 08:00 | 5 | 8 | 0.79753 | 885.1025
2017-05-08 09:00 | 5 | 9 | 0.79965 | 887.4523
2017-05-08 10:00 | 5 | 10 | 0.79728 | 884.8246
2017-05-08 11:00 | 5 | 11 | 0.77218 | 856.9668
2017-05-08 12:00 | 5 | 12 | 0.74036 | 821.6524
2017-05-08 13:00 | 5 | 13 | 0.72374 | 803.2029
2017-05-08 14:00 | 5 | 14 | 0.74878 | 830.9965
2017-05-08 15:00 | 5 | 15 | 0.86514 | 960.1297
2017-05-08 16:00 | 5 | 16 | 1.0579 | 1174.0058
2017-05-08 17:00 | 5 | 17 | 1.1568 | 1283.8737
2017-05-08 18:00 | 5 | 18 | 1.2283 | 1363.1181
2017-05-08 19:00 | 5 | 19 | 1.4489 | 1607.9502
2017-05-08 20:00 | 5 | 20 | 1.5913 | 1766.0519
2017-05-08 21:00 | 5 | 21 | 1.3233 | 1468.6435
2017-05-08 22:00 | 5 | 22 | 1.0366 | 1150.3964
2017-05-08 23:00 | 5 | 23 | 0.73697 | 817.8852
2017-05-09 | 5 | 0 | 0.62401 | 692.5325
2017-05-09 01:00 | 5 | 1 | 0.5781 | 641.5741
2017-05-09 02:00 | 5 | 2 | 0.57207 | 634.8879
2017-05-09 03:00 | 5 | 3 | 0.57347 | 636.4368
2017-05-09 04:00 | 5 | 4 | 0.62769 | 696.6089
2017-05-09 05:00 | 5 | 5 | 0.76357 | 847.4133
2017-05-09 06:00 | 5 | 6 | 0.95231 | 1056.879
2017-05-09 07:00 | 5 | 7 | 0.88106 | 977.8028
2017-05-09 08:00 | 5 | 8 | 0.81628 | 905.9035
2017-05-09 09:00 | 5 | 9 | 0.83323 | 924.7239
2017-05-09 10:00 | 5 | 10 | 0.84196 | 934.4119
2017-05-09 11:00 | 5 | 11 | 0.81259 | 901.815
2017-05-09 12:00 | 5 | 12 | 0.7822 | 868.0897
2017-05-09 13:00 | 5 | 13 | 0.76734 | 851.5901
2017-05-09 14:00 | 5 | 14 | 0.79139 | 878.2889
2017-05-09 15:00 | 5 | 15 | 0.90455 | 1003.8695
2017-05-09 16:00 | 5 | 16 | 1.1019 | 1222.9451
2017-05-09 17:00 | 5 | 17 | 1.1911 | 1321.906
2017-05-09 18:00 | 5 | 18 | 1.2585 | 1396.7277
2017-05-09 19:00 | 5 | 19 | 1.4707 | 1632.2182
2017-05-09 20:00 | 5 | 20 | 1.6076 | 1784.1334
2017-05-09 21:00 | 5 | 21 | 1.3323 | 1478.6092
2017-05-09 22:00 | 5 | 22 | 1.0397 | 1153.8272
2017-05-09 23:00 | 5 | 23 | 0.7395 | 820.6982
2017-05-10 | 5 | 0 | 0.62516 | 693.8056
2017-05-10 01:00 | 5 | 1 | 0.5753 | 638.4652
2017-05-10 02:00 | 5 | 2 | 0.56934 | 631.8515
2017-05-10 03:00 | 5 | 3 | 0.57187 | 634.6574
2017-05-10 04:00 | 5 | 4 | 0.62426 | 692.8019
2017-05-10 05:00 | 5 | 5 | 0.7637 | 847.5559
2017-05-10 06:00 | 5 | 6 | 0.94283 | 1046.3589
2017-05-10 07:00 | 5 | 7 | 0.86254 | 957.2482
2017-05-10 08:00 | 5 | 8 | 0.78734 | 873.7958
2017-05-10 09:00 | 5 | 9 | 0.79211 | 879.0858
2017-05-10 10:00 | 5 | 10 | 0.79283 | 879.8813
2017-05-10 11:00 | 5 | 11 | 0.77042 | 855.0093
2017-05-10 12:00 | 5 | 12 | 0.73754 | 818.5285
2017-05-10 13:00 | 5 | 13 | 0.72273 | 802.0839
2017-05-10 14:00 | 5 | 14 | 0.74878 | 830.9965
2017-05-10 15:00 | 5 | 15 | 0.86514 | 960.1297
2017-05-10 16:00 | 5 | 16 | 1.0579 | 1174.0058
2017-05-10 17:00 | 5 | 17 | 1.1552 | 1282.078
2017-05-10 18:00 | 5 | 18 | 1.219 | 1352.8778
2017-05-10 19:00 | 5 | 19 | 1.4346 | 1592.1039
2017-05-10 20:00 | 5 | 20 | 1.5767 | 1749.8139
2017-05-10 21:00 | 5 | 21 | 1.3092 | 1452.8994
2017-05-10 22:00 | 5 | 22 | 1.0249 | 1137.4148
2017-05-10 23:00 | 5 | 23 | 0.72821 | 808.1705
2017-05-11 | 5 | 0 | 0.62217 | 690.4856
2017-05-11 01:00 | 5 | 1 | 0.57499 | 638.125
2017-05-11 02:00 | 5 | 2 | 0.57059 | 633.2435
2017-05-11 03:00 | 5 | 3 | 0.57529 | 638.4623
2017-05-11 04:00 | 5 | 4 | 0.63055 | 699.7881
2017-05-11 05:00 | 5 | 5 | 0.7718 | 856.5398
2017-05-11 06:00 | 5 | 6 | 0.9531 | 1057.7475
2017-05-11 07:00 | 5 | 7 | 0.87395 | 969.9108
2017-05-11 08:00 | 5 | 8 | 0.80035 | 888.2278
2017-05-11 09:00 | 5 | 9 | 0.80658 | 895.1463
2017-05-11 10:00 | 5 | 10 | 0.80789 | 896.5985
2017-05-11 11:00 | 5 | 11 | 0.7832 | 869.1967
2017-05-11 12:00 | 5 | 12 | 0.75137 | 833.8749
2017-05-11 13:00 | 5 | 13 | 0.73208 | 812.4669
2017-05-11 14:00 | 5 | 14 | 0.75377 | 836.5322
2017-05-11 15:00 | 5 | 15 | 0.87011 | 965.6494
2017-05-11 16:00 | 5 | 16 | 1.0651 | 1181.9977
2017-05-11 17:00 | 5 | 17 | 1.1566 | 1283.6001
2017-05-11 18:00 | 5 | 18 | 1.2256 | 1360.1972
2017-05-11 19:00 | 5 | 19 | 1.4449 | 1603.5274
2017-05-11 20:00 | 5 | 20 | 1.5873 | 1761.5327
2017-05-11 21:00 | 5 | 21 | 1.3198 | 1464.7083
2017-05-11 22:00 | 5 | 22 | 1.0364 | 1150.2071
2017-05-11 23:00 | 5 | 23 | 0.742 | 823.469
2017-05-12 | 5 | 0 | 0.6345 | 704.1674
2017-05-12 01:00 | 5 | 1 | 0.59081 | 655.6768
2017-05-12 02:00 | 5 | 2 | 0.58583 | 650.1581
2017-05-12 03:00 | 5 | 3 | 0.59065 | 655.5004
2017-05-12 04:00 | 5 | 4 | 0.64514 | 715.9752
2017-05-12 05:00 | 5 | 5 | 0.7853 | 871.5271
2017-05-12 06:00 | 5 | 6 | 0.95788 | 1063.0554
2017-05-12 07:00 | 5 | 7 | 0.87772 | 974.0956
2017-05-12 08:00 | 5 | 8 | 0.80118 | 889.1531
2017-05-12 09:00 | 5 | 9 | 0.7956 | 882.9613
2017-05-12 10:00 | 5 | 10 | 0.79519 | 882.5042
2017-05-12 11:00 | 5 | 11 | 0.77208 | 856.8515
2017-05-12 12:00 | 5 | 12 | 0.73689 | 817.799
2017-05-12 13:00 | 5 | 13 | 0.72134 | 800.5394
2017-05-12 14:00 | 5 | 14 | 0.74878 | 830.9965
2017-05-12 15:00 | 5 | 15 | 0.86514 | 960.1297
2017-05-12 16:00 | 5 | 16 | 1.0579 | 1174.0058
2017-05-12 17:00 | 5 | 17 | 1.1552 | 1282.078
2017-05-12 18:00 | 5 | 18 | 1.219 | 1352.8778
2017-05-12 19:00 | 5 | 19 | 1.4311 | 1588.2639
2017-05-12 20:00 | 5 | 20 | 1.5648 | 1736.5987
2017-05-12 21:00 | 5 | 21 | 1.2925 | 1434.4497
2017-05-12 22:00 | 5 | 22 | 1.0118 | 1122.884
2017-05-12 23:00 | 5 | 23 | 0.71938 | 798.3683
2017-05-13 | 5 | 0 | 0.61777 | 685.598
2017-05-13 01:00 | 5 | 1 | 0.5716 | 634.3628
2017-05-13 02:00 | 5 | 2 | 0.56593 | 628.0716
2017-05-13 03:00 | 5 | 3 | 0.57299 | 635.9019
2017-05-13 04:00 | 5 | 4 | 0.63142 | 700.7459
2017-05-13 05:00 | 5 | 5 | 0.77528 | 860.4121
2017-05-13 06:00 | 5 | 6 | 0.97323 | 1080.0958
2017-05-13 07:00 | 5 | 7 | 0.91334 | 1013.6293
2017-05-13 08:00 | 5 | 8 | 0.85405 | 947.8215
2017-05-13 09:00 | 5 | 9 | 0.8712 | 966.8576
2017-05-13 10:00 | 5 | 10 | 0.86966 | 965.1536
2017-05-13 11:00 | 5 | 11 | 0.83933 | 931.4862
2017-05-13 12:00 | 5 | 12 | 0.80683 | 895.4162
2017-05-13 13:00 | 5 | 13 | 0.78497 | 871.164
2017-05-13 14:00 | 5 | 14 | 0.79889 | 886.6109
2017-05-13 15:00 | 5 | 15 | 0.90806 | 1007.7672
2017-05-13 16:00 | 5 | 16 | 1.0964 | 1216.8199
2017-05-13 17:00 | 5 | 17 | 1.1919 | 1322.822
2017-05-13 18:00 | 5 | 18 | 1.2612 | 1399.7026
2017-05-13 19:00 | 5 | 19 | 1.4782 | 1640.4894
2017-05-13 20:00 | 5 | 20 | 1.6248 | 1803.1878
2017-05-13 21:00 | 5 | 21 | 1.3497 | 1497.9409
2017-05-13 22:00 | 5 | 22 | 1.0495 | 1164.7258
2017-05-13 23:00 | 5 | 23 | 0.74712 | 829.16
2017-05-14 | 5 | 0 | 0.63488 | 704.5919
2017-05-14 01:00 | 5 | 1 | 0.58612 | 650.4714
2017-05-14 02:00 | 5 | 2 | 0.57814 | 641.616
2017-05-14 03:00 | 5 | 3 | 0.58189 | 645.7857
2017-05-14 04:00 | 5 | 4 | 0.63712 | 707.0775
2017-05-14 05:00 | 5 | 5 | 0.77779 | 863.1941
2017-05-14 06:00 | 5 | 6 | 0.97703 | 1084.3055
2017-05-14 07:00 | 5 | 7 | 0.91628 | 1016.8857
2017-05-14 08:00 | 5 | 8 | 0.86118 | 955.7392
2017-05-14 09:00 | 5 | 9 | 0.87721 | 973.533
2017-05-14 10:00 | 5 | 10 | 0.88059 | 977.2747
2017-05-14 11:00 | 5 | 11 | 0.85419 | 947.9819
2017-05-14 12:00 | 5 | 12 | 0.82216 | 912.4339
2017-05-14 13:00 | 5 | 13 | 0.80927 | 898.1323
2017-05-14 14:00 | 5 | 14 | 0.83442 | 926.042
2017-05-14 15:00 | 5 | 15 | 0.95344 | 1058.1347
2017-05-14 16:00 | 5 | 16 | 1.1628 | 1290.4438
2017-05-14 17:00 | 5 | 17 | 1.2512 | 1388.6107
2017-05-14 18:00 | 5 | 18 | 1.3219 | 1467.0562
2017-05-14 19:00 | 5 | 19 | 1.5381 | 1706.9443
2017-05-14 20:00 | 5 | 20 | 1.677 | 1861.1757
2017-05-14 21:00 | 5 | 21 | 1.3987 | 1552.3336
2017-05-14 22:00 | 5 | 22 | 1.097 | 1217.4096
2017-05-14 23:00 | 5 | 23 | 0.78796 | 874.4829
2017-05-15 | 5 | 0 | 0.66915 | 742.626
2017-05-15 01:00 | 5 | 1 | 0.6205 | 688.635
2017-05-15 02:00 | 5 | 2 | 0.61687 | 684.6068
2017-05-15 03:00 | 5 | 3 | 0.61739 | 685.1793
2017-05-15 04:00 | 5 | 4 | 0.66703 | 740.2686
2017-05-15 05:00 | 5 | 5 | 0.79979 | 887.6069
2017-05-15 06:00 | 5 | 6 | 0.99745 | 1106.9696
2017-05-15 07:00 | 5 | 7 | 0.91949 | 1020.4475
2017-05-15 08:00 | 5 | 8 | 0.85866 | 952.9437
2017-05-15 09:00 | 5 | 9 | 0.87875 | 975.237
2017-05-15 10:00 | 5 | 10 | 0.87901 | 975.5226
2017-05-15 11:00 | 5 | 11 | 0.86119 | 955.7456
2017-05-15 12:00 | 5 | 12 | 0.83677 | 928.6532
2017-05-15 13:00 | 5 | 13 | 0.82386 | 914.3203
2017-05-15 14:00 | 5 | 14 | 0.84687 | 939.8602
2017-05-15 15:00 | 5 | 15 | 0.96054 | 1066.0059
2017-05-15 16:00 | 5 | 16 | 1.1657 | 1293.7363
2017-05-15 17:00 | 5 | 17 | 1.2483 | 1385.3473
2017-05-15 18:00 | 5 | 18 | 1.3093 | 1453.0686
2017-05-15 19:00 | 5 | 19 | 1.518 | 1684.6892
2017-05-15 20:00 | 5 | 20 | 1.6527 | 1834.1141
2017-05-15 21:00 | 5 | 21 | 1.3777 | 1529.0278
2017-05-15 22:00 | 5 | 22 | 1.0851 | 1204.2945
2017-05-15 23:00 | 5 | 23 | 0.77907 | 864.6126
2017-05-16 | 5 | 0 | 0.6649 | 737.9054
2017-05-16 01:00 | 5 | 1 | 0.61633 | 684.0029
2017-05-16 02:00 | 5 | 2 | 0.60587 | 672.3993
2017-05-16 03:00 | 5 | 3 | 0.60441 | 670.7753
2017-05-16 04:00 | 5 | 4 | 0.65318 | 724.8991
2017-05-16 05:00 | 5 | 5 | 0.78737 | 873.8263
2017-05-16 06:00 | 5 | 6 | 0.98439 | 1092.4797
2017-05-16 07:00 | 5 | 7 | 0.91035 | 1010.3077
2017-05-16 08:00 | 5 | 8 | 0.84754 | 940.6001
2017-05-16 09:00 | 5 | 9 | 0.87152 | 967.2184
2017-05-16 10:00 | 5 | 10 | 0.86729 | 962.5205
2017-05-16 11:00 | 5 | 11 | 0.84813 | 941.2539
2017-05-16 12:00 | 5 | 12 | 0.82345 | 913.8682
2017-05-16 13:00 | 5 | 13 | 0.82578 | 916.4512
2017-05-16 14:00 | 5 | 14 | 0.85337 | 947.0662
2017-05-16 15:00 | 5 | 15 | 0.96816 | 1074.4653
2017-05-16 16:00 | 5 | 16 | 1.1655 | 1293.4201
2017-05-16 17:00 | 5 | 17 | 1.2475 | 1384.517
2017-05-16 18:00 | 5 | 18 | 1.3079 | 1451.5431
2017-05-16 19:00 | 5 | 19 | 1.5149 | 1681.2563
2017-05-16 20:00 | 5 | 20 | 1.6429 | 1823.3156
2017-05-16 21:00 | 5 | 21 | 1.3653 | 1515.254
2017-05-16 22:00 | 5 | 22 | 1.0686 | 1185.8885
2017-05-16 23:00 | 5 | 23 | 0.7655 | 849.5576
2017-05-17 | 5 | 0 | 0.64891 | 720.158
2017-05-17 01:00 | 5 | 1 | 0.59689 | 662.4273
2017-05-17 02:00 | 5 | 2 | 0.58631 | 650.6829
2017-05-17 03:00 | 5 | 3 | 0.58523 | 649.4862
2017-05-17 04:00 | 5 | 4 | 0.63751 | 707.5117
2017-05-17 05:00 | 5 | 5 | 0.7724 | 857.2125
2017-05-17 06:00 | 5 | 6 | 0.96117 | 1066.7037
2017-05-17 07:00 | 5 | 7 | 0.89182 | 989.7387
2017-05-17 08:00 | 5 | 8 | 0.8282 | 919.1415
2017-05-17 09:00 | 5 | 9 | 0.84415 | 936.8356
2017-05-17 10:00 | 5 | 10 | 0.83698 | 928.8779
2017-05-17 11:00 | 5 | 11 | 0.80625 | 894.7814
2017-05-17 12:00 | 5 | 12 | 0.77818 | 863.62
2017-05-17 13:00 | 5 | 13 | 0.76002 | 843.4728
2017-05-17 14:00 | 5 | 14 | 0.78303 | 869.0045
2017-05-17 15:00 | 5 | 15 | 0.89655 | 994.9872
2017-05-17 16:00 | 5 | 16 | 1.1043 | 1225.6038
2017-05-17 17:00 | 5 | 17 | 1.1945 | 1325.647
2017-05-17 18:00 | 5 | 18 | 1.264 | 1402.8316
2017-05-17 19:00 | 5 | 19 | 1.4805 | 1643.0532
2017-05-17 20:00 | 5 | 20 | 1.6215 | 1799.5167
2017-05-17 21:00 | 5 | 21 | 1.3539 | 1502.559
2017-05-17 22:00 | 5 | 22 | 1.0658 | 1182.8506
2017-05-17 23:00 | 5 | 23 | 0.76653 | 850.6995
2017-05-18 | 5 | 0 | 0.65462 | 726.4939
2017-05-18 01:00 | 5 | 1 | 0.60432 | 670.6698
2017-05-18 02:00 | 5 | 2 | 0.59715 | 662.7234
2017-05-18 03:00 | 5 | 3 | 0.59794 | 663.5943
2017-05-18 04:00 | 5 | 4 | 0.65026 | 721.6552
2017-05-18 05:00 | 5 | 5 | 0.78592 | 872.2143
2017-05-18 06:00 | 5 | 6 | 0.97374 | 1080.6537
2017-05-18 07:00 | 5 | 7 | 0.90187 | 1000.8994
2017-05-18 08:00 | 5 | 8 | 0.83379 | 925.3408
2017-05-18 09:00 | 5 | 9 | 0.85007 | 943.4144
2017-05-18 10:00 | 5 | 10 | 0.84347 | 936.0809
2017-05-18 11:00 | 5 | 11 | 0.81514 | 904.6416
2017-05-18 12:00 | 5 | 12 | 0.7925 | 879.5226
2017-05-18 13:00 | 5 | 13 | 0.78316 | 869.1524
2017-05-18 14:00 | 5 | 14 | 0.80632 | 894.8536
2017-05-18 15:00 | 5 | 15 | 0.92055 | 1021.6303
2017-05-18 16:00 | 5 | 16 | 1.1278 | 1251.6773
2017-05-18 17:00 | 5 | 17 | 1.2078 | 1340.4634
2017-05-18 18:00 | 5 | 18 | 1.2712 | 1410.7625
2017-05-18 19:00 | 5 | 19 | 1.4818 | 1644.5328
2017-05-18 20:00 | 5 | 20 | 1.6162 | 1793.634
2017-05-18 21:00 | 5 | 21 | 1.3415 | 1488.8241
2017-05-18 22:00 | 5 | 22 | 1.05 | 1165.237
2017-05-18 23:00 | 5 | 23 | 0.74502 | 826.8196
2017-05-19 | 5 | 0 | 0.63232 | 701.7447
2017-05-19 01:00 | 5 | 1 | 0.58579 | 650.1066
2017-05-19 02:00 | 5 | 2 | 0.57744 | 640.8411
2017-05-19 03:00 | 5 | 3 | 0.57735 | 640.7436
2017-05-19 04:00 | 5 | 4 | 0.63064 | 699.8892
2017-05-19 05:00 | 5 | 5 | 0.77476 | 859.8252
2017-05-19 06:00 | 5 | 6 | 0.95351 | 1058.2104
2017-05-19 07:00 | 5 | 7 | 0.87087 | 966.4962
2017-05-19 08:00 | 5 | 8 | 0.79276 | 879.8033
2017-05-19 09:00 | 5 | 9 | 0.79064 | 877.4494
2017-05-19 10:00 | 5 | 10 | 0.78862 | 875.2091
2017-05-19 11:00 | 5 | 11 | 0.76471 | 848.6769
2017-05-19 12:00 | 5 | 12 | 0.73691 | 817.8206
2017-05-19 13:00 | 5 | 13 | 0.72134 | 800.5394
2017-05-19 14:00 | 5 | 14 | 0.74878 | 830.9965
2017-05-19 15:00 | 5 | 15 | 0.86514 | 960.1297
2017-05-19 16:00 | 5 | 16 | 1.0579 | 1174.0058
2017-05-19 17:00 | 5 | 17 | 1.1552 | 1282.078
2017-05-19 18:00 | 5 | 18 | 1.219 | 1352.8778
2017-05-19 19:00 | 5 | 19 | 1.4311 | 1588.2639
2017-05-19 20:00 | 5 | 20 | 1.5648 | 1736.5987
2017-05-19 21:00 | 5 | 21 | 1.2885 | 1430.0299
2017-05-19 22:00 | 5 | 22 | 1.0024 | 1112.4899
2017-05-19 23:00 | 5 | 23 | 0.70653 | 784.1044
2017-05-20 | 5 | 0 | 0.60294 | 669.1406
2017-05-20 01:00 | 5 | 1 | 0.55659 | 617.7073
2017-05-20 02:00 | 5 | 2 | 0.5509 | 611.3879
2017-05-20 03:00 | 5 | 3 | 0.55632 | 617.4015
2017-05-20 04:00 | 5 | 4 | 0.61187 | 679.0572
2017-05-20 05:00 | 5 | 5 | 0.75526 | 838.1855
2017-05-20 06:00 | 5 | 6 | 0.94162 | 1045.0073
2017-05-20 07:00 | 5 | 7 | 0.86969 | 965.1863
2017-05-20 08:00 | 5 | 8 | 0.8025 | 890.6172
2017-05-20 09:00 | 5 | 9 | 0.80059 | 888.4956
2017-05-20 10:00 | 5 | 10 | 0.81747 | 907.2331
2017-05-20 11:00 | 5 | 11 | 0.79781 | 885.4087
2017-05-20 12:00 | 5 | 12 | 0.77189 | 856.6399
2017-05-20 13:00 | 5 | 13 | 0.76046 | 843.9611
2017-05-20 14:00 | 5 | 14 | 0.78584 | 872.1246
2017-05-20 15:00 | 5 | 15 | 0.90105 | 999.9915
2017-05-20 16:00 | 5 | 16 | 1.0932 | 1213.2394
2017-05-20 17:00 | 5 | 17 | 1.1895 | 1320.1557
2017-05-20 18:00 | 5 | 18 | 1.2533 | 1390.8827
2017-05-20 19:00 | 5 | 19 | 1.466 | 1626.9465
2017-05-20 20:00 | 5 | 20 | 1.6004 | 1776.1153
2017-05-20 21:00 | 5 | 21 | 1.3118 | 1455.8321
2017-05-20 22:00 | 5 | 22 | 0.99882 | 1108.494
2017-05-20 23:00 | 5 | 23 | 0.67906 | 753.62
2017-05-21 | 5 | 0 | 0.55562 | 616.6278
2017-05-21 01:00 | 5 | 1 | 0.49985 | 554.7377
2017-05-21 02:00 | 5 | 2 | 0.49427 | 548.5423
2017-05-21 03:00 | 5 | 3 | 0.5028 | 558.0081
2017-05-21 04:00 | 5 | 4 | 0.56129 | 622.9212
2017-05-21 05:00 | 5 | 5 | 0.70768 | 785.3873
2017-05-21 06:00 | 5 | 6 | 0.91564 | 1016.1773
2017-05-21 07:00 | 5 | 7 | 0.85573 | 949.6873
2017-05-21 08:00 | 5 | 8 | 0.79975 | 887.5639
2017-05-21 09:00 | 5 | 9 | 0.80971 | 898.6209
2017-05-21 10:00 | 5 | 10 | 0.81747 | 907.2331
2017-05-21 11:00 | 5 | 11 | 0.79781 | 885.4087
2017-05-21 12:00 | 5 | 12 | 0.77189 | 856.6399
2017-05-21 13:00 | 5 | 13 | 0.76046 | 843.9611
2017-05-21 14:00 | 5 | 14 | 0.78584 | 872.1246
2017-05-21 15:00 | 5 | 15 | 0.90105 | 999.9915
2017-05-21 16:00 | 5 | 16 | 1.0932 | 1213.2394
2017-05-21 17:00 | 5 | 17 | 1.1895 | 1320.1557
2017-05-21 18:00 | 5 | 18 | 1.2533 | 1390.8827
2017-05-21 19:00 | 5 | 19 | 1.466 | 1626.9465
2017-05-21 20:00 | 5 | 20 | 1.6004 | 1776.1153
2017-05-21 21:00 | 5 | 21 | 1.3118 | 1455.8321
2017-05-21 22:00 | 5 | 22 | 1.0099 | 1120.7391
2017-05-21 23:00 | 5 | 23 | 0.70794 | 785.6773
2017-05-22 | 5 | 0 | 0.59712 | 662.6805
2017-05-22 01:00 | 5 | 1 | 0.55369 | 614.4852
2017-05-22 02:00 | 5 | 2 | 0.55202 | 612.6358
2017-05-22 03:00 | 5 | 3 | 0.55578 | 616.8026
2017-05-22 04:00 | 5 | 4 | 0.61003 | 677.0118
2017-05-22 05:00 | 5 | 5 | 0.75178 | 834.3248
2017-05-22 06:00 | 5 | 6 | 0.93208 | 1034.4284
2017-05-22 07:00 | 5 | 7 | 0.85009 | 943.4332
2017-05-22 08:00 | 5 | 8 | 0.7754 | 860.538
2017-05-22 09:00 | 5 | 9 | 0.77622 | 861.4457
2017-05-22 10:00 | 5 | 10 | 0.77829 | 863.7511
2017-05-22 11:00 | 5 | 11 | 0.75 | 832.3486
2017-05-22 12:00 | 5 | 12 | 0.7283 | 808.2658
2017-05-22 13:00 | 5 | 13 | 0.72134 | 800.5394
2017-05-22 14:00 | 5 | 14 | 0.74878 | 830.9965
2017-05-22 15:00 | 5 | 15 | 0.86514 | 960.1297
2017-05-22 16:00 | 5 | 16 | 1.0579 | 1174.0058
2017-05-22 17:00 | 5 | 17 | 1.1552 | 1282.078
2017-05-22 18:00 | 5 | 18 | 1.219 | 1352.8778
2017-05-22 19:00 | 5 | 19 | 1.4311 | 1588.2639
2017-05-22 20:00 | 5 | 20 | 1.5648 | 1736.5987
2017-05-22 21:00 | 5 | 21 | 1.2835 | 1424.4323
2017-05-22 22:00 | 5 | 22 | 0.98329 | 1091.2534
2017-05-22 23:00 | 5 | 23 | 0.67248 | 746.3246
2017-05-23 | 5 | 0 | 0.56261 | 624.3857
2017-05-23 01:00 | 5 | 1 | 0.52599 | 583.7465
2017-05-23 02:00 | 5 | 2 | 0.52632 | 584.1067
2017-05-23 03:00 | 5 | 3 | 0.53496 | 593.6991
2017-05-23 04:00 | 5 | 4 | 0.59404 | 659.2638
2017-05-23 05:00 | 5 | 5 | 0.73495 | 815.6532
2017-05-23 06:00 | 5 | 6 | 0.91572 | 1016.2637
2017-05-23 07:00 | 5 | 7 | 0.83384 | 925.4024
2017-05-23 08:00 | 5 | 8 | 0.76006 | 843.5154
2017-05-23 09:00 | 5 | 9 | 0.75551 | 838.4702
2017-05-23 10:00 | 5 | 10 | 0.76498 | 848.981
2017-05-23 11:00 | 5 | 11 | 0.75 | 832.3486
2017-05-23 12:00 | 5 | 12 | 0.7283 | 808.2658
2017-05-23 13:00 | 5 | 13 | 0.72134 | 800.5394
2017-05-23 14:00 | 5 | 14 | 0.74878 | 830.9965
2017-05-23 15:00 | 5 | 15 | 0.86514 | 960.1297
2017-05-23 16:00 | 5 | 16 | 1.0579 | 1174.0058
2017-05-23 17:00 | 5 | 17 | 1.1552 | 1282.078
2017-05-23 18:00 | 5 | 18 | 1.219 | 1352.8778
2017-05-23 19:00 | 5 | 19 | 1.4311 | 1588.2639
2017-05-23 20:00 | 5 | 20 | 1.5648 | 1736.5987
2017-05-23 21:00 | 5 | 21 | 1.2835 | 1424.4323
2017-05-23 22:00 | 5 | 22 | 0.98329 | 1091.2534
2017-05-23 23:00 | 5 | 23 | 0.67248 | 746.3246
2017-05-24 | 5 | 0 | 0.55167 | 612.2474
2017-05-24 01:00 | 5 | 1 | 0.51004 | 566.044
2017-05-24 02:00 | 5 | 2 | 0.51362 | 570.0109
2017-05-24 03:00 | 5 | 3 | 0.52413 | 581.6772
2017-05-24 04:00 | 5 | 4 | 0.58486 | 649.0819
2017-05-24 05:00 | 5 | 5 | 0.72781 | 807.7214
2017-05-24 06:00 | 5 | 6 | 0.91188 | 1012.0077
2017-05-24 07:00 | 5 | 7 | 0.8401 | 932.3416
2017-05-24 08:00 | 5 | 8 | 0.76707 | 851.2958
2017-05-24 09:00 | 5 | 9 | 0.76406 | 847.9525
2017-05-24 10:00 | 5 | 10 | 0.77113 | 855.8018
2017-05-24 11:00 | 5 | 11 | 0.75 | 832.3486
2017-05-24 12:00 | 5 | 12 | 0.7283 | 808.2658
2017-05-24 13:00 | 5 | 13 | 0.72134 | 800.5394
2017-05-24 14:00 | 5 | 14 | 0.74878 | 830.9965
2017-05-24 15:00 | 5 | 15 | 0.86514 | 960.1297
2017-05-24 16:00 | 5 | 16 | 1.0579 | 1174.0058
2017-05-24 17:00 | 5 | 17 | 1.1552 | 1282.078
2017-05-24 18:00 | 5 | 18 | 1.219 | 1352.8778
2017-05-24 19:00 | 5 | 19 | 1.4311 | 1588.2639
2017-05-24 20:00 | 5 | 20 | 1.568 | 1740.1709
2017-05-24 21:00 | 5 | 21 | 1.3 | 1442.7163
2017-05-24 22:00 | 5 | 22 | 1.014 | 1125.3634
2017-05-24 23:00 | 5 | 23 | 0.71896 | 797.9027
2017-05-25 | 5 | 0 | 0.60821 | 674.9949
2017-05-25 01:00 | 5 | 1 | 0.56354 | 625.4151
2017-05-25 02:00 | 5 | 2 | 0.55734 | 618.5378
2017-05-25 03:00 | 5 | 3 | 0.55884 | 620.205
2017-05-25 04:00 | 5 | 4 | 0.61235 | 679.5895
2017-05-25 05:00 | 5 | 5 | 0.74985 | 832.1843
2017-05-25 06:00 | 5 | 6 | 0.94781 | 1051.8865
2017-05-25 07:00 | 5 | 7 | 0.8751 | 971.1856
2017-05-25 08:00 | 5 | 8 | 0.81485 | 904.3189
2017-05-25 09:00 | 5 | 9 | 0.83579 | 927.5649
2017-05-25 10:00 | 5 | 10 | 0.83835 | 930.4011
2017-05-25 11:00 | 5 | 11 | 0.81756 | 907.326
2017-05-25 12:00 | 5 | 12 | 0.79159 | 878.5027
2017-05-25 13:00 | 5 | 13 | 0.78361 | 869.6487
2017-05-25 14:00 | 5 | 14 | 0.80801 | 896.7336
2017-05-25 15:00 | 5 | 15 | 0.92169 | 1022.8904
2017-05-25 16:00 | 5 | 16 | 1.1225 | 1245.782
2017-05-25 17:00 | 5 | 17 | 1.2062 | 1338.5917
2017-05-25 18:00 | 5 | 18 | 1.2668 | 1405.9503
2017-05-25 19:00 | 5 | 19 | 1.4762 | 1638.2902
2017-05-25 20:00 | 5 | 20 | 1.6095 | 1786.2663
2017-05-25 21:00 | 5 | 21 | 1.3331 | 1479.5189
2017-05-25 22:00 | 5 | 22 | 1.04 | 1154.1875
2017-05-25 23:00 | 5 | 23 | 0.73611 | 816.9412
2017-05-26 | 5 | 0 | 0.60687 | 673.508
2017-05-26 01:00 | 5 | 1 | 0.5621 | 623.8209
2017-05-26 02:00 | 5 | 2 | 0.55885 | 620.2176
2017-05-26 03:00 | 5 | 3 | 0.55253 | 613.1945
2017-05-26 04:00 | 5 | 4 | 0.59931 | 665.1167
2017-05-26 05:00 | 5 | 5 | 0.70551 | 782.9753
2017-05-26 06:00 | 5 | 6 | 0.8518 | 945.3313
2017-05-26 07:00 | 5 | 7 | 0.71704 | 795.7722
2017-05-26 08:00 | 5 | 8 | 0.58881 | 653.4611
2017-05-26 09:00 | 5 | 9 | 0.56937 | 631.8849
2017-05-26 10:00 | 5 | 10 | 0.56982 | 632.3872
2017-05-26 11:00 | 5 | 11 | 0.57308 | 636.009
2017-05-26 12:00 | 5 | 12 | 0.5632 | 625.0384
2017-05-26 13:00 | 5 | 13 | 0.57519 | 638.3419
2017-05-26 14:00 | 5 | 14 | 0.61 | 676.9832
2017-05-26 15:00 | 5 | 15 | 0.7319 | 812.2638
2017-05-26 16:00 | 5 | 16 | 0.93655 | 1039.3866
2017-05-26 17:00 | 5 | 17 | 1.0243 | 1136.7793
2017-05-26 18:00 | 5 | 18 | 1.0885 | 1208.0734
2017-05-26 19:00 | 5 | 19 | 1.3052 | 1448.5633
2017-05-26 20:00 | 5 | 20 | 1.445 | 1603.6752
2017-05-26 21:00 | 5 | 21 | 1.2083 | 1340.995
2017-05-26 22:00 | 5 | 22 | 0.9772 | 1084.497
2017-05-26 23:00 | 5 | 23 | 0.72084 | 799.9891
2017-05-27 | 5 | 0 | 0.62073 | 688.8872
2017-05-27 01:00 | 5 | 1 | 0.57611 | 639.3724
2017-05-27 02:00 | 5 | 2 | 0.57319 | 636.1253
2017-05-27 03:00 | 5 | 3 | 0.56686 | 629.1012
2017-05-27 04:00 | 5 | 4 | 0.6121 | 679.3106
2017-05-27 05:00 | 5 | 5 | 0.7173 | 796.0559
2017-05-27 06:00 | 5 | 6 | 0.85665 | 950.7136
2017-05-27 07:00 | 5 | 7 | 0.72841 | 808.3853
2017-05-27 08:00 | 5 | 8 | 0.60336 | 669.6122
2017-05-27 09:00 | 5 | 9 | 0.60086 | 666.8314
2017-05-27 10:00 | 5 | 10 | 0.58952 | 654.25
2017-05-27 11:00 | 5 | 11 | 0.58536 | 649.6315
2017-05-27 12:00 | 5 | 12 | 0.57265 | 635.5227
2017-05-27 13:00 | 5 | 13 | 0.5777 | 641.1367
2017-05-27 14:00 | 5 | 14 | 0.60774 | 674.468
2017-05-27 15:00 | 5 | 15 | 0.72733 | 807.1945
2017-05-27 16:00 | 5 | 16 | 0.93029 | 1032.439
2017-05-27 17:00 | 5 | 17 | 1.017 | 1128.6259
2017-05-27 18:00 | 5 | 18 | 1.081 | 1199.7301
2017-05-27 19:00 | 5 | 19 | 1.2979 | 1440.4647
2017-05-27 20:00 | 5 | 20 | 1.4367 | 1594.4511
2017-05-27 21:00 | 5 | 21 | 1.2013 | 1333.2029
2017-05-27 22:00 | 5 | 22 | 0.97179 | 1078.4921
2017-05-27 23:00 | 5 | 23 | 0.71517 | 793.6948
2017-05-28 | 5 | 0 | 0.61451 | 681.9822
2017-05-28 01:00 | 5 | 1 | 0.57119 | 633.9121
2017-05-28 02:00 | 5 | 2 | 0.56902 | 631.5011
2017-05-28 03:00 | 5 | 3 | 0.56392 | 625.8343
2017-05-28 04:00 | 5 | 4 | 0.60897 | 675.8407
2017-05-28 05:00 | 5 | 5 | 0.7197 | 798.7235
2017-05-28 06:00 | 5 | 6 | 0.84866 | 941.8414
2017-05-28 07:00 | 5 | 7 | 0.70773 | 785.4443
2017-05-28 08:00 | 5 | 8 | 0.57264 | 635.5168
2017-05-28 09:00 | 5 | 9 | 0.548 | 608.1718
2017-05-28 10:00 | 5 | 10 | 0.54133 | 600.7712
2017-05-28 11:00 | 5 | 11 | 0.53427 | 592.9337
2017-05-28 12:00 | 5 | 12 | 0.52548 | 583.1818
2017-05-28 13:00 | 5 | 13 | 0.53992 | 599.207
2017-05-28 14:00 | 5 | 14 | 0.5769 | 640.2477
2017-05-28 15:00 | 5 | 15 | 0.69808 | 774.7319
2017-05-28 16:00 | 5 | 16 | 0.89133 | 989.203
2017-05-28 17:00 | 5 | 17 | 0.98709 | 1095.4789
2017-05-28 18:00 | 5 | 18 | 1.0472 | 1162.1693
2017-05-28 19:00 | 5 | 19 | 1.26 | 1398.324
2017-05-28 20:00 | 5 | 20 | 1.3943 | 1547.3607
2017-05-28 21:00 | 5 | 21 | 1.1494 | 1275.6455
2017-05-28 22:00 | 5 | 22 | 0.90861 | 1008.3802
2017-05-28 23:00 | 5 | 23 | 0.643 | 713.6009
2017-05-29 | 5 | 0 | 0.56171 | 623.3883
2017-05-29 01:00 | 5 | 1 | 0.51745 | 574.2723
2017-05-29 02:00 | 5 | 2 | 0.51454 | 571.0326
2017-05-29 03:00 | 5 | 3 | 0.51948 | 576.5231
2017-05-29 04:00 | 5 | 4 | 0.57444 | 637.5113
2017-05-29 05:00 | 5 | 5 | 0.71298 | 791.2714
2017-05-29 06:00 | 5 | 6 | 0.90046 | 999.331
2017-05-29 07:00 | 5 | 7 | 0.82302 | 913.3834
2017-05-29 08:00 | 5 | 8 | 0.75249 | 835.1167
2017-05-29 09:00 | 5 | 9 | 0.75209 | 834.6759
2017-05-29 10:00 | 5 | 10 | 0.76498 | 848.981
2017-05-29 11:00 | 5 | 11 | 0.75 | 832.3486
2017-05-29 12:00 | 5 | 12 | 0.7283 | 808.2658
2017-05-29 13:00 | 5 | 13 | 0.72134 | 800.5394
2017-05-29 14:00 | 5 | 14 | 0.74878 | 830.9965
2017-05-29 15:00 | 5 | 15 | 0.86514 | 960.1297
2017-05-29 16:00 | 5 | 16 | 1.0579 | 1174.0058
2017-05-29 17:00 | 5 | 17 | 1.1552 | 1282.078
2017-05-29 18:00 | 5 | 18 | 1.219 | 1352.8778
2017-05-29 19:00 | 5 | 19 | 1.4311 | 1588.2639
2017-05-29 20:00 | 5 | 20 | 1.5648 | 1736.5987
2017-05-29 21:00 | 5 | 21 | 1.2835 | 1424.4323
2017-05-29 22:00 | 5 | 22 | 0.98329 | 1091.2534
2017-05-29 23:00 | 5 | 23 | 0.67248 | 746.3246
2017-05-30 | 5 | 0 | 0.55167 | 612.2474
2017-05-30 01:00 | 5 | 1 | 0.4967 | 551.2375
2017-05-30 02:00 | 5 | 2 | 0.49089 | 544.7922
2017-05-30 03:00 | 5 | 3 | 0.50192 | 557.0311
2017-05-30 04:00 | 5 | 4 | 0.56042 | 621.9505
2017-05-30 05:00 | 5 | 5 | 0.70409 | 781.4013
2017-05-30 06:00 | 5 | 6 | 0.89269 | 990.7104
2017-05-30 07:00 | 5 | 7 | 0.81851 | 908.3835
2017-05-30 08:00 | 5 | 8 | 0.74877 | 830.9829
2017-05-30 09:00 | 5 | 9 | 0.75382 | 836.5877
2017-05-30 10:00 | 5 | 10 | 0.76498 | 848.981
2017-05-30 11:00 | 5 | 11 | 0.75 | 832.3486
2017-05-30 12:00 | 5 | 12 | 0.7283 | 808.2658
2017-05-30 13:00 | 5 | 13 | 0.72134 | 800.5394
2017-05-30 14:00 | 5 | 14 | 0.74878 | 830.9965
2017-05-30 15:00 | 5 | 15 | 0.86514 | 960.1297
2017-05-30 16:00 | 5 | 16 | 1.0579 | 1174.0058
2017-05-30 17:00 | 5 | 17 | 1.1552 | 1282.078
2017-05-30 18:00 | 5 | 18 | 1.219 | 1352.8778
2017-05-30 19:00 | 5 | 19 | 1.4311 | 1588.2639
2017-05-30 20:00 | 5 | 20 | 1.5648 | 1736.5987
2017-05-30 21:00 | 5 | 21 | 1.2835 | 1424.4323
2017-05-30 22:00 | 5 | 22 | 0.98329 | 1091.2534
2017-05-30 23:00 | 5 | 23 | 0.67248 | 746.3246
2017-05-31 | 5 | 0 | 0.55167 | 612.2474
2017-05-31 01:00 | 5 | 1 | 0.50389 | 559.2168
2017-05-31 02:00 | 5 | 2 | 0.50525 | 560.7286
2017-05-31 03:00 | 5 | 3 | 0.51714 | 573.9266
2017-05-31 04:00 | 5 | 4 | 0.57701 | 640.3698
2017-05-31 05:00 | 5 | 5 | 0.71894 | 797.8825
2017-05-31 06:00 | 5 | 6 | 0.91178 | 1011.8932
2017-05-31 07:00 | 5 | 7 | 0.84386 | 936.519
2017-05-31 08:00 | 5 | 8 | 0.78132 | 867.1148
2017-05-31 09:00 | 5 | 9 | 0.79819 | 885.8333
2017-05-31 10:00 | 5 | 10 | 0.80133 | 889.3175
2017-05-31 11:00 | 5 | 11 | 0.78057 | 866.2802
2017-05-31 12:00 | 5 | 12 | 0.75473 | 837.5974
2017-05-31 13:00 | 5 | 13 | 0.73981 | 821.0463
2017-05-31 14:00 | 5 | 14 | 0.76763 | 851.9126
2017-05-31 15:00 | 5 | 15 | 0.88313 | 980.0936
2017-05-31 16:00 | 5 | 16 | 1.0861 | 1205.4043
2017-05-31 17:00 | 5 | 17 | 1.1768 | 1306.0335
2017-05-31 18:00 | 5 | 18 | 1.2438 | 1380.3547
2017-05-31 19:00 | 5 | 19 | 1.458 | 1618.1362
2017-05-31 20:00 | 5 | 20 | 1.5948 | 1769.9371
2017-05-31 21:00 | 5 | 21 | 1.3202 | 1465.2121
2017-05-31 22:00 | 5 | 22 | 1.0278 | 1140.6274
2017-05-31 23:00 | 5 | 23 | 0.72522 | 804.8492
2017-06-01 | 6 | 0 | 0.5669 | 629.1481
2017-06-01 01:00 | 6 | 1 | 0.51341 | 569.7781
2017-06-01 02:00 | 6 | 2 | 0.50181 | 556.909
2017-06-01 03:00 | 6 | 3 | 0.49872 | 553.4816
2017-06-01 04:00 | 6 | 4 | 0.54325 | 602.8992
2017-06-01 05:00 | 6 | 5 | 0.66185 | 734.5217
2017-06-01 06:00 | 6 | 6 | 0.82952 | 920.6065
2017-06-01 07:00 | 6 | 7 | 0.76053 | 844.0427
2017-06-01 08:00 | 6 | 8 | 0.7053 | 782.7415
2017-06-01 09:00 | 6 | 9 | 0.70564 | 783.1187
2017-06-01 10:00 | 6 | 10 | 0.7156 | 794.1786
2017-06-01 11:00 | 6 | 11 | 0.70032 | 777.2173
2017-06-01 12:00 | 6 | 12 | 0.67877 | 753.3045
2017-06-01 13:00 | 6 | 13 | 0.66988 | 743.4332
2017-06-01 14:00 | 6 | 14 | 0.69727 | 773.8357
2017-06-01 15:00 | 6 | 15 | 0.79643 | 883.8759
2017-06-01 16:00 | 6 | 16 | 0.96884 | 1075.218
2017-06-01 17:00 | 6 | 17 | 1.049 | 1164.1397
2017-06-01 18:00 | 6 | 18 | 1.088 | 1207.4263
2017-06-01 19:00 | 6 | 19 | 1.2694 | 1408.7309
2017-06-01 20:00 | 6 | 20 | 1.4432 | 1601.6645
2017-06-01 21:00 | 6 | 21 | 1.2193 | 1353.1276
2017-06-01 22:00 | 6 | 22 | 0.92692 | 1028.6956
2017-06-01 23:00 | 6 | 23 | 0.62648 | 695.2705
2017-06-02 | 6 | 0 | 0.51046 | 566.513
2017-06-02 01:00 | 6 | 1 | 0.45507 | 505.0422
2017-06-02 02:00 | 6 | 2 | 0.4435 | 492.2011
2017-06-02 03:00 | 6 | 3 | 0.44205 | 490.5838
2017-06-02 04:00 | 6 | 4 | 0.48978 | 543.5541
2017-06-02 05:00 | 6 | 5 | 0.62431 | 692.8615
2017-06-02 06:00 | 6 | 6 | 0.80192 | 889.9695
2017-06-02 07:00 | 6 | 7 | 0.74898 | 831.2163
2017-06-02 08:00 | 6 | 8 | 0.70573 | 783.2161
2017-06-02 09:00 | 6 | 9 | 0.71154 | 789.6634
2017-06-02 10:00 | 6 | 10 | 0.7156 | 794.1786
2017-06-02 11:00 | 6 | 11 | 0.70032 | 777.2173
2017-06-02 12:00 | 6 | 12 | 0.67877 | 753.3045
2017-06-02 13:00 | 6 | 13 | 0.66988 | 743.4332
2017-06-02 14:00 | 6 | 14 | 0.69727 | 773.8357
2017-06-02 15:00 | 6 | 15 | 0.79643 | 883.8759
2017-06-02 16:00 | 6 | 16 | 0.96884 | 1075.218
2017-06-02 17:00 | 6 | 17 | 1.049 | 1164.1397
2017-06-02 18:00 | 6 | 18 | 1.088 | 1207.4263
2017-06-02 19:00 | 6 | 19 | 1.2694 | 1408.7309
2017-06-02 20:00 | 6 | 20 | 1.4432 | 1601.6645
2017-06-02 21:00 | 6 | 21 | 1.2194 | 1353.3314
2017-06-02 22:00 | 6 | 22 | 0.94063 | 1043.9097
2017-06-02 23:00 | 6 | 23 | 0.65854 | 730.8475
2017-06-03 | 6 | 0 | 0.56109 | 622.6978
2017-06-03 01:00 | 6 | 1 | 0.5168 | 573.5503
2017-06-03 02:00 | 6 | 2 | 0.51611 | 572.7845
2017-06-03 03:00 | 6 | 3 | 0.52232 | 579.6768
2017-06-03 04:00 | 6 | 4 | 0.57693 | 640.2816
2017-06-03 05:00 | 6 | 5 | 0.71216 | 790.3543
2017-06-03 06:00 | 6 | 6 | 0.88589 | 983.1641
2017-06-03 07:00 | 6 | 7 | 0.82793 | 918.8342
2017-06-03 08:00 | 6 | 8 | 0.78725 | 873.6916
2017-06-03 09:00 | 6 | 9 | 0.80329 | 891.4903
2017-06-03 10:00 | 6 | 10 | 0.79987 | 887.7021
2017-06-03 11:00 | 6 | 11 | 0.76729 | 851.5353
2017-06-03 12:00 | 6 | 12 | 0.73185 | 812.2069
2017-06-03 13:00 | 6 | 13 | 0.709 | 786.8548
2017-06-03 14:00 | 6 | 14 | 0.73433 | 814.9638
2017-06-03 15:00 | 6 | 15 | 0.83234 | 923.7376
2017-06-03 16:00 | 6 | 16 | 1.0042 | 1114.4517
2017-06-03 17:00 | 6 | 17 | 1.0833 | 1202.2173
2017-06-03 18:00 | 6 | 18 | 1.1222 | 1245.4312
2017-06-03 19:00 | 6 | 19 | 1.3042 | 1447.4134
2017-06-03 20:00 | 6 | 20 | 1.4788 | 1641.181
2017-06-03 21:00 | 6 | 21 | 1.2475 | 1384.5274
2017-06-03 22:00 | 6 | 22 | 0.95202 | 1056.5495
2017-06-03 23:00 | 6 | 23 | 0.66482 | 737.8193
2017-06-04 | 6 | 0 | 0.56089 | 622.4742
2017-06-04 01:00 | 6 | 1 | 0.52103 | 578.2376
2017-06-04 02:00 | 6 | 2 | 0.51877 | 575.7286
2017-06-04 03:00 | 6 | 3 | 0.52522 | 582.8932
2017-06-04 04:00 | 6 | 4 | 0.57955 | 643.1879
2017-06-04 05:00 | 6 | 5 | 0.71135 | 789.4569
2017-06-04 06:00 | 6 | 6 | 0.88447 | 981.5888
2017-06-04 07:00 | 6 | 7 | 0.82704 | 917.8533
2017-06-04 08:00 | 6 | 8 | 0.78402 | 870.108
2017-06-04 09:00 | 6 | 9 | 0.80456 | 892.9019
2017-06-04 10:00 | 6 | 10 | 0.80061 | 888.523
2017-06-04 11:00 | 6 | 11 | 0.77152 | 856.2288
2017-06-04 12:00 | 6 | 12 | 0.73894 | 820.0807
2017-06-04 13:00 | 6 | 13 | 0.72001 | 799.0714
2017-06-04 14:00 | 6 | 14 | 0.74103 | 822.4013
2017-06-04 15:00 | 6 | 15 | 0.83507 | 926.7591
2017-06-04 16:00 | 6 | 16 | 1.008 | 1118.6657
2017-06-04 17:00 | 6 | 17 | 1.0833 | 1202.2173
2017-06-04 18:00 | 6 | 18 | 1.1222 | 1245.4312
2017-06-04 19:00 | 6 | 19 | 1.3042 | 1447.4134
2017-06-04 20:00 | 6 | 20 | 1.4804 | 1642.9537
2017-06-04 21:00 | 6 | 21 | 1.2568 | 1394.8486
2017-06-04 22:00 | 6 | 22 | 0.96304 | 1068.7828
2017-06-04 23:00 | 6 | 23 | 0.6656 | 738.6839
2017-06-05 | 6 | 0 | 0.55108 | 611.5889
2017-06-05 01:00 | 6 | 1 | 0.50219 | 557.336
2017-06-05 02:00 | 6 | 2 | 0.49725 | 551.8507
2017-06-05 03:00 | 6 | 3 | 0.49863 | 553.3762
2017-06-05 04:00 | 6 | 4 | 0.54555 | 605.4506
2017-06-05 05:00 | 6 | 5 | 0.66908 | 742.5465
2017-06-05 06:00 | 6 | 6 | 0.8367 | 928.5739
2017-06-05 07:00 | 6 | 7 | 0.77812 | 863.5587
2017-06-05 08:00 | 6 | 8 | 0.73332 | 813.8419
2017-06-05 09:00 | 6 | 9 | 0.74816 | 830.3077
2017-06-05 10:00 | 6 | 10 | 0.75236 | 834.9696
2017-06-05 11:00 | 6 | 11 | 0.73083 | 811.0773
2017-06-05 12:00 | 6 | 12 | 0.70121 | 778.2063
2017-06-05 13:00 | 6 | 13 | 0.68797 | 763.5149
2017-06-05 14:00 | 6 | 14 | 0.70998 | 787.9375
2017-06-05 15:00 | 6 | 15 | 0.79941 | 887.1851
2017-06-05 16:00 | 6 | 16 | 0.96884 | 1075.218
2017-06-05 17:00 | 6 | 17 | 1.049 | 1164.1397
2017-06-05 18:00 | 6 | 18 | 1.088 | 1207.4263
2017-06-05 19:00 | 6 | 19 | 1.2694 | 1408.7309
2017-06-05 20:00 | 6 | 20 | 1.4432 | 1601.6645
2017-06-05 21:00 | 6 | 21 | 1.2193 | 1353.1276
2017-06-05 22:00 | 6 | 22 | 0.92692 | 1028.6956
2017-06-05 23:00 | 6 | 23 | 0.62719 | 696.0602
2017-06-06 | 6 | 0 | 0.51712 | 573.897
2017-06-06 01:00 | 6 | 1 | 0.46946 | 521.0096
2017-06-06 02:00 | 6 | 2 | 0.4639 | 514.8366
2017-06-06 03:00 | 6 | 3 | 0.46571 | 516.8417
2017-06-06 04:00 | 6 | 4 | 0.51531 | 571.8962
2017-06-06 05:00 | 6 | 5 | 0.63865 | 708.7778
2017-06-06 06:00 | 6 | 6 | 0.8104 | 899.3881
2017-06-06 07:00 | 6 | 7 | 0.75443 | 837.2709
2017-06-06 08:00 | 6 | 8 | 0.71219 | 790.3846
2017-06-06 09:00 | 6 | 9 | 0.73221 | 812.6055
2017-06-06 10:00 | 6 | 10 | 0.74996 | 832.3069
2017-06-06 11:00 | 6 | 11 | 0.73536 | 816.1061
2017-06-06 12:00 | 6 | 12 | 0.71633 | 794.98
2017-06-06 13:00 | 6 | 13 | 0.71079 | 788.8397
2017-06-06 14:00 | 6 | 14 | 0.74111 | 822.4869
2017-06-06 15:00 | 6 | 15 | 0.84067 | 932.9716
2017-06-06 16:00 | 6 | 16 | 1.0279 | 1140.7132
2017-06-06 17:00 | 6 | 17 | 1.094 | 1214.0748
2017-06-06 18:00 | 6 | 18 | 1.1322 | 1256.5469
2017-06-06 19:00 | 6 | 19 | 1.3154 | 1459.864
2017-06-06 20:00 | 6 | 20 | 1.4892 | 1652.7175
2017-06-06 21:00 | 6 | 21 | 1.2706 | 1410.1576
2017-06-06 22:00 | 6 | 22 | 0.98731 | 1095.7145
2017-06-06 23:00 | 6 | 23 | 0.69585 | 772.2595
2017-06-07 | 6 | 0 | 0.5853 | 649.5664
2017-06-07 01:00 | 6 | 1 | 0.5338 | 592.4138
2017-06-07 02:00 | 6 | 2 | 0.52546 | 583.153
2017-06-07 03:00 | 6 | 3 | 0.52759 | 585.5231
2017-06-07 04:00 | 6 | 4 | 0.5739 | 636.9161
2017-06-07 05:00 | 6 | 5 | 0.70057 | 777.4899
2017-06-07 06:00 | 6 | 6 | 0.86469 | 959.6393
2017-06-07 07:00 | 6 | 7 | 0.80875 | 897.5557
2017-06-07 08:00 | 6 | 8 | 0.76785 | 852.1644
2017-06-07 09:00 | 6 | 9 | 0.78352 | 869.5477
2017-06-07 10:00 | 6 | 10 | 0.79816 | 885.8018
2017-06-07 11:00 | 6 | 11 | 0.78334 | 869.3575
2017-06-07 12:00 | 6 | 12 | 0.75988 | 843.3109
2017-06-07 13:00 | 6 | 13 | 0.74721 | 829.2556
2017-06-07 14:00 | 6 | 14 | 0.77044 | 855.0335
2017-06-07 15:00 | 6 | 15 | 0.85904 | 953.3609
2017-06-07 16:00 | 6 | 16 | 1.0388 | 1152.8433
2017-06-07 17:00 | 6 | 17 | 1.0981 | 1218.6341
2017-06-07 18:00 | 6 | 18 | 1.133 | 1257.353
2017-06-07 19:00 | 6 | 19 | 1.3147 | 1459.0548
2017-06-07 20:00 | 6 | 20 | 1.4919 | 1655.7444
2017-06-07 21:00 | 6 | 21 | 1.2758 | 1415.8662
2017-06-07 22:00 | 6 | 22 | 0.99588 | 1105.2274
2017-06-07 23:00 | 6 | 23 | 0.71082 | 788.8707
2017-06-08 | 6 | 0 | 0.60386 | 670.1596
2017-06-08 01:00 | 6 | 1 | 0.55706 | 618.2302
2017-06-08 02:00 | 6 | 2 | 0.55052 | 610.9698
2017-06-08 03:00 | 6 | 3 | 0.55255 | 613.2226
2017-06-08 04:00 | 6 | 4 | 0.60079 | 666.7627
2017-06-08 05:00 | 6 | 5 | 0.7258 | 805.4943
2017-06-08 06:00 | 6 | 6 | 0.87972 | 976.3136
2017-06-08 07:00 | 6 | 7 | 0.80866 | 897.457
2017-06-08 08:00 | 6 | 8 | 0.75142 | 833.9245
2017-06-08 09:00 | 6 | 9 | 0.76952 | 854.0126
2017-06-08 10:00 | 6 | 10 | 0.75519 | 838.1134
2017-06-08 11:00 | 6 | 11 | 0.72912 | 809.1785
2017-06-08 12:00 | 6 | 12 | 0.69854 | 775.2379
2017-06-08 13:00 | 6 | 13 | 0.67925 | 753.8352
2017-06-08 14:00 | 6 | 14 | 0.7021 | 779.1948
2017-06-08 15:00 | 6 | 15 | 0.79823 | 885.8759
2017-06-08 16:00 | 6 | 16 | 0.97711 | 1084.3939
2017-06-08 17:00 | 6 | 17 | 1.049 | 1164.1397
2017-06-08 18:00 | 6 | 18 | 1.088 | 1207.4263
2017-06-08 19:00 | 6 | 19 | 1.2725 | 1412.2591
2017-06-08 20:00 | 6 | 20 | 1.4545 | 1614.232
2017-06-08 21:00 | 6 | 21 | 1.2418 | 1378.1296
2017-06-08 22:00 | 6 | 22 | 0.96428 | 1070.1591
2017-06-08 23:00 | 6 | 23 | 0.67759 | 751.9951
2017-06-09 | 6 | 0 | 0.5724 | 635.254
2017-06-09 01:00 | 6 | 1 | 0.52661 | 584.438
2017-06-09 02:00 | 6 | 2 | 0.52042 | 577.5638
2017-06-09 03:00 | 6 | 3 | 0.52361 | 581.1082
2017-06-09 04:00 | 6 | 4 | 0.57195 | 634.7498
2017-06-09 05:00 | 6 | 5 | 0.69795 | 774.5911
2017-06-09 06:00 | 6 | 6 | 0.86107 | 955.622
2017-06-09 07:00 | 6 | 7 | 0.79428 | 881.489
2017-06-09 08:00 | 6 | 8 | 0.74614 | 828.0687
2017-06-09 09:00 | 6 | 9 | 0.75603 | 839.0484
2017-06-09 10:00 | 6 | 10 | 0.74367 | 825.325
2017-06-09 11:00 | 6 | 11 | 0.71838 | 797.26
2017-06-09 12:00 | 6 | 12 | 0.68022 | 754.91
2017-06-09 13:00 | 6 | 13 | 0.66988 | 743.4332
2017-06-09 14:00 | 6 | 14 | 0.69727 | 773.8357
2017-06-09 15:00 | 6 | 15 | 0.79643 | 883.8759
2017-06-09 16:00 | 6 | 16 | 0.96884 | 1075.218
2017-06-09 17:00 | 6 | 17 | 1.049 | 1164.1397
2017-06-09 18:00 | 6 | 18 | 1.088 | 1207.4263
2017-06-09 19:00 | 6 | 19 | 1.2694 | 1408.7309
2017-06-09 20:00 | 6 | 20 | 1.4432 | 1601.6645
2017-06-09 21:00 | 6 | 21 | 1.2193 | 1353.1276
2017-06-09 22:00 | 6 | 22 | 0.92692 | 1028.6956
2017-06-09 23:00 | 6 | 23 | 0.62648 | 695.2705
2017-06-10 | 6 | 0 | 0.51441 | 570.8934
2017-06-10 01:00 | 6 | 1 | 0.45769 | 507.9402
2017-06-10 02:00 | 6 | 2 | 0.44487 | 493.7164
2017-06-10 03:00 | 6 | 3 | 0.44677 | 495.8293
2017-06-10 04:00 | 6 | 4 | 0.50427 | 559.6374
2017-06-10 05:00 | 6 | 5 | 0.63929 | 709.4815
2017-06-10 06:00 | 6 | 6 | 0.82318 | 913.5716
2017-06-10 07:00 | 6 | 7 | 0.77444 | 859.4778
2017-06-10 08:00 | 6 | 8 | 0.73829 | 819.3575
2017-06-10 09:00 | 6 | 9 | 0.75653 | 839.6008
2017-06-10 10:00 | 6 | 10 | 0.76809 | 852.4307
2017-06-10 11:00 | 6 | 11 | 0.74813 | 830.2774
2017-06-10 12:00 | 6 | 12 | 0.72236 | 801.6786
2017-06-10 13:00 | 6 | 13 | 0.709 | 786.8548
2017-06-10 14:00 | 6 | 14 | 0.73433 | 814.9638
2017-06-10 15:00 | 6 | 15 | 0.83234 | 923.7376
2017-06-10 16:00 | 6 | 16 | 1.0042 | 1114.4517
2017-06-10 17:00 | 6 | 17 | 1.0833 | 1202.2173
2017-06-10 18:00 | 6 | 18 | 1.1222 | 1245.4312
2017-06-10 19:00 | 6 | 19 | 1.3042 | 1447.4134
2017-06-10 20:00 | 6 | 20 | 1.4788 | 1641.181
2017-06-10 21:00 | 6 | 21 | 1.2475 | 1384.5274
2017-06-10 22:00 | 6 | 22 | 0.94245 | 1045.9362
2017-06-10 23:00 | 6 | 23 | 0.63306 | 702.566
2017-06-11 | 6 | 0 | 0.51704 | 573.8168
2017-06-11 01:00 | 6 | 1 | 0.4727 | 524.6023
2017-06-11 02:00 | 6 | 2 | 0.47128 | 523.0248
2017-06-11 03:00 | 6 | 3 | 0.47991 | 532.6081
2017-06-11 04:00 | 6 | 4 | 0.5335 | 592.0819
2017-06-11 05:00 | 6 | 5 | 0.66808 | 741.4412
2017-06-11 06:00 | 6 | 6 | 0.84681 | 939.7893
2017-06-11 07:00 | 6 | 7 | 0.79248 | 879.5008
2017-06-11 08:00 | 6 | 8 | 0.74951 | 831.8106
2017-06-11 09:00 | 6 | 9 | 0.75622 | 839.2523
2017-06-11 10:00 | 6 | 10 | 0.76809 | 852.4307
2017-06-11 11:00 | 6 | 11 | 0.74813 | 830.2774
2017-06-11 12:00 | 6 | 12 | 0.72236 | 801.6786
2017-06-11 13:00 | 6 | 13 | 0.709 | 786.8548
2017-06-11 14:00 | 6 | 14 | 0.73433 | 814.9638
2017-06-11 15:00 | 6 | 15 | 0.83234 | 923.7376
2017-06-11 16:00 | 6 | 16 | 1.0042 | 1114.4517
2017-06-11 17:00 | 6 | 17 | 1.0833 | 1202.2173
2017-06-11 18:00 | 6 | 18 | 1.1222 | 1245.4312
2017-06-11 19:00 | 6 | 19 | 1.3042 | 1447.4134
2017-06-11 20:00 | 6 | 20 | 1.4788 | 1641.181
2017-06-11 21:00 | 6 | 21 | 1.2475 | 1384.5274
2017-06-11 22:00 | 6 | 22 | 0.94458 | 1048.2941
2017-06-11 23:00 | 6 | 23 | 0.65045 | 721.8668
2017-06-12 | 6 | 0 | 0.54279 | 602.3914
2017-06-12 01:00 | 6 | 1 | 0.49999 | 554.8937
2017-06-12 02:00 | 6 | 2 | 0.49748 | 552.0994
2017-06-12 03:00 | 6 | 3 | 0.50265 | 557.8469
2017-06-12 04:00 | 6 | 4 | 0.55341 | 614.179
2017-06-12 05:00 | 6 | 5 | 0.6765 | 750.785
2017-06-12 06:00 | 6 | 6 | 0.84975 | 943.0522
2017-06-12 07:00 | 6 | 7 | 0.79423 | 881.4425
2017-06-12 08:00 | 6 | 8 | 0.75297 | 835.6454
2017-06-12 09:00 | 6 | 9 | 0.78229 | 868.1829
2017-06-12 10:00 | 6 | 10 | 0.77762 | 863.0073
2017-06-12 11:00 | 6 | 11 | 0.75875 | 842.0632
2017-06-12 12:00 | 6 | 12 | 0.73578 | 816.5688
2017-06-12 13:00 | 6 | 13 | 0.72633 | 806.086
2017-06-12 14:00 | 6 | 14 | 0.75713 | 840.263
2017-06-12 15:00 | 6 | 15 | 0.85436 | 948.1677
2017-06-12 16:00 | 6 | 16 | 1.0415 | 1155.8183
2017-06-12 17:00 | 6 | 17 | 1.1112 | 1233.2113
2017-06-12 18:00 | 6 | 18 | 1.1466 | 1272.4605
2017-06-12 19:00 | 6 | 19 | 1.3277 | 1473.4681
2017-06-12 20:00 | 6 | 20 | 1.5029 | 1667.9089
2017-06-12 21:00 | 6 | 21 | 1.2827 | 1423.5546
2017-06-12 22:00 | 6 | 22 | 0.99836 | 1107.983
2017-06-12 23:00 | 6 | 23 | 0.70671 | 784.3064
2017-06-13 | 6 | 0 | 0.59523 | 660.5832
2017-06-13 01:00 | 6 | 1 | 0.54475 | 604.5606
2017-06-13 02:00 | 6 | 2 | 0.53459 | 593.2908
2017-06-13 03:00 | 6 | 3 | 0.53532 | 594.103
2017-06-13 04:00 | 6 | 4 | 0.58115 | 644.9565
2017-06-13 05:00 | 6 | 5 | 0.7012 | 778.1957
2017-06-13 06:00 | 6 | 6 | 0.86929 | 964.7408
2017-06-13 07:00 | 6 | 7 | 0.81055 | 899.5547
2017-06-13 08:00 | 6 | 8 | 0.76391 | 847.7916
2017-06-13 09:00 | 6 | 9 | 0.78897 | 875.6046
2017-06-13 10:00 | 6 | 10 | 0.7788 | 864.3134
2017-06-13 11:00 | 6 | 11 | 0.75262 | 835.2614
2017-06-13 12:00 | 6 | 12 | 0.72296 | 802.3468
2017-06-13 13:00 | 6 | 13 | 0.70067 | 777.5996
2017-06-13 14:00 | 6 | 14 | 0.71809 | 796.9365
2017-06-13 15:00 | 6 | 15 | 0.81123 | 900.299
2017-06-13 16:00 | 6 | 16 | 0.99352 | 1102.6062
2017-06-13 17:00 | 6 | 17 | 1.0595 | 1175.8022
2017-06-13 18:00 | 6 | 18 | 1.097 | 1217.4146
2017-06-13 19:00 | 6 | 19 | 1.2767 | 1416.8392
2017-06-13 20:00 | 6 | 20 | 1.453 | 1612.5434
2017-06-13 21:00 | 6 | 21 | 1.2366 | 1372.337
2017-06-13 22:00 | 6 | 22 | 0.95597 | 1060.9422
2017-06-13 23:00 | 6 | 23 | 0.66857 | 741.9808
2017-06-14 | 6 | 0 | 0.56371 | 625.6052
2017-06-14 01:00 | 6 | 1 | 0.51538 | 571.966
2017-06-14 02:00 | 6 | 2 | 0.51022 | 566.2459
2017-06-14 03:00 | 6 | 3 | 0.51277 | 569.0766
2017-06-14 04:00 | 6 | 4 | 0.56188 | 623.5722
2017-06-14 05:00 | 6 | 5 | 0.69031 | 766.1033
2017-06-14 06:00 | 6 | 6 | 0.85429 | 948.0947
2017-06-14 07:00 | 6 | 7 | 0.78927 | 875.9314
2017-06-14 08:00 | 6 | 8 | 0.74248 | 824.0109
2017-06-14 09:00 | 6 | 9 | 0.75864 | 841.9366
2017-06-14 10:00 | 6 | 10 | 0.77043 | 855.0258
2017-06-14 11:00 | 6 | 11 | 0.73986 | 821.1017
2017-06-14 12:00 | 6 | 12 | 0.71768 | 796.4823
2017-06-14 13:00 | 6 | 13 | 0.70847 | 786.2594
2017-06-14 14:00 | 6 | 14 | 0.73588 | 816.6811
2017-06-14 15:00 | 6 | 15 | 0.83605 | 927.8512
2017-06-14 16:00 | 6 | 16 | 1.0229 | 1135.2526
2017-06-14 17:00 | 6 | 17 | 1.0905 | 1210.257
2017-06-14 18:00 | 6 | 18 | 1.1305 | 1254.6725
2017-06-14 19:00 | 6 | 19 | 1.3152 | 1459.5854
2017-06-14 20:00 | 6 | 20 | 1.4882 | 1651.5668
2017-06-14 21:00 | 6 | 21 | 1.27 | 1409.4955
2017-06-14 22:00 | 6 | 22 | 0.98556 | 1093.7772
2017-06-14 23:00 | 6 | 23 | 0.69358 | 769.7329
2017-06-15 | 6 | 0 | 0.5846 | 648.7883
2017-06-15 01:00 | 6 | 1 | 0.53517 | 593.928
2017-06-15 02:00 | 6 | 2 | 0.52672 | 584.5543
2017-06-15 03:00 | 6 | 3 | 0.52902 | 587.1095
2017-06-15 04:00 | 6 | 4 | 0.57881 | 642.3624
2017-06-15 05:00 | 6 | 5 | 0.69888 | 775.6177
2017-06-15 06:00 | 6 | 6 | 0.87989 | 976.4984
2017-06-15 07:00 | 6 | 7 | 0.82003 | 910.0741
2017-06-15 08:00 | 6 | 8 | 0.77607 | 861.2881
2017-06-15 09:00 | 6 | 9 | 0.80465 | 893.0037
2017-06-15 10:00 | 6 | 10 | 0.79948 | 887.259
2017-06-15 11:00 | 6 | 11 | 0.7782 | 863.6481
2017-06-15 12:00 | 6 | 12 | 0.75263 | 835.269
2017-06-15 13:00 | 6 | 13 | 0.74065 | 821.9769
2017-06-15 14:00 | 6 | 14 | 0.76993 | 854.4654
2017-06-15 15:00 | 6 | 15 | 0.86476 | 959.7158
2017-06-15 16:00 | 6 | 16 | 1.0468 | 1161.7068
2017-06-15 17:00 | 6 | 17 | 1.1131 | 1235.2665
2017-06-15 18:00 | 6 | 18 | 1.1482 | 1274.2594
2017-06-15 19:00 | 6 | 19 | 1.333 | 1479.334
2017-06-15 20:00 | 6 | 20 | 1.5067 | 1672.1566
2017-06-15 21:00 | 6 | 21 | 1.2874 | 1428.8078
2017-06-15 22:00 | 6 | 22 | 1.0012 | 1111.1877
2017-06-15 23:00 | 6 | 23 | 0.70963 | 787.5444
2017-06-16 | 6 | 0 | 0.59954 | 665.3756
2017-06-16 01:00 | 6 | 1 | 0.54894 | 609.2132
2017-06-16 02:00 | 6 | 2 | 0.54006 | 599.354
2017-06-16 03:00 | 6 | 3 | 0.53815 | 597.2397
2017-06-16 04:00 | 6 | 4 | 0.58423 | 648.3739
2017-06-16 05:00 | 6 | 5 | 0.71268 | 790.9383
2017-06-16 06:00 | 6 | 6 | 0.87316 | 969.0389
2017-06-16 07:00 | 6 | 7 | 0.81441 | 903.8336
2017-06-16 08:00 | 6 | 8 | 0.77087 | 855.5143
2017-06-16 09:00 | 6 | 9 | 0.80154 | 889.5455
2017-06-16 10:00 | 6 | 10 | 0.79343 | 880.5447
2017-06-16 11:00 | 6 | 11 | 0.77191 | 856.6722
2017-06-16 12:00 | 6 | 12 | 0.74047 | 821.78
2017-06-16 13:00 | 6 | 13 | 0.72017 | 799.2508
2017-06-16 14:00 | 6 | 14 | 0.74184 | 823.2949
2017-06-16 15:00 | 6 | 15 | 0.83326 | 924.7556
2017-06-16 16:00 | 6 | 16 | 1.017 | 1128.6169
2017-06-16 17:00 | 6 | 17 | 1.0823 | 1201.1448
2017-06-16 18:00 | 6 | 18 | 1.1198 | 1242.7965
2017-06-16 19:00 | 6 | 19 | 1.3019 | 1444.8726
2017-06-16 20:00 | 6 | 20 | 1.4763 | 1638.3709
2017-06-16 21:00 | 6 | 21 | 1.2586 | 1396.7975
2017-06-16 22:00 | 6 | 22 | 0.97485 | 1081.89
2017-06-16 23:00 | 6 | 23 | 0.68491 | 760.1088
2017-06-17 | 6 | 0 | 0.57905 | 642.6319
2017-06-17 01:00 | 6 | 1 | 0.52699 | 584.8543
2017-06-17 02:00 | 6 | 2 | 0.51684 | 573.5865
2017-06-17 03:00 | 6 | 3 | 0.51796 | 574.833
2017-06-17 04:00 | 6 | 4 | 0.56589 | 628.0205
2017-06-17 05:00 | 6 | 5 | 0.69756 | 774.1574
2017-06-17 06:00 | 6 | 6 | 0.87008 | 965.6159
2017-06-17 07:00 | 6 | 7 | 0.81092 | 899.9576
2017-06-17 08:00 | 6 | 8 | 0.76383 | 847.6983
2017-06-17 09:00 | 6 | 9 | 0.77147 | 856.1747
2017-06-17 10:00 | 6 | 10 | 0.77098 | 855.6335
2017-06-17 11:00 | 6 | 11 | 0.74813 | 830.2774
2017-06-17 12:00 | 6 | 12 | 0.72236 | 801.6786
2017-06-17 13:00 | 6 | 13 | 0.709 | 786.8548
2017-06-17 14:00 | 6 | 14 | 0.73433 | 814.9638
2017-06-17 15:00 | 6 | 15 | 0.83234 | 923.7376
2017-06-17 16:00 | 6 | 16 | 1.0042 | 1114.4517
2017-06-17 17:00 | 6 | 17 | 1.0833 | 1202.2173
2017-06-17 18:00 | 6 | 18 | 1.1222 | 1245.4312
2017-06-17 19:00 | 6 | 19 | 1.3042 | 1447.4134
2017-06-17 20:00 | 6 | 20 | 1.4788 | 1641.181
2017-06-17 21:00 | 6 | 21 | 1.2475 | 1384.5274
2017-06-17 22:00 | 6 | 22 | 0.94245 | 1045.9362
2017-06-17 23:00 | 6 | 23 | 0.63306 | 702.566
2017-06-18 | 6 | 0 | 0.51441 | 570.8934
2017-06-18 01:00 | 6 | 1 | 0.46528 | 516.3642
2017-06-18 02:00 | 6 | 2 | 0.46332 | 514.1968
2017-06-18 03:00 | 6 | 3 | 0.47539 | 527.5854
2017-06-18 04:00 | 6 | 4 | 0.52991 | 588.0963
2017-06-18 05:00 | 6 | 5 | 0.66173 | 734.3899
2017-06-18 06:00 | 6 | 6 | 0.84026 | 932.5226
2017-06-18 07:00 | 6 | 7 | 0.78654 | 872.9009
2017-06-18 08:00 | 6 | 8 | 0.74649 | 828.4503
2017-06-18 09:00 | 6 | 9 | 0.75878 | 842.0983
2017-06-18 10:00 | 6 | 10 | 0.76809 | 852.4307
2017-06-18 11:00 | 6 | 11 | 0.74813 | 830.2774
2017-06-18 12:00 | 6 | 12 | 0.72236 | 801.6786
2017-06-18 13:00 | 6 | 13 | 0.709 | 786.8548
2017-06-18 14:00 | 6 | 14 | 0.73433 | 814.9638
2017-06-18 15:00 | 6 | 15 | 0.83234 | 923.7376
2017-06-18 16:00 | 6 | 16 | 1.0042 | 1114.4517
2017-06-18 17:00 | 6 | 17 | 1.0833 | 1202.2173
2017-06-18 18:00 | 6 | 18 | 1.1222 | 1245.4312
2017-06-18 19:00 | 6 | 19 | 1.3042 | 1447.4134
2017-06-18 20:00 | 6 | 20 | 1.4788 | 1641.181
2017-06-18 21:00 | 6 | 21 | 1.2475 | 1384.5274
2017-06-18 22:00 | 6 | 22 | 0.94245 | 1045.9362
2017-06-18 23:00 | 6 | 23 | 0.63306 | 702.566
2017-06-19 | 6 | 0 | 0.51046 | 566.513
2017-06-19 01:00 | 6 | 1 | 0.45507 | 505.0422
2017-06-19 02:00 | 6 | 2 | 0.45147 | 501.0453
2017-06-19 03:00 | 6 | 3 | 0.45991 | 510.4109
2017-06-19 04:00 | 6 | 4 | 0.51337 | 569.7438
2017-06-19 05:00 | 6 | 5 | 0.64327 | 713.9004
2017-06-19 06:00 | 6 | 6 | 0.81224 | 901.4246
2017-06-19 07:00 | 6 | 7 | 0.75107 | 833.535
2017-06-19 08:00 | 6 | 8 | 0.70857 | 786.3766
2017-06-19 09:00 | 6 | 9 | 0.73041 | 810.6067
2017-06-19 10:00 | 6 | 10 | 0.73446 | 815.1024
2017-06-19 11:00 | 6 | 11 | 0.71396 | 792.3518
2017-06-19 12:00 | 6 | 12 | 0.6846 | 759.7668
2017-06-19 13:00 | 6 | 13 | 0.66988 | 743.4332
2017-06-19 14:00 | 6 | 14 | 0.69727 | 773.8357
2017-06-19 15:00 | 6 | 15 | 0.79643 | 883.8759
2017-06-19 16:00 | 6 | 16 | 0.96884 | 1075.218
2017-06-19 17:00 | 6 | 17 | 1.049 | 1164.1397
2017-06-19 18:00 | 6 | 18 | 1.088 | 1207.4263
2017-06-19 19:00 | 6 | 19 | 1.2694 | 1408.7309
2017-06-19 20:00 | 6 | 20 | 1.4432 | 1601.6645
2017-06-19 21:00 | 6 | 21 | 1.2193 | 1353.1276
2017-06-19 22:00 | 6 | 22 | 0.92905 | 1031.0658
2017-06-19 23:00 | 6 | 23 | 0.64273 | 713.3043
2017-06-20 | 6 | 0 | 0.54083 | 600.214
2017-06-20 01:00 | 6 | 1 | 0.49599 | 550.4549
2017-06-20 02:00 | 6 | 2 | 0.49368 | 547.892
2017-06-20 03:00 | 6 | 3 | 0.49955 | 554.4051
2017-06-20 04:00 | 6 | 4 | 0.54716 | 607.2431
2017-06-20 05:00 | 6 | 5 | 0.67227 | 746.0887
2017-06-20 06:00 | 6 | 6 | 0.83322 | 924.7067
2017-06-20 07:00 | 6 | 7 | 0.76642 | 850.5793
2017-06-20 08:00 | 6 | 8 | 0.71257 | 790.8137
2017-06-20 09:00 | 6 | 9 | 0.72278 | 802.1423
2017-06-20 10:00 | 6 | 10 | 0.71938 | 798.3697
2017-06-20 11:00 | 6 | 11 | 0.70032 | 777.2173
2017-06-20 12:00 | 6 | 12 | 0.67877 | 753.3045
2017-06-20 13:00 | 6 | 13 | 0.66988 | 743.4332
2017-06-20 14:00 | 6 | 14 | 0.69727 | 773.8357
2017-06-20 15:00 | 6 | 15 | 0.79643 | 883.8759
2017-06-20 16:00 | 6 | 16 | 0.96884 | 1075.218
2017-06-20 17:00 | 6 | 17 | 1.049 | 1164.1397
2017-06-20 18:00 | 6 | 18 | 1.088 | 1207.4263
2017-06-20 19:00 | 6 | 19 | 1.2694 | 1408.7309
2017-06-20 20:00 | 6 | 20 | 1.4432 | 1601.6645
2017-06-20 21:00 | 6 | 21 | 1.2193 | 1353.1276
2017-06-20 22:00 | 6 | 22 | 0.92692 | 1028.6956
2017-06-20 23:00 | 6 | 23 | 0.62648 | 695.2705
2017-06-21 | 6 | 0 | 0.51046 | 566.513
2017-06-21 01:00 | 6 | 1 | 0.46038 | 510.9249
2017-06-21 02:00 | 6 | 2 | 0.46171 | 512.4047
2017-06-21 03:00 | 6 | 3 | 0.47049 | 522.1498
2017-06-21 04:00 | 6 | 4 | 0.52396 | 581.4871
2017-06-21 05:00 | 6 | 5 | 0.64985 | 721.1996
2017-06-21 06:00 | 6 | 6 | 0.81465 | 904.1019
2017-06-21 07:00 | 6 | 7 | 0.74614 | 828.0709
2017-06-21 08:00 | 6 | 8 | 0.69099 | 766.867
2017-06-21 09:00 | 6 | 9 | 0.7053 | 782.7454
2017-06-21 10:00 | 6 | 10 | 0.7156 | 794.1786
2017-06-21 11:00 | 6 | 11 | 0.70032 | 777.2173
2017-06-21 12:00 | 6 | 12 | 0.67877 | 753.3045
2017-06-21 13:00 | 6 | 13 | 0.66988 | 743.4332
2017-06-21 14:00 | 6 | 14 | 0.69727 | 773.8357
2017-06-21 15:00 | 6 | 15 | 0.79643 | 883.8759
2017-06-21 16:00 | 6 | 16 | 1.0613 | 1177.7798
2017-06-21 17:00 | 6 | 17 | 1.1607 | 1288.1232
2017-06-21 18:00 | 6 | 18 | 1.1793 | 1308.7576
2017-06-21 19:00 | 6 | 19 | 1.2694 | 1408.7309
2017-06-21 20:00 | 6 | 20 | 1.4432 | 1601.6645
2017-06-21 21:00 | 6 | 21 | 1.2193 | 1353.1276
2017-06-21 22:00 | 6 | 22 | 0.92692 | 1028.6956
2017-06-21 23:00 | 6 | 23 | 0.62648 | 695.2705
2017-06-22 | 6 | 0 | 0.51046 | 566.513
2017-06-22 01:00 | 6 | 1 | 0.45507 | 505.0422
2017-06-22 02:00 | 6 | 2 | 0.4435 | 492.2011
2017-06-22 03:00 | 6 | 3 | 0.44205 | 490.5838
2017-06-22 04:00 | 6 | 4 | 0.48978 | 543.5541
2017-06-22 05:00 | 6 | 5 | 0.61584 | 683.4632
2017-06-22 06:00 | 6 | 6 | 0.79063 | 877.4393
2017-06-22 07:00 | 6 | 7 | 0.73376 | 814.3266
2017-06-22 08:00 | 6 | 8 | 0.69099 | 766.867
2017-06-22 09:00 | 6 | 9 | 0.7053 | 782.7454
2017-06-22 10:00 | 6 | 10 | 0.7156 | 794.1786
2017-06-22 11:00 | 6 | 11 | 0.70032 | 777.2173
2017-06-22 12:00 | 6 | 12 | 0.67877 | 753.3045
2017-06-22 13:00 | 6 | 13 | 0.66988 | 743.4332
2017-06-22 14:00 | 6 | 14 | 0.69727 | 773.8357
2017-06-22 15:00 | 6 | 15 | 0.79643 | 883.8759
2017-06-22 16:00 | 6 | 16 | 0.96884 | 1075.218
2017-06-22 17:00 | 6 | 17 | 1.049 | 1164.1397
2017-06-22 18:00 | 6 | 18 | 1.088 | 1207.4263
2017-06-22 19:00 | 6 | 19 | 1.2694 | 1408.7309
2017-06-22 20:00 | 6 | 20 | 1.4432 | 1601.6645
2017-06-22 21:00 | 6 | 21 | 1.2193 | 1353.1276
2017-06-22 22:00 | 6 | 22 | 0.92692 | 1028.6956
2017-06-22 23:00 | 6 | 23 | 0.62648 | 695.2705
2017-06-23 | 6 | 0 | 0.51046 | 566.513
2017-06-23 01:00 | 6 | 1 | 0.45507 | 505.0422
2017-06-23 02:00 | 6 | 2 | 0.44928 | 498.6164
2017-06-23 03:00 | 6 | 3 | 0.45705 | 507.2348
2017-06-23 04:00 | 6 | 4 | 0.5103 | 566.328
2017-06-23 05:00 | 6 | 5 | 0.6364 | 706.2804
2017-06-23 06:00 | 6 | 6 | 0.81203 | 901.191
2017-06-23 07:00 | 6 | 7 | 0.75697 | 840.0908
2017-06-23 08:00 | 6 | 8 | 0.7119 | 790.0632
2017-06-23 09:00 | 6 | 9 | 0.72301 | 802.3922
2017-06-23 10:00 | 6 | 10 | 0.72033 | 799.4288
2017-06-23 11:00 | 6 | 11 | 0.70032 | 777.2173
2017-06-23 12:00 | 6 | 12 | 0.67877 | 753.3045
2017-06-23 13:00 | 6 | 13 | 0.66988 | 743.4332
2017-06-23 14:00 | 6 | 14 | 0.69727 | 773.8357
2017-06-23 15:00 | 6 | 15 | 0.79643 | 883.8759
2017-06-23 16:00 | 6 | 16 | 0.96884 | 1075.218
2017-06-23 17:00 | 6 | 17 | 1.049 | 1164.1397
2017-06-23 18:00 | 6 | 18 | 1.088 | 1207.4263
2017-06-23 19:00 | 6 | 19 | 1.2694 | 1408.7309
2017-06-23 20:00 | 6 | 20 | 1.4432 | 1601.6645
2017-06-23 21:00 | 6 | 21 | 1.2193 | 1353.1276
2017-06-23 22:00 | 6 | 22 | 0.92692 | 1028.6956
2017-06-23 23:00 | 6 | 23 | 0.62648 | 695.2705
2017-06-24 | 6 | 0 | 0.51441 | 570.8934
2017-06-24 01:00 | 6 | 1 | 0.45769 | 507.9402
2017-06-24 02:00 | 6 | 2 | 0.44487 | 493.7164
2017-06-24 03:00 | 6 | 3 | 0.44472 | 493.5482
2017-06-24 04:00 | 6 | 4 | 0.49387 | 548.1006
2017-06-24 05:00 | 6 | 5 | 0.62647 | 695.2554
2017-06-24 06:00 | 6 | 6 | 0.81179 | 900.9242
2017-06-24 07:00 | 6 | 7 | 0.7662 | 850.3256
2017-06-24 08:00 | 6 | 8 | 0.73603 | 816.8425
2017-06-24 09:00 | 6 | 9 | 0.75622 | 839.2523
2017-06-24 10:00 | 6 | 10 | 0.76809 | 852.4307
2017-06-24 11:00 | 6 | 11 | 0.74813 | 830.2774
2017-06-24 12:00 | 6 | 12 | 0.72236 | 801.6786
2017-06-24 13:00 | 6 | 13 | 0.75243 | 835.0518
2017-06-24 14:00 | 6 | 14 | 0.94718 | 1051.1838
2017-06-24 15:00 | 6 | 15 | 1.1478 | 1273.8353
2017-06-24 16:00 | 6 | 16 | 1.4751 | 1637.0698
2017-06-24 17:00 | 6 | 17 | 1.5024 | 1667.3182
2017-06-24 18:00 | 6 | 18 | 1.4934 | 1657.4048
2017-06-24 19:00 | 6 | 19 | 1.5895 | 1764.0299
2017-06-24 20:00 | 6 | 20 | 1.6977 | 1884.0924
2017-06-24 21:00 | 6 | 21 | 1.3586 | 1507.7917
2017-06-24 22:00 | 6 | 22 | 0.94245 | 1045.9362
2017-06-24 23:00 | 6 | 23 | 0.63306 | 702.566
2017-06-25 | 6 | 0 | 0.51441 | 570.8934
2017-06-25 01:00 | 6 | 1 | 0.45769 | 507.9402
2017-06-25 02:00 | 6 | 2 | 0.44487 | 493.7164
2017-06-25 03:00 | 6 | 3 | 0.44472 | 493.5482
2017-06-25 04:00 | 6 | 4 | 0.49387 | 548.1006
2017-06-25 05:00 | 6 | 5 | 0.62647 | 695.2554
2017-06-25 06:00 | 6 | 6 | 0.81179 | 900.9242
2017-06-25 07:00 | 6 | 7 | 0.7662 | 850.3256
2017-06-25 08:00 | 6 | 8 | 0.73603 | 816.8425
2017-06-25 09:00 | 6 | 9 | 0.75622 | 839.2523
2017-06-25 10:00 | 6 | 10 | 0.76809 | 852.4307
2017-06-25 11:00 | 6 | 11 | 0.74813 | 830.2774
2017-06-25 12:00 | 6 | 12 | 0.72236 | 801.6786
2017-06-25 13:00 | 6 | 13 | 0.709 | 786.8548
2017-06-25 14:00 | 6 | 14 | 0.73433 | 814.9638
2017-06-25 15:00 | 6 | 15 | 0.90029 | 999.141
2017-06-25 16:00 | 6 | 16 | 1.2069 | 1339.4564
2017-06-25 17:00 | 6 | 17 | 1.2999 | 1442.576
2017-06-25 18:00 | 6 | 18 | 1.3096 | 1453.3453
2017-06-25 19:00 | 6 | 19 | 1.4339 | 1591.3616
2017-06-25 20:00 | 6 | 20 | 1.5707 | 1743.1628
2017-06-25 21:00 | 6 | 21 | 1.2513 | 1388.653
2017-06-25 22:00 | 6 | 22 | 0.94245 | 1045.9362
2017-06-25 23:00 | 6 | 23 | 0.63306 | 702.566
2017-06-26 | 6 | 0 | 0.51046 | 566.513
2017-06-26 01:00 | 6 | 1 | 0.45507 | 505.0422
2017-06-26 02:00 | 6 | 2 | 0.4435 | 492.2011
2017-06-26 03:00 | 6 | 3 | 0.44205 | 490.5838
2017-06-26 04:00 | 6 | 4 | 0.48978 | 543.5541
2017-06-26 05:00 | 6 | 5 | 0.61584 | 683.4632
2017-06-26 06:00 | 6 | 6 | 0.79063 | 877.4393
2017-06-26 07:00 | 6 | 7 | 0.73376 | 814.3266
2017-06-26 08:00 | 6 | 8 | 0.69099 | 766.867
2017-06-26 09:00 | 6 | 9 | 0.7053 | 782.7454
2017-06-26 10:00 | 6 | 10 | 0.7156 | 794.1786
2017-06-26 11:00 | 6 | 11 | 0.70032 | 777.2173
2017-06-26 12:00 | 6 | 12 | 0.83484 | 926.5071
2017-06-26 13:00 | 6 | 13 | 1.0672 | 1184.399
2017-06-26 14:00 | 6 | 14 | 1.1868 | 1317.1221
2017-06-26 15:00 | 6 | 15 | 1.4165 | 1572.0805
2017-06-26 16:00 | 6 | 16 | 1.7212 | 1910.2275
2017-06-26 17:00 | 6 | 17 | 1.7566 | 1949.5045
2017-06-26 18:00 | 6 | 18 | 1.6841 | 1869.0111
2017-06-26 19:00 | 6 | 19 | 1.7809 | 1976.4749
2017-06-26 20:00 | 6 | 20 | 1.8964 | 2104.6063
2017-06-26 21:00 | 6 | 21 | 1.5435 | 1712.925
2017-06-26 22:00 | 6 | 22 | 1.0985 | 1219.1412
2017-06-26 23:00 | 6 | 23 | 0.69991 | 776.758
2017-06-27 | 6 | 0 | 0.51046 | 566.513
2017-06-27 01:00 | 6 | 1 | 0.45507 | 505.0422
2017-06-27 02:00 | 6 | 2 | 0.4435 | 492.2011
2017-06-27 03:00 | 6 | 3 | 0.44205 | 490.5838
2017-06-27 04:00 | 6 | 4 | 0.48978 | 543.5541
2017-06-27 05:00 | 6 | 5 | 0.61584 | 683.4632
2017-06-27 06:00 | 6 | 6 | 0.79063 | 877.4393
2017-06-27 07:00 | 6 | 7 | 0.73376 | 814.3266
2017-06-27 08:00 | 6 | 8 | 0.69099 | 766.867
2017-06-27 09:00 | 6 | 9 | 0.84264 | 935.1585
2017-06-27 10:00 | 6 | 10 | 0.95455 | 1059.3599
2017-06-27 11:00 | 6 | 11 | 1.0185 | 1130.3201
2017-06-27 12:00 | 6 | 12 | 1.1279 | 1251.6912
2017-06-27 13:00 | 6 | 13 | 1.2809 | 1421.5882
2017-06-27 14:00 | 6 | 14 | 1.4095 | 1564.3027
2017-06-27 15:00 | 6 | 15 | 1.5654 | 1737.3256
2017-06-27 16:00 | 6 | 16 | 1.8727 | 2078.2785
2017-06-27 17:00 | 6 | 17 | 1.5723 | 1744.922
2017-06-27 18:00 | 6 | 18 | 1.5194 | 1686.1812
2017-06-27 19:00 | 6 | 19 | 1.5781 | 1751.4068
2017-06-27 20:00 | 6 | 20 | 1.6813 | 1865.9205
2017-06-27 21:00 | 6 | 21 | 1.354 | 1502.6833
2017-06-27 22:00 | 6 | 22 | 0.95782 | 1062.9847
2017-06-27 23:00 | 6 | 23 | 0.62648 | 695.2705
2017-06-28 | 6 | 0 | 0.51046 | 566.513
2017-06-28 01:00 | 6 | 1 | 0.45507 | 505.0422
2017-06-28 02:00 | 6 | 2 | 0.4435 | 492.2011
2017-06-28 03:00 | 6 | 3 | 0.44205 | 490.5838
2017-06-28 04:00 | 6 | 4 | 0.48978 | 543.5541
2017-06-28 05:00 | 6 | 5 | 0.61584 | 683.4632
2017-06-28 06:00 | 6 | 6 | 0.79063 | 877.4393
2017-06-28 07:00 | 6 | 7 | 0.73376 | 814.3266
2017-06-28 08:00 | 6 | 8 | 0.69099 | 766.867
2017-06-28 09:00 | 6 | 9 | 0.7053 | 782.7454
2017-06-28 10:00 | 6 | 10 | 0.7156 | 794.1786
2017-06-28 11:00 | 6 | 11 | 0.70032 | 777.2173
2017-06-28 12:00 | 6 | 12 | 0.6844 | 759.5451
2017-06-28 13:00 | 6 | 13 | 0.82893 | 919.9514
2017-06-28 14:00 | 6 | 14 | 0.87716 | 973.471
2017-06-28 15:00 | 6 | 15 | 1.0427 | 1157.1914
2017-06-28 16:00 | 6 | 16 | 1.2289 | 1363.8481
2017-06-28 17:00 | 6 | 17 | 1.3307 | 1476.845
2017-06-28 18:00 | 6 | 18 | 1.2721 | 1411.7338
2017-06-28 19:00 | 6 | 19 | 1.4006 | 1554.3735
2017-06-28 20:00 | 6 | 20 | 1.5592 | 1730.3931
2017-06-28 21:00 | 6 | 21 | 1.2516 | 1389.0228
2017-06-28 22:00 | 6 | 22 | 0.92692 | 1028.6956
2017-06-28 23:00 | 6 | 23 | 0.62648 | 695.2705
2017-06-29 | 6 | 0 | 0.51046 | 566.513
2017-06-29 01:00 | 6 | 1 | 0.45507 | 505.0422
2017-06-29 02:00 | 6 | 2 | 0.4435 | 492.2011
2017-06-29 03:00 | 6 | 3 | 0.44205 | 490.5838
2017-06-29 04:00 | 6 | 4 | 0.48978 | 543.5541
2017-06-29 05:00 | 6 | 5 | 0.61584 | 683.4632
2017-06-29 06:00 | 6 | 6 | 0.79063 | 877.4393
2017-06-29 07:00 | 6 | 7 | 0.73376 | 814.3266
2017-06-29 08:00 | 6 | 8 | 0.69099 | 766.867
2017-06-29 09:00 | 6 | 9 | 0.7053 | 782.7454
2017-06-29 10:00 | 6 | 10 | 0.7156 | 794.1786
2017-06-29 11:00 | 6 | 11 | 0.70032 | 777.2173
2017-06-29 12:00 | 6 | 12 | 0.67877 | 753.3045
2017-06-29 13:00 | 6 | 13 | 0.66988 | 743.4332
2017-06-29 14:00 | 6 | 14 | 0.69727 | 773.8357
2017-06-29 15:00 | 6 | 15 | 0.80124 | 889.2154
2017-06-29 16:00 | 6 | 16 | 0.96884 | 1075.218
2017-06-29 17:00 | 6 | 17 | 1.1126 | 1234.7109
2017-06-29 18:00 | 6 | 18 | 1.1337 | 1258.2269
2017-06-29 19:00 | 6 | 19 | 1.2694 | 1408.7309
2017-06-29 20:00 | 6 | 20 | 1.4432 | 1601.6645
2017-06-29 21:00 | 6 | 21 | 1.2193 | 1353.1276
2017-06-29 22:00 | 6 | 22 | 0.92692 | 1028.6956
2017-06-29 23:00 | 6 | 23 | 0.62648 | 695.2705
2017-06-30 | 6 | 0 | 0.51046 | 566.513
2017-06-30 01:00 | 6 | 1 | 0.45507 | 505.0422
2017-06-30 02:00 | 6 | 2 | 0.4435 | 492.2011
2017-06-30 03:00 | 6 | 3 | 0.44205 | 490.5838
2017-06-30 04:00 | 6 | 4 | 0.48978 | 543.5541
2017-06-30 05:00 | 6 | 5 | 0.61584 | 683.4632
2017-06-30 06:00 | 6 | 6 | 0.79063 | 877.4393
2017-06-30 07:00 | 6 | 7 | 0.73376 | 814.3266
2017-06-30 08:00 | 6 | 8 | 0.69099 | 766.867
2017-06-30 09:00 | 6 | 9 | 0.7053 | 782.7454
2017-06-30 10:00 | 6 | 10 | 0.7156 | 794.1786
2017-06-30 11:00 | 6 | 11 | 0.70032 | 777.2173
2017-06-30 12:00 | 6 | 12 | 0.67877 | 753.3045
2017-06-30 13:00 | 6 | 13 | 0.66988 | 743.4332
2017-06-30 14:00 | 6 | 14 | 0.69727 | 773.8357
2017-06-30 15:00 | 6 | 15 | 0.82899 | 920.017
2017-06-30 16:00 | 6 | 16 | 1.2168 | 1350.3611
2017-06-30 17:00 | 6 | 17 | 1.2914 | 1433.2304
2017-06-30 18:00 | 6 | 18 | 1.3019 | 1444.9061
2017-06-30 19:00 | 6 | 19 | 1.4373 | 1595.1697
2017-06-30 20:00 | 6 | 20 | 1.5619 | 1733.4065
2017-06-30 21:00 | 6 | 21 | 1.2283 | 1363.1592
2017-06-30 22:00 | 6 | 22 | 0.92692 | 1028.6956
2017-06-30 23:00 | 6 | 23 | 0.62648 | 695.2705
2017-07-01 | 7 | 0 | 0.51555 | 572.1553
2017-07-01 01:00 | 7 | 1 | 0.45798 | 508.2675
2017-07-01 02:00 | 7 | 2 | 0.44518 | 494.0641
2017-07-01 03:00 | 7 | 3 | 0.44511 | 493.9859
2017-07-01 04:00 | 7 | 4 | 0.49424 | 548.5066
2017-07-01 05:00 | 7 | 5 | 0.63143 | 700.7588
2017-07-01 06:00 | 7 | 6 | 0.82633 | 917.0629
2017-07-01 07:00 | 7 | 7 | 0.78351 | 869.5445
2017-07-01 08:00 | 7 | 8 | 0.74643 | 828.3843
2017-07-01 09:00 | 7 | 9 | 0.76516 | 849.1746
2017-07-01 10:00 | 7 | 10 | 0.77296 | 857.8334
2017-07-01 11:00 | 7 | 11 | 0.75276 | 835.4142
2017-07-01 12:00 | 7 | 12 | 0.72685 | 806.6603
2017-07-01 13:00 | 7 | 13 | 0.7134 | 791.7355
2017-07-01 14:00 | 7 | 14 | 0.73475 | 815.4321
2017-07-01 15:00 | 7 | 15 | 0.83693 | 928.8291
2017-07-01 16:00 | 7 | 16 | 1.0052 | 1115.5493
2017-07-01 17:00 | 7 | 17 | 1.0848 | 1203.8816
2017-07-01 18:00 | 7 | 18 | 1.1215 | 1244.6359
2017-07-01 19:00 | 7 | 19 | 1.3072 | 1450.7645
2017-07-01 20:00 | 7 | 20 | 1.4818 | 1644.5115
2017-07-01 21:00 | 7 | 21 | 1.2486 | 1385.7285
2017-07-01 22:00 | 7 | 22 | 0.94037 | 1043.6238
2017-07-01 23:00 | 7 | 23 | 0.63886 | 709.0123
2017-07-02 | 7 | 0 | 0.52942 | 587.5487
2017-07-02 01:00 | 7 | 1 | 0.47664 | 528.9771
2017-07-02 02:00 | 7 | 2 | 0.46982 | 521.41
2017-07-02 03:00 | 7 | 3 | 0.4737 | 525.7078
2017-07-02 04:00 | 7 | 4 | 0.52252 | 579.8905
2017-07-02 05:00 | 7 | 5 | 0.65599 | 728.0147
2017-07-02 06:00 | 7 | 6 | 0.84794 | 941.0499
2017-07-02 07:00 | 7 | 7 | 0.80239 | 890.4976
2017-07-02 08:00 | 7 | 8 | 0.7609 | 844.443
2017-07-02 09:00 | 7 | 9 | 0.77699 | 862.3001
2017-07-02 10:00 | 7 | 10 | 0.7815 | 867.3143
2017-07-02 11:00 | 7 | 11 | 0.75353 | 836.2708
2017-07-02 12:00 | 7 | 12 | 0.72685 | 806.6603
2017-07-02 13:00 | 7 | 13 | 0.7134 | 791.7355
2017-07-02 14:00 | 7 | 14 | 0.73475 | 815.4321
2017-07-02 15:00 | 7 | 15 | 0.83693 | 928.8291
2017-07-02 16:00 | 7 | 16 | 1.0052 | 1115.5493
2017-07-02 17:00 | 7 | 17 | 1.0848 | 1203.8816
2017-07-02 18:00 | 7 | 18 | 1.1215 | 1244.6359
2017-07-02 19:00 | 7 | 19 | 1.3072 | 1450.7645
2017-07-02 20:00 | 7 | 20 | 1.4818 | 1644.5115
2017-07-02 21:00 | 7 | 21 | 1.2486 | 1385.7285
2017-07-02 22:00 | 7 | 22 | 0.94037 | 1043.6238
2017-07-02 23:00 | 7 | 23 | 0.64451 | 715.2743
2017-07-03 | 7 | 0 | 0.52991 | 588.0897
2017-07-03 01:00 | 7 | 1 | 0.48046 | 533.2152
2017-07-03 02:00 | 7 | 2 | 0.47422 | 526.2947
2017-07-03 03:00 | 7 | 3 | 0.47508 | 527.2445
2017-07-03 04:00 | 7 | 4 | 0.52257 | 579.9514
2017-07-03 05:00 | 7 | 5 | 0.65325 | 724.9789
2017-07-03 06:00 | 7 | 6 | 0.82877 | 919.7694
2017-07-03 07:00 | 7 | 7 | 0.77046 | 855.0617
2017-07-03 08:00 | 7 | 8 | 0.71411 | 792.5254
2017-07-03 09:00 | 7 | 9 | 0.71852 | 797.4112
2017-07-03 10:00 | 7 | 10 | 0.72113 | 800.3072
2017-07-03 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-03 12:00 | 7 | 12 | 0.68326 | 758.2862
2017-07-03 13:00 | 7 | 13 | 0.67428 | 748.3139
2017-07-03 14:00 | 7 | 14 | 0.6977 | 774.304
2017-07-03 15:00 | 7 | 15 | 0.80101 | 888.9674
2017-07-03 16:00 | 7 | 16 | 0.96983 | 1076.3157
2017-07-03 17:00 | 7 | 17 | 1.0505 | 1165.804
2017-07-03 18:00 | 7 | 18 | 1.0872 | 1206.631
2017-07-03 19:00 | 7 | 19 | 1.2724 | 1412.0819
2017-07-03 20:00 | 7 | 20 | 1.4462 | 1604.9949
2017-07-03 21:00 | 7 | 21 | 1.2203 | 1354.3286
2017-07-03 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-03 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-04 | 7 | 0 | 0.5116 | 567.7749
2017-07-04 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-04 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-04 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-04 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-04 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-04 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-04 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-04 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-04 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-04 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-04 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-04 12:00 | 7 | 12 | 0.68326 | 758.2862
2017-07-04 13:00 | 7 | 13 | 0.67428 | 748.3139
2017-07-04 14:00 | 7 | 14 | 0.6977 | 774.304
2017-07-04 15:00 | 7 | 15 | 0.80101 | 888.9674
2017-07-04 16:00 | 7 | 16 | 0.96983 | 1076.3157
2017-07-04 17:00 | 7 | 17 | 1.0505 | 1165.804
2017-07-04 18:00 | 7 | 18 | 1.0872 | 1206.631
2017-07-04 19:00 | 7 | 19 | 1.2724 | 1412.0819
2017-07-04 20:00 | 7 | 20 | 1.4462 | 1604.9949
2017-07-04 21:00 | 7 | 21 | 1.2203 | 1354.3286
2017-07-04 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-04 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-05 | 7 | 0 | 0.5116 | 567.7749
2017-07-05 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-05 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-05 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-05 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-05 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-05 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-05 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-05 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-05 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-05 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-05 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-05 12:00 | 7 | 12 | 0.68326 | 758.2862
2017-07-05 13:00 | 7 | 13 | 0.67428 | 748.3139
2017-07-05 14:00 | 7 | 14 | 0.6977 | 774.304
2017-07-05 15:00 | 7 | 15 | 0.80101 | 888.9674
2017-07-05 16:00 | 7 | 16 | 0.96983 | 1076.3157
2017-07-05 17:00 | 7 | 17 | 1.0505 | 1165.804
2017-07-05 18:00 | 7 | 18 | 1.0872 | 1206.631
2017-07-05 19:00 | 7 | 19 | 1.2724 | 1412.0819
2017-07-05 20:00 | 7 | 20 | 1.4462 | 1604.9949
2017-07-05 21:00 | 7 | 21 | 1.2203 | 1354.3286
2017-07-05 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-05 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-06 | 7 | 0 | 0.5116 | 567.7749
2017-07-06 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-06 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-06 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-06 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-06 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-06 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-06 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-06 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-06 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-06 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-06 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-06 12:00 | 7 | 12 | 0.73139 | 811.6943
2017-07-06 13:00 | 7 | 13 | 0.90313 | 1002.2936
2017-07-06 14:00 | 7 | 14 | 1.2031 | 1335.2567
2017-07-06 15:00 | 7 | 15 | 1.3631 | 1512.7565
2017-07-06 16:00 | 7 | 16 | 1.7015 | 1888.292
2017-07-06 17:00 | 7 | 17 | 1.7451 | 1936.6721
2017-07-06 18:00 | 7 | 18 | 1.8081 | 2006.6401
2017-07-06 19:00 | 7 | 19 | 1.9348 | 2147.2208
2017-07-06 20:00 | 7 | 20 | 2.0261 | 2248.5233
2017-07-06 21:00 | 7 | 21 | 1.6757 | 1859.7278
2017-07-06 22:00 | 7 | 22 | 1.2401 | 1376.2629
2017-07-06 23:00 | 7 | 23 | 0.79017 | 876.9368
2017-07-07 | 7 | 0 | 0.58563 | 649.937
2017-07-07 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-07 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-07 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-07 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-07 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-07 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-07 07:00 | 7 | 7 | 0.754 | 836.7924
2017-07-07 08:00 | 7 | 8 | 0.83914 | 931.278
2017-07-07 09:00 | 7 | 9 | 1.1963 | 1327.6084
2017-07-07 10:00 | 7 | 10 | 1.2299 | 1364.9614
2017-07-07 11:00 | 7 | 11 | 1.4105 | 1565.3876
2017-07-07 12:00 | 7 | 12 | 1.5308 | 1698.8766
2017-07-07 13:00 | 7 | 13 | 1.7303 | 1920.2678
2017-07-07 14:00 | 7 | 14 | 1.8395 | 2041.5011
2017-07-07 15:00 | 7 | 15 | 1.987 | 2205.1866
2017-07-07 16:00 | 7 | 16 | 2.3487 | 2606.6424
2017-07-07 17:00 | 7 | 17 | 2.1813 | 2420.7584
2017-07-07 18:00 | 7 | 18 | 2.0995 | 2329.9877
2017-07-07 19:00 | 7 | 19 | 2.1134 | 2345.5101
2017-07-07 20:00 | 7 | 20 | 2.2108 | 2453.552
2017-07-07 21:00 | 7 | 21 | 1.811 | 2009.8975
2017-07-07 22:00 | 7 | 22 | 1.3493 | 1497.4498
2017-07-07 23:00 | 7 | 23 | 0.86819 | 963.5204
2017-07-08 | 7 | 0 | 0.65583 | 727.8464
2017-07-08 01:00 | 7 | 1 | 0.50592 | 561.4758
2017-07-08 02:00 | 7 | 2 | 0.44518 | 494.0641
2017-07-08 03:00 | 7 | 3 | 0.44511 | 493.9859
2017-07-08 04:00 | 7 | 4 | 0.49424 | 548.5066
2017-07-08 05:00 | 7 | 5 | 0.63143 | 700.7588
2017-07-08 06:00 | 7 | 6 | 0.82633 | 917.0629
2017-07-08 07:00 | 7 | 7 | 0.80748 | 896.1453
2017-07-08 08:00 | 7 | 8 | 0.91981 | 1020.8087
2017-07-08 09:00 | 7 | 9 | 1.2737 | 1413.5066
2017-07-08 10:00 | 7 | 10 | 1.2755 | 1415.5541
2017-07-08 11:00 | 7 | 11 | 1.4837 | 1646.65
2017-07-08 12:00 | 7 | 12 | 1.6892 | 1874.7026
2017-07-08 13:00 | 7 | 13 | 1.8963 | 2104.5644
2017-07-08 14:00 | 7 | 14 | 2.0769 | 2304.9615
2017-07-08 15:00 | 7 | 15 | 2.2416 | 2487.7845
2017-07-08 16:00 | 7 | 16 | 2.5889 | 2873.181
2017-07-08 17:00 | 7 | 17 | 2.4679 | 2738.9255
2017-07-08 18:00 | 7 | 18 | 2.3429 | 2600.169
2017-07-08 19:00 | 7 | 19 | 2.3885 | 2650.7983
2017-07-08 20:00 | 7 | 20 | 2.4198 | 2685.4494
2017-07-08 21:00 | 7 | 21 | 1.9974 | 2216.6761
2017-07-08 22:00 | 7 | 22 | 1.5469 | 1716.7913
2017-07-08 23:00 | 7 | 23 | 1.104 | 1225.1722
2017-07-09 | 7 | 0 | 0.83238 | 923.7718
2017-07-09 01:00 | 7 | 1 | 0.69432 | 770.5526
2017-07-09 02:00 | 7 | 2 | 0.61378 | 681.173
2017-07-09 03:00 | 7 | 3 | 0.56746 | 629.7682
2017-07-09 04:00 | 7 | 4 | 0.59448 | 659.7512
2017-07-09 05:00 | 7 | 5 | 0.80679 | 895.3762
2017-07-09 06:00 | 7 | 6 | 1.0427 | 1157.1511
2017-07-09 07:00 | 7 | 7 | 1.0167 | 1128.3715
2017-07-09 08:00 | 7 | 8 | 1.1342 | 1258.7842
2017-07-09 09:00 | 7 | 9 | 1.4508 | 1610.0504
2017-07-09 10:00 | 7 | 10 | 1.4939 | 1657.9409
2017-07-09 11:00 | 7 | 11 | 1.6108 | 1787.64
2017-07-09 12:00 | 7 | 12 | 1.7992 | 1996.7889
2017-07-09 13:00 | 7 | 13 | 2.0154 | 2236.665
2017-07-09 14:00 | 7 | 14 | 2.1856 | 2425.6281
2017-07-09 15:00 | 7 | 15 | 2.2776 | 2527.7032
2017-07-09 16:00 | 7 | 16 | 2.6334 | 2922.551
2017-07-09 17:00 | 7 | 17 | 2.4977 | 2771.9665
2017-07-09 18:00 | 7 | 18 | 2.4548 | 2724.3199
2017-07-09 19:00 | 7 | 19 | 2.487 | 2760.1127
2017-07-09 20:00 | 7 | 20 | 2.5684 | 2850.3821
2017-07-09 21:00 | 7 | 21 | 1.9061 | 2115.4311
2017-07-09 22:00 | 7 | 22 | 1.4198 | 1575.7281
2017-07-09 23:00 | 7 | 23 | 0.99595 | 1105.3049
2017-07-10 | 7 | 0 | 0.76101 | 844.565
2017-07-10 01:00 | 7 | 1 | 0.63149 | 700.8301
2017-07-10 02:00 | 7 | 2 | 0.56561 | 627.71
2017-07-10 03:00 | 7 | 3 | 0.48175 | 534.6493
2017-07-10 04:00 | 7 | 4 | 0.50617 | 561.7475
2017-07-10 05:00 | 7 | 5 | 0.68447 | 759.6241
2017-07-10 06:00 | 7 | 6 | 0.91086 | 1010.8728
2017-07-10 07:00 | 7 | 7 | 0.88483 | 981.9819
2017-07-10 08:00 | 7 | 8 | 0.91497 | 1015.434
2017-07-10 09:00 | 7 | 9 | 1.0982 | 1218.7949
2017-07-10 10:00 | 7 | 10 | 1.0564 | 1172.3599
2017-07-10 11:00 | 7 | 11 | 1.1326 | 1257.0146
2017-07-10 12:00 | 7 | 12 | 1.2919 | 1433.7786
2017-07-10 13:00 | 7 | 13 | 1.4087 | 1563.329
2017-07-10 14:00 | 7 | 14 | 1.5441 | 1713.6407
2017-07-10 15:00 | 7 | 15 | 1.6932 | 1879.0774
2017-07-10 16:00 | 7 | 16 | 2.0256 | 2248.0333
2017-07-10 17:00 | 7 | 17 | 1.9881 | 2206.413
2017-07-10 18:00 | 7 | 18 | 1.9168 | 2127.2417
2017-07-10 19:00 | 7 | 19 | 2.0165 | 2237.9135
2017-07-10 20:00 | 7 | 20 | 2.1085 | 2340.0452
2017-07-10 21:00 | 7 | 21 | 1.664 | 1846.7071
2017-07-10 22:00 | 7 | 22 | 1.2212 | 1355.2875
2017-07-10 23:00 | 7 | 23 | 0.79699 | 884.5032
2017-07-11 | 7 | 0 | 0.60481 | 671.2194
2017-07-11 01:00 | 7 | 1 | 0.46198 | 512.7106
2017-07-11 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-11 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-11 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-11 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-11 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-11 07:00 | 7 | 7 | 0.79066 | 877.477
2017-07-11 08:00 | 7 | 8 | 0.86437 | 959.2778
2017-07-11 09:00 | 7 | 9 | 1.1622 | 1289.8598
2017-07-11 10:00 | 7 | 10 | 1.2039 | 1336.0969
2017-07-11 11:00 | 7 | 11 | 1.3271 | 1472.8078
2017-07-11 12:00 | 7 | 12 | 1.4596 | 1619.8319
2017-07-11 13:00 | 7 | 13 | 1.5773 | 1750.4766
2017-07-11 14:00 | 7 | 14 | 1.7008 | 1887.5405
2017-07-11 15:00 | 7 | 15 | 1.8647 | 2069.4657
2017-07-11 16:00 | 7 | 16 | 2.1536 | 2390.0915
2017-07-11 17:00 | 7 | 17 | 2.0588 | 2284.9057
2017-07-11 18:00 | 7 | 18 | 2.0035 | 2223.493
2017-07-11 19:00 | 7 | 19 | 2.0691 | 2296.3134
2017-07-11 20:00 | 7 | 20 | 2.1278 | 2361.4246
2017-07-11 21:00 | 7 | 21 | 1.7794 | 1974.8253
2017-07-11 22:00 | 7 | 22 | 1.327 | 1472.7273
2017-07-11 23:00 | 7 | 23 | 0.88687 | 984.25
2017-07-12 | 7 | 0 | 0.66628 | 739.4343
2017-07-12 01:00 | 7 | 1 | 0.53155 | 589.9114
2017-07-12 02:00 | 7 | 2 | 0.46582 | 516.9687
2017-07-12 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-12 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-12 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-12 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-12 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-12 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-12 09:00 | 7 | 9 | 0.84115 | 933.5107
2017-07-12 10:00 | 7 | 10 | 0.9213 | 1022.4619
2017-07-12 11:00 | 7 | 11 | 0.98498 | 1093.1293
2017-07-12 12:00 | 7 | 12 | 1.0759 | 1194.036
2017-07-12 13:00 | 7 | 13 | 1.1596 | 1286.881
2017-07-12 14:00 | 7 | 14 | 1.2919 | 1433.7068
2017-07-12 15:00 | 7 | 15 | 1.3597 | 1508.9999
2017-07-12 16:00 | 7 | 16 | 1.7256 | 1915.1001
2017-07-12 17:00 | 7 | 17 | 1.7074 | 1894.8331
2017-07-12 18:00 | 7 | 18 | 1.6301 | 1809.0733
2017-07-12 19:00 | 7 | 19 | 1.7473 | 1939.1993
2017-07-12 20:00 | 7 | 20 | 1.8448 | 2047.3154
2017-07-12 21:00 | 7 | 21 | 1.5364 | 1705.0732
2017-07-12 22:00 | 7 | 22 | 1.1401 | 1265.3098
2017-07-12 23:00 | 7 | 23 | 0.74119 | 822.5747
2017-07-13 | 7 | 0 | 0.56507 | 627.1211
2017-07-13 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-13 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-13 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-13 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-13 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-13 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-13 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-13 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-13 09:00 | 7 | 9 | 0.84068 | 932.9879
2017-07-13 10:00 | 7 | 10 | 0.90219 | 1001.2547
2017-07-13 11:00 | 7 | 11 | 0.95792 | 1063.105
2017-07-13 12:00 | 7 | 12 | 0.93673 | 1039.5831
2017-07-13 13:00 | 7 | 13 | 0.96107 | 1066.596
2017-07-13 14:00 | 7 | 14 | 0.99207 | 1100.9993
2017-07-13 15:00 | 7 | 15 | 1.0173 | 1128.9851
2017-07-13 16:00 | 7 | 16 | 1.1659 | 1293.863
2017-07-13 17:00 | 7 | 17 | 1.276 | 1416.0629
2017-07-13 18:00 | 7 | 18 | 1.2953 | 1437.5433
2017-07-13 19:00 | 7 | 19 | 1.4158 | 1571.2431
2017-07-13 20:00 | 7 | 20 | 1.5537 | 1724.2959
2017-07-13 21:00 | 7 | 21 | 1.2681 | 1407.3335
2017-07-13 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-13 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-14 | 7 | 0 | 0.5116 | 567.7749
2017-07-14 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-14 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-14 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-14 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-14 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-14 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-14 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-14 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-14 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-14 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-14 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-14 12:00 | 7 | 12 | 0.69197 | 767.9549
2017-07-14 13:00 | 7 | 13 | 0.75589 | 838.8886
2017-07-14 14:00 | 7 | 14 | 0.80837 | 897.1283
2017-07-14 15:00 | 7 | 15 | 1.0157 | 1127.1985
2017-07-14 16:00 | 7 | 16 | 1.0715 | 1189.1694
2017-07-14 17:00 | 7 | 17 | 1.1605 | 1287.9541
2017-07-14 18:00 | 7 | 18 | 1.0872 | 1206.631
2017-07-14 19:00 | 7 | 19 | 1.2724 | 1412.0819
2017-07-14 20:00 | 7 | 20 | 1.4462 | 1604.9949
2017-07-14 21:00 | 7 | 21 | 1.2203 | 1354.3286
2017-07-14 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-14 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-15 | 7 | 0 | 0.51555 | 572.1553
2017-07-15 01:00 | 7 | 1 | 0.45798 | 508.2675
2017-07-15 02:00 | 7 | 2 | 0.44518 | 494.0641
2017-07-15 03:00 | 7 | 3 | 0.44511 | 493.9859
2017-07-15 04:00 | 7 | 4 | 0.49424 | 548.5066
2017-07-15 05:00 | 7 | 5 | 0.63143 | 700.7588
2017-07-15 06:00 | 7 | 6 | 0.82633 | 917.0629
2017-07-15 07:00 | 7 | 7 | 0.78013 | 865.784
2017-07-15 08:00 | 7 | 8 | 0.74083 | 822.1765
2017-07-15 09:00 | 7 | 9 | 0.75668 | 839.763
2017-07-15 10:00 | 7 | 10 | 0.77264 | 857.4722
2017-07-15 11:00 | 7 | 11 | 0.75276 | 835.4142
2017-07-15 12:00 | 7 | 12 | 0.76549 | 849.5421
2017-07-15 13:00 | 7 | 13 | 0.85839 | 952.6476
2017-07-15 14:00 | 7 | 14 | 1.0536 | 1169.2774
2017-07-15 15:00 | 7 | 15 | 1.2437 | 1380.2093
2017-07-15 16:00 | 7 | 16 | 1.5677 | 1739.8045
2017-07-15 17:00 | 7 | 17 | 1.602 | 1777.9249
2017-07-15 18:00 | 7 | 18 | 1.613 | 1790.0588
2017-07-15 19:00 | 7 | 19 | 1.7263 | 1915.801
2017-07-15 20:00 | 7 | 20 | 1.8357 | 2037.2312
2017-07-15 21:00 | 7 | 21 | 1.5072 | 1672.7403
2017-07-15 22:00 | 7 | 22 | 1.0885 | 1208.0309
2017-07-15 23:00 | 7 | 23 | 0.66799 | 741.3323
2017-07-16 | 7 | 0 | 0.51555 | 572.1553
2017-07-16 01:00 | 7 | 1 | 0.45798 | 508.2675
2017-07-16 02:00 | 7 | 2 | 0.44518 | 494.0641
2017-07-16 03:00 | 7 | 3 | 0.44511 | 493.9859
2017-07-16 04:00 | 7 | 4 | 0.49424 | 548.5066
2017-07-16 05:00 | 7 | 5 | 0.63143 | 700.7588
2017-07-16 06:00 | 7 | 6 | 0.82633 | 917.0629
2017-07-16 07:00 | 7 | 7 | 0.78013 | 865.784
2017-07-16 08:00 | 7 | 8 | 0.74083 | 822.1765
2017-07-16 09:00 | 7 | 9 | 0.75883 | 842.1462
2017-07-16 10:00 | 7 | 10 | 0.81639 | 906.0345
2017-07-16 11:00 | 7 | 11 | 0.93067 | 1032.8644
2017-07-16 12:00 | 7 | 12 | 1.0175 | 1129.2571
2017-07-16 13:00 | 7 | 13 | 1.1313 | 1255.5293
2017-07-16 14:00 | 7 | 14 | 1.2753 | 1415.3299
2017-07-16 15:00 | 7 | 15 | 1.5039 | 1669.0501
2017-07-16 16:00 | 7 | 16 | 1.64 | 1820.0816
2017-07-16 17:00 | 7 | 17 | 1.6563 | 1838.156
2017-07-16 18:00 | 7 | 18 | 1.5967 | 1772.0312
2017-07-16 19:00 | 7 | 19 | 1.7059 | 1893.1633
2017-07-16 20:00 | 7 | 20 | 1.8226 | 2022.7782
2017-07-16 21:00 | 7 | 21 | 1.4859 | 1649.0333
2017-07-16 22:00 | 7 | 22 | 1.0635 | 1180.2711
2017-07-16 23:00 | 7 | 23 | 0.6553 | 727.2579
2017-07-17 | 7 | 0 | 0.5116 | 567.7749
2017-07-17 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-17 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-17 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-17 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-17 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-17 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-17 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-17 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-17 09:00 | 7 | 9 | 0.71622 | 794.8595
2017-07-17 10:00 | 7 | 10 | 0.74635 | 828.2979
2017-07-17 11:00 | 7 | 11 | 0.81742 | 907.1778
2017-07-17 12:00 | 7 | 12 | 0.8651 | 960.0864
2017-07-17 13:00 | 7 | 13 | 0.90702 | 1006.6113
2017-07-17 14:00 | 7 | 14 | 1.1836 | 1313.5896
2017-07-17 15:00 | 7 | 15 | 1.183 | 1312.8949
2017-07-17 16:00 | 7 | 16 | 1.2502 | 1387.4382
2017-07-17 17:00 | 7 | 17 | 1.4231 | 1579.3598
2017-07-17 18:00 | 7 | 18 | 1.4315 | 1588.7128
2017-07-17 19:00 | 7 | 19 | 1.5948 | 1769.9222
2017-07-17 20:00 | 7 | 20 | 1.6655 | 1848.3895
2017-07-17 21:00 | 7 | 21 | 1.4043 | 1558.452
2017-07-17 22:00 | 7 | 22 | 1.021 | 1133.1424
2017-07-17 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-18 | 7 | 0 | 0.5116 | 567.7749
2017-07-18 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-18 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-18 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-18 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-18 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-18 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-18 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-18 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-18 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-18 10:00 | 7 | 10 | 0.73569 | 816.4677
2017-07-18 11:00 | 7 | 11 | 0.83041 | 921.5912
2017-07-18 12:00 | 7 | 12 | 0.90401 | 1003.2703
2017-07-18 13:00 | 7 | 13 | 1.0087 | 1119.4454
2017-07-18 14:00 | 7 | 14 | 1.0574 | 1173.4746
2017-07-18 15:00 | 7 | 15 | 1.199 | 1330.597
2017-07-18 16:00 | 7 | 16 | 1.3487 | 1496.7449
2017-07-18 17:00 | 7 | 17 | 1.4385 | 1596.4385
2017-07-18 18:00 | 7 | 18 | 1.4303 | 1587.3489
2017-07-18 19:00 | 7 | 19 | 1.5235 | 1690.742
2017-07-18 20:00 | 7 | 20 | 1.6348 | 1814.254
2017-07-18 21:00 | 7 | 21 | 1.2993 | 1441.9747
2017-07-18 22:00 | 7 | 22 | 0.94425 | 1047.9283
2017-07-18 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-19 | 7 | 0 | 0.5116 | 567.7749
2017-07-19 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-19 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-19 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-19 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-19 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-19 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-19 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-19 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-19 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-19 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-19 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-19 12:00 | 7 | 12 | 0.71288 | 791.1589
2017-07-19 13:00 | 7 | 13 | 0.77016 | 854.7225
2017-07-19 14:00 | 7 | 14 | 0.88394 | 981.0008
2017-07-19 15:00 | 7 | 15 | 1.0546 | 1170.3502
2017-07-19 16:00 | 7 | 16 | 1.2322 | 1367.4598
2017-07-19 17:00 | 7 | 17 | 1.33 | 1476.0468
2017-07-19 18:00 | 7 | 18 | 1.3184 | 1463.1332
2017-07-19 19:00 | 7 | 19 | 1.4612 | 1621.6193
2017-07-19 20:00 | 7 | 20 | 1.6012 | 1777.0325
2017-07-19 21:00 | 7 | 21 | 1.3048 | 1448.0633
2017-07-19 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-19 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-20 | 7 | 0 | 0.5116 | 567.7749
2017-07-20 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-20 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-20 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-20 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-20 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-20 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-20 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-20 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-20 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-20 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-20 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-20 12:00 | 7 | 12 | 0.68326 | 758.2862
2017-07-20 13:00 | 7 | 13 | 0.67428 | 748.3139
2017-07-20 14:00 | 7 | 14 | 0.6977 | 774.304
2017-07-20 15:00 | 7 | 15 | 0.80101 | 888.9674
2017-07-20 16:00 | 7 | 16 | 0.96983 | 1076.3157
2017-07-20 17:00 | 7 | 17 | 1.0835 | 1202.4409
2017-07-20 18:00 | 7 | 18 | 1.0876 | 1207.0084
2017-07-20 19:00 | 7 | 19 | 1.2724 | 1412.0819
2017-07-20 20:00 | 7 | 20 | 1.4462 | 1604.9949
2017-07-20 21:00 | 7 | 21 | 1.2203 | 1354.3286
2017-07-20 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-20 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-21 | 7 | 0 | 0.5116 | 567.7749
2017-07-21 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-21 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-21 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-21 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-21 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-21 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-21 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-21 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-21 09:00 | 7 | 9 | 0.81772 | 907.5058
2017-07-21 10:00 | 7 | 10 | 0.87136 | 967.0364
2017-07-21 11:00 | 7 | 11 | 0.98012 | 1087.7394
2017-07-21 12:00 | 7 | 12 | 1.0777 | 1196.065
2017-07-21 13:00 | 7 | 13 | 1.2978 | 1440.3033
2017-07-21 14:00 | 7 | 14 | 1.5161 | 1682.5393
2017-07-21 15:00 | 7 | 15 | 1.3191 | 1463.9238
2017-07-21 16:00 | 7 | 16 | 1.4886 | 1652.0758
2017-07-21 17:00 | 7 | 17 | 1.556 | 1726.8165
2017-07-21 18:00 | 7 | 18 | 1.5758 | 1748.8472
2017-07-21 19:00 | 7 | 19 | 1.7208 | 1909.7883
2017-07-21 20:00 | 7 | 20 | 1.8501 | 2053.2332
2017-07-21 21:00 | 7 | 21 | 1.5305 | 1698.5243
2017-07-21 22:00 | 7 | 22 | 1.1247 | 1248.1427
2017-07-21 23:00 | 7 | 23 | 0.73488 | 815.5742
2017-07-22 | 7 | 0 | 0.5282 | 586.1975
2017-07-22 01:00 | 7 | 1 | 0.45798 | 508.2675
2017-07-22 02:00 | 7 | 2 | 0.44518 | 494.0641
2017-07-22 03:00 | 7 | 3 | 0.44511 | 493.9859
2017-07-22 04:00 | 7 | 4 | 0.49424 | 548.5066
2017-07-22 05:00 | 7 | 5 | 0.63143 | 700.7588
2017-07-22 06:00 | 7 | 6 | 0.82633 | 917.0629
2017-07-22 07:00 | 7 | 7 | 0.78013 | 865.784
2017-07-22 08:00 | 7 | 8 | 0.74083 | 822.1765
2017-07-22 09:00 | 7 | 9 | 0.75668 | 839.763
2017-07-22 10:00 | 7 | 10 | 0.77264 | 857.4722
2017-07-22 11:00 | 7 | 11 | 0.75276 | 835.4142
2017-07-22 12:00 | 7 | 12 | 0.72685 | 806.6603
2017-07-22 13:00 | 7 | 13 | 0.74563 | 827.5004
2017-07-22 14:00 | 7 | 14 | 0.8839 | 980.9568
2017-07-22 15:00 | 7 | 15 | 1.0501 | 1165.4237
2017-07-22 16:00 | 7 | 16 | 1.2248 | 1359.3206
2017-07-22 17:00 | 7 | 17 | 1.3648 | 1514.642
2017-07-22 18:00 | 7 | 18 | 1.3812 | 1532.8185
2017-07-22 19:00 | 7 | 19 | 1.543 | 1712.4245
2017-07-22 20:00 | 7 | 20 | 1.7234 | 1912.6031
2017-07-22 21:00 | 7 | 21 | 1.3918 | 1544.6012
2017-07-22 22:00 | 7 | 22 | 0.94506 | 1048.8296
2017-07-22 23:00 | 7 | 23 | 0.63565 | 705.441
2017-07-23 | 7 | 0 | 0.51555 | 572.1553
2017-07-23 01:00 | 7 | 1 | 0.45798 | 508.2675
2017-07-23 02:00 | 7 | 2 | 0.44518 | 494.0641
2017-07-23 03:00 | 7 | 3 | 0.44511 | 493.9859
2017-07-23 04:00 | 7 | 4 | 0.49424 | 548.5066
2017-07-23 05:00 | 7 | 5 | 0.63143 | 700.7588
2017-07-23 06:00 | 7 | 6 | 0.82633 | 917.0629
2017-07-23 07:00 | 7 | 7 | 0.78013 | 865.784
2017-07-23 08:00 | 7 | 8 | 0.74083 | 822.1765
2017-07-23 09:00 | 7 | 9 | 0.75668 | 839.763
2017-07-23 10:00 | 7 | 10 | 0.77264 | 857.4722
2017-07-23 11:00 | 7 | 11 | 0.75276 | 835.4142
2017-07-23 12:00 | 7 | 12 | 0.72685 | 806.6603
2017-07-23 13:00 | 7 | 13 | 0.78068 | 866.3959
2017-07-23 14:00 | 7 | 14 | 0.89312 | 991.191
2017-07-23 15:00 | 7 | 15 | 1.0653 | 1182.2416
2017-07-23 16:00 | 7 | 16 | 1.2171 | 1350.7669
2017-07-23 17:00 | 7 | 17 | 1.3277 | 1473.4694
2017-07-23 18:00 | 7 | 18 | 1.3536 | 1502.1745
2017-07-23 19:00 | 7 | 19 | 1.4819 | 1644.5868
2017-07-23 20:00 | 7 | 20 | 1.624 | 1802.3059
2017-07-23 21:00 | 7 | 21 | 1.3135 | 1457.7073
2017-07-23 22:00 | 7 | 22 | 0.94037 | 1043.6238
2017-07-23 23:00 | 7 | 23 | 0.63565 | 705.441
2017-07-24 | 7 | 0 | 0.5116 | 567.7749
2017-07-24 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-24 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-24 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-24 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-24 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-24 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-24 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-24 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-24 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-24 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-24 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-24 12:00 | 7 | 12 | 0.68326 | 758.2862
2017-07-24 13:00 | 7 | 13 | 0.67428 | 748.3139
2017-07-24 14:00 | 7 | 14 | 0.6977 | 774.304
2017-07-24 15:00 | 7 | 15 | 0.80101 | 888.9674
2017-07-24 16:00 | 7 | 16 | 0.96983 | 1076.3157
2017-07-24 17:00 | 7 | 17 | 1.0505 | 1165.804
2017-07-24 18:00 | 7 | 18 | 1.0872 | 1206.631
2017-07-24 19:00 | 7 | 19 | 1.2724 | 1412.0819
2017-07-24 20:00 | 7 | 20 | 1.4462 | 1604.9949
2017-07-24 21:00 | 7 | 21 | 1.2203 | 1354.3286
2017-07-24 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-24 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-25 | 7 | 0 | 0.5116 | 567.7749
2017-07-25 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-25 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-25 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-25 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-25 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-25 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-25 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-25 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-25 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-25 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-25 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-25 12:00 | 7 | 12 | 0.68326 | 758.2862
2017-07-25 13:00 | 7 | 13 | 0.67428 | 748.3139
2017-07-25 14:00 | 7 | 14 | 0.6977 | 774.304
2017-07-25 15:00 | 7 | 15 | 0.8564 | 950.4351
2017-07-25 16:00 | 7 | 16 | 1.1117 | 1233.7698
2017-07-25 17:00 | 7 | 17 | 1.2028 | 1334.8223
2017-07-25 18:00 | 7 | 18 | 1.2379 | 1373.8221
2017-07-25 19:00 | 7 | 19 | 1.3783 | 1529.6439
2017-07-25 20:00 | 7 | 20 | 1.5184 | 1685.1101
2017-07-25 21:00 | 7 | 21 | 1.2203 | 1354.3286
2017-07-25 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-25 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-26 | 7 | 0 | 0.5116 | 567.7749
2017-07-26 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-26 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-26 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-26 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-26 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-26 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-26 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-26 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-26 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-26 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-26 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-26 12:00 | 7 | 12 | 0.68326 | 758.2862
2017-07-26 13:00 | 7 | 13 | 0.75098 | 833.4397
2017-07-26 14:00 | 7 | 14 | 0.93347 | 1035.9681
2017-07-26 15:00 | 7 | 15 | 1.0914 | 1211.2617
2017-07-26 16:00 | 7 | 16 | 1.3189 | 1463.7679
2017-07-26 17:00 | 7 | 17 | 1.3757 | 1526.7899
2017-07-26 18:00 | 7 | 18 | 1.2681 | 1407.337
2017-07-26 19:00 | 7 | 19 | 1.2724 | 1412.0819
2017-07-26 20:00 | 7 | 20 | 1.5855 | 1759.5989
2017-07-26 21:00 | 7 | 21 | 1.3333 | 1479.6683
2017-07-26 22:00 | 7 | 22 | 0.95606 | 1061.0323
2017-07-26 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-27 | 7 | 0 | 0.5116 | 567.7749
2017-07-27 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-27 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-27 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-27 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-27 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-27 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-27 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-27 08:00 | 7 | 8 | 0.69825 | 774.9205
2017-07-27 09:00 | 7 | 9 | 0.87226 | 968.0404
2017-07-27 10:00 | 7 | 10 | 0.96438 | 1070.276
2017-07-27 11:00 | 7 | 11 | 1.0601 | 1176.5251
2017-07-27 12:00 | 7 | 12 | 1.1132 | 1235.4373
2017-07-27 13:00 | 7 | 13 | 1.1971 | 1328.5321
2017-07-27 14:00 | 7 | 14 | 1.2998 | 1442.5049
2017-07-27 15:00 | 7 | 15 | 1.4377 | 1595.6058
2017-07-27 16:00 | 7 | 16 | 1.6362 | 1815.8683
2017-07-27 17:00 | 7 | 17 | 1.6132 | 1790.2931
2017-07-27 18:00 | 7 | 18 | 1.569 | 1741.3249
2017-07-27 19:00 | 7 | 19 | 1.6604 | 1842.7668
2017-07-27 20:00 | 7 | 20 | 1.7661 | 1960.0222
2017-07-27 21:00 | 7 | 21 | 1.411 | 1565.9309
2017-07-27 22:00 | 7 | 22 | 0.98967 | 1098.3371
2017-07-27 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-28 | 7 | 0 | 0.5116 | 567.7749
2017-07-28 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-28 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-28 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-28 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-28 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-28 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-28 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-28 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-28 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-28 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-28 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-28 12:00 | 7 | 12 | 0.68326 | 758.2862
2017-07-28 13:00 | 7 | 13 | 0.67428 | 748.3139
2017-07-28 14:00 | 7 | 14 | 0.6977 | 774.304
2017-07-28 15:00 | 7 | 15 | 0.80101 | 888.9674
2017-07-28 16:00 | 7 | 16 | 0.96983 | 1076.3157
2017-07-28 17:00 | 7 | 17 | 1.0505 | 1165.804
2017-07-28 18:00 | 7 | 18 | 1.0872 | 1206.631
2017-07-28 19:00 | 7 | 19 | 1.2724 | 1412.0819
2017-07-28 20:00 | 7 | 20 | 1.4462 | 1604.9949
2017-07-28 21:00 | 7 | 21 | 1.2203 | 1354.3286
2017-07-28 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-28 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-07-29 | 7 | 0 | 0.51555 | 572.1553
2017-07-29 01:00 | 7 | 1 | 0.45798 | 508.2675
2017-07-29 02:00 | 7 | 2 | 0.44518 | 494.0641
2017-07-29 03:00 | 7 | 3 | 0.44511 | 493.9859
2017-07-29 04:00 | 7 | 4 | 0.49424 | 548.5066
2017-07-29 05:00 | 7 | 5 | 0.63143 | 700.7588
2017-07-29 06:00 | 7 | 6 | 0.82633 | 917.0629
2017-07-29 07:00 | 7 | 7 | 0.78013 | 865.784
2017-07-29 08:00 | 7 | 8 | 0.74083 | 822.1765
2017-07-29 09:00 | 7 | 9 | 0.75668 | 839.763
2017-07-29 10:00 | 7 | 10 | 0.77264 | 857.4722
2017-07-29 11:00 | 7 | 11 | 0.75276 | 835.4142
2017-07-29 12:00 | 7 | 12 | 0.72685 | 806.6603
2017-07-29 13:00 | 7 | 13 | 0.7134 | 791.7355
2017-07-29 14:00 | 7 | 14 | 0.73475 | 815.4321
2017-07-29 15:00 | 7 | 15 | 0.83693 | 928.8291
2017-07-29 16:00 | 7 | 16 | 1.0052 | 1115.5493
2017-07-29 17:00 | 7 | 17 | 1.0848 | 1203.8816
2017-07-29 18:00 | 7 | 18 | 1.1215 | 1244.6359
2017-07-29 19:00 | 7 | 19 | 1.3072 | 1450.7645
2017-07-29 20:00 | 7 | 20 | 1.4818 | 1644.5115
2017-07-29 21:00 | 7 | 21 | 1.2486 | 1385.7285
2017-07-29 22:00 | 7 | 22 | 0.94037 | 1043.6238
2017-07-29 23:00 | 7 | 23 | 0.63565 | 705.441
2017-07-30 | 7 | 0 | 0.51816 | 575.0591
2017-07-30 01:00 | 7 | 1 | 0.46917 | 520.6897
2017-07-30 02:00 | 7 | 2 | 0.46209 | 512.8238
2017-07-30 03:00 | 7 | 3 | 0.46559 | 516.7141
2017-07-30 04:00 | 7 | 4 | 0.51578 | 572.4099
2017-07-30 05:00 | 7 | 5 | 0.65021 | 721.6053
2017-07-30 06:00 | 7 | 6 | 0.84051 | 932.7988
2017-07-30 07:00 | 7 | 7 | 0.79522 | 882.5356
2017-07-30 08:00 | 7 | 8 | 0.75136 | 833.8643
2017-07-30 09:00 | 7 | 9 | 0.75668 | 839.763
2017-07-30 10:00 | 7 | 10 | 0.77264 | 857.4722
2017-07-30 11:00 | 7 | 11 | 0.75276 | 835.4142
2017-07-30 12:00 | 7 | 12 | 0.72685 | 806.6603
2017-07-30 13:00 | 7 | 13 | 0.7134 | 791.7355
2017-07-30 14:00 | 7 | 14 | 0.73475 | 815.4321
2017-07-30 15:00 | 7 | 15 | 0.83693 | 928.8291
2017-07-30 16:00 | 7 | 16 | 1.0052 | 1115.5493
2017-07-30 17:00 | 7 | 17 | 1.0848 | 1203.8816
2017-07-30 18:00 | 7 | 18 | 1.1215 | 1244.6359
2017-07-30 19:00 | 7 | 19 | 1.3072 | 1450.7645
2017-07-30 20:00 | 7 | 20 | 1.4818 | 1644.5115
2017-07-30 21:00 | 7 | 21 | 1.2486 | 1385.7285
2017-07-30 22:00 | 7 | 22 | 0.94037 | 1043.6238
2017-07-30 23:00 | 7 | 23 | 0.63565 | 705.441
2017-07-31 | 7 | 0 | 0.5116 | 567.7749
2017-07-31 01:00 | 7 | 1 | 0.45537 | 505.3696
2017-07-31 02:00 | 7 | 2 | 0.44382 | 492.5488
2017-07-31 03:00 | 7 | 3 | 0.44244 | 491.0215
2017-07-31 04:00 | 7 | 4 | 0.49014 | 543.9601
2017-07-31 05:00 | 7 | 5 | 0.6208 | 688.9666
2017-07-31 06:00 | 7 | 6 | 0.80517 | 893.578
2017-07-31 07:00 | 7 | 7 | 0.74769 | 829.785
2017-07-31 08:00 | 7 | 8 | 0.6958 | 772.2009
2017-07-31 09:00 | 7 | 9 | 0.70576 | 783.2561
2017-07-31 10:00 | 7 | 10 | 0.72015 | 799.2201
2017-07-31 11:00 | 7 | 11 | 0.70495 | 782.354
2017-07-31 12:00 | 7 | 12 | 0.68326 | 758.2862
2017-07-31 13:00 | 7 | 13 | 0.79925 | 887.0109
2017-07-31 14:00 | 7 | 14 | 0.96422 | 1070.0909
2017-07-31 15:00 | 7 | 15 | 1.1995 | 1331.1871
2017-07-31 16:00 | 7 | 16 | 1.4769 | 1639.1031
2017-07-31 17:00 | 7 | 17 | 1.52 | 1686.9489
2017-07-31 18:00 | 7 | 18 | 1.5072 | 1672.7343
2017-07-31 19:00 | 7 | 19 | 1.4838 | 1646.7256
2017-07-31 20:00 | 7 | 20 | 1.563 | 1734.5722
2017-07-31 21:00 | 7 | 21 | 1.2203 | 1354.3286
2017-07-31 22:00 | 7 | 22 | 0.92483 | 1026.3832
2017-07-31 23:00 | 7 | 23 | 0.62907 | 698.1455
2017-08-01 | 8 | 0 | 0.50757 | 563.3025
2017-08-01 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-01 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-01 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-01 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-01 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-01 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-01 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-01 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-01 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-01 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-01 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-01 12:00 | 8 | 12 | 0.69118 | 767.0738
2017-08-01 13:00 | 8 | 13 | 0.6822 | 757.1015
2017-08-01 14:00 | 8 | 14 | 0.70561 | 783.0916
2017-08-01 15:00 | 8 | 15 | 0.80943 | 898.3042
2017-08-01 16:00 | 8 | 16 | 0.98892 | 1097.5002
2017-08-01 17:00 | 8 | 17 | 1.0893 | 1208.8791
2017-08-01 18:00 | 8 | 18 | 1.168 | 1296.2336
2017-08-01 19:00 | 8 | 19 | 1.3866 | 1538.7967
2017-08-01 20:00 | 8 | 20 | 1.5203 | 1687.2222
2017-08-01 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-01 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-01 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-02 | 8 | 0 | 0.50757 | 563.3025
2017-08-02 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-02 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-02 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-02 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-02 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-02 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-02 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-02 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-02 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-02 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-02 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-02 12:00 | 8 | 12 | 0.69118 | 767.0738
2017-08-02 13:00 | 8 | 13 | 0.6822 | 757.1015
2017-08-02 14:00 | 8 | 14 | 0.70561 | 783.0916
2017-08-02 15:00 | 8 | 15 | 0.80943 | 898.3042
2017-08-02 16:00 | 8 | 16 | 0.98892 | 1097.5002
2017-08-02 17:00 | 8 | 17 | 1.101 | 1221.8616
2017-08-02 18:00 | 8 | 18 | 1.168 | 1296.2336
2017-08-02 19:00 | 8 | 19 | 1.3866 | 1538.7967
2017-08-02 20:00 | 8 | 20 | 1.5203 | 1687.2222
2017-08-02 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-02 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-02 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-03 | 8 | 0 | 0.50757 | 563.3025
2017-08-03 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-03 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-03 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-03 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-03 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-03 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-03 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-03 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-03 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-03 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-03 11:00 | 8 | 11 | 0.79731 | 884.8566
2017-08-03 12:00 | 8 | 12 | 0.89196 | 989.9029
2017-08-03 13:00 | 8 | 13 | 1.0013 | 1111.2732
2017-08-03 14:00 | 8 | 14 | 1.0614 | 1177.9525
2017-08-03 15:00 | 8 | 15 | 1.2269 | 1361.6309
2017-08-03 16:00 | 8 | 16 | 1.3719 | 1522.4834
2017-08-03 17:00 | 8 | 17 | 1.4748 | 1636.7849
2017-08-03 18:00 | 8 | 18 | 1.5028 | 1667.8495
2017-08-03 19:00 | 8 | 19 | 1.6828 | 1867.5385
2017-08-03 20:00 | 8 | 20 | 1.778 | 1973.2678
2017-08-03 21:00 | 8 | 21 | 1.3726 | 1523.2685
2017-08-03 22:00 | 8 | 22 | 0.98287 | 1090.7884
2017-08-03 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-04 | 8 | 0 | 0.50757 | 563.3025
2017-08-04 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-04 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-04 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-04 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-04 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-04 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-04 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-04 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-04 09:00 | 8 | 9 | 0.86434 | 959.2433
2017-08-04 10:00 | 8 | 10 | 0.9879 | 1096.374
2017-08-04 11:00 | 8 | 11 | 1.0927 | 1212.7017
2017-08-04 12:00 | 8 | 12 | 1.2219 | 1356.0475
2017-08-04 13:00 | 8 | 13 | 1.2493 | 1386.5234
2017-08-04 14:00 | 8 | 14 | 1.2868 | 1428.0803
2017-08-04 15:00 | 8 | 15 | 1.4118 | 1566.8294
2017-08-04 16:00 | 8 | 16 | 1.7126 | 1900.5976
2017-08-04 17:00 | 8 | 17 | 1.7135 | 1901.6561
2017-08-04 18:00 | 8 | 18 | 1.7258 | 1915.322
2017-08-04 19:00 | 8 | 19 | 1.8803 | 2086.7865
2017-08-04 20:00 | 8 | 20 | 1.9634 | 2179.0206
2017-08-04 21:00 | 8 | 21 | 1.5541 | 1724.7902
2017-08-04 22:00 | 8 | 22 | 1.1409 | 1266.2013
2017-08-04 23:00 | 8 | 23 | 0.74296 | 824.5422
2017-08-05 | 8 | 0 | 0.54993 | 610.3133
2017-08-05 01:00 | 8 | 1 | 0.45819 | 508.5029
2017-08-05 02:00 | 8 | 2 | 0.44539 | 494.2995
2017-08-05 03:00 | 8 | 3 | 0.44532 | 494.2213
2017-08-05 04:00 | 8 | 4 | 0.49495 | 549.2912
2017-08-05 05:00 | 8 | 5 | 0.64988 | 721.2371
2017-08-05 06:00 | 8 | 6 | 0.87207 | 967.8272
2017-08-05 07:00 | 8 | 7 | 0.83126 | 922.5336
2017-08-05 08:00 | 8 | 8 | 0.82044 | 910.5296
2017-08-05 09:00 | 8 | 9 | 0.91059 | 1010.5718
2017-08-05 10:00 | 8 | 10 | 1 | 1109.8018
2017-08-05 11:00 | 8 | 11 | 1.0162 | 1127.7366
2017-08-05 12:00 | 8 | 12 | 1.0315 | 1144.7592
2017-08-05 13:00 | 8 | 13 | 1.1758 | 1304.8827
2017-08-05 14:00 | 8 | 14 | 1.4044 | 1558.5659
2017-08-05 15:00 | 8 | 15 | 1.5994 | 1774.9657
2017-08-05 16:00 | 8 | 16 | 1.8986 | 2107.1217
2017-08-05 17:00 | 8 | 17 | 2.0221 | 2244.1268
2017-08-05 18:00 | 8 | 18 | 1.947 | 2160.7572
2017-08-05 19:00 | 8 | 19 | 2.1513 | 2387.5356
2017-08-05 20:00 | 8 | 20 | 2.1802 | 2419.6324
2017-08-05 21:00 | 8 | 21 | 1.7448 | 1936.3918
2017-08-05 22:00 | 8 | 22 | 1.2974 | 1439.8971
2017-08-05 23:00 | 8 | 23 | 0.81236 | 901.5597
2017-08-06 | 8 | 0 | 0.59399 | 659.2143
2017-08-06 01:00 | 8 | 1 | 0.47602 | 528.2879
2017-08-06 02:00 | 8 | 2 | 0.44539 | 494.2995
2017-08-06 03:00 | 8 | 3 | 0.44532 | 494.2213
2017-08-06 04:00 | 8 | 4 | 0.49495 | 549.2912
2017-08-06 05:00 | 8 | 5 | 0.64988 | 721.2371
2017-08-06 06:00 | 8 | 6 | 0.87207 | 967.8272
2017-08-06 07:00 | 8 | 7 | 0.82042 | 910.5069
2017-08-06 08:00 | 8 | 8 | 0.75483 | 837.7118
2017-08-06 09:00 | 8 | 9 | 0.7646 | 848.5507
2017-08-06 10:00 | 8 | 10 | 0.82646 | 917.2095
2017-08-06 11:00 | 8 | 11 | 0.90776 | 1007.4377
2017-08-06 12:00 | 8 | 12 | 1.0829 | 1201.7816
2017-08-06 13:00 | 8 | 13 | 1.2783 | 1418.7072
2017-08-06 14:00 | 8 | 14 | 1.4678 | 1628.9737
2017-08-06 15:00 | 8 | 15 | 1.7065 | 1893.8836
2017-08-06 16:00 | 8 | 16 | 1.9636 | 2179.1627
2017-08-06 17:00 | 8 | 17 | 1.8133 | 2012.395
2017-08-06 18:00 | 8 | 18 | 1.8531 | 2056.5678
2017-08-06 19:00 | 8 | 19 | 1.9464 | 2160.0684
2017-08-06 20:00 | 8 | 20 | 2.0544 | 2279.9314
2017-08-06 21:00 | 8 | 21 | 1.5908 | 1765.423
2017-08-06 22:00 | 8 | 22 | 1.1662 | 1294.2539
2017-08-06 23:00 | 8 | 23 | 0.73329 | 813.8086
2017-08-07 | 8 | 0 | 0.52696 | 584.8188
2017-08-07 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-07 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-07 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-07 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-07 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-07 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-07 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-07 08:00 | 8 | 8 | 0.77749 | 862.8647
2017-08-07 09:00 | 8 | 9 | 1.063 | 1179.7144
2017-08-07 10:00 | 8 | 10 | 1.0625 | 1179.1451
2017-08-07 11:00 | 8 | 11 | 1.1844 | 1314.4848
2017-08-07 12:00 | 8 | 12 | 1.2293 | 1364.2859
2017-08-07 13:00 | 8 | 13 | 1.3184 | 1463.1734
2017-08-07 14:00 | 8 | 14 | 1.3557 | 1504.6061
2017-08-07 15:00 | 8 | 15 | 1.4484 | 1607.4448
2017-08-07 16:00 | 8 | 16 | 1.5644 | 1736.1492
2017-08-07 17:00 | 8 | 17 | 1.6459 | 1826.588
2017-08-07 18:00 | 8 | 18 | 1.6323 | 1811.5205
2017-08-07 19:00 | 8 | 19 | 1.8035 | 2001.4906
2017-08-07 20:00 | 8 | 20 | 1.8556 | 2059.3484
2017-08-07 21:00 | 8 | 21 | 1.45 | 1609.1644
2017-08-07 22:00 | 8 | 22 | 0.98109 | 1088.8141
2017-08-07 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-08 | 8 | 0 | 0.50757 | 563.3025
2017-08-08 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-08 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-08 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-08 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-08 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-08 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-08 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-08 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-08 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-08 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-08 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-08 12:00 | 8 | 12 | 0.69118 | 767.0738
2017-08-08 13:00 | 8 | 13 | 0.6822 | 757.1015
2017-08-08 14:00 | 8 | 14 | 0.75282 | 835.4817
2017-08-08 15:00 | 8 | 15 | 0.9338 | 1036.3366
2017-08-08 16:00 | 8 | 16 | 1.1507 | 1277.0286
2017-08-08 17:00 | 8 | 17 | 1.3059 | 1449.3416
2017-08-08 18:00 | 8 | 18 | 1.3471 | 1494.9752
2017-08-08 19:00 | 8 | 19 | 1.5368 | 1705.5244
2017-08-08 20:00 | 8 | 20 | 1.6216 | 1799.6062
2017-08-08 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-08 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-08 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-09 | 8 | 0 | 0.50757 | 563.3025
2017-08-09 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-09 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-09 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-09 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-09 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-09 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-09 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-09 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-09 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-09 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-09 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-09 12:00 | 8 | 12 | 0.69118 | 767.0738
2017-08-09 13:00 | 8 | 13 | 0.6822 | 757.1015
2017-08-09 14:00 | 8 | 14 | 0.70561 | 783.0916
2017-08-09 15:00 | 8 | 15 | 0.80943 | 898.3042
2017-08-09 16:00 | 8 | 16 | 0.98892 | 1097.5002
2017-08-09 17:00 | 8 | 17 | 1.1196 | 1242.5535
2017-08-09 18:00 | 8 | 18 | 1.183 | 1312.8762
2017-08-09 19:00 | 8 | 19 | 1.4058 | 1560.1118
2017-08-09 20:00 | 8 | 20 | 1.5203 | 1687.2222
2017-08-09 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-09 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-09 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-10 | 8 | 0 | 0.50757 | 563.3025
2017-08-10 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-10 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-10 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-10 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-10 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-10 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-10 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-10 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-10 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-10 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-10 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-10 12:00 | 8 | 12 | 0.69118 | 767.0738
2017-08-10 13:00 | 8 | 13 | 0.6822 | 757.1015
2017-08-10 14:00 | 8 | 14 | 0.70561 | 783.0916
2017-08-10 15:00 | 8 | 15 | 0.89177 | 989.6917
2017-08-10 16:00 | 8 | 16 | 1.0753 | 1193.3878
2017-08-10 17:00 | 8 | 17 | 1.257 | 1394.9823
2017-08-10 18:00 | 8 | 18 | 1.3143 | 1458.5709
2017-08-10 19:00 | 8 | 19 | 1.5188 | 1685.5158
2017-08-10 20:00 | 8 | 20 | 1.6391 | 1819.0936
2017-08-10 21:00 | 8 | 21 | 1.2471 | 1384.0235
2017-08-10 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-10 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-11 | 8 | 0 | 0.50757 | 563.3025
2017-08-11 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-11 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-11 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-11 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-11 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-11 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-11 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-11 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-11 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-11 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-11 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-11 12:00 | 8 | 12 | 0.69118 | 767.0738
2017-08-11 13:00 | 8 | 13 | 0.6822 | 757.1015
2017-08-11 14:00 | 8 | 14 | 0.70561 | 783.0916
2017-08-11 15:00 | 8 | 15 | 0.80943 | 898.3042
2017-08-11 16:00 | 8 | 16 | 0.98892 | 1097.5002
2017-08-11 17:00 | 8 | 17 | 1.0893 | 1208.8791
2017-08-11 18:00 | 8 | 18 | 1.168 | 1296.2336
2017-08-11 19:00 | 8 | 19 | 1.3866 | 1538.7967
2017-08-11 20:00 | 8 | 20 | 1.5203 | 1687.2222
2017-08-11 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-11 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-11 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-12 | 8 | 0 | 0.48876 | 542.4289
2017-08-12 01:00 | 8 | 1 | 0.44304 | 491.6845
2017-08-12 02:00 | 8 | 2 | 0.43735 | 485.3683
2017-08-12 03:00 | 8 | 3 | 0.43013 | 477.3544
2017-08-12 04:00 | 8 | 4 | 0.4708 | 522.4945
2017-08-12 05:00 | 8 | 5 | 0.58827 | 652.8607
2017-08-12 06:00 | 8 | 6 | 0.75105 | 833.5182
2017-08-12 07:00 | 8 | 7 | 0.63308 | 702.5987
2017-08-12 08:00 | 8 | 8 | 0.49739 | 551.9992
2017-08-12 09:00 | 8 | 9 | 0.47635 | 528.6546
2017-08-12 10:00 | 8 | 10 | 0.48512 | 538.3902
2017-08-12 11:00 | 8 | 11 | 0.49201 | 546.0322
2017-08-12 12:00 | 8 | 12 | 0.48837 | 541.9898
2017-08-12 13:00 | 8 | 13 | 0.50078 | 555.7691
2017-08-12 14:00 | 8 | 14 | 0.53374 | 592.3428
2017-08-12 15:00 | 8 | 15 | 0.64237 | 712.9064
2017-08-12 16:00 | 8 | 16 | 0.8224 | 912.6975
2017-08-12 17:00 | 8 | 17 | 0.92114 | 1022.2799
2017-08-12 18:00 | 8 | 18 | 0.99615 | 1105.5251
2017-08-12 19:00 | 8 | 19 | 1.2154 | 1348.8568
2017-08-12 20:00 | 8 | 20 | 1.3498 | 1497.9841
2017-08-12 21:00 | 8 | 21 | 1.0832 | 1202.0895
2017-08-12 22:00 | 8 | 22 | 0.84974 | 943.0393
2017-08-12 23:00 | 8 | 23 | 0.59326 | 658.403
2017-08-13 | 8 | 0 | 0.48876 | 542.4289
2017-08-13 01:00 | 8 | 1 | 0.44304 | 491.6845
2017-08-13 02:00 | 8 | 2 | 0.43735 | 485.3683
2017-08-13 03:00 | 8 | 3 | 0.43013 | 477.3544
2017-08-13 04:00 | 8 | 4 | 0.4708 | 522.4945
2017-08-13 05:00 | 8 | 5 | 0.58827 | 652.8607
2017-08-13 06:00 | 8 | 6 | 0.75105 | 833.5182
2017-08-13 07:00 | 8 | 7 | 0.63308 | 702.5987
2017-08-13 08:00 | 8 | 8 | 0.49739 | 551.9992
2017-08-13 09:00 | 8 | 9 | 0.47635 | 528.6546
2017-08-13 10:00 | 8 | 10 | 0.48512 | 538.3902
2017-08-13 11:00 | 8 | 11 | 0.49201 | 546.0322
2017-08-13 12:00 | 8 | 12 | 0.48837 | 541.9898
2017-08-13 13:00 | 8 | 13 | 0.50078 | 555.7691
2017-08-13 14:00 | 8 | 14 | 0.53374 | 592.3428
2017-08-13 15:00 | 8 | 15 | 0.64237 | 712.9064
2017-08-13 16:00 | 8 | 16 | 0.8224 | 912.6975
2017-08-13 17:00 | 8 | 17 | 0.92114 | 1022.2799
2017-08-13 18:00 | 8 | 18 | 0.99615 | 1105.5251
2017-08-13 19:00 | 8 | 19 | 1.2154 | 1348.8568
2017-08-13 20:00 | 8 | 20 | 1.3498 | 1497.9841
2017-08-13 21:00 | 8 | 21 | 1.0832 | 1202.0895
2017-08-13 22:00 | 8 | 22 | 0.84974 | 943.0393
2017-08-13 23:00 | 8 | 23 | 0.59326 | 658.403
2017-08-14 | 8 | 0 | 0.48876 | 542.4289
2017-08-14 01:00 | 8 | 1 | 0.44304 | 491.6845
2017-08-14 02:00 | 8 | 2 | 0.43735 | 485.3683
2017-08-14 03:00 | 8 | 3 | 0.43013 | 477.3544
2017-08-14 04:00 | 8 | 4 | 0.4708 | 522.4945
2017-08-14 05:00 | 8 | 5 | 0.58827 | 652.8607
2017-08-14 06:00 | 8 | 6 | 0.75105 | 833.5182
2017-08-14 07:00 | 8 | 7 | 0.63308 | 702.5987
2017-08-14 08:00 | 8 | 8 | 0.49739 | 551.9992
2017-08-14 09:00 | 8 | 9 | 0.47635 | 528.6546
2017-08-14 10:00 | 8 | 10 | 0.48512 | 538.3902
2017-08-14 11:00 | 8 | 11 | 0.55672 | 617.848
2017-08-14 12:00 | 8 | 12 | 0.72203 | 801.3143
2017-08-14 13:00 | 8 | 13 | 0.86045 | 954.9321
2017-08-14 14:00 | 8 | 14 | 1.0344 | 1147.9796
2017-08-14 15:00 | 8 | 15 | 1.1617 | 1289.2524
2017-08-14 16:00 | 8 | 16 | 1.3796 | 1531.0438
2017-08-14 17:00 | 8 | 17 | 1.4261 | 1582.6457
2017-08-14 18:00 | 8 | 18 | 1.4114 | 1566.4183
2017-08-14 19:00 | 8 | 19 | 1.5742 | 1747.0511
2017-08-14 20:00 | 8 | 20 | 1.666 | 1848.8756
2017-08-14 21:00 | 8 | 21 | 1.3014 | 1444.253
2017-08-14 22:00 | 8 | 22 | 0.96171 | 1067.3107
2017-08-14 23:00 | 8 | 23 | 0.60608 | 672.6288
2017-08-15 | 8 | 0 | 0.48876 | 542.4289
2017-08-15 01:00 | 8 | 1 | 0.44304 | 491.6845
2017-08-15 02:00 | 8 | 2 | 0.43735 | 485.3683
2017-08-15 03:00 | 8 | 3 | 0.43013 | 477.3544
2017-08-15 04:00 | 8 | 4 | 0.4708 | 522.4945
2017-08-15 05:00 | 8 | 5 | 0.58827 | 652.8607
2017-08-15 06:00 | 8 | 6 | 0.75105 | 833.5182
2017-08-15 07:00 | 8 | 7 | 0.63308 | 702.5987
2017-08-15 08:00 | 8 | 8 | 0.49739 | 551.9992
2017-08-15 09:00 | 8 | 9 | 0.47635 | 528.6546
2017-08-15 10:00 | 8 | 10 | 0.49951 | 554.3557
2017-08-15 11:00 | 8 | 11 | 0.61204 | 679.247
2017-08-15 12:00 | 8 | 12 | 0.7069 | 784.5172
2017-08-15 13:00 | 8 | 13 | 0.88172 | 978.5335
2017-08-15 14:00 | 8 | 14 | 0.92496 | 1026.5169
2017-08-15 15:00 | 8 | 15 | 1.004 | 1114.2172
2017-08-15 16:00 | 8 | 16 | 1.1934 | 1324.3963
2017-08-15 17:00 | 8 | 17 | 1.2933 | 1435.3459
2017-08-15 18:00 | 8 | 18 | 1.2937 | 1435.7896
2017-08-15 19:00 | 8 | 19 | 1.4864 | 1649.5692
2017-08-15 20:00 | 8 | 20 | 1.5762 | 1749.2738
2017-08-15 21:00 | 8 | 21 | 1.235 | 1370.5603
2017-08-15 22:00 | 8 | 22 | 0.92648 | 1028.2144
2017-08-15 23:00 | 8 | 23 | 0.59326 | 658.403
2017-08-16 | 8 | 0 | 0.48876 | 542.4289
2017-08-16 01:00 | 8 | 1 | 0.44304 | 491.6845
2017-08-16 02:00 | 8 | 2 | 0.43735 | 485.3683
2017-08-16 03:00 | 8 | 3 | 0.43013 | 477.3544
2017-08-16 04:00 | 8 | 4 | 0.4708 | 522.4945
2017-08-16 05:00 | 8 | 5 | 0.58827 | 652.8607
2017-08-16 06:00 | 8 | 6 | 0.75105 | 833.5182
2017-08-16 07:00 | 8 | 7 | 0.63308 | 702.5987
2017-08-16 08:00 | 8 | 8 | 0.49739 | 551.9992
2017-08-16 09:00 | 8 | 9 | 0.52468 | 582.2856
2017-08-16 10:00 | 8 | 10 | 0.64374 | 714.419
2017-08-16 11:00 | 8 | 11 | 0.78998 | 876.7197
2017-08-16 12:00 | 8 | 12 | 0.9693 | 1075.7253
2017-08-16 13:00 | 8 | 13 | 1.1648 | 1292.7084
2017-08-16 14:00 | 8 | 14 | 1.2986 | 1441.1681
2017-08-16 15:00 | 8 | 15 | 1.4375 | 1595.3429
2017-08-16 16:00 | 8 | 16 | 1.5651 | 1736.9377
2017-08-16 17:00 | 8 | 17 | 1.5094 | 1675.0803
2017-08-16 18:00 | 8 | 18 | 1.4306 | 1587.7109
2017-08-16 19:00 | 8 | 19 | 1.6116 | 1788.5391
2017-08-16 20:00 | 8 | 20 | 1.6914 | 1877.0651
2017-08-16 21:00 | 8 | 21 | 1.3118 | 1455.8218
2017-08-16 22:00 | 8 | 22 | 0.96174 | 1067.3453
2017-08-16 23:00 | 8 | 23 | 0.6116 | 678.7529
2017-08-17 | 8 | 0 | 0.48876 | 542.4289
2017-08-17 01:00 | 8 | 1 | 0.44304 | 491.6845
2017-08-17 02:00 | 8 | 2 | 0.43735 | 485.3683
2017-08-17 03:00 | 8 | 3 | 0.43013 | 477.3544
2017-08-17 04:00 | 8 | 4 | 0.4708 | 522.4945
2017-08-17 05:00 | 8 | 5 | 0.58827 | 652.8607
2017-08-17 06:00 | 8 | 6 | 0.75105 | 833.5182
2017-08-17 07:00 | 8 | 7 | 0.63308 | 702.5987
2017-08-17 08:00 | 8 | 8 | 0.49739 | 551.9992
2017-08-17 09:00 | 8 | 9 | 0.47635 | 528.6546
2017-08-17 10:00 | 8 | 10 | 0.48512 | 538.3902
2017-08-17 11:00 | 8 | 11 | 0.49286 | 546.9775
2017-08-17 12:00 | 8 | 12 | 0.55657 | 617.6812
2017-08-17 13:00 | 8 | 13 | 0.66163 | 734.2836
2017-08-17 14:00 | 8 | 14 | 0.7597 | 843.1165
2017-08-17 15:00 | 8 | 15 | 0.90658 | 1006.1235
2017-08-17 16:00 | 8 | 16 | 1.0477 | 1162.7626
2017-08-17 17:00 | 8 | 17 | 1.1766 | 1305.7673
2017-08-17 18:00 | 8 | 18 | 1.1727 | 1301.4915
2017-08-17 19:00 | 8 | 19 | 1.3759 | 1526.9762
2017-08-17 20:00 | 8 | 20 | 1.4627 | 1623.2619
2017-08-17 21:00 | 8 | 21 | 1.1016 | 1222.5414
2017-08-17 22:00 | 8 | 22 | 0.84974 | 943.0393
2017-08-17 23:00 | 8 | 23 | 0.59326 | 658.403
2017-08-18 | 8 | 0 | 0.48876 | 542.4289
2017-08-18 01:00 | 8 | 1 | 0.44304 | 491.6845
2017-08-18 02:00 | 8 | 2 | 0.43735 | 485.3683
2017-08-18 03:00 | 8 | 3 | 0.43013 | 477.3544
2017-08-18 04:00 | 8 | 4 | 0.4708 | 522.4945
2017-08-18 05:00 | 8 | 5 | 0.58827 | 652.8607
2017-08-18 06:00 | 8 | 6 | 0.75105 | 833.5182
2017-08-18 07:00 | 8 | 7 | 0.63308 | 702.5987
2017-08-18 08:00 | 8 | 8 | 0.49739 | 551.9992
2017-08-18 09:00 | 8 | 9 | 0.47635 | 528.6546
2017-08-18 10:00 | 8 | 10 | 0.48512 | 538.3902
2017-08-18 11:00 | 8 | 11 | 0.49201 | 546.0322
2017-08-18 12:00 | 8 | 12 | 0.48837 | 541.9898
2017-08-18 13:00 | 8 | 13 | 0.50078 | 555.7691
2017-08-18 14:00 | 8 | 14 | 0.53374 | 592.3428
2017-08-18 15:00 | 8 | 15 | 0.64237 | 712.9064
2017-08-18 16:00 | 8 | 16 | 0.8224 | 912.6975
2017-08-18 17:00 | 8 | 17 | 0.92114 | 1022.2799
2017-08-18 18:00 | 8 | 18 | 0.99615 | 1105.5251
2017-08-18 19:00 | 8 | 19 | 1.2154 | 1348.8568
2017-08-18 20:00 | 8 | 20 | 1.3498 | 1497.9841
2017-08-18 21:00 | 8 | 21 | 1.0832 | 1202.0895
2017-08-18 22:00 | 8 | 22 | 0.84974 | 943.0393
2017-08-18 23:00 | 8 | 23 | 0.59326 | 658.403
2017-08-19 | 8 | 0 | 0.51152 | 567.6829
2017-08-19 01:00 | 8 | 1 | 0.45819 | 508.5029
2017-08-19 02:00 | 8 | 2 | 0.44539 | 494.2995
2017-08-19 03:00 | 8 | 3 | 0.44532 | 494.2213
2017-08-19 04:00 | 8 | 4 | 0.49495 | 549.2912
2017-08-19 05:00 | 8 | 5 | 0.64988 | 721.2371
2017-08-19 06:00 | 8 | 6 | 0.87207 | 967.8272
2017-08-19 07:00 | 8 | 7 | 0.82042 | 910.5069
2017-08-19 08:00 | 8 | 8 | 0.75483 | 837.7118
2017-08-19 09:00 | 8 | 9 | 0.7646 | 848.5507
2017-08-19 10:00 | 8 | 10 | 0.78055 | 866.2598
2017-08-19 11:00 | 8 | 11 | 0.76068 | 844.2019
2017-08-19 12:00 | 8 | 12 | 0.73477 | 815.4479
2017-08-19 13:00 | 8 | 13 | 0.72132 | 800.5231
2017-08-19 14:00 | 8 | 14 | 0.74267 | 824.2197
2017-08-19 15:00 | 8 | 15 | 0.84535 | 938.166
2017-08-19 16:00 | 8 | 16 | 1.0243 | 1136.7338
2017-08-19 17:00 | 8 | 17 | 1.1325 | 1256.8129
2017-08-19 18:00 | 8 | 18 | 1.2022 | 1334.2385
2017-08-19 19:00 | 8 | 19 | 1.4214 | 1577.4792
2017-08-19 20:00 | 8 | 20 | 1.5559 | 1726.7387
2017-08-19 21:00 | 8 | 21 | 1.2455 | 1382.2762
2017-08-19 22:00 | 8 | 22 | 0.93995 | 1043.1531
2017-08-19 23:00 | 8 | 23 | 0.63183 | 701.2041
2017-08-20 | 8 | 0 | 0.51152 | 567.6829
2017-08-20 01:00 | 8 | 1 | 0.45819 | 508.5029
2017-08-20 02:00 | 8 | 2 | 0.44539 | 494.2995
2017-08-20 03:00 | 8 | 3 | 0.44532 | 494.2213
2017-08-20 04:00 | 8 | 4 | 0.49495 | 549.2912
2017-08-20 05:00 | 8 | 5 | 0.64988 | 721.2371
2017-08-20 06:00 | 8 | 6 | 0.87207 | 967.8272
2017-08-20 07:00 | 8 | 7 | 0.82042 | 910.5069
2017-08-20 08:00 | 8 | 8 | 0.75483 | 837.7118
2017-08-20 09:00 | 8 | 9 | 0.7646 | 848.5507
2017-08-20 10:00 | 8 | 10 | 0.78055 | 866.2598
2017-08-20 11:00 | 8 | 11 | 0.76068 | 844.2019
2017-08-20 12:00 | 8 | 12 | 0.75005 | 832.4086
2017-08-20 13:00 | 8 | 13 | 0.85731 | 951.4452
2017-08-20 14:00 | 8 | 14 | 1.0211 | 1133.2537
2017-08-20 15:00 | 8 | 15 | 1.2293 | 1364.2685
2017-08-20 16:00 | 8 | 16 | 1.4888 | 1652.2303
2017-08-20 17:00 | 8 | 17 | 1.5818 | 1755.4979
2017-08-20 18:00 | 8 | 18 | 1.6073 | 1783.7772
2017-08-20 19:00 | 8 | 19 | 1.7963 | 1993.5834
2017-08-20 20:00 | 8 | 20 | 1.8961 | 2104.3254
2017-08-20 21:00 | 8 | 21 | 1.4943 | 1658.4039
2017-08-20 22:00 | 8 | 22 | 1.092 | 1211.8636
2017-08-20 23:00 | 8 | 23 | 0.67486 | 748.9568
2017-08-21 | 8 | 0 | 0.50757 | 563.3025
2017-08-21 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-21 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-21 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-21 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-21 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-21 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-21 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-21 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-21 09:00 | 8 | 9 | 0.93132 | 1033.5822
2017-08-21 10:00 | 8 | 10 | 0.99792 | 1107.4956
2017-08-21 11:00 | 8 | 11 | 1.117 | 1239.6207
2017-08-21 12:00 | 8 | 12 | 1.2603 | 1398.652
2017-08-21 13:00 | 8 | 13 | 1.3748 | 1525.7172
2017-08-21 14:00 | 8 | 14 | 1.4742 | 1636.1137
2017-08-21 15:00 | 8 | 15 | 1.3376 | 1484.4891
2017-08-21 16:00 | 8 | 16 | 1.6744 | 1858.2803
2017-08-21 17:00 | 8 | 17 | 1.7267 | 1916.2542
2017-08-21 18:00 | 8 | 18 | 1.7164 | 1904.8502
2017-08-21 19:00 | 8 | 19 | 1.8765 | 2082.5563
2017-08-21 20:00 | 8 | 20 | 1.9502 | 2164.3519
2017-08-21 21:00 | 8 | 21 | 1.5669 | 1738.9959
2017-08-21 22:00 | 8 | 22 | 1.1289 | 1252.8076
2017-08-21 23:00 | 8 | 23 | 0.74106 | 822.4311
2017-08-22 | 8 | 0 | 0.54908 | 609.3697
2017-08-22 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-22 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-22 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-22 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-22 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-22 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-22 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-22 08:00 | 8 | 8 | 0.73873 | 819.8383
2017-08-22 09:00 | 8 | 9 | 0.86935 | 964.8066
2017-08-22 10:00 | 8 | 10 | 0.97216 | 1078.9074
2017-08-22 11:00 | 8 | 11 | 1.0551 | 1170.9144
2017-08-22 12:00 | 8 | 12 | 1.1308 | 1254.911
2017-08-22 13:00 | 8 | 13 | 1.2812 | 1421.8858
2017-08-22 14:00 | 8 | 14 | 1.3638 | 1513.5739
2017-08-22 15:00 | 8 | 15 | 1.5373 | 1706.0535
2017-08-22 16:00 | 8 | 16 | 1.52 | 1686.8443
2017-08-22 17:00 | 8 | 17 | 1.587 | 1761.2179
2017-08-22 18:00 | 8 | 18 | 1.584 | 1757.9431
2017-08-22 19:00 | 8 | 19 | 1.7316 | 1921.7866
2017-08-22 20:00 | 8 | 20 | 1.8199 | 2019.711
2017-08-22 21:00 | 8 | 21 | 1.4212 | 1577.2501
2017-08-22 22:00 | 8 | 22 | 1.0067 | 1117.284
2017-08-22 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-23 | 8 | 0 | 0.50757 | 563.3025
2017-08-23 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-23 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-23 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-23 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-23 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-23 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-23 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-23 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-23 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-23 10:00 | 8 | 10 | 0.75206 | 834.6337
2017-08-23 11:00 | 8 | 11 | 0.81592 | 905.5093
2017-08-23 12:00 | 8 | 12 | 0.91456 | 1014.9819
2017-08-23 13:00 | 8 | 13 | 1.1233 | 1246.6308
2017-08-23 14:00 | 8 | 14 | 1.2382 | 1374.1413
2017-08-23 15:00 | 8 | 15 | 1.4545 | 1614.2242
2017-08-23 16:00 | 8 | 16 | 1.5018 | 1666.7549
2017-08-23 17:00 | 8 | 17 | 1.573 | 1745.6785
2017-08-23 18:00 | 8 | 18 | 1.5884 | 1762.8043
2017-08-23 19:00 | 8 | 19 | 1.7292 | 1919.1094
2017-08-23 20:00 | 8 | 20 | 1.7771 | 1972.2261
2017-08-23 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-23 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-23 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-24 | 8 | 0 | 0.50757 | 563.3025
2017-08-24 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-24 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-24 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-24 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-24 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-24 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-24 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-24 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-24 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-24 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-24 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-24 12:00 | 8 | 12 | 0.71662 | 795.3047
2017-08-24 13:00 | 8 | 13 | 0.80926 | 898.1199
2017-08-24 14:00 | 8 | 14 | 0.92995 | 1032.0594
2017-08-24 15:00 | 8 | 15 | 1.1043 | 1225.5569
2017-08-24 16:00 | 8 | 16 | 1.3347 | 1481.2755
2017-08-24 17:00 | 8 | 17 | 1.4099 | 1564.731
2017-08-24 18:00 | 8 | 18 | 1.4163 | 1571.8451
2017-08-24 19:00 | 8 | 19 | 1.5439 | 1713.4077
2017-08-24 20:00 | 8 | 20 | 1.6059 | 1782.2691
2017-08-24 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-24 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-24 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-25 | 8 | 0 | 0.50757 | 563.3025
2017-08-25 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-25 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-25 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-25 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-25 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-25 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-25 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-25 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-25 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-25 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-25 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-25 12:00 | 8 | 12 | 0.69118 | 767.0738
2017-08-25 13:00 | 8 | 13 | 0.6822 | 757.1015
2017-08-25 14:00 | 8 | 14 | 0.70561 | 783.0916
2017-08-25 15:00 | 8 | 15 | 0.80943 | 898.3042
2017-08-25 16:00 | 8 | 16 | 0.98892 | 1097.5002
2017-08-25 17:00 | 8 | 17 | 1.0893 | 1208.8791
2017-08-25 18:00 | 8 | 18 | 1.168 | 1296.2336
2017-08-25 19:00 | 8 | 19 | 1.3866 | 1538.7967
2017-08-25 20:00 | 8 | 20 | 1.5203 | 1687.2222
2017-08-25 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-25 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-25 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-26 | 8 | 0 | 0.51152 | 567.6829
2017-08-26 01:00 | 8 | 1 | 0.45819 | 508.5029
2017-08-26 02:00 | 8 | 2 | 0.44539 | 494.2995
2017-08-26 03:00 | 8 | 3 | 0.44532 | 494.2213
2017-08-26 04:00 | 8 | 4 | 0.49495 | 549.2912
2017-08-26 05:00 | 8 | 5 | 0.64988 | 721.2371
2017-08-26 06:00 | 8 | 6 | 0.87207 | 967.8272
2017-08-26 07:00 | 8 | 7 | 0.82042 | 910.5069
2017-08-26 08:00 | 8 | 8 | 0.75483 | 837.7118
2017-08-26 09:00 | 8 | 9 | 0.7646 | 848.5507
2017-08-26 10:00 | 8 | 10 | 0.78055 | 866.2598
2017-08-26 11:00 | 8 | 11 | 0.76068 | 844.2019
2017-08-26 12:00 | 8 | 12 | 0.73477 | 815.4479
2017-08-26 13:00 | 8 | 13 | 0.72132 | 800.5231
2017-08-26 14:00 | 8 | 14 | 0.74267 | 824.2197
2017-08-26 15:00 | 8 | 15 | 0.84535 | 938.166
2017-08-26 16:00 | 8 | 16 | 1.0243 | 1136.7338
2017-08-26 17:00 | 8 | 17 | 1.1236 | 1246.9568
2017-08-26 18:00 | 8 | 18 | 1.2022 | 1334.2385
2017-08-26 19:00 | 8 | 19 | 1.4214 | 1577.4792
2017-08-26 20:00 | 8 | 20 | 1.5559 | 1726.7387
2017-08-26 21:00 | 8 | 21 | 1.2455 | 1382.2762
2017-08-26 22:00 | 8 | 22 | 0.93995 | 1043.1531
2017-08-26 23:00 | 8 | 23 | 0.63183 | 701.2041
2017-08-27 | 8 | 0 | 0.51152 | 567.6829
2017-08-27 01:00 | 8 | 1 | 0.45819 | 508.5029
2017-08-27 02:00 | 8 | 2 | 0.44539 | 494.2995
2017-08-27 03:00 | 8 | 3 | 0.44532 | 494.2213
2017-08-27 04:00 | 8 | 4 | 0.49495 | 549.2912
2017-08-27 05:00 | 8 | 5 | 0.64988 | 721.2371
2017-08-27 06:00 | 8 | 6 | 0.87207 | 967.8272
2017-08-27 07:00 | 8 | 7 | 0.82042 | 910.5069
2017-08-27 08:00 | 8 | 8 | 0.75483 | 837.7118
2017-08-27 09:00 | 8 | 9 | 0.7646 | 848.5507
2017-08-27 10:00 | 8 | 10 | 0.78055 | 866.2598
2017-08-27 11:00 | 8 | 11 | 0.76068 | 844.2019
2017-08-27 12:00 | 8 | 12 | 0.73477 | 815.4479
2017-08-27 13:00 | 8 | 13 | 0.72132 | 800.5231
2017-08-27 14:00 | 8 | 14 | 0.74267 | 824.2197
2017-08-27 15:00 | 8 | 15 | 0.84535 | 938.166
2017-08-27 16:00 | 8 | 16 | 1.0243 | 1136.7338
2017-08-27 17:00 | 8 | 17 | 1.1236 | 1246.9568
2017-08-27 18:00 | 8 | 18 | 1.2022 | 1334.2385
2017-08-27 19:00 | 8 | 19 | 1.4214 | 1577.4792
2017-08-27 20:00 | 8 | 20 | 1.5559 | 1726.7387
2017-08-27 21:00 | 8 | 21 | 1.2455 | 1382.2762
2017-08-27 22:00 | 8 | 22 | 0.93995 | 1043.1531
2017-08-27 23:00 | 8 | 23 | 0.63183 | 701.2041
2017-08-28 | 8 | 0 | 0.50757 | 563.3025
2017-08-28 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-28 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-28 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-28 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-28 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-28 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-28 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-28 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-28 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-28 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-28 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-28 12:00 | 8 | 12 | 0.69118 | 767.0738
2017-08-28 13:00 | 8 | 13 | 0.6822 | 757.1015
2017-08-28 14:00 | 8 | 14 | 0.70561 | 783.0916
2017-08-28 15:00 | 8 | 15 | 0.80943 | 898.3042
2017-08-28 16:00 | 8 | 16 | 0.98892 | 1097.5002
2017-08-28 17:00 | 8 | 17 | 1.0893 | 1208.8791
2017-08-28 18:00 | 8 | 18 | 1.168 | 1296.2336
2017-08-28 19:00 | 8 | 19 | 1.3866 | 1538.7967
2017-08-28 20:00 | 8 | 20 | 1.5203 | 1687.2222
2017-08-28 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-28 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-28 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-29 | 8 | 0 | 0.50757 | 563.3025
2017-08-29 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-29 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-29 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-29 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-29 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-29 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-29 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-29 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-29 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-29 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-29 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-29 12:00 | 8 | 12 | 0.69118 | 767.0738
2017-08-29 13:00 | 8 | 13 | 0.6822 | 757.1015
2017-08-29 14:00 | 8 | 14 | 0.70561 | 783.0916
2017-08-29 15:00 | 8 | 15 | 0.80943 | 898.3042
2017-08-29 16:00 | 8 | 16 | 0.98892 | 1097.5002
2017-08-29 17:00 | 8 | 17 | 1.0893 | 1208.8791
2017-08-29 18:00 | 8 | 18 | 1.168 | 1296.2336
2017-08-29 19:00 | 8 | 19 | 1.3866 | 1538.7967
2017-08-29 20:00 | 8 | 20 | 1.5203 | 1687.2222
2017-08-29 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-29 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-29 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-30 | 8 | 0 | 0.50757 | 563.3025
2017-08-30 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-30 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-30 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-30 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-30 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-30 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-30 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-30 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-30 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-30 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-30 11:00 | 8 | 11 | 0.71526 | 793.8011
2017-08-30 12:00 | 8 | 12 | 0.86385 | 958.7037
2017-08-30 13:00 | 8 | 13 | 1.0296 | 1142.6456
2017-08-30 14:00 | 8 | 14 | 1.1382 | 1263.1965
2017-08-30 15:00 | 8 | 15 | 1.2914 | 1433.1599
2017-08-30 16:00 | 8 | 16 | 1.599 | 1774.5914
2017-08-30 17:00 | 8 | 17 | 1.6117 | 1788.6356
2017-08-30 18:00 | 8 | 18 | 1.5677 | 1739.8305
2017-08-30 19:00 | 8 | 19 | 1.5786 | 1751.9435
2017-08-30 20:00 | 8 | 20 | 1.5203 | 1687.2222
2017-08-30 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-30 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-30 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-08-31 | 8 | 0 | 0.50757 | 563.3025
2017-08-31 01:00 | 8 | 1 | 0.45558 | 505.605
2017-08-31 02:00 | 8 | 2 | 0.44403 | 492.7842
2017-08-31 03:00 | 8 | 3 | 0.44265 | 491.2568
2017-08-31 04:00 | 8 | 4 | 0.49085 | 544.7447
2017-08-31 05:00 | 8 | 5 | 0.63925 | 709.4449
2017-08-31 06:00 | 8 | 6 | 0.85091 | 944.3422
2017-08-31 07:00 | 8 | 7 | 0.78799 | 874.5079
2017-08-31 08:00 | 8 | 8 | 0.7098 | 787.7362
2017-08-31 09:00 | 8 | 9 | 0.71368 | 792.0438
2017-08-31 10:00 | 8 | 10 | 0.72807 | 808.0077
2017-08-31 11:00 | 8 | 11 | 0.71287 | 791.1417
2017-08-31 12:00 | 8 | 12 | 0.69118 | 767.0738
2017-08-31 13:00 | 8 | 13 | 0.7275 | 807.3845
2017-08-31 14:00 | 8 | 14 | 0.7994 | 887.1798
2017-08-31 15:00 | 8 | 15 | 0.96133 | 1066.8809
2017-08-31 16:00 | 8 | 16 | 1.1761 | 1305.2855
2017-08-31 17:00 | 8 | 17 | 1.2739 | 1413.8047
2017-08-31 18:00 | 8 | 18 | 1.3209 | 1465.8874
2017-08-31 19:00 | 8 | 19 | 1.5302 | 1698.2568
2017-08-31 20:00 | 8 | 20 | 1.5858 | 1759.9233
2017-08-31 21:00 | 8 | 21 | 1.2172 | 1350.8763
2017-08-31 22:00 | 8 | 22 | 0.92441 | 1025.9125
2017-08-31 23:00 | 8 | 23 | 0.62525 | 693.9086
2017-09-01 | 9 | 0 | 0.51054 | 566.5941
2017-09-01 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-01 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-01 03:00 | 9 | 3 | 0.44343 | 492.1242
2017-09-01 04:00 | 9 | 4 | 0.4927 | 546.7972
2017-09-01 05:00 | 9 | 5 | 0.66282 | 735.5954
2017-09-01 06:00 | 9 | 6 | 0.91212 | 1012.2696
2017-09-01 07:00 | 9 | 7 | 0.84948 | 942.7518
2017-09-01 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-01 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-01 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-01 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-01 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-01 13:00 | 9 | 13 | 0.71963 | 798.6484
2017-09-01 14:00 | 9 | 14 | 0.75779 | 840.9937
2017-09-01 15:00 | 9 | 15 | 0.93969 | 1042.8724
2017-09-01 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-01 17:00 | 9 | 17 | 1.3288 | 1474.6892
2017-09-01 18:00 | 9 | 18 | 1.509 | 1674.6483
2017-09-01 19:00 | 9 | 19 | 1.7489 | 1940.967
2017-09-01 20:00 | 9 | 20 | 1.6264 | 1804.9698
2017-09-01 21:00 | 9 | 21 | 1.245 | 1381.707
2017-09-01 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-01 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-02 | 9 | 0 | 0.51448 | 570.9746
2017-09-02 01:00 | 9 | 1 | 0.45907 | 509.4806
2017-09-02 02:00 | 9 | 2 | 0.44626 | 495.2568
2017-09-02 03:00 | 9 | 3 | 0.44611 | 495.0887
2017-09-02 04:00 | 9 | 4 | 0.49679 | 551.3437
2017-09-02 05:00 | 9 | 5 | 0.67344 | 747.3876
2017-09-02 06:00 | 9 | 6 | 0.93328 | 1035.7545
2017-09-02 07:00 | 9 | 7 | 0.88192 | 978.7508
2017-09-02 08:00 | 9 | 8 | 0.78585 | 872.1367
2017-09-02 09:00 | 9 | 9 | 0.78632 | 872.6558
2017-09-02 10:00 | 9 | 10 | 0.80221 | 890.2934
2017-09-02 11:00 | 9 | 11 | 0.78225 | 868.1401
2017-09-02 12:00 | 9 | 12 | 0.75648 | 839.5413
2017-09-02 13:00 | 9 | 13 | 0.74312 | 824.7175
2017-09-02 14:00 | 9 | 14 | 0.76443 | 848.3673
2017-09-02 15:00 | 9 | 15 | 0.87355 | 969.4648
2017-09-02 16:00 | 9 | 16 | 1.0818 | 1200.6209
2017-09-02 17:00 | 9 | 17 | 1.2434 | 1379.937
2017-09-02 18:00 | 9 | 18 | 1.4005 | 1554.3325
2017-09-02 19:00 | 9 | 19 | 1.6466 | 1827.4188
2017-09-02 20:00 | 9 | 20 | 1.5648 | 1736.6081
2017-09-02 21:00 | 9 | 21 | 1.2548 | 1392.5539
2017-09-02 22:00 | 9 | 22 | 0.95118 | 1055.6227
2017-09-02 23:00 | 9 | 23 | 0.6489 | 720.1527
2017-09-03 | 9 | 0 | 0.53879 | 597.9517
2017-09-03 01:00 | 9 | 1 | 0.49072 | 544.6031
2017-09-03 02:00 | 9 | 2 | 0.48376 | 536.8763
2017-09-03 03:00 | 9 | 3 | 0.48969 | 543.4596
2017-09-03 04:00 | 9 | 4 | 0.54293 | 602.543
2017-09-03 05:00 | 9 | 5 | 0.71627 | 794.9132
2017-09-03 06:00 | 9 | 6 | 0.96906 | 1075.4681
2017-09-03 07:00 | 9 | 7 | 0.91468 | 1015.1178
2017-09-03 08:00 | 9 | 8 | 0.80837 | 897.1276
2017-09-03 09:00 | 9 | 9 | 0.80152 | 889.5336
2017-09-03 10:00 | 9 | 10 | 0.80221 | 890.2934
2017-09-03 11:00 | 9 | 11 | 0.78225 | 868.1401
2017-09-03 12:00 | 9 | 12 | 0.75648 | 839.5413
2017-09-03 13:00 | 9 | 13 | 0.74312 | 824.7175
2017-09-03 14:00 | 9 | 14 | 0.76443 | 848.3673
2017-09-03 15:00 | 9 | 15 | 0.87355 | 969.4648
2017-09-03 16:00 | 9 | 16 | 1.0793 | 1197.7983
2017-09-03 17:00 | 9 | 17 | 1.2434 | 1379.937
2017-09-03 18:00 | 9 | 18 | 1.4005 | 1554.3325
2017-09-03 19:00 | 9 | 19 | 1.6466 | 1827.4188
2017-09-03 20:00 | 9 | 20 | 1.5648 | 1736.6081
2017-09-03 21:00 | 9 | 21 | 1.2548 | 1392.5539
2017-09-03 22:00 | 9 | 22 | 0.94786 | 1051.9359
2017-09-03 23:00 | 9 | 23 | 0.63452 | 704.1876
2017-09-04 | 9 | 0 | 0.51128 | 567.4246
2017-09-04 01:00 | 9 | 1 | 0.466 | 517.1632
2017-09-04 02:00 | 9 | 2 | 0.4636 | 514.4986
2017-09-04 03:00 | 9 | 3 | 0.46873 | 520.2015
2017-09-04 04:00 | 9 | 4 | 0.52213 | 579.4622
2017-09-04 05:00 | 9 | 5 | 0.69765 | 774.2539
2017-09-04 06:00 | 9 | 6 | 0.93733 | 1040.2518
2017-09-04 07:00 | 9 | 7 | 0.8692 | 964.6345
2017-09-04 08:00 | 9 | 8 | 0.74846 | 830.6416
2017-09-04 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-04 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-04 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-04 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-04 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-04 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-04 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-04 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-04 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-04 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-04 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-04 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-04 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-04 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-04 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-05 | 9 | 0 | 0.51054 | 566.5941
2017-09-05 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-05 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-05 03:00 | 9 | 3 | 0.44343 | 492.1242
2017-09-05 04:00 | 9 | 4 | 0.4927 | 546.7972
2017-09-05 05:00 | 9 | 5 | 0.66282 | 735.5954
2017-09-05 06:00 | 9 | 6 | 0.91212 | 1012.2696
2017-09-05 07:00 | 9 | 7 | 0.84948 | 942.7518
2017-09-05 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-05 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-05 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-05 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-05 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-05 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-05 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-05 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-05 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-05 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-05 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-05 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-05 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-05 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-05 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-05 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-06 | 9 | 0 | 0.51054 | 566.5941
2017-09-06 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-06 02:00 | 9 | 2 | 0.45071 | 500.2025
2017-09-06 03:00 | 9 | 3 | 0.45799 | 508.2813
2017-09-06 04:00 | 9 | 4 | 0.51357 | 569.9575
2017-09-06 05:00 | 9 | 5 | 0.68437 | 759.5104
2017-09-06 06:00 | 9 | 6 | 0.93368 | 1036.2043
2017-09-06 07:00 | 9 | 7 | 0.87097 | 966.6075
2017-09-06 08:00 | 9 | 8 | 0.75447 | 837.3074
2017-09-06 09:00 | 9 | 9 | 0.74675 | 828.7399
2017-09-06 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-06 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-06 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-06 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-06 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-06 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-06 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-06 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-06 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-06 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-06 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-06 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-06 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-06 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-07 | 9 | 0 | 0.51738 | 574.1877
2017-09-07 01:00 | 9 | 1 | 0.47699 | 529.3589
2017-09-07 02:00 | 9 | 2 | 0.47274 | 524.6515
2017-09-07 03:00 | 9 | 3 | 0.47787 | 530.336
2017-09-07 04:00 | 9 | 4 | 0.5353 | 594.0815
2017-09-07 05:00 | 9 | 5 | 0.70308 | 780.2832
2017-09-07 06:00 | 9 | 6 | 0.94631 | 1050.2159
2017-09-07 07:00 | 9 | 7 | 0.8767 | 972.9603
2017-09-07 08:00 | 9 | 8 | 0.75619 | 839.219
2017-09-07 09:00 | 9 | 9 | 0.74067 | 821.9941
2017-09-07 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-07 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-07 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-07 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-07 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-07 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-07 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-07 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-07 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-07 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-07 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-07 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-07 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-07 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-08 | 9 | 0 | 0.51054 | 566.5941
2017-09-08 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-08 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-08 03:00 | 9 | 3 | 0.44487 | 493.7194
2017-09-08 04:00 | 9 | 4 | 0.4999 | 554.7864
2017-09-08 05:00 | 9 | 5 | 0.6773 | 751.6734
2017-09-08 06:00 | 9 | 6 | 0.91901 | 1019.9166
2017-09-08 07:00 | 9 | 7 | 0.85152 | 945.0147
2017-09-08 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-08 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-08 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-08 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-08 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-08 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-08 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-08 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-08 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-08 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-08 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-08 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-08 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-08 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-08 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-08 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-09 | 9 | 0 | 0.51598 | 572.6371
2017-09-09 01:00 | 9 | 1 | 0.46795 | 519.3267
2017-09-09 02:00 | 9 | 2 | 0.46767 | 519.0204
2017-09-09 03:00 | 9 | 3 | 0.47744 | 529.8632
2017-09-09 04:00 | 9 | 4 | 0.53281 | 591.3111
2017-09-09 05:00 | 9 | 5 | 0.70846 | 786.2479
2017-09-09 06:00 | 9 | 6 | 0.96374 | 1069.5569
2017-09-09 07:00 | 9 | 7 | 0.90437 | 1003.6735
2017-09-09 08:00 | 9 | 8 | 0.79747 | 885.0327
2017-09-09 09:00 | 9 | 9 | 0.79073 | 877.5491
2017-09-09 10:00 | 9 | 10 | 0.80221 | 890.2934
2017-09-09 11:00 | 9 | 11 | 0.78225 | 868.1401
2017-09-09 12:00 | 9 | 12 | 0.75648 | 839.5413
2017-09-09 13:00 | 9 | 13 | 0.74312 | 824.7175
2017-09-09 14:00 | 9 | 14 | 0.76443 | 848.3673
2017-09-09 15:00 | 9 | 15 | 0.87355 | 969.4648
2017-09-09 16:00 | 9 | 16 | 1.0793 | 1197.7983
2017-09-09 17:00 | 9 | 17 | 1.2434 | 1379.937
2017-09-09 18:00 | 9 | 18 | 1.4005 | 1554.3325
2017-09-09 19:00 | 9 | 19 | 1.6466 | 1827.4188
2017-09-09 20:00 | 9 | 20 | 1.5648 | 1736.6081
2017-09-09 21:00 | 9 | 21 | 1.2548 | 1392.5539
2017-09-09 22:00 | 9 | 22 | 0.94786 | 1051.9359
2017-09-09 23:00 | 9 | 23 | 0.63452 | 704.1876
2017-09-10 | 9 | 0 | 0.51448 | 570.9746
2017-09-10 01:00 | 9 | 1 | 0.45907 | 509.4806
2017-09-10 02:00 | 9 | 2 | 0.45232 | 501.9828
2017-09-10 03:00 | 9 | 3 | 0.4594 | 509.8418
2017-09-10 04:00 | 9 | 4 | 0.51341 | 569.7853
2017-09-10 05:00 | 9 | 5 | 0.68936 | 765.0555
2017-09-10 06:00 | 9 | 6 | 0.94439 | 1048.0805
2017-09-10 07:00 | 9 | 7 | 0.88808 | 985.5895
2017-09-10 08:00 | 9 | 8 | 0.78585 | 872.1367
2017-09-10 09:00 | 9 | 9 | 0.78632 | 872.6558
2017-09-10 10:00 | 9 | 10 | 0.80221 | 890.2934
2017-09-10 11:00 | 9 | 11 | 0.78225 | 868.1401
2017-09-10 12:00 | 9 | 12 | 0.75648 | 839.5413
2017-09-10 13:00 | 9 | 13 | 0.74312 | 824.7175
2017-09-10 14:00 | 9 | 14 | 0.76443 | 848.3673
2017-09-10 15:00 | 9 | 15 | 0.87355 | 969.4648
2017-09-10 16:00 | 9 | 16 | 1.0793 | 1197.7983
2017-09-10 17:00 | 9 | 17 | 1.2434 | 1379.937
2017-09-10 18:00 | 9 | 18 | 1.4005 | 1554.3325
2017-09-10 19:00 | 9 | 19 | 1.6466 | 1827.4188
2017-09-10 20:00 | 9 | 20 | 1.5648 | 1736.6081
2017-09-10 21:00 | 9 | 21 | 1.2548 | 1392.5539
2017-09-10 22:00 | 9 | 22 | 0.94786 | 1051.9359
2017-09-10 23:00 | 9 | 23 | 0.63452 | 704.1876
2017-09-11 | 9 | 0 | 0.51054 | 566.5941
2017-09-11 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-11 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-11 03:00 | 9 | 3 | 0.44343 | 492.1242
2017-09-11 04:00 | 9 | 4 | 0.4927 | 546.7972
2017-09-11 05:00 | 9 | 5 | 0.6674 | 740.6854
2017-09-11 06:00 | 9 | 6 | 0.91212 | 1012.2696
2017-09-11 07:00 | 9 | 7 | 0.84948 | 942.7518
2017-09-11 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-11 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-11 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-11 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-11 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-11 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-11 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-11 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-11 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-11 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-11 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-11 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-11 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-11 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-11 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-11 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-12 | 9 | 0 | 0.51054 | 566.5941
2017-09-12 01:00 | 9 | 1 | 0.46401 | 514.9565
2017-09-12 02:00 | 9 | 2 | 0.45947 | 509.9256
2017-09-12 03:00 | 9 | 3 | 0.46587 | 517.0204
2017-09-12 04:00 | 9 | 4 | 0.52045 | 577.5929
2017-09-12 05:00 | 9 | 5 | 0.68968 | 765.4076
2017-09-12 06:00 | 9 | 6 | 0.93804 | 1041.0381
2017-09-12 07:00 | 9 | 7 | 0.87228 | 968.0568
2017-09-12 08:00 | 9 | 8 | 0.75362 | 836.364
2017-09-12 09:00 | 9 | 9 | 0.74082 | 822.1614
2017-09-12 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-12 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-12 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-12 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-12 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-12 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-12 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-12 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-12 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-12 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-12 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-12 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-12 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-12 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-13 | 9 | 0 | 0.51054 | 566.5941
2017-09-13 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-13 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-13 03:00 | 9 | 3 | 0.4467 | 495.7492
2017-09-13 04:00 | 9 | 4 | 0.5024 | 557.5622
2017-09-13 05:00 | 9 | 5 | 0.67309 | 746.9951
2017-09-13 06:00 | 9 | 6 | 0.91875 | 1019.627
2017-09-13 07:00 | 9 | 7 | 0.85321 | 946.8923
2017-09-13 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-13 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-13 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-13 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-13 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-13 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-13 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-13 15:00 | 9 | 15 | 0.91251 | 1012.7042
2017-09-13 16:00 | 9 | 16 | 1.2482 | 1385.2061
2017-09-13 17:00 | 9 | 17 | 1.4174 | 1572.9978
2017-09-13 18:00 | 9 | 18 | 1.567 | 1739.1109
2017-09-13 19:00 | 9 | 19 | 1.7953 | 1992.4794
2017-09-13 20:00 | 9 | 20 | 1.6502 | 1831.4478
2017-09-13 21:00 | 9 | 21 | 1.2577 | 1395.8203
2017-09-13 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-13 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-14 | 9 | 0 | 0.51054 | 566.5941
2017-09-14 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-14 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-14 03:00 | 9 | 3 | 0.44343 | 492.1242
2017-09-14 04:00 | 9 | 4 | 0.4927 | 546.7972
2017-09-14 05:00 | 9 | 5 | 0.66282 | 735.5954
2017-09-14 06:00 | 9 | 6 | 0.91212 | 1012.2696
2017-09-14 07:00 | 9 | 7 | 0.84948 | 942.7518
2017-09-14 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-14 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-14 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-14 11:00 | 9 | 11 | 0.78014 | 865.8044
2017-09-14 12:00 | 9 | 12 | 0.94112 | 1044.454
2017-09-14 13:00 | 9 | 13 | 1.1387 | 1263.7279
2017-09-14 14:00 | 9 | 14 | 1.2861 | 1427.2647
2017-09-14 15:00 | 9 | 15 | 1.4294 | 1586.2999
2017-09-14 16:00 | 9 | 16 | 1.7416 | 1932.7818
2017-09-14 17:00 | 9 | 17 | 1.7352 | 1925.6861
2017-09-14 18:00 | 9 | 18 | 1.7846 | 1980.5814
2017-09-14 19:00 | 9 | 19 | 1.9813 | 2198.8694
2017-09-14 20:00 | 9 | 20 | 1.8057 | 2004.0054
2017-09-14 21:00 | 9 | 21 | 1.396 | 1549.2909
2017-09-14 22:00 | 9 | 22 | 1.0143 | 1125.6211
2017-09-14 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-15 | 9 | 0 | 0.51054 | 566.5941
2017-09-15 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-15 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-15 03:00 | 9 | 3 | 0.44343 | 492.1242
2017-09-15 04:00 | 9 | 4 | 0.4927 | 546.7972
2017-09-15 05:00 | 9 | 5 | 0.66282 | 735.5954
2017-09-15 06:00 | 9 | 6 | 0.91212 | 1012.2696
2017-09-15 07:00 | 9 | 7 | 0.84948 | 942.7518
2017-09-15 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-15 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-15 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-15 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-15 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-15 13:00 | 9 | 13 | 0.76274 | 846.4903
2017-09-15 14:00 | 9 | 14 | 0.85039 | 943.7595
2017-09-15 15:00 | 9 | 15 | 1.0085 | 1119.2132
2017-09-15 16:00 | 9 | 16 | 1.275 | 1415.0177
2017-09-15 17:00 | 9 | 17 | 1.4414 | 1599.6242
2017-09-15 18:00 | 9 | 18 | 1.5899 | 1764.5042
2017-09-15 19:00 | 9 | 19 | 1.8049 | 2003.0493
2017-09-15 20:00 | 9 | 20 | 1.6898 | 1875.3266
2017-09-15 21:00 | 9 | 21 | 1.3019 | 1444.8648
2017-09-15 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-15 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-16 | 9 | 0 | 0.51448 | 570.9746
2017-09-16 01:00 | 9 | 1 | 0.45907 | 509.4806
2017-09-16 02:00 | 9 | 2 | 0.44626 | 495.2568
2017-09-16 03:00 | 9 | 3 | 0.44611 | 495.0887
2017-09-16 04:00 | 9 | 4 | 0.49679 | 551.3437
2017-09-16 05:00 | 9 | 5 | 0.67344 | 747.3876
2017-09-16 06:00 | 9 | 6 | 0.93328 | 1035.7545
2017-09-16 07:00 | 9 | 7 | 0.88192 | 978.7508
2017-09-16 08:00 | 9 | 8 | 0.78585 | 872.1367
2017-09-16 09:00 | 9 | 9 | 0.78632 | 872.6558
2017-09-16 10:00 | 9 | 10 | 0.80221 | 890.2934
2017-09-16 11:00 | 9 | 11 | 0.78225 | 868.1401
2017-09-16 12:00 | 9 | 12 | 0.75648 | 839.5413
2017-09-16 13:00 | 9 | 13 | 0.74312 | 824.7175
2017-09-16 14:00 | 9 | 14 | 0.76443 | 848.3673
2017-09-16 15:00 | 9 | 15 | 0.87355 | 969.4648
2017-09-16 16:00 | 9 | 16 | 1.0793 | 1197.7983
2017-09-16 17:00 | 9 | 17 | 1.2434 | 1379.937
2017-09-16 18:00 | 9 | 18 | 1.4005 | 1554.3325
2017-09-16 19:00 | 9 | 19 | 1.6466 | 1827.4188
2017-09-16 20:00 | 9 | 20 | 1.5648 | 1736.6081
2017-09-16 21:00 | 9 | 21 | 1.2548 | 1392.5539
2017-09-16 22:00 | 9 | 22 | 0.94786 | 1051.9359
2017-09-16 23:00 | 9 | 23 | 0.63452 | 704.1876
2017-09-17 | 9 | 0 | 0.51448 | 570.9746
2017-09-17 01:00 | 9 | 1 | 0.45907 | 509.4806
2017-09-17 02:00 | 9 | 2 | 0.44626 | 495.2568
2017-09-17 03:00 | 9 | 3 | 0.44611 | 495.0887
2017-09-17 04:00 | 9 | 4 | 0.49679 | 551.3437
2017-09-17 05:00 | 9 | 5 | 0.67344 | 747.3876
2017-09-17 06:00 | 9 | 6 | 0.93328 | 1035.7545
2017-09-17 07:00 | 9 | 7 | 0.88192 | 978.7508
2017-09-17 08:00 | 9 | 8 | 0.78585 | 872.1367
2017-09-17 09:00 | 9 | 9 | 0.78641 | 872.7539
2017-09-17 10:00 | 9 | 10 | 0.80221 | 890.2934
2017-09-17 11:00 | 9 | 11 | 0.78225 | 868.1401
2017-09-17 12:00 | 9 | 12 | 0.75648 | 839.5413
2017-09-17 13:00 | 9 | 13 | 0.74312 | 824.7175
2017-09-17 14:00 | 9 | 14 | 0.76443 | 848.3673
2017-09-17 15:00 | 9 | 15 | 0.87355 | 969.4648
2017-09-17 16:00 | 9 | 16 | 1.0793 | 1197.7983
2017-09-17 17:00 | 9 | 17 | 1.2434 | 1379.937
2017-09-17 18:00 | 9 | 18 | 1.4005 | 1554.3325
2017-09-17 19:00 | 9 | 19 | 1.6466 | 1827.4188
2017-09-17 20:00 | 9 | 20 | 1.5648 | 1736.6081
2017-09-17 21:00 | 9 | 21 | 1.2548 | 1392.5539
2017-09-17 22:00 | 9 | 22 | 0.94786 | 1051.9359
2017-09-17 23:00 | 9 | 23 | 0.63452 | 704.1876
2017-09-18 | 9 | 0 | 0.51054 | 566.5941
2017-09-18 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-18 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-18 03:00 | 9 | 3 | 0.44343 | 492.1242
2017-09-18 04:00 | 9 | 4 | 0.4927 | 546.7972
2017-09-18 05:00 | 9 | 5 | 0.66282 | 735.5954
2017-09-18 06:00 | 9 | 6 | 0.91212 | 1012.2696
2017-09-18 07:00 | 9 | 7 | 0.84948 | 942.7518
2017-09-18 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-18 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-18 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-18 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-18 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-18 13:00 | 9 | 13 | 0.71227 | 790.4769
2017-09-18 14:00 | 9 | 14 | 0.8147 | 904.1572
2017-09-18 15:00 | 9 | 15 | 1.0126 | 1123.7581
2017-09-18 16:00 | 9 | 16 | 1.2304 | 1365.4461
2017-09-18 17:00 | 9 | 17 | 1.3946 | 1547.7031
2017-09-18 18:00 | 9 | 18 | 1.5384 | 1707.2966
2017-09-18 19:00 | 9 | 19 | 1.7769 | 1971.9988
2017-09-18 20:00 | 9 | 20 | 1.643 | 1823.3741
2017-09-18 21:00 | 9 | 21 | 1.2497 | 1386.9388
2017-09-18 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-18 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-19 | 9 | 0 | 0.51054 | 566.5941
2017-09-19 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-19 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-19 03:00 | 9 | 3 | 0.44343 | 492.1242
2017-09-19 04:00 | 9 | 4 | 0.4927 | 546.7972
2017-09-19 05:00 | 9 | 5 | 0.66282 | 735.5954
2017-09-19 06:00 | 9 | 6 | 0.91212 | 1012.2696
2017-09-19 07:00 | 9 | 7 | 0.84948 | 942.7518
2017-09-19 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-19 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-19 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-19 11:00 | 9 | 11 | 0.7363 | 817.1454
2017-09-19 12:00 | 9 | 12 | 0.84717 | 940.1958
2017-09-19 13:00 | 9 | 13 | 0.93735 | 1040.2722
2017-09-19 14:00 | 9 | 14 | 0.99073 | 1099.5157
2017-09-19 15:00 | 9 | 15 | 1.1551 | 1281.9005
2017-09-19 16:00 | 9 | 16 | 1.3893 | 1541.861
2017-09-19 17:00 | 9 | 17 | 1.5265 | 1694.1049
2017-09-19 18:00 | 9 | 18 | 1.6267 | 1805.3188
2017-09-19 19:00 | 9 | 19 | 1.8247 | 2025.0994
2017-09-19 20:00 | 9 | 20 | 1.7028 | 1889.7435
2017-09-19 21:00 | 9 | 21 | 1.3067 | 1450.1478
2017-09-19 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-19 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-20 | 9 | 0 | 0.51054 | 566.5941
2017-09-20 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-20 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-20 03:00 | 9 | 3 | 0.44343 | 492.1242
2017-09-20 04:00 | 9 | 4 | 0.4927 | 546.7972
2017-09-20 05:00 | 9 | 5 | 0.66282 | 735.5954
2017-09-20 06:00 | 9 | 6 | 0.91212 | 1012.2696
2017-09-20 07:00 | 9 | 7 | 0.84948 | 942.7518
2017-09-20 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-20 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-20 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-20 11:00 | 9 | 11 | 0.78207 | 867.9426
2017-09-20 12:00 | 9 | 12 | 0.95057 | 1054.9446
2017-09-20 13:00 | 9 | 13 | 1.0342 | 1147.7623
2017-09-20 14:00 | 9 | 14 | 1.1131 | 1235.3037
2017-09-20 15:00 | 9 | 15 | 1.2416 | 1377.8854
2017-09-20 16:00 | 9 | 16 | 1.4709 | 1632.3534
2017-09-20 17:00 | 9 | 17 | 1.3855 | 1537.5973
2017-09-20 18:00 | 9 | 18 | 1.6364 | 1816.0378
2017-09-20 19:00 | 9 | 19 | 1.8766 | 2082.6449
2017-09-20 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-20 21:00 | 9 | 21 | 1.2877 | 1429.146
2017-09-20 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-20 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-21 | 9 | 0 | 0.51054 | 566.5941
2017-09-21 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-21 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-21 03:00 | 9 | 3 | 0.44343 | 492.1242
2017-09-21 04:00 | 9 | 4 | 0.4927 | 546.7972
2017-09-21 05:00 | 9 | 5 | 0.66282 | 735.5954
2017-09-21 06:00 | 9 | 6 | 0.91212 | 1012.2696
2017-09-21 07:00 | 9 | 7 | 0.84948 | 942.7518
2017-09-21 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-21 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-21 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-21 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-21 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-21 13:00 | 9 | 13 | 0.72777 | 807.681
2017-09-21 14:00 | 9 | 14 | 0.75852 | 841.8024
2017-09-21 15:00 | 9 | 15 | 0.87148 | 967.166
2017-09-21 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-21 17:00 | 9 | 17 | 1.2589 | 1397.1041
2017-09-21 18:00 | 9 | 18 | 1.3991 | 1552.7149
2017-09-21 19:00 | 9 | 19 | 1.6246 | 1803.0343
2017-09-21 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-21 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-21 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-21 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-22 | 9 | 0 | 0.51054 | 566.5941
2017-09-22 01:00 | 9 | 1 | 0.45646 | 506.5827
2017-09-22 02:00 | 9 | 2 | 0.44489 | 493.7415
2017-09-22 03:00 | 9 | 3 | 0.44493 | 493.7862
2017-09-22 04:00 | 9 | 4 | 0.50196 | 557.0813
2017-09-22 05:00 | 9 | 5 | 0.68331 | 758.3335
2017-09-22 06:00 | 9 | 6 | 0.92511 | 1026.689
2017-09-22 07:00 | 9 | 7 | 0.86001 | 954.4379
2017-09-22 08:00 | 9 | 8 | 0.74702 | 829.0482
2017-09-22 09:00 | 9 | 9 | 0.74011 | 821.3765
2017-09-22 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-22 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-22 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-22 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-22 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-22 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-22 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-22 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-22 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-22 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-22 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-22 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-22 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-22 23:00 | 9 | 23 | 0.63225 | 701.6688
2017-09-23 | 9 | 0 | 0.5299 | 588.0833
2017-09-23 01:00 | 9 | 1 | 0.48337 | 536.4438
2017-09-23 02:00 | 9 | 2 | 0.48001 | 532.7179
2017-09-23 03:00 | 9 | 3 | 0.48984 | 543.6277
2017-09-23 04:00 | 9 | 4 | 0.54528 | 605.1572
2017-09-23 05:00 | 9 | 5 | 0.73236 | 812.7707
2017-09-23 06:00 | 9 | 6 | 0.97981 | 1087.3992
2017-09-23 07:00 | 9 | 7 | 0.91827 | 1019.0949
2017-09-23 08:00 | 9 | 8 | 0.80976 | 898.672
2017-09-23 09:00 | 9 | 9 | 0.80476 | 893.1215
2017-09-23 10:00 | 9 | 10 | 0.80221 | 890.2934
2017-09-23 11:00 | 9 | 11 | 0.78225 | 868.1401
2017-09-23 12:00 | 9 | 12 | 0.75648 | 839.5413
2017-09-23 13:00 | 9 | 13 | 0.74312 | 824.7175
2017-09-23 14:00 | 9 | 14 | 0.76443 | 848.3673
2017-09-23 15:00 | 9 | 15 | 0.87355 | 969.4648
2017-09-23 16:00 | 9 | 16 | 1.0793 | 1197.7983
2017-09-23 17:00 | 9 | 17 | 1.2434 | 1379.937
2017-09-23 18:00 | 9 | 18 | 1.4005 | 1554.3325
2017-09-23 19:00 | 9 | 19 | 1.6466 | 1827.4188
2017-09-23 20:00 | 9 | 20 | 1.5648 | 1736.6081
2017-09-23 21:00 | 9 | 21 | 1.2548 | 1392.5539
2017-09-23 22:00 | 9 | 22 | 0.94786 | 1051.9359
2017-09-23 23:00 | 9 | 23 | 0.63452 | 704.1876
2017-09-24 | 9 | 0 | 0.51448 | 570.9746
2017-09-24 01:00 | 9 | 1 | 0.45907 | 509.4806
2017-09-24 02:00 | 9 | 2 | 0.44626 | 495.2568
2017-09-24 03:00 | 9 | 3 | 0.44903 | 498.3317
2017-09-24 04:00 | 9 | 4 | 0.50585 | 561.3924
2017-09-24 05:00 | 9 | 5 | 0.68891 | 764.5516
2017-09-24 06:00 | 9 | 6 | 0.9437 | 1047.3208
2017-09-24 07:00 | 9 | 7 | 0.8955 | 993.8256
2017-09-24 08:00 | 9 | 8 | 0.80254 | 890.6635
2017-09-24 09:00 | 9 | 9 | 0.80972 | 898.6338
2017-09-24 10:00 | 9 | 10 | 0.80719 | 895.8189
2017-09-24 11:00 | 9 | 11 | 0.78225 | 868.1401
2017-09-24 12:00 | 9 | 12 | 0.75648 | 839.5413
2017-09-24 13:00 | 9 | 13 | 0.74312 | 824.7175
2017-09-24 14:00 | 9 | 14 | 0.76443 | 848.3673
2017-09-24 15:00 | 9 | 15 | 0.87355 | 969.4648
2017-09-24 16:00 | 9 | 16 | 1.0793 | 1197.7983
2017-09-24 17:00 | 9 | 17 | 1.2434 | 1379.937
2017-09-24 18:00 | 9 | 18 | 1.4005 | 1554.3325
2017-09-24 19:00 | 9 | 19 | 1.6466 | 1827.4188
2017-09-24 20:00 | 9 | 20 | 1.5648 | 1736.6081
2017-09-24 21:00 | 9 | 21 | 1.2548 | 1392.5539
2017-09-24 22:00 | 9 | 22 | 0.94936 | 1053.5998
2017-09-24 23:00 | 9 | 23 | 0.6512 | 722.6986
2017-09-25 | 9 | 0 | 0.54158 | 601.0428
2017-09-25 01:00 | 9 | 1 | 0.50021 | 555.1308
2017-09-25 02:00 | 9 | 2 | 0.50116 | 556.1833
2017-09-25 03:00 | 9 | 3 | 0.50711 | 562.7862
2017-09-25 04:00 | 9 | 4 | 0.56003 | 621.5183
2017-09-25 05:00 | 9 | 5 | 0.7406 | 821.9241
2017-09-25 06:00 | 9 | 6 | 0.97473 | 1081.7553
2017-09-25 07:00 | 9 | 7 | 0.9014 | 1000.3735
2017-09-25 08:00 | 9 | 8 | 0.77871 | 864.214
2017-09-25 09:00 | 9 | 9 | 0.7645 | 848.4413
2017-09-25 10:00 | 9 | 10 | 0.75383 | 836.6032
2017-09-25 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-25 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-25 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-25 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-25 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-25 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-25 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-25 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-25 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-25 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-25 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-25 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-25 23:00 | 9 | 23 | 0.63478 | 704.4749
2017-09-26 | 9 | 0 | 0.52981 | 587.9887
2017-09-26 01:00 | 9 | 1 | 0.48434 | 537.5222
2017-09-26 02:00 | 9 | 2 | 0.48212 | 535.0587
2017-09-26 03:00 | 9 | 3 | 0.48802 | 541.6081
2017-09-26 04:00 | 9 | 4 | 0.5403 | 599.6279
2017-09-26 05:00 | 9 | 5 | 0.70955 | 787.4594
2017-09-26 06:00 | 9 | 6 | 0.95211 | 1056.6492
2017-09-26 07:00 | 9 | 7 | 0.88662 | 983.9708
2017-09-26 08:00 | 9 | 8 | 0.76724 | 851.4828
2017-09-26 09:00 | 9 | 9 | 0.76233 | 846.0342
2017-09-26 10:00 | 9 | 10 | 0.75489 | 837.7782
2017-09-26 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-26 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-26 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-26 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-26 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-26 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-26 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-26 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-26 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-26 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-26 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-26 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-26 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-27 | 9 | 0 | 0.51054 | 566.5941
2017-09-27 01:00 | 9 | 1 | 0.45746 | 507.6848
2017-09-27 02:00 | 9 | 2 | 0.4498 | 499.1909
2017-09-27 03:00 | 9 | 3 | 0.45039 | 499.8417
2017-09-27 04:00 | 9 | 4 | 0.50002 | 554.926
2017-09-27 05:00 | 9 | 5 | 0.66697 | 740.2041
2017-09-27 06:00 | 9 | 6 | 0.91212 | 1012.2696
2017-09-27 07:00 | 9 | 7 | 0.84948 | 942.7518
2017-09-27 08:00 | 9 | 8 | 0.74082 | 822.1611
2017-09-27 09:00 | 9 | 9 | 0.7354 | 816.1489
2017-09-27 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-27 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-27 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-27 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-27 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-27 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-27 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-27 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-27 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-27 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-27 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-27 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-27 22:00 | 9 | 22 | 0.93232 | 1034.6953
2017-09-27 23:00 | 9 | 23 | 0.62794 | 696.8921
2017-09-28 | 9 | 0 | 0.51054 | 566.5941
2017-09-28 01:00 | 9 | 1 | 0.46268 | 513.4775
2017-09-28 02:00 | 9 | 2 | 0.45964 | 510.1132
2017-09-28 03:00 | 9 | 3 | 0.4645 | 515.4983
2017-09-28 04:00 | 9 | 4 | 0.51881 | 575.7715
2017-09-28 05:00 | 9 | 5 | 0.68711 | 762.5513
2017-09-28 06:00 | 9 | 6 | 0.94234 | 1045.8103
2017-09-28 07:00 | 9 | 7 | 0.87594 | 972.119
2017-09-28 08:00 | 9 | 8 | 0.75731 | 840.4585
2017-09-28 09:00 | 9 | 9 | 0.74751 | 829.585
2017-09-28 10:00 | 9 | 10 | 0.74972 | 832.0413
2017-09-28 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-28 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-28 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-28 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-28 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-28 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-28 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-28 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-28 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-28 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-28 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-28 22:00 | 9 | 22 | 0.93977 | 1042.9632
2017-09-28 23:00 | 9 | 23 | 0.65191 | 723.495
2017-09-29 | 9 | 0 | 0.55132 | 611.8512
2017-09-29 01:00 | 9 | 1 | 0.50869 | 564.5433
2017-09-29 02:00 | 9 | 2 | 0.50658 | 562.2033
2017-09-29 03:00 | 9 | 3 | 0.51416 | 570.6193
2017-09-29 04:00 | 9 | 4 | 0.56587 | 628.0037
2017-09-29 05:00 | 9 | 5 | 0.74777 | 829.8815
2017-09-29 06:00 | 9 | 6 | 0.98212 | 1089.955
2017-09-29 07:00 | 9 | 7 | 0.91146 | 1011.5385
2017-09-29 08:00 | 9 | 8 | 0.78902 | 875.6595
2017-09-29 09:00 | 9 | 9 | 0.77818 | 863.6282
2017-09-29 10:00 | 9 | 10 | 0.76373 | 847.5859
2017-09-29 11:00 | 9 | 11 | 0.73444 | 815.08
2017-09-29 12:00 | 9 | 12 | 0.71289 | 791.1673
2017-09-29 13:00 | 9 | 13 | 0.704 | 781.2959
2017-09-29 14:00 | 9 | 14 | 0.72737 | 807.2392
2017-09-29 15:00 | 9 | 15 | 0.83763 | 929.603
2017-09-29 16:00 | 9 | 16 | 1.0439 | 1158.5647
2017-09-29 17:00 | 9 | 17 | 1.2091 | 1341.8593
2017-09-29 18:00 | 9 | 18 | 1.3663 | 1516.3276
2017-09-29 19:00 | 9 | 19 | 1.6118 | 1788.7363
2017-09-29 20:00 | 9 | 20 | 1.5292 | 1697.0916
2017-09-29 21:00 | 9 | 21 | 1.2265 | 1361.1541
2017-09-29 22:00 | 9 | 22 | 0.93881 | 1041.888
2017-09-29 23:00 | 9 | 23 | 0.64773 | 718.8559
2017-09-30 | 9 | 0 | 0.54504 | 604.8875
2017-09-30 01:00 | 9 | 1 | 0.49739 | 552.0091
2017-09-30 02:00 | 9 | 2 | 0.49042 | 544.2701
2017-09-30 03:00 | 9 | 3 | 0.49727 | 551.8744
2017-09-30 04:00 | 9 | 4 | 0.54936 | 609.6788
2017-09-30 05:00 | 9 | 5 | 0.72282 | 802.1888
2017-09-30 06:00 | 9 | 6 | 0.97527 | 1082.3613
2017-09-30 07:00 | 9 | 7 | 0.91503 | 1015.4982
2017-09-30 08:00 | 9 | 8 | 0.80616 | 894.6784
2017-09-30 09:00 | 9 | 9 | 0.79913 | 886.878
2017-09-30 10:00 | 9 | 10 | 0.80221 | 890.2934
2017-09-30 11:00 | 9 | 11 | 0.78225 | 868.1401
2017-09-30 12:00 | 9 | 12 | 0.75648 | 839.5413
2017-09-30 13:00 | 9 | 13 | 0.74312 | 824.7175
2017-09-30 14:00 | 9 | 14 | 0.76443 | 848.3673
2017-09-30 15:00 | 9 | 15 | 0.87355 | 969.4648
2017-09-30 16:00 | 9 | 16 | 1.0793 | 1197.7983
2017-09-30 17:00 | 9 | 17 | 1.2434 | 1379.937
2017-09-30 18:00 | 9 | 18 | 1.4005 | 1554.3325
2017-09-30 19:00 | 9 | 19 | 1.6466 | 1827.4188
2017-09-30 20:00 | 9 | 20 | 1.5648 | 1736.6081
2017-09-30 21:00 | 9 | 21 | 1.2548 | 1392.5539
2017-09-30 22:00 | 9 | 22 | 0.94786 | 1051.9359
2017-09-30 23:00 | 9 | 23 | 0.63452 | 704.1876
2017-10-01 | 10 | 0 | 0.54033 | 599.6597
2017-10-01 01:00 | 10 | 1 | 0.48281 | 535.8208
2017-10-01 02:00 | 10 | 2 | 0.46983 | 521.4157
2017-10-01 03:00 | 10 | 3 | 0.46967 | 521.2374
2017-10-01 04:00 | 10 | 4 | 0.52559 | 583.2978
2017-10-01 05:00 | 10 | 5 | 0.73135 | 811.6572
2017-10-01 06:00 | 10 | 6 | 1.045 | 1159.7308
2017-10-01 07:00 | 10 | 7 | 0.99865 | 1108.305
2017-10-01 08:00 | 10 | 8 | 0.85429 | 948.092
2017-10-01 09:00 | 10 | 9 | 0.84872 | 941.9113
2017-10-01 10:00 | 10 | 10 | 0.86652 | 961.6601
2017-10-01 11:00 | 10 | 11 | 0.84755 | 940.6123
2017-10-01 12:00 | 10 | 12 | 0.81988 | 909.9079
2017-10-01 13:00 | 10 | 13 | 0.80767 | 896.3553
2017-10-01 14:00 | 10 | 14 | 0.84058 | 932.872
2017-10-01 15:00 | 10 | 15 | 0.98656 | 1094.8808
2017-10-01 16:00 | 10 | 16 | 1.2713 | 1410.8665
2017-10-01 17:00 | 10 | 17 | 1.5228 | 1689.9706
2017-10-01 18:00 | 10 | 18 | 1.7137 | 1901.8268
2017-10-01 19:00 | 10 | 19 | 1.774 | 1968.733
2017-10-01 20:00 | 10 | 20 | 1.6042 | 1780.3507
2017-10-01 21:00 | 10 | 21 | 1.289 | 1430.5826
2017-10-01 22:00 | 10 | 22 | 0.97603 | 1083.1953
2017-10-01 23:00 | 10 | 23 | 0.65808 | 730.3347
2017-10-02 | 10 | 0 | 0.53638 | 595.2793
2017-10-02 01:00 | 10 | 1 | 0.4802 | 532.9229
2017-10-02 02:00 | 10 | 2 | 0.46846 | 519.9003
2017-10-02 03:00 | 10 | 3 | 0.467 | 518.2729
2017-10-02 04:00 | 10 | 4 | 0.52149 | 578.7513
2017-10-02 05:00 | 10 | 5 | 0.72073 | 799.865
2017-10-02 06:00 | 10 | 6 | 1.0238 | 1136.2459
2017-10-02 07:00 | 10 | 7 | 0.96621 | 1072.3061
2017-10-02 08:00 | 10 | 8 | 0.80926 | 898.1164
2017-10-02 09:00 | 10 | 9 | 0.7978 | 885.4044
2017-10-02 10:00 | 10 | 10 | 0.81403 | 903.408
2017-10-02 11:00 | 10 | 11 | 0.79974 | 887.5521
2017-10-02 12:00 | 10 | 12 | 0.7763 | 861.5338
2017-10-02 13:00 | 10 | 13 | 0.76855 | 852.9336
2017-10-02 14:00 | 10 | 14 | 0.80352 | 891.7439
2017-10-02 15:00 | 10 | 15 | 0.95064 | 1055.019
2017-10-02 16:00 | 10 | 16 | 1.2359 | 1371.6329
2017-10-02 17:00 | 10 | 17 | 1.4885 | 1651.8929
2017-10-02 18:00 | 10 | 18 | 1.6794 | 1863.822
2017-10-02 19:00 | 10 | 19 | 1.7391 | 1930.0504
2017-10-02 20:00 | 10 | 20 | 1.5686 | 1740.8342
2017-10-02 21:00 | 10 | 21 | 1.2608 | 1399.1827
2017-10-02 22:00 | 10 | 22 | 0.96655 | 1072.6758
2017-10-02 23:00 | 10 | 23 | 0.67105 | 744.7371
2017-10-03 | 10 | 0 | 0.5662 | 628.3714
2017-10-03 01:00 | 10 | 1 | 0.51842 | 575.3378
2017-10-03 02:00 | 10 | 2 | 0.51237 | 568.6319
2017-10-03 03:00 | 10 | 3 | 0.51765 | 574.4839
2017-10-03 04:00 | 10 | 4 | 0.57453 | 637.615
2017-10-03 05:00 | 10 | 5 | 0.78349 | 869.516
2017-10-03 06:00 | 10 | 6 | 1.069 | 1186.3391
2017-10-03 07:00 | 10 | 7 | 1.0038 | 1114.0419
2017-10-03 08:00 | 10 | 8 | 0.84331 | 935.9018
2017-10-03 09:00 | 10 | 9 | 0.83523 | 926.9428
2017-10-03 10:00 | 10 | 10 | 0.83529 | 927.0036
2017-10-03 11:00 | 10 | 11 | 0.81322 | 902.5156
2017-10-03 12:00 | 10 | 12 | 0.78491 | 871.0925
2017-10-03 13:00 | 10 | 13 | 0.77808 | 863.5143
2017-10-03 14:00 | 10 | 14 | 0.81391 | 903.2791
2017-10-03 15:00 | 10 | 15 | 0.9609 | 1066.4119
2017-10-03 16:00 | 10 | 16 | 1.256 | 1393.8697
2017-10-03 17:00 | 10 | 17 | 1.4944 | 1658.4993
2017-10-03 18:00 | 10 | 18 | 1.6829 | 1867.7099
2017-10-03 19:00 | 10 | 19 | 1.7416 | 1932.8788
2017-10-03 20:00 | 10 | 20 | 1.5744 | 1747.3136
2017-10-03 21:00 | 10 | 21 | 1.2736 | 1413.3976
2017-10-03 22:00 | 10 | 22 | 0.98038 | 1088.0245
2017-10-03 23:00 | 10 | 23 | 0.6785 | 752.9986
2017-10-04 | 10 | 0 | 0.56778 | 630.1287
2017-10-04 01:00 | 10 | 1 | 0.51446 | 570.9457
2017-10-04 02:00 | 10 | 2 | 0.50494 | 560.3876
2017-10-04 03:00 | 10 | 3 | 0.50378 | 559.0957
2017-10-04 04:00 | 10 | 4 | 0.55631 | 617.3949
2017-10-04 05:00 | 10 | 5 | 0.74823 | 830.3907
2017-10-04 06:00 | 10 | 6 | 1.0462 | 1161.0537
2017-10-04 07:00 | 10 | 7 | 0.98911 | 1097.7126
2017-10-04 08:00 | 10 | 8 | 0.82675 | 917.5333
2017-10-04 09:00 | 10 | 9 | 0.80467 | 893.021
2017-10-04 10:00 | 10 | 10 | 0.81403 | 903.408
2017-10-04 11:00 | 10 | 11 | 0.79974 | 887.5521
2017-10-04 12:00 | 10 | 12 | 0.7763 | 861.5338
2017-10-04 13:00 | 10 | 13 | 0.76855 | 852.9336
2017-10-04 14:00 | 10 | 14 | 0.80352 | 891.7439
2017-10-04 15:00 | 10 | 15 | 0.95064 | 1055.019
2017-10-04 16:00 | 10 | 16 | 1.2359 | 1371.6329
2017-10-04 17:00 | 10 | 17 | 1.4885 | 1651.8929
2017-10-04 18:00 | 10 | 18 | 1.6794 | 1863.822
2017-10-04 19:00 | 10 | 19 | 1.7391 | 1930.0504
2017-10-04 20:00 | 10 | 20 | 1.5686 | 1740.8342
2017-10-04 21:00 | 10 | 21 | 1.2608 | 1399.1827
2017-10-04 22:00 | 10 | 22 | 0.96049 | 1065.9547
2017-10-04 23:00 | 10 | 23 | 0.65311 | 724.8192
2017-10-05 | 10 | 0 | 0.54608 | 606.0436
2017-10-05 01:00 | 10 | 1 | 0.5032 | 558.4548
2017-10-05 02:00 | 10 | 2 | 0.49929 | 554.1138
2017-10-05 03:00 | 10 | 3 | 0.50622 | 561.8064
2017-10-05 04:00 | 10 | 4 | 0.56458 | 626.5703
2017-10-05 05:00 | 10 | 5 | 0.76 | 843.4443
2017-10-05 06:00 | 10 | 6 | 1.0635 | 1180.2557
2017-10-05 07:00 | 10 | 7 | 1.0061 | 1116.5553
2017-10-05 08:00 | 10 | 8 | 0.84542 | 938.247
2017-10-05 09:00 | 10 | 9 | 0.83421 | 925.8038
2017-10-05 10:00 | 10 | 10 | 0.84078 | 933.0988
2017-10-05 11:00 | 10 | 11 | 0.81949 | 909.4732
2017-10-05 12:00 | 10 | 12 | 0.78851 | 875.0931
2017-10-05 13:00 | 10 | 13 | 0.78018 | 865.8443
2017-10-05 14:00 | 10 | 14 | 0.81544 | 904.9752
2017-10-05 15:00 | 10 | 15 | 0.96267 | 1068.3772
2017-10-05 16:00 | 10 | 16 | 1.2563 | 1394.1944
2017-10-05 17:00 | 10 | 17 | 1.4962 | 1660.4903
2017-10-05 18:00 | 10 | 18 | 1.6873 | 1872.5687
2017-10-05 19:00 | 10 | 19 | 1.7534 | 1945.9662
2017-10-05 20:00 | 10 | 20 | 1.5892 | 1763.7505
2017-10-05 21:00 | 10 | 21 | 1.2925 | 1434.3671
2017-10-05 22:00 | 10 | 22 | 1.0048 | 1115.1235
2017-10-05 23:00 | 10 | 23 | 0.7052 | 782.6364
2017-10-06 | 10 | 0 | 0.59978 | 665.6345
2017-10-06 01:00 | 10 | 1 | 0.5552 | 616.157
2017-10-06 02:00 | 10 | 2 | 0.54879 | 609.0446
2017-10-06 03:00 | 10 | 3 | 0.55071 | 611.1836
2017-10-06 04:00 | 10 | 4 | 0.60405 | 670.3753
2017-10-06 05:00 | 10 | 5 | 0.80305 | 891.226
2017-10-06 06:00 | 10 | 6 | 1.0929 | 1212.9401
2017-10-06 07:00 | 10 | 7 | 1.0326 | 1145.961
2017-10-06 08:00 | 10 | 8 | 0.87231 | 968.088
2017-10-06 09:00 | 10 | 9 | 0.85939 | 953.7475
2017-10-06 10:00 | 10 | 10 | 0.85437 | 948.1854
2017-10-06 11:00 | 10 | 11 | 0.83245 | 923.8496
2017-10-06 12:00 | 10 | 12 | 0.80272 | 890.8623
2017-10-06 13:00 | 10 | 13 | 0.79239 | 879.3934
2017-10-06 14:00 | 10 | 14 | 0.82811 | 919.0402
2017-10-06 15:00 | 10 | 15 | 0.98133 | 1089.0802
2017-10-06 16:00 | 10 | 16 | 1.2876 | 1428.9549
2017-10-06 17:00 | 10 | 17 | 1.5302 | 1698.2179
2017-10-06 18:00 | 10 | 18 | 1.7282 | 1917.9177
2017-10-06 19:00 | 10 | 19 | 1.7961 | 1993.3611
2017-10-06 20:00 | 10 | 20 | 1.6274 | 1806.1075
2017-10-06 21:00 | 10 | 21 | 1.3335 | 1479.9615
2017-10-06 22:00 | 10 | 22 | 1.0457 | 1160.517
2017-10-06 23:00 | 10 | 23 | 0.74966 | 831.9701
2017-10-07 | 10 | 0 | 0.65221 | 723.8237
2017-10-07 01:00 | 10 | 1 | 0.59965 | 665.4898
2017-10-07 02:00 | 10 | 2 | 0.59524 | 660.6032
2017-10-07 03:00 | 10 | 3 | 0.60122 | 667.2366
2017-10-07 04:00 | 10 | 4 | 0.65712 | 729.2724
2017-10-07 05:00 | 10 | 5 | 0.87627 | 972.4866
2017-10-07 06:00 | 10 | 6 | 1.1677 | 1295.8813
2017-10-07 07:00 | 10 | 7 | 1.1081 | 1229.7962
2017-10-07 08:00 | 10 | 8 | 0.9502 | 1054.5337
2017-10-07 09:00 | 10 | 9 | 0.94354 | 1047.1394
2017-10-07 10:00 | 10 | 10 | 0.92268 | 1023.9947
2017-10-07 11:00 | 10 | 11 | 0.88454 | 981.6661
2017-10-07 12:00 | 10 | 12 | 0.84322 | 935.8084
2017-10-07 13:00 | 10 | 13 | 0.81881 | 908.7158
2017-10-07 14:00 | 10 | 14 | 0.85241 | 946.0071
2017-10-07 15:00 | 10 | 15 | 0.99591 | 1105.2663
2017-10-07 16:00 | 10 | 16 | 1.2972 | 1439.6872
2017-10-07 17:00 | 10 | 17 | 1.5371 | 1705.838
2017-10-07 18:00 | 10 | 18 | 1.7277 | 1917.3663
2017-10-07 19:00 | 10 | 19 | 1.7941 | 1991.1122
2017-10-07 20:00 | 10 | 20 | 1.6357 | 1815.297
2017-10-07 21:00 | 10 | 21 | 1.3368 | 1483.6333
2017-10-07 22:00 | 10 | 22 | 1.0392 | 1153.3067
2017-10-07 23:00 | 10 | 23 | 0.73526 | 815.9924
2017-10-08 | 10 | 0 | 0.63247 | 701.9111
2017-10-08 01:00 | 10 | 1 | 0.58458 | 648.7692
2017-10-08 02:00 | 10 | 2 | 0.57661 | 639.9187
2017-10-08 03:00 | 10 | 3 | 0.58057 | 644.3178
2017-10-08 04:00 | 10 | 4 | 0.63473 | 704.4232
2017-10-08 05:00 | 10 | 5 | 0.84262 | 935.1457
2017-10-08 06:00 | 10 | 6 | 1.1408 | 1266.0925
2017-10-08 07:00 | 10 | 7 | 1.0716 | 1189.2323
2017-10-08 08:00 | 10 | 8 | 0.90281 | 1001.9362
2017-10-08 09:00 | 10 | 9 | 0.88291 | 979.8546
2017-10-08 10:00 | 10 | 10 | 0.87261 | 968.4253
2017-10-08 11:00 | 10 | 11 | 0.84755 | 940.6123
2017-10-08 12:00 | 10 | 12 | 0.81988 | 909.9079
2017-10-08 13:00 | 10 | 13 | 0.80767 | 896.3553
2017-10-08 14:00 | 10 | 14 | 0.84058 | 932.872
2017-10-08 15:00 | 10 | 15 | 0.98656 | 1094.8808
2017-10-08 16:00 | 10 | 16 | 1.2713 | 1410.8665
2017-10-08 17:00 | 10 | 17 | 1.5228 | 1689.9706
2017-10-08 18:00 | 10 | 18 | 1.7137 | 1901.8268
2017-10-08 19:00 | 10 | 19 | 1.774 | 1968.733
2017-10-08 20:00 | 10 | 20 | 1.6042 | 1780.3507
2017-10-08 21:00 | 10 | 21 | 1.289 | 1430.5826
2017-10-08 22:00 | 10 | 22 | 0.97794 | 1085.3227
2017-10-08 23:00 | 10 | 23 | 0.67375 | 747.7339
2017-10-09 | 10 | 0 | 0.56265 | 624.426
2017-10-09 01:00 | 10 | 1 | 0.51194 | 568.153
2017-10-09 02:00 | 10 | 2 | 0.50396 | 559.2931
2017-10-09 03:00 | 10 | 3 | 0.5054 | 560.8932
2017-10-09 04:00 | 10 | 4 | 0.56113 | 622.7425
2017-10-09 05:00 | 10 | 5 | 0.75595 | 838.9551
2017-10-09 06:00 | 10 | 6 | 1.0525 | 1168.0892
2017-10-09 07:00 | 10 | 7 | 0.98425 | 1092.322
2017-10-09 08:00 | 10 | 8 | 0.81319 | 902.4813
2017-10-09 09:00 | 10 | 9 | 0.7978 | 885.4044
2017-10-09 10:00 | 10 | 10 | 0.81403 | 903.408
2017-10-09 11:00 | 10 | 11 | 0.79974 | 887.5521
2017-10-09 12:00 | 10 | 12 | 0.7763 | 861.5338
2017-10-09 13:00 | 10 | 13 | 0.76855 | 852.9336
2017-10-09 14:00 | 10 | 14 | 0.80352 | 891.7439
2017-10-09 15:00 | 10 | 15 | 0.95064 | 1055.019
2017-10-09 16:00 | 10 | 16 | 1.2359 | 1371.6329
2017-10-09 17:00 | 10 | 17 | 1.4885 | 1651.8929
2017-10-09 18:00 | 10 | 18 | 1.6794 | 1863.822
2017-10-09 19:00 | 10 | 19 | 1.7391 | 1930.0504
2017-10-09 20:00 | 10 | 20 | 1.5686 | 1740.8342
2017-10-09 21:00 | 10 | 21 | 1.2608 | 1399.1827
2017-10-09 22:00 | 10 | 22 | 0.97265 | 1079.4458
2017-10-09 23:00 | 10 | 23 | 0.68322 | 758.2389
2017-10-10 | 10 | 0 | 0.59114 | 656.0507
2017-10-10 01:00 | 10 | 1 | 0.54653 | 606.5387
2017-10-10 02:00 | 10 | 2 | 0.54914 | 609.4364
2017-10-10 03:00 | 10 | 3 | 0.56306 | 624.8835
2017-10-10 04:00 | 10 | 4 | 0.62345 | 691.9109
2017-10-10 05:00 | 10 | 5 | 0.83942 | 931.5926
2017-10-10 06:00 | 10 | 6 | 1.1332 | 1257.5904
2017-10-10 07:00 | 10 | 7 | 1.0706 | 1188.1095
2017-10-10 08:00 | 10 | 8 | 0.90214 | 1001.192
2017-10-10 09:00 | 10 | 9 | 0.89513 | 993.4127
2017-10-10 10:00 | 10 | 10 | 0.87061 | 966.2047
2017-10-10 11:00 | 10 | 11 | 0.83928 | 931.4378
2017-10-10 12:00 | 10 | 12 | 0.80538 | 893.8129
2017-10-10 13:00 | 10 | 13 | 0.79165 | 878.5702
2017-10-10 14:00 | 10 | 14 | 0.82806 | 918.9859
2017-10-10 15:00 | 10 | 15 | 0.98124 | 1088.9769
2017-10-10 16:00 | 10 | 16 | 1.2937 | 1435.7017
2017-10-10 17:00 | 10 | 17 | 1.5313 | 1699.4669
2017-10-10 18:00 | 10 | 18 | 1.7239 | 1913.1658
2017-10-10 19:00 | 10 | 19 | 1.7888 | 1985.1641
2017-10-10 20:00 | 10 | 20 | 1.6277 | 1806.4166
2017-10-10 21:00 | 10 | 21 | 1.3319 | 1478.138
2017-10-10 22:00 | 10 | 22 | 1.0456 | 1160.4034
2017-10-10 23:00 | 10 | 23 | 0.75272 | 835.3748
2017-10-11 | 10 | 0 | 0.64542 | 716.2907
2017-10-11 01:00 | 10 | 1 | 0.60215 | 668.2712
2017-10-11 02:00 | 10 | 2 | 0.5986 | 664.324
2017-10-11 03:00 | 10 | 3 | 0.60167 | 667.7297
2017-10-11 04:00 | 10 | 4 | 0.6554 | 727.3597
2017-10-11 05:00 | 10 | 5 | 0.84955 | 942.8327
2017-10-11 06:00 | 10 | 6 | 1.144 | 1269.5906
2017-10-11 07:00 | 10 | 7 | 1.0777 | 1196.0096
2017-10-11 08:00 | 10 | 8 | 0.90338 | 1002.5765
2017-10-11 09:00 | 10 | 9 | 0.89346 | 991.5649
2017-10-11 10:00 | 10 | 10 | 0.89191 | 989.8438
2017-10-11 11:00 | 10 | 11 | 0.85495 | 948.8291
2017-10-11 12:00 | 10 | 12 | 0.81102 | 900.0659
2017-10-11 13:00 | 10 | 13 | 0.79686 | 884.3584
2017-10-11 14:00 | 10 | 14 | 0.83263 | 924.0515
2017-10-11 15:00 | 10 | 15 | 0.97939 | 1086.9289
2017-10-11 16:00 | 10 | 16 | 1.2856 | 1426.7677
2017-10-11 17:00 | 10 | 17 | 1.522 | 1689.1669
2017-10-11 18:00 | 10 | 18 | 1.7144 | 1902.6506
2017-10-11 19:00 | 10 | 19 | 1.7768 | 1971.8585
2017-10-11 20:00 | 10 | 20 | 1.6136 | 1790.7449
2017-10-11 21:00 | 10 | 21 | 1.3141 | 1458.3768
2017-10-11 22:00 | 10 | 22 | 1.0272 | 1139.9521
2017-10-11 23:00 | 10 | 23 | 0.72679 | 806.5968
2017-10-12 | 10 | 0 | 0.61792 | 685.7636
2017-10-12 01:00 | 10 | 1 | 0.57459 | 637.6795
2017-10-12 02:00 | 10 | 2 | 0.56833 | 630.7342
2017-10-12 03:00 | 10 | 3 | 0.56984 | 632.4085
2017-10-12 04:00 | 10 | 4 | 0.62487 | 693.4838
2017-10-12 05:00 | 10 | 5 | 0.81902 | 908.9443
2017-10-12 06:00 | 10 | 6 | 1.1279 | 1251.7733
2017-10-12 07:00 | 10 | 7 | 1.0563 | 1172.2921
2017-10-12 08:00 | 10 | 8 | 0.89514 | 993.43
2017-10-12 09:00 | 10 | 9 | 0.89902 | 997.7378
2017-10-12 10:00 | 10 | 10 | 0.88436 | 981.4633
2017-10-12 11:00 | 10 | 11 | 0.85738 | 951.5208
2017-10-12 12:00 | 10 | 12 | 0.82486 | 915.4354
2017-10-12 13:00 | 10 | 13 | 0.80608 | 894.5868
2017-10-12 14:00 | 10 | 14 | 0.83963 | 931.8267
2017-10-12 15:00 | 10 | 15 | 0.98133 | 1089.0789
2017-10-12 16:00 | 10 | 16 | 1.2803 | 1420.8259
2017-10-12 17:00 | 10 | 17 | 1.5149 | 1681.2895
2017-10-12 18:00 | 10 | 18 | 1.7023 | 1889.1999
2017-10-12 19:00 | 10 | 19 | 1.7646 | 1958.4013
2017-10-12 20:00 | 10 | 20 | 1.5974 | 1772.773
2017-10-12 21:00 | 10 | 21 | 1.297 | 1439.4297
2017-10-12 22:00 | 10 | 22 | 1.0072 | 1117.8428
2017-10-12 23:00 | 10 | 23 | 0.71028 | 788.2746
2017-10-13 | 10 | 0 | 0.60027 | 666.1768
2017-10-13 01:00 | 10 | 1 | 0.54702 | 607.0842
2017-10-13 02:00 | 10 | 2 | 0.54104 | 600.4429
2017-10-13 03:00 | 10 | 3 | 0.53933 | 598.5516
2017-10-13 04:00 | 10 | 4 | 0.59341 | 658.5725
2017-10-13 05:00 | 10 | 5 | 0.78543 | 871.6676
2017-10-13 06:00 | 10 | 6 | 1.0788 | 1197.2063
2017-10-13 07:00 | 10 | 7 | 1.0188 | 1130.6661
2017-10-13 08:00 | 10 | 8 | 0.84936 | 942.6203
2017-10-13 09:00 | 10 | 9 | 0.84692 | 939.9168
2017-10-13 10:00 | 10 | 10 | 0.84245 | 934.948
2017-10-13 11:00 | 10 | 11 | 0.81349 | 902.8102
2017-10-13 12:00 | 10 | 12 | 0.78321 | 869.2066
2017-10-13 13:00 | 10 | 13 | 0.77477 | 859.8394
2017-10-13 14:00 | 10 | 14 | 0.80649 | 895.0477
2017-10-13 15:00 | 10 | 15 | 0.95122 | 1055.6608
2017-10-13 16:00 | 10 | 16 | 1.2405 | 1376.6688
2017-10-13 17:00 | 10 | 17 | 1.4885 | 1651.8929
2017-10-13 18:00 | 10 | 18 | 1.6794 | 1863.822
2017-10-13 19:00 | 10 | 19 | 1.7391 | 1930.0504
2017-10-13 20:00 | 10 | 20 | 1.5686 | 1740.8342
2017-10-13 21:00 | 10 | 21 | 1.2624 | 1400.9966
2017-10-13 22:00 | 10 | 22 | 0.97123 | 1077.8677
2017-10-13 23:00 | 10 | 23 | 0.67103 | 744.7129
2017-10-14 | 10 | 0 | 0.56516 | 627.2198
2017-10-14 01:00 | 10 | 1 | 0.5126 | 568.8887
2017-10-14 02:00 | 10 | 2 | 0.50527 | 560.7455
2017-10-14 03:00 | 10 | 3 | 0.50664 | 562.2724
2017-10-14 04:00 | 10 | 4 | 0.56227 | 624.0127
2017-10-14 05:00 | 10 | 5 | 0.76405 | 847.948
2017-10-14 06:00 | 10 | 6 | 1.0801 | 1198.6704
2017-10-14 07:00 | 10 | 7 | 1.0288 | 1141.7203
2017-10-14 08:00 | 10 | 8 | 0.88778 | 985.2632
2017-10-14 09:00 | 10 | 9 | 0.88498 | 982.1524
2017-10-14 10:00 | 10 | 10 | 0.88706 | 984.4631
2017-10-14 11:00 | 10 | 11 | 0.85931 | 953.6595
2017-10-14 12:00 | 10 | 12 | 0.82086 | 910.9964
2017-10-14 13:00 | 10 | 13 | 0.80767 | 896.3553
2017-10-14 14:00 | 10 | 14 | 0.84058 | 932.872
2017-10-14 15:00 | 10 | 15 | 0.98656 | 1094.8808
2017-10-14 16:00 | 10 | 16 | 1.2713 | 1410.8665
2017-10-14 17:00 | 10 | 17 | 1.5228 | 1689.9706
2017-10-14 18:00 | 10 | 18 | 1.7137 | 1901.8268
2017-10-14 19:00 | 10 | 19 | 1.774 | 1968.733
2017-10-14 20:00 | 10 | 20 | 1.6042 | 1780.3507
2017-10-14 21:00 | 10 | 21 | 1.289 | 1430.5826
2017-10-14 22:00 | 10 | 22 | 0.97603 | 1083.1953
2017-10-14 23:00 | 10 | 23 | 0.65928 | 731.6677
2017-10-15 | 10 | 0 | 0.55283 | 613.5278
2017-10-15 01:00 | 10 | 1 | 0.51125 | 567.3851
2017-10-15 02:00 | 10 | 2 | 0.50773 | 563.4783
2017-10-15 03:00 | 10 | 3 | 0.51875 | 575.7095
2017-10-15 04:00 | 10 | 4 | 0.58289 | 646.8908
2017-10-15 05:00 | 10 | 5 | 0.79703 | 884.5484
2017-10-15 06:00 | 10 | 6 | 1.1105 | 1232.4542
2017-10-15 07:00 | 10 | 7 | 1.0547 | 1170.4708
2017-10-15 08:00 | 10 | 8 | 0.896 | 994.3842
2017-10-15 09:00 | 10 | 9 | 0.88994 | 987.654
2017-10-15 10:00 | 10 | 10 | 0.88053 | 977.2088
2017-10-15 11:00 | 10 | 11 | 0.84989 | 943.2047
2017-10-15 12:00 | 10 | 12 | 0.82059 | 910.692
2017-10-15 13:00 | 10 | 13 | 0.80767 | 896.3553
2017-10-15 14:00 | 10 | 14 | 0.84086 | 933.184
2017-10-15 15:00 | 10 | 15 | 0.98728 | 1095.687
2017-10-15 16:00 | 10 | 16 | 1.2899 | 1431.518
2017-10-15 17:00 | 10 | 17 | 1.5303 | 1698.3482
2017-10-15 18:00 | 10 | 18 | 1.7258 | 1915.2884
2017-10-15 19:00 | 10 | 19 | 1.7918 | 1988.5297
2017-10-15 20:00 | 10 | 20 | 1.6324 | 1811.6793
2017-10-15 21:00 | 10 | 21 | 1.3296 | 1475.6183
2017-10-15 22:00 | 10 | 22 | 1.0317 | 1145.0046
2017-10-15 23:00 | 10 | 23 | 0.72719 | 807.0369
2017-10-16 | 10 | 0 | 0.61467 | 682.166
2017-10-16 01:00 | 10 | 1 | 0.56556 | 627.6629
2017-10-16 02:00 | 10 | 2 | 0.56137 | 623.0075
2017-10-16 03:00 | 10 | 3 | 0.56267 | 624.4554
2017-10-16 04:00 | 10 | 4 | 0.61958 | 687.6122
2017-10-16 05:00 | 10 | 5 | 0.82981 | 920.9292
2017-10-16 06:00 | 10 | 6 | 1.1289 | 1252.8428
2017-10-16 07:00 | 10 | 7 | 1.054 | 1169.714
2017-10-16 08:00 | 10 | 8 | 0.87578 | 971.9374
2017-10-16 09:00 | 10 | 9 | 0.86265 | 957.372
2017-10-16 10:00 | 10 | 10 | 0.8479 | 941.0031
2017-10-16 11:00 | 10 | 11 | 0.81779 | 907.5841
2017-10-16 12:00 | 10 | 12 | 0.78618 | 872.4995
2017-10-16 13:00 | 10 | 13 | 0.77523 | 860.346
2017-10-16 14:00 | 10 | 14 | 0.81051 | 899.5074
2017-10-16 15:00 | 10 | 15 | 0.95897 | 1064.2639
2017-10-16 16:00 | 10 | 16 | 1.2616 | 1400.09
2017-10-16 17:00 | 10 | 17 | 1.5021 | 1667.0211
2017-10-16 18:00 | 10 | 18 | 1.6946 | 1880.634
2017-10-16 19:00 | 10 | 19 | 1.7586 | 1951.6825
2017-10-16 20:00 | 10 | 20 | 1.5959 | 1771.1417
2017-10-16 21:00 | 10 | 21 | 1.2999 | 1442.593
2017-10-16 22:00 | 10 | 22 | 1.0142 | 1125.5543
2017-10-16 23:00 | 10 | 23 | 0.71916 | 798.1201
2017-10-17 | 10 | 0 | 0.61353 | 680.902
2017-10-17 01:00 | 10 | 1 | 0.56659 | 628.7978
2017-10-17 02:00 | 10 | 2 | 0.56029 | 621.812
2017-10-17 03:00 | 10 | 3 | 0.56339 | 625.256
2017-10-17 04:00 | 10 | 4 | 0.6194 | 687.4106
2017-10-17 05:00 | 10 | 5 | 0.83041 | 921.588
2017-10-17 06:00 | 10 | 6 | 1.1313 | 1255.5517
2017-10-17 07:00 | 10 | 7 | 1.0472 | 1162.2309
2017-10-17 08:00 | 10 | 8 | 0.87594 | 972.125
2017-10-17 09:00 | 10 | 9 | 0.898 | 996.6055
2017-10-17 10:00 | 10 | 10 | 0.91912 | 1020.046
2017-10-17 11:00 | 10 | 11 | 0.88388 | 980.9336
2017-10-17 12:00 | 10 | 12 | 0.85203 | 945.5826
2017-10-17 13:00 | 10 | 13 | 0.84467 | 937.4155
2017-10-17 14:00 | 10 | 14 | 0.87929 | 975.8367
2017-10-17 15:00 | 10 | 15 | 1.0221 | 1134.2855
2017-10-17 16:00 | 10 | 16 | 1.3276 | 1473.4161
2017-10-17 17:00 | 10 | 17 | 1.5573 | 1728.2992
2017-10-17 18:00 | 10 | 18 | 1.746 | 1937.7087
2017-10-17 19:00 | 10 | 19 | 1.8044 | 2002.5121
2017-10-17 20:00 | 10 | 20 | 1.6428 | 1823.2099
2017-10-17 21:00 | 10 | 21 | 1.3432 | 1490.7347
2017-10-17 22:00 | 10 | 22 | 1.0542 | 1169.9879
2017-10-17 23:00 | 10 | 23 | 0.75529 | 838.2203
2017-10-18 | 10 | 0 | 0.64985 | 721.2085
2017-10-18 01:00 | 10 | 1 | 0.59884 | 664.5923
2017-10-18 02:00 | 10 | 2 | 0.58931 | 654.0135
2017-10-18 03:00 | 10 | 3 | 0.58878 | 653.4319
2017-10-18 04:00 | 10 | 4 | 0.64379 | 714.4765
2017-10-18 05:00 | 10 | 5 | 0.83616 | 927.9735
2017-10-18 06:00 | 10 | 6 | 1.1459 | 1271.678
2017-10-18 07:00 | 10 | 7 | 1.0697 | 1187.1949
2017-10-18 08:00 | 10 | 8 | 0.89455 | 992.7686
2017-10-18 09:00 | 10 | 9 | 0.8922 | 990.1643
2017-10-18 10:00 | 10 | 10 | 0.87451 | 970.533
2017-10-18 11:00 | 10 | 11 | 0.84832 | 941.4625
2017-10-18 12:00 | 10 | 12 | 0.81807 | 907.9001
2017-10-18 13:00 | 10 | 13 | 0.81384 | 903.1981
2017-10-18 14:00 | 10 | 14 | 0.84977 | 943.0718
2017-10-18 15:00 | 10 | 15 | 0.99702 | 1106.4957
2017-10-18 16:00 | 10 | 16 | 1.3091 | 1452.8035
2017-10-18 17:00 | 10 | 17 | 1.5461 | 1715.8499
2017-10-18 18:00 | 10 | 18 | 1.7376 | 1928.3497
2017-10-18 19:00 | 10 | 19 | 1.8014 | 1999.1976
2017-10-18 20:00 | 10 | 20 | 1.6366 | 1816.3257
2017-10-18 21:00 | 10 | 21 | 1.342 | 1489.3613
2017-10-18 22:00 | 10 | 22 | 1.0546 | 1170.4217
2017-10-18 23:00 | 10 | 23 | 0.75979 | 843.2119
2017-10-19 | 10 | 0 | 0.65482 | 726.7226
2017-10-19 01:00 | 10 | 1 | 0.60782 | 674.5619
2017-10-19 02:00 | 10 | 2 | 0.60228 | 668.4113
2017-10-19 03:00 | 10 | 3 | 0.60761 | 674.3289
2017-10-19 04:00 | 10 | 4 | 0.66429 | 737.2329
2017-10-19 05:00 | 10 | 5 | 0.85979 | 954.1909
2017-10-19 06:00 | 10 | 6 | 1.1537 | 1280.4079
2017-10-19 07:00 | 10 | 7 | 1.0802 | 1198.8539
2017-10-19 08:00 | 10 | 8 | 0.89968 | 998.4698
2017-10-19 09:00 | 10 | 9 | 0.8846 | 981.7296
2017-10-19 10:00 | 10 | 10 | 0.86255 | 957.2549
2017-10-19 11:00 | 10 | 11 | 0.83983 | 932.0411
2017-10-19 12:00 | 10 | 12 | 0.80525 | 893.669
2017-10-19 13:00 | 10 | 13 | 0.7871 | 873.5257
2017-10-19 14:00 | 10 | 14 | 0.81635 | 905.9898
2017-10-19 15:00 | 10 | 15 | 0.96155 | 1067.125
2017-10-19 16:00 | 10 | 16 | 1.2569 | 1394.962
2017-10-19 17:00 | 10 | 17 | 1.4984 | 1662.9326
2017-10-19 18:00 | 10 | 18 | 1.6918 | 1877.5256
2017-10-19 19:00 | 10 | 19 | 1.7532 | 1945.7291
2017-10-19 20:00 | 10 | 20 | 1.5949 | 1770.0132
2017-10-19 21:00 | 10 | 21 | 1.2989 | 1441.5226
2017-10-19 22:00 | 10 | 22 | 1.0107 | 1121.7271
2017-10-19 23:00 | 10 | 23 | 0.71565 | 794.2311
2017-10-20 | 10 | 0 | 0.61056 | 677.5984
2017-10-20 01:00 | 10 | 1 | 0.5633 | 625.1471
2017-10-20 02:00 | 10 | 2 | 0.55744 | 618.6443
2017-10-20 03:00 | 10 | 3 | 0.55971 | 621.1686
2017-10-20 04:00 | 10 | 4 | 0.61763 | 685.4444
2017-10-20 05:00 | 10 | 5 | 0.82295 | 913.3082
2017-10-20 06:00 | 10 | 6 | 1.1107 | 1232.6134
2017-10-20 07:00 | 10 | 7 | 1.0413 | 1155.5851
2017-10-20 08:00 | 10 | 8 | 0.8634 | 958.2079
2017-10-20 09:00 | 10 | 9 | 0.84625 | 939.1675
2017-10-20 10:00 | 10 | 10 | 0.83451 | 926.1435
2017-10-20 11:00 | 10 | 11 | 0.80979 | 898.7055
2017-10-20 12:00 | 10 | 12 | 0.78057 | 866.2777
2017-10-20 13:00 | 10 | 13 | 0.77065 | 855.271
2017-10-20 14:00 | 10 | 14 | 0.80942 | 898.2953
2017-10-20 15:00 | 10 | 15 | 0.96107 | 1066.5953
2017-10-20 16:00 | 10 | 16 | 1.2699 | 1409.3389
2017-10-20 17:00 | 10 | 17 | 1.5103 | 1676.1783
2017-10-20 18:00 | 10 | 18 | 1.7037 | 1890.7677
2017-10-20 19:00 | 10 | 19 | 1.7709 | 1965.3828
2017-10-20 20:00 | 10 | 20 | 1.6127 | 1789.8106
2017-10-20 21:00 | 10 | 21 | 1.3168 | 1461.3721
2017-10-20 22:00 | 10 | 22 | 1.0305 | 1143.6673
2017-10-20 23:00 | 10 | 23 | 0.73428 | 814.9002
2017-10-21 | 10 | 0 | 0.63427 | 703.9159
2017-10-21 01:00 | 10 | 1 | 0.58334 | 647.3883
2017-10-21 02:00 | 10 | 2 | 0.57445 | 637.5216
2017-10-21 03:00 | 10 | 3 | 0.57536 | 638.5313
2017-10-21 04:00 | 10 | 4 | 0.62755 | 696.4608
2017-10-21 05:00 | 10 | 5 | 0.83553 | 927.2697
2017-10-21 06:00 | 10 | 6 | 1.1351 | 1259.7424
2017-10-21 07:00 | 10 | 7 | 1.0834 | 1202.4025
2017-10-21 08:00 | 10 | 8 | 0.91973 | 1020.72
2017-10-21 09:00 | 10 | 9 | 0.90465 | 1003.9812
2017-10-21 10:00 | 10 | 10 | 0.88917 | 986.8035
2017-10-21 11:00 | 10 | 11 | 0.85165 | 945.161
2017-10-21 12:00 | 10 | 12 | 0.81988 | 909.9079
2017-10-21 13:00 | 10 | 13 | 0.80767 | 896.3553
2017-10-21 14:00 | 10 | 14 | 0.84058 | 932.872
2017-10-21 15:00 | 10 | 15 | 0.98656 | 1094.8808
2017-10-21 16:00 | 10 | 16 | 1.2713 | 1410.8665
2017-10-21 17:00 | 10 | 17 | 1.5228 | 1689.9706
2017-10-21 18:00 | 10 | 18 | 1.7137 | 1901.8268
2017-10-21 19:00 | 10 | 19 | 1.774 | 1968.733
2017-10-21 20:00 | 10 | 20 | 1.6042 | 1780.3507
2017-10-21 21:00 | 10 | 21 | 1.289 | 1430.5826
2017-10-21 22:00 | 10 | 22 | 0.98268 | 1090.5826
2017-10-21 23:00 | 10 | 23 | 0.67791 | 752.344
2017-10-22 | 10 | 0 | 0.57163 | 634.4006
2017-10-22 01:00 | 10 | 1 | 0.52304 | 580.4658
2017-10-22 02:00 | 10 | 2 | 0.51807 | 574.9527
2017-10-22 03:00 | 10 | 3 | 0.52459 | 582.1893
2017-10-22 04:00 | 10 | 4 | 0.58586 | 650.1839
2017-10-22 05:00 | 10 | 5 | 0.79798 | 885.5958
2017-10-22 06:00 | 10 | 6 | 1.1067 | 1228.2553
2017-10-22 07:00 | 10 | 7 | 1.0423 | 1156.7903
2017-10-22 08:00 | 10 | 8 | 0.87941 | 975.9758
2017-10-22 09:00 | 10 | 9 | 0.86885 | 964.2462
2017-10-22 10:00 | 10 | 10 | 0.86652 | 961.6601
2017-10-22 11:00 | 10 | 11 | 0.84755 | 940.6123
2017-10-22 12:00 | 10 | 12 | 0.81988 | 909.9079
2017-10-22 13:00 | 10 | 13 | 0.80767 | 896.3553
2017-10-22 14:00 | 10 | 14 | 0.84058 | 932.872
2017-10-22 15:00 | 10 | 15 | 0.98656 | 1094.8808
2017-10-22 16:00 | 10 | 16 | 1.2713 | 1410.8665
2017-10-22 17:00 | 10 | 17 | 1.5228 | 1689.9706
2017-10-22 18:00 | 10 | 18 | 1.7137 | 1901.8268
2017-10-22 19:00 | 10 | 19 | 1.774 | 1968.733
2017-10-22 20:00 | 10 | 20 | 1.6042 | 1780.3507
2017-10-22 21:00 | 10 | 21 | 1.289 | 1430.5826
2017-10-22 22:00 | 10 | 22 | 0.98315 | 1091.0998
2017-10-22 23:00 | 10 | 23 | 0.68266 | 757.6199
2017-10-23 | 10 | 0 | 0.57573 | 638.9414
2017-10-23 01:00 | 10 | 1 | 0.53076 | 589.0412
2017-10-23 02:00 | 10 | 2 | 0.52546 | 583.1597
2017-10-23 03:00 | 10 | 3 | 0.53164 | 590.0177
2017-10-23 04:00 | 10 | 4 | 0.5875 | 652.0126
2017-10-23 05:00 | 10 | 5 | 0.78262 | 868.552
2017-10-23 06:00 | 10 | 6 | 1.0767 | 1194.9322
2017-10-23 07:00 | 10 | 7 | 1.0092 | 1119.9876
2017-10-23 08:00 | 10 | 8 | 0.83674 | 928.6123
2017-10-23 09:00 | 10 | 9 | 0.81248 | 901.6953
2017-10-23 10:00 | 10 | 10 | 0.81403 | 903.408
2017-10-23 11:00 | 10 | 11 | 0.79974 | 887.5521
2017-10-23 12:00 | 10 | 12 | 0.7763 | 861.5338
2017-10-23 13:00 | 10 | 13 | 0.76855 | 852.9336
2017-10-23 14:00 | 10 | 14 | 0.80352 | 891.7439
2017-10-23 15:00 | 10 | 15 | 0.95064 | 1055.019
2017-10-23 16:00 | 10 | 16 | 1.2359 | 1371.6329
2017-10-23 17:00 | 10 | 17 | 1.4885 | 1651.8929
2017-10-23 18:00 | 10 | 18 | 1.6794 | 1863.822
2017-10-23 19:00 | 10 | 19 | 1.7391 | 1930.0504
2017-10-23 20:00 | 10 | 20 | 1.5686 | 1740.8342
2017-10-23 21:00 | 10 | 21 | 1.2608 | 1399.1827
2017-10-23 22:00 | 10 | 22 | 0.96975 | 1076.2287
2017-10-23 23:00 | 10 | 23 | 0.67768 | 752.0947
2017-10-24 | 10 | 0 | 0.57892 | 642.4841
2017-10-24 01:00 | 10 | 1 | 0.53601 | 594.8671
2017-10-24 02:00 | 10 | 2 | 0.53361 | 592.2048
2017-10-24 03:00 | 10 | 3 | 0.5416 | 601.0664
2017-10-24 04:00 | 10 | 4 | 0.59978 | 665.6367
2017-10-24 05:00 | 10 | 5 | 0.80887 | 897.6864
2017-10-24 06:00 | 10 | 6 | 1.105 | 1226.3503
2017-10-24 07:00 | 10 | 7 | 1.0407 | 1154.9817
2017-10-24 08:00 | 10 | 8 | 0.86982 | 965.3327
2017-10-24 09:00 | 10 | 9 | 0.85948 | 953.8476
2017-10-24 10:00 | 10 | 10 | 0.84171 | 934.1293
2017-10-24 11:00 | 10 | 11 | 0.8133 | 902.6009
2017-10-24 12:00 | 10 | 12 | 0.78031 | 865.9877
2017-10-24 13:00 | 10 | 13 | 0.76855 | 852.9336
2017-10-24 14:00 | 10 | 14 | 0.80626 | 894.792
2017-10-24 15:00 | 10 | 15 | 0.95932 | 1064.6601
2017-10-24 16:00 | 10 | 16 | 1.2677 | 1406.8839
2017-10-24 17:00 | 10 | 17 | 1.5099 | 1675.6854
2017-10-24 18:00 | 10 | 18 | 1.705 | 1892.2445
2017-10-24 19:00 | 10 | 19 | 1.7775 | 1972.6713
2017-10-24 20:00 | 10 | 20 | 1.6188 | 1796.5553
2017-10-24 21:00 | 10 | 21 | 1.3276 | 1473.3179
2017-10-24 22:00 | 10 | 22 | 1.0425 | 1157.0103
2017-10-24 23:00 | 10 | 23 | 0.75048 | 832.8831
2017-10-25 | 10 | 0 | 0.64677 | 717.7835
2017-10-25 01:00 | 10 | 1 | 0.60207 | 668.1827
2017-10-25 02:00 | 10 | 2 | 0.59597 | 661.4093
2017-10-25 03:00 | 10 | 3 | 0.60049 | 666.4261
2017-10-25 04:00 | 10 | 4 | 0.6583 | 730.5825
2017-10-25 05:00 | 10 | 5 | 0.86831 | 963.6484
2017-10-25 06:00 | 10 | 6 | 1.1509 | 1277.2179
2017-10-25 07:00 | 10 | 7 | 1.0782 | 1196.5516
2017-10-25 08:00 | 10 | 8 | 0.89614 | 994.5359
2017-10-25 09:00 | 10 | 9 | 0.88505 | 982.2302
2017-10-25 10:00 | 10 | 10 | 0.86423 | 959.1202
2017-10-25 11:00 | 10 | 11 | 0.82878 | 919.783
2017-10-25 12:00 | 10 | 12 | 0.78765 | 874.1338
2017-10-25 13:00 | 10 | 13 | 0.77217 | 856.9576
2017-10-25 14:00 | 10 | 14 | 0.80411 | 892.4052
2017-10-25 15:00 | 10 | 15 | 0.9548 | 1059.6378
2017-10-25 16:00 | 10 | 16 | 1.2552 | 1393.0424
2017-10-25 17:00 | 10 | 17 | 1.5027 | 1667.7099
2017-10-25 18:00 | 10 | 18 | 1.6976 | 1883.9699
2017-10-25 19:00 | 10 | 19 | 1.7629 | 1956.4951
2017-10-25 20:00 | 10 | 20 | 1.602 | 1777.9403
2017-10-25 21:00 | 10 | 21 | 1.3071 | 1450.611
2017-10-25 22:00 | 10 | 22 | 1.0173 | 1129.0451
2017-10-25 23:00 | 10 | 23 | 0.72167 | 800.9114
2017-10-26 | 10 | 0 | 0.61298 | 680.2914
2017-10-26 01:00 | 10 | 1 | 0.56385 | 625.7624
2017-10-26 02:00 | 10 | 2 | 0.55536 | 616.3447
2017-10-26 03:00 | 10 | 3 | 0.55425 | 615.1049
2017-10-26 04:00 | 10 | 4 | 0.61107 | 678.1632
2017-10-26 05:00 | 10 | 5 | 0.81647 | 906.1145
2017-10-26 06:00 | 10 | 6 | 1.1153 | 1237.787
2017-10-26 07:00 | 10 | 7 | 1.0462 | 1161.111
2017-10-26 08:00 | 10 | 8 | 0.88959 | 987.2646
2017-10-26 09:00 | 10 | 9 | 0.90114 | 1000.089
2017-10-26 10:00 | 10 | 10 | 0.89693 | 995.4198
2017-10-26 11:00 | 10 | 11 | 0.87473 | 970.7775
2017-10-26 12:00 | 10 | 12 | 0.84591 | 938.7921
2017-10-26 13:00 | 10 | 13 | 0.83321 | 924.6962
2017-10-26 14:00 | 10 | 14 | 0.86638 | 961.5104
2017-10-26 15:00 | 10 | 15 | 1.0126 | 1123.837
2017-10-26 16:00 | 10 | 16 | 1.3169 | 1461.4654
2017-10-26 17:00 | 10 | 17 | 1.5516 | 1721.9772
2017-10-26 18:00 | 10 | 18 | 1.7388 | 1929.7286
2017-10-26 19:00 | 10 | 19 | 1.7969 | 1994.1904
2017-10-26 20:00 | 10 | 20 | 1.6272 | 1805.8637
2017-10-26 21:00 | 10 | 21 | 1.3284 | 1474.268
2017-10-26 22:00 | 10 | 22 | 1.0419 | 1156.331
2017-10-26 23:00 | 10 | 23 | 0.74069 | 822.0213
2017-10-27 | 10 | 0 | 0.62976 | 698.9072
2017-10-27 01:00 | 10 | 1 | 0.57683 | 640.1661
2017-10-27 02:00 | 10 | 2 | 0.56767 | 629.9982
2017-10-27 03:00 | 10 | 3 | 0.56257 | 624.3455
2017-10-27 04:00 | 10 | 4 | 0.61549 | 683.0669
2017-10-27 05:00 | 10 | 5 | 0.8081 | 896.8281
2017-10-27 06:00 | 10 | 6 | 1.1157 | 1238.2458
2017-10-27 07:00 | 10 | 7 | 1.0482 | 1163.2937
2017-10-27 08:00 | 10 | 8 | 0.89109 | 988.9345
2017-10-27 09:00 | 10 | 9 | 0.89108 | 988.9221
2017-10-27 10:00 | 10 | 10 | 0.88806 | 985.5746
2017-10-27 11:00 | 10 | 11 | 0.86295 | 957.7049
2017-10-27 12:00 | 10 | 12 | 0.83428 | 925.8906
2017-10-27 13:00 | 10 | 13 | 0.82213 | 912.3984
2017-10-27 14:00 | 10 | 14 | 0.85654 | 950.5935
2017-10-27 15:00 | 10 | 15 | 1.0011 | 1111.0508
2017-10-27 16:00 | 10 | 16 | 1.3031 | 1446.189
2017-10-27 17:00 | 10 | 17 | 1.5355 | 1704.1319
2017-10-27 18:00 | 10 | 18 | 1.7226 | 1911.7399
2017-10-27 19:00 | 10 | 19 | 1.7832 | 1978.9476
2017-10-27 20:00 | 10 | 20 | 1.6166 | 1794.0952
2017-10-27 21:00 | 10 | 21 | 1.3157 | 1460.1559
2017-10-27 22:00 | 10 | 22 | 1.0231 | 1135.4693
2017-10-27 23:00 | 10 | 23 | 0.72244 | 801.7701
2017-10-28 | 10 | 0 | 0.61747 | 685.2649
2017-10-28 01:00 | 10 | 1 | 0.56241 | 624.1633
2017-10-28 02:00 | 10 | 2 | 0.55193 | 612.5352
2017-10-28 03:00 | 10 | 3 | 0.55242 | 613.0734
2017-10-28 04:00 | 10 | 4 | 0.60775 | 674.4874
2017-10-28 05:00 | 10 | 5 | 0.8062 | 894.7236
2017-10-28 06:00 | 10 | 6 | 1.1137 | 1235.9838
2017-10-28 07:00 | 10 | 7 | 1.0655 | 1182.4755
2017-10-28 08:00 | 10 | 8 | 0.91761 | 1018.3652
2017-10-28 09:00 | 10 | 9 | 0.91741 | 1018.1387
2017-10-28 10:00 | 10 | 10 | 0.90649 | 1006.0231
2017-10-28 11:00 | 10 | 11 | 0.88167 | 978.4827
2017-10-28 12:00 | 10 | 12 | 0.85036 | 943.7277
2017-10-28 13:00 | 10 | 13 | 0.82778 | 918.6676
2017-10-28 14:00 | 10 | 14 | 0.86023 | 954.685
2017-10-28 15:00 | 10 | 15 | 1.0024 | 1112.4629
2017-10-28 16:00 | 10 | 16 | 1.2916 | 1433.4006
2017-10-28 17:00 | 10 | 17 | 1.5343 | 1702.8127
2017-10-28 18:00 | 10 | 18 | 1.7234 | 1912.5941
2017-10-28 19:00 | 10 | 19 | 1.7864 | 1982.5377
2017-10-28 20:00 | 10 | 20 | 1.622 | 1800.1257
2017-10-28 21:00 | 10 | 21 | 1.318 | 1462.6729
2017-10-28 22:00 | 10 | 22 | 1.0175 | 1129.2029
2017-10-28 23:00 | 10 | 23 | 0.71289 | 791.1641
2017-10-29 | 10 | 0 | 0.72143 | 800.6388
2017-10-29 01:00 | 10 | 1 | 0.61243 | 679.6725
2017-10-29 02:00 | 10 | 2 | 0.56483 | 626.8547
2017-10-29 03:00 | 10 | 3 | 0.55604 | 617.0887
2017-10-29 04:00 | 10 | 4 | 0.56468 | 626.6859
2017-10-29 05:00 | 10 | 5 | 0.61951 | 687.5306
2017-10-29 06:00 | 10 | 6 | 0.82008 | 910.1293
2017-10-29 07:00 | 10 | 7 | 1.1128 | 1234.9678
2017-10-29 08:00 | 10 | 8 | 1.0406 | 1154.8452
2017-10-29 09:00 | 10 | 9 | 0.87483 | 970.8839
2017-10-29 10:00 | 10 | 10 | 0.8541 | 947.8804
2017-10-29 11:00 | 10 | 11 | 0.86652 | 961.6601
2017-10-29 12:00 | 10 | 12 | 0.84755 | 940.6123
2017-10-29 13:00 | 10 | 13 | 0.81988 | 909.9079
2017-10-29 14:00 | 10 | 14 | 0.80767 | 896.3553
2017-10-29 15:00 | 10 | 15 | 0.84058 | 932.872
2017-10-29 16:00 | 10 | 16 | 0.98656 | 1094.8808
2017-10-29 17:00 | 10 | 17 | 1.2713 | 1410.8665
2017-10-29 18:00 | 10 | 18 | 1.5228 | 1689.9706
2017-10-29 19:00 | 10 | 19 | 1.7137 | 1901.8268
2017-10-29 20:00 | 10 | 20 | 1.774 | 1968.733
2017-10-29 21:00 | 10 | 21 | 1.6044 | 1780.5874
2017-10-29 22:00 | 10 | 22 | 1.2974 | 1439.8092
2017-10-29 23:00 | 10 | 23 | 0.99779 | 1107.3472
2017-10-30 | 10 | 0 | 0.68678 | 762.1894
2017-10-30 01:00 | 10 | 1 | 0.57965 | 643.2948
2017-10-30 02:00 | 10 | 2 | 0.53039 | 588.6328
2017-10-30 03:00 | 10 | 3 | 0.52315 | 580.5967
2017-10-30 04:00 | 10 | 4 | 0.52618 | 583.9516
2017-10-30 05:00 | 10 | 5 | 0.58112 | 644.9303
2017-10-30 06:00 | 10 | 6 | 0.77316 | 858.0551
2017-10-30 07:00 | 10 | 7 | 1.0612 | 1177.6841
2017-10-30 08:00 | 10 | 8 | 0.98104 | 1088.7599
2017-10-30 09:00 | 10 | 9 | 0.8102 | 899.162
2017-10-30 10:00 | 10 | 10 | 0.7978 | 885.4044
2017-10-30 11:00 | 10 | 11 | 0.81403 | 903.408
2017-10-30 12:00 | 10 | 12 | 0.79974 | 887.5521
2017-10-30 13:00 | 10 | 13 | 0.7763 | 861.5338
2017-10-30 14:00 | 10 | 14 | 0.76855 | 852.9336
2017-10-30 15:00 | 10 | 15 | 0.80352 | 891.7439
2017-10-30 16:00 | 10 | 16 | 0.95111 | 1055.5408
2017-10-30 17:00 | 10 | 17 | 1.2677 | 1406.919
2017-10-30 18:00 | 10 | 18 | 1.5164 | 1682.8903
2017-10-30 19:00 | 10 | 19 | 1.7168 | 1905.3156
2017-10-30 20:00 | 10 | 20 | 1.7879 | 1984.1795
2017-10-30 21:00 | 10 | 21 | 1.6317 | 1810.8811
2017-10-30 22:00 | 10 | 22 | 1.3433 | 1490.7683
2017-10-30 23:00 | 10 | 23 | 1.0597 | 1176.0202
2017-10-31 | 10 | 0 | 0.76981 | 854.3392
2017-10-31 01:00 | 10 | 1 | 0.66432 | 737.2599
2017-10-31 02:00 | 10 | 2 | 0.6193 | 687.2981
2017-10-31 03:00 | 10 | 3 | 0.61495 | 682.4775
2017-10-31 04:00 | 10 | 4 | 0.61828 | 686.1628
2017-10-31 05:00 | 10 | 5 | 0.67766 | 752.0696
2017-10-31 06:00 | 10 | 6 | 0.86968 | 965.1758
2017-10-31 07:00 | 10 | 7 | 1.1501 | 1276.3926
2017-10-31 08:00 | 10 | 8 | 1.0642 | 1181.089
2017-10-31 09:00 | 10 | 9 | 0.88425 | 981.3443
2017-10-31 10:00 | 10 | 10 | 0.88324 | 980.2177
2017-10-31 11:00 | 10 | 11 | 0.86537 | 960.3916
2017-10-31 12:00 | 10 | 12 | 0.83822 | 930.2595
2017-10-31 13:00 | 10 | 13 | 0.80841 | 897.172
2017-10-31 14:00 | 10 | 14 | 0.8044 | 892.7297
2017-10-31 15:00 | 10 | 15 | 0.85116 | 944.6201
2017-10-31 16:00 | 10 | 16 | 1.0124 | 1123.5201
2017-10-31 17:00 | 10 | 17 | 1.3322 | 1478.4339
2017-10-31 18:00 | 10 | 18 | 1.5686 | 1740.7819
2017-10-31 19:00 | 10 | 19 | 1.7587 | 1951.7705
2017-10-31 20:00 | 10 | 20 | 1.8268 | 2027.3452
2017-10-31 21:00 | 10 | 21 | 1.6622 | 1844.7515
2017-10-31 22:00 | 10 | 22 | 1.3602 | 1509.5533
2017-10-31 23:00 | 10 | 23 | 1.065 | 1181.9509
2017-11-01 | 11 | 0 | 0.76334 | 847.1552
2017-11-01 01:00 | 11 | 1 | 0.64445 | 715.2146
2017-11-01 02:00 | 11 | 2 | 0.58815 | 652.7307
2017-11-01 03:00 | 11 | 3 | 0.57423 | 637.2769
2017-11-01 04:00 | 11 | 4 | 0.57325 | 636.1978
2017-11-01 05:00 | 11 | 5 | 0.62903 | 698.0979
2017-11-01 06:00 | 11 | 6 | 0.80192 | 889.9735
2017-11-01 07:00 | 11 | 7 | 1.0388 | 1152.9105
2017-11-01 08:00 | 11 | 8 | 0.99054 | 1099.3034
2017-11-01 09:00 | 11 | 9 | 0.87482 | 970.8754
2017-11-01 10:00 | 11 | 10 | 0.87518 | 971.279
2017-11-01 11:00 | 11 | 11 | 0.86027 | 954.7337
2017-11-01 12:00 | 11 | 12 | 0.83317 | 924.6485
2017-11-01 13:00 | 11 | 13 | 0.806 | 894.4986
2017-11-01 14:00 | 11 | 14 | 0.81671 | 906.3896
2017-11-01 15:00 | 11 | 15 | 0.91656 | 1017.1961
2017-11-01 16:00 | 11 | 16 | 1.2147 | 1348.0261
2017-11-01 17:00 | 11 | 17 | 1.7214 | 1910.358
2017-11-01 18:00 | 11 | 18 | 1.9806 | 2198.0396
2017-11-01 19:00 | 11 | 19 | 1.8907 | 2098.3567
2017-11-01 20:00 | 11 | 20 | 1.8085 | 2007.0991
2017-11-01 21:00 | 11 | 21 | 1.6532 | 1834.701
2017-11-01 22:00 | 11 | 22 | 1.3464 | 1494.2085
2017-11-01 23:00 | 11 | 23 | 1.0604 | 1176.8361
2017-11-02 | 11 | 0 | 0.76794 | 852.2616
2017-11-02 01:00 | 11 | 1 | 0.65541 | 727.3781
2017-11-02 02:00 | 11 | 2 | 0.60605 | 672.5936
2017-11-02 03:00 | 11 | 3 | 0.59844 | 664.1471
2017-11-02 04:00 | 11 | 4 | 0.59712 | 662.6869
2017-11-02 05:00 | 11 | 5 | 0.65012 | 721.5008
2017-11-02 06:00 | 11 | 6 | 0.81222 | 901.4016
2017-11-02 07:00 | 11 | 7 | 1.0507 | 1166.086
2017-11-02 08:00 | 11 | 8 | 0.99551 | 1104.8152
2017-11-02 09:00 | 11 | 9 | 0.85396 | 947.7298
2017-11-02 10:00 | 11 | 10 | 0.8367 | 928.574
2017-11-02 11:00 | 11 | 11 | 0.82324 | 913.6378
2017-11-02 12:00 | 11 | 12 | 0.80604 | 894.5446
2017-11-02 13:00 | 11 | 13 | 0.78256 | 868.4857
2017-11-02 14:00 | 11 | 14 | 0.79052 | 877.3244
2017-11-02 15:00 | 11 | 15 | 0.88188 | 978.7144
2017-11-02 16:00 | 11 | 16 | 1.1691 | 1297.4233
2017-11-02 17:00 | 11 | 17 | 1.6521 | 1833.457
2017-11-02 18:00 | 11 | 18 | 1.9263 | 2137.8143
2017-11-02 19:00 | 11 | 19 | 1.8315 | 2032.5705
2017-11-02 20:00 | 11 | 20 | 1.7463 | 1938.0993
2017-11-02 21:00 | 11 | 21 | 1.591 | 1765.6705
2017-11-02 22:00 | 11 | 22 | 1.2869 | 1428.1703
2017-11-02 23:00 | 11 | 23 | 1.002 | 1112.0174
2017-11-03 | 11 | 0 | 0.71447 | 792.9153
2017-11-03 01:00 | 11 | 1 | 0.60567 | 672.1726
2017-11-03 02:00 | 11 | 2 | 0.55897 | 620.3441
2017-11-03 03:00 | 11 | 3 | 0.55317 | 613.9086
2017-11-03 04:00 | 11 | 4 | 0.56322 | 625.0617
2017-11-03 05:00 | 11 | 5 | 0.62498 | 693.6052
2017-11-03 06:00 | 11 | 6 | 0.78958 | 876.2801
2017-11-03 07:00 | 11 | 7 | 1.0343 | 1147.8889
2017-11-03 08:00 | 11 | 8 | 0.98512 | 1093.2922
2017-11-03 09:00 | 11 | 9 | 0.8455 | 938.3424
2017-11-03 10:00 | 11 | 10 | 0.83734 | 929.2796
2017-11-03 11:00 | 11 | 11 | 0.82932 | 920.3788
2017-11-03 12:00 | 11 | 12 | 0.80604 | 894.5446
2017-11-03 13:00 | 11 | 13 | 0.78256 | 868.4857
2017-11-03 14:00 | 11 | 14 | 0.79264 | 879.6694
2017-11-03 15:00 | 11 | 15 | 0.8915 | 989.3888
2017-11-03 16:00 | 11 | 16 | 1.1914 | 1322.1816
2017-11-03 17:00 | 11 | 17 | 1.6945 | 1880.5952
2017-11-03 18:00 | 11 | 18 | 1.957 | 2171.9345
2017-11-03 19:00 | 11 | 19 | 1.8679 | 2072.9716
2017-11-03 20:00 | 11 | 20 | 1.7886 | 1984.9616
2017-11-03 21:00 | 11 | 21 | 1.6327 | 1811.9819
2017-11-03 22:00 | 11 | 22 | 1.3294 | 1475.388
2017-11-03 23:00 | 11 | 23 | 1.0426 | 1157.0432
2017-11-04 | 11 | 0 | 0.75905 | 842.3982
2017-11-04 01:00 | 11 | 1 | 0.64457 | 715.3493
2017-11-04 02:00 | 11 | 2 | 0.59563 | 661.0342
2017-11-04 03:00 | 11 | 3 | 0.58653 | 650.9293
2017-11-04 04:00 | 11 | 4 | 0.59153 | 656.484
2017-11-04 05:00 | 11 | 5 | 0.64919 | 720.4736
2017-11-04 06:00 | 11 | 6 | 0.8192 | 909.144
2017-11-04 07:00 | 11 | 7 | 1.0814 | 1200.1735
2017-11-04 08:00 | 11 | 8 | 1.066 | 1183.0844
2017-11-04 09:00 | 11 | 9 | 0.95738 | 1062.5034
2017-11-04 10:00 | 11 | 10 | 0.97219 | 1078.9407
2017-11-04 11:00 | 11 | 11 | 0.95733 | 1062.4484
2017-11-04 12:00 | 11 | 12 | 0.92881 | 1030.7926
2017-11-04 13:00 | 11 | 13 | 0.89633 | 994.7507
2017-11-04 14:00 | 11 | 14 | 0.89727 | 995.7926
2017-11-04 15:00 | 11 | 15 | 0.98312 | 1091.0715
2017-11-04 16:00 | 11 | 16 | 1.2675 | 1406.6966
2017-11-04 17:00 | 11 | 17 | 1.7603 | 1953.5636
2017-11-04 18:00 | 11 | 18 | 2.0143 | 2235.456
2017-11-04 19:00 | 11 | 19 | 1.9165 | 2126.9289
2017-11-04 20:00 | 11 | 20 | 1.83 | 2030.9635
2017-11-04 21:00 | 11 | 21 | 1.6709 | 1854.3912
2017-11-04 22:00 | 11 | 22 | 1.354 | 1502.6475
2017-11-04 23:00 | 11 | 23 | 1.0507 | 1166.0687
2017-11-05 | 11 | 0 | 0.75076 | 833.1916
2017-11-05 01:00 | 11 | 1 | 0.63621 | 706.069
2017-11-05 02:00 | 11 | 2 | 0.58302 | 647.0417
2017-11-05 03:00 | 11 | 3 | 0.57351 | 636.4791
2017-11-05 04:00 | 11 | 4 | 0.5768 | 640.1363
2017-11-05 05:00 | 11 | 5 | 0.6324 | 701.8432
2017-11-05 06:00 | 11 | 6 | 0.80293 | 891.0972
2017-11-05 07:00 | 11 | 7 | 1.0674 | 1184.6226
2017-11-05 08:00 | 11 | 8 | 1.052 | 1167.4872
2017-11-05 09:00 | 11 | 9 | 0.94697 | 1050.9456
2017-11-05 10:00 | 11 | 10 | 0.97172 | 1078.4148
2017-11-05 11:00 | 11 | 11 | 0.9625 | 1068.1812
2017-11-05 12:00 | 11 | 12 | 0.93341 | 1035.9011
2017-11-05 13:00 | 11 | 13 | 0.87878 | 975.2713
2017-11-05 14:00 | 11 | 14 | 0.87776 | 974.1373
2017-11-05 15:00 | 11 | 15 | 0.97039 | 1076.9382
2017-11-05 16:00 | 11 | 16 | 1.2604 | 1398.7892
2017-11-05 17:00 | 11 | 17 | 1.7554 | 1948.171
2017-11-05 18:00 | 11 | 18 | 2.0137 | 2234.8003
2017-11-05 19:00 | 11 | 19 | 1.9159 | 2126.2973
2017-11-05 20:00 | 11 | 20 | 1.8293 | 2030.179
2017-11-05 21:00 | 11 | 21 | 1.6717 | 1855.2471
2017-11-05 22:00 | 11 | 22 | 1.3547 | 1503.4794
2017-11-05 23:00 | 11 | 23 | 1.0516 | 1167.0315
2017-11-06 | 11 | 0 | 0.74163 | 823.0642
2017-11-06 01:00 | 11 | 1 | 0.62731 | 696.1895
2017-11-06 02:00 | 11 | 2 | 0.57578 | 639.0068
2017-11-06 03:00 | 11 | 3 | 0.56611 | 628.2703
2017-11-06 04:00 | 11 | 4 | 0.56716 | 629.4328
2017-11-06 05:00 | 11 | 5 | 0.62237 | 690.7038
2017-11-06 06:00 | 11 | 6 | 0.79922 | 886.9743
2017-11-06 07:00 | 11 | 7 | 1.0534 | 1169.0595
2017-11-06 08:00 | 11 | 8 | 0.99857 | 1108.2118
2017-11-06 09:00 | 11 | 9 | 0.8626 | 957.3122
2017-11-06 10:00 | 11 | 10 | 0.85563 | 949.5851
2017-11-06 11:00 | 11 | 11 | 0.83861 | 930.6926
2017-11-06 12:00 | 11 | 12 | 0.81297 | 902.2339
2017-11-06 13:00 | 11 | 13 | 0.7859 | 872.1986
2017-11-06 14:00 | 11 | 14 | 0.79052 | 877.3244
2017-11-06 15:00 | 11 | 15 | 0.88188 | 978.7144
2017-11-06 16:00 | 11 | 16 | 1.1739 | 1302.7842
2017-11-06 17:00 | 11 | 17 | 1.667 | 1850.0698
2017-11-06 18:00 | 11 | 18 | 1.9313 | 2143.4035
2017-11-06 19:00 | 11 | 19 | 1.8416 | 2043.7851
2017-11-06 20:00 | 11 | 20 | 1.7567 | 1949.6226
2017-11-06 21:00 | 11 | 21 | 1.6008 | 1776.5402
2017-11-06 22:00 | 11 | 22 | 1.2937 | 1435.7877
2017-11-06 23:00 | 11 | 23 | 1.0044 | 1114.7395
2017-11-07 | 11 | 0 | 0.71265 | 790.9048
2017-11-07 01:00 | 11 | 1 | 0.59958 | 665.4133
2017-11-07 02:00 | 11 | 2 | 0.54952 | 609.8541
2017-11-07 03:00 | 11 | 3 | 0.54075 | 600.128
2017-11-07 04:00 | 11 | 4 | 0.54305 | 602.683
2017-11-07 05:00 | 11 | 5 | 0.60114 | 667.1473
2017-11-07 06:00 | 11 | 6 | 0.77286 | 857.7228
2017-11-07 07:00 | 11 | 7 | 1.0111 | 1122.0741
2017-11-07 08:00 | 11 | 8 | 0.96707 | 1073.2507
2017-11-07 09:00 | 11 | 9 | 0.83217 | 923.5389
2017-11-07 10:00 | 11 | 10 | 0.83812 | 930.1472
2017-11-07 11:00 | 11 | 11 | 0.86283 | 957.5657
2017-11-07 12:00 | 11 | 12 | 0.83705 | 928.9577
2017-11-07 13:00 | 11 | 13 | 0.81366 | 903.0049
2017-11-07 14:00 | 11 | 14 | 0.8277 | 918.5843
2017-11-07 15:00 | 11 | 15 | 0.92358 | 1024.9851
2017-11-07 16:00 | 11 | 16 | 1.215 | 1348.4096
2017-11-07 17:00 | 11 | 17 | 1.7087 | 1896.3265
2017-11-07 18:00 | 11 | 18 | 1.9693 | 2185.4885
2017-11-07 19:00 | 11 | 19 | 1.8765 | 2082.5631
2017-11-07 20:00 | 11 | 20 | 1.7906 | 1987.1754
2017-11-07 21:00 | 11 | 21 | 1.6344 | 1813.8438
2017-11-07 22:00 | 11 | 22 | 1.3284 | 1474.3024
2017-11-07 23:00 | 11 | 23 | 1.0389 | 1152.9493
2017-11-08 | 11 | 0 | 0.74258 | 824.1218
2017-11-08 01:00 | 11 | 1 | 0.63192 | 701.3012
2017-11-08 02:00 | 11 | 2 | 0.58151 | 645.3624
2017-11-08 03:00 | 11 | 3 | 0.57359 | 636.5657
2017-11-08 04:00 | 11 | 4 | 0.5759 | 639.1319
2017-11-08 05:00 | 11 | 5 | 0.63264 | 702.1021
2017-11-08 06:00 | 11 | 6 | 0.79762 | 885.1983
2017-11-08 07:00 | 11 | 7 | 1.0653 | 1182.2261
2017-11-08 08:00 | 11 | 8 | 1.0316 | 1144.8906
2017-11-08 09:00 | 11 | 9 | 0.90987 | 1009.778
2017-11-08 10:00 | 11 | 10 | 0.92908 | 1031.0938
2017-11-08 11:00 | 11 | 11 | 0.92031 | 1021.3646
2017-11-08 12:00 | 11 | 12 | 0.89578 | 994.1359
2017-11-08 13:00 | 11 | 13 | 0.86938 | 964.8396
2017-11-08 14:00 | 11 | 14 | 0.87682 | 973.1002
2017-11-08 15:00 | 11 | 15 | 0.96596 | 1072.0283
2017-11-08 16:00 | 11 | 16 | 1.2505 | 1387.7639
2017-11-08 17:00 | 11 | 17 | 1.7456 | 1937.2934
2017-11-08 18:00 | 11 | 18 | 2.0008 | 2220.486
2017-11-08 19:00 | 11 | 19 | 1.9037 | 2112.7722
2017-11-08 20:00 | 11 | 20 | 1.8149 | 2014.1552
2017-11-08 21:00 | 11 | 21 | 1.6549 | 1836.5684
2017-11-08 22:00 | 11 | 22 | 1.3434 | 1490.9129
2017-11-08 23:00 | 11 | 23 | 1.0532 | 1168.8944
2017-11-09 | 11 | 0 | 0.75832 | 841.5873
2017-11-09 01:00 | 11 | 1 | 0.64369 | 714.3654
2017-11-09 02:00 | 11 | 2 | 0.5947 | 660.0023
2017-11-09 03:00 | 11 | 3 | 0.59122 | 656.1333
2017-11-09 04:00 | 11 | 4 | 0.59092 | 655.8011
2017-11-09 05:00 | 11 | 5 | 0.64861 | 719.8332
2017-11-09 06:00 | 11 | 6 | 0.81337 | 902.68
2017-11-09 07:00 | 11 | 7 | 1.0614 | 1177.9061
2017-11-09 08:00 | 11 | 8 | 1.0151 | 1126.5777
2017-11-09 09:00 | 11 | 9 | 0.8763 | 972.5239
2017-11-09 10:00 | 11 | 10 | 0.86454 | 959.4634
2017-11-09 11:00 | 11 | 11 | 0.84694 | 939.9324
2017-11-09 12:00 | 11 | 12 | 0.814 | 903.3801
2017-11-09 13:00 | 11 | 13 | 0.78256 | 868.4857
2017-11-09 14:00 | 11 | 14 | 0.79052 | 877.3244
2017-11-09 15:00 | 11 | 15 | 0.88449 | 981.6061
2017-11-09 16:00 | 11 | 16 | 1.1807 | 1310.3792
2017-11-09 17:00 | 11 | 17 | 1.6753 | 1859.2264
2017-11-09 18:00 | 11 | 18 | 1.9422 | 2155.4863
2017-11-09 19:00 | 11 | 19 | 1.851 | 2054.2237
2017-11-09 20:00 | 11 | 20 | 1.7659 | 1959.7743
2017-11-09 21:00 | 11 | 21 | 1.6107 | 1787.5365
2017-11-09 22:00 | 11 | 22 | 1.3032 | 1446.2672
2017-11-09 23:00 | 11 | 23 | 1.0203 | 1132.3806
2017-11-10 | 11 | 0 | 0.72797 | 807.9067
2017-11-10 01:00 | 11 | 1 | 0.61907 | 687.0487
2017-11-10 02:00 | 11 | 2 | 0.57141 | 634.1494
2017-11-10 03:00 | 11 | 3 | 0.56835 | 630.7504
2017-11-10 04:00 | 11 | 4 | 0.57143 | 634.1757
2017-11-10 05:00 | 11 | 5 | 0.62732 | 696.2025
2017-11-10 06:00 | 11 | 6 | 0.79165 | 878.5764
2017-11-10 07:00 | 11 | 7 | 1.04 | 1154.2323
2017-11-10 08:00 | 11 | 8 | 0.99641 | 1105.8163
2017-11-10 09:00 | 11 | 9 | 0.86248 | 957.186
2017-11-10 10:00 | 11 | 10 | 0.85324 | 946.9249
2017-11-10 11:00 | 11 | 11 | 0.83954 | 931.7283
2017-11-10 12:00 | 11 | 12 | 0.81384 | 903.1983
2017-11-10 13:00 | 11 | 13 | 0.7849 | 871.0868
2017-11-10 14:00 | 11 | 14 | 0.79818 | 885.8227
2017-11-10 15:00 | 11 | 15 | 0.89817 | 996.7954
2017-11-10 16:00 | 11 | 16 | 1.1965 | 1327.8317
2017-11-10 17:00 | 11 | 17 | 1.6992 | 1885.8109
2017-11-10 18:00 | 11 | 18 | 1.9626 | 2178.1027
2017-11-10 19:00 | 11 | 19 | 1.871 | 2076.4006
2017-11-10 20:00 | 11 | 20 | 1.787 | 1983.2556
2017-11-10 21:00 | 11 | 21 | 1.632 | 1811.1437
2017-11-10 22:00 | 11 | 22 | 1.3247 | 1470.133
2017-11-10 23:00 | 11 | 23 | 1.034 | 1147.5375
2017-11-11 | 11 | 0 | 0.74591 | 827.8109
2017-11-11 01:00 | 11 | 1 | 0.62852 | 697.5355
2017-11-11 02:00 | 11 | 2 | 0.57449 | 637.5748
2017-11-11 03:00 | 11 | 3 | 0.56306 | 624.8805
2017-11-11 04:00 | 11 | 4 | 0.56558 | 627.6788
2017-11-11 05:00 | 11 | 5 | 0.62292 | 691.3161
2017-11-11 06:00 | 11 | 6 | 0.79202 | 878.9818
2017-11-11 07:00 | 11 | 7 | 1.0549 | 1170.7606
2017-11-11 08:00 | 11 | 8 | 1.0403 | 1154.5286
2017-11-11 09:00 | 11 | 9 | 0.93174 | 1034.0469
2017-11-11 10:00 | 11 | 10 | 0.95152 | 1056.003
2017-11-11 11:00 | 11 | 11 | 0.93893 | 1042.0228
2017-11-11 12:00 | 11 | 12 | 0.89798 | 996.5776
2017-11-11 13:00 | 11 | 13 | 0.86354 | 958.3625
2017-11-11 14:00 | 11 | 14 | 0.86367 | 958.5061
2017-11-11 15:00 | 11 | 15 | 0.95588 | 1060.839
2017-11-11 16:00 | 11 | 16 | 1.2487 | 1385.8381
2017-11-11 17:00 | 11 | 17 | 1.7481 | 1940.0913
2017-11-11 18:00 | 11 | 18 | 2.0065 | 2226.8451
2017-11-11 19:00 | 11 | 19 | 1.914 | 2124.1638
2017-11-11 20:00 | 11 | 20 | 1.8281 | 2028.8826
2017-11-11 21:00 | 11 | 21 | 1.6693 | 1852.5795
2017-11-11 22:00 | 11 | 22 | 1.3519 | 1500.3315
2017-11-11 23:00 | 11 | 23 | 1.0494 | 1164.6734
2017-11-12 | 11 | 0 | 0.74622 | 828.1599
2017-11-12 01:00 | 11 | 1 | 0.62838 | 697.3785
2017-11-12 02:00 | 11 | 2 | 0.5766 | 639.9061
2017-11-12 03:00 | 11 | 3 | 0.56587 | 628.0017
2017-11-12 04:00 | 11 | 4 | 0.56996 | 632.5429
2017-11-12 05:00 | 11 | 5 | 0.6283 | 697.2868
2017-11-12 06:00 | 11 | 6 | 0.81222 | 901.3988
2017-11-12 07:00 | 11 | 7 | 1.0797 | 1198.2235
2017-11-12 08:00 | 11 | 8 | 1.0558 | 1171.6987
2017-11-12 09:00 | 11 | 9 | 0.95325 | 1057.9159
2017-11-12 10:00 | 11 | 10 | 0.98205 | 1089.8826
2017-11-12 11:00 | 11 | 11 | 1.0088 | 1119.5144
2017-11-12 12:00 | 11 | 12 | 0.95678 | 1061.8357
2017-11-12 13:00 | 11 | 13 | 0.92566 | 1027.3007
2017-11-12 14:00 | 11 | 14 | 0.92938 | 1031.4292
2017-11-12 15:00 | 11 | 15 | 1.0224 | 1134.649
2017-11-12 16:00 | 11 | 16 | 1.3109 | 1454.7871
2017-11-12 17:00 | 11 | 17 | 1.8148 | 2014.0243
2017-11-12 18:00 | 11 | 18 | 2.0661 | 2292.9885
2017-11-12 19:00 | 11 | 19 | 1.9695 | 2185.7499
2017-11-12 20:00 | 11 | 20 | 1.8827 | 2089.407
2017-11-12 21:00 | 11 | 21 | 1.7219 | 1911.0186
2017-11-12 22:00 | 11 | 22 | 1.4104 | 1565.3028
2017-11-12 23:00 | 11 | 23 | 1.1121 | 1234.2034
2017-11-13 | 11 | 0 | 0.80915 | 897.9994
2017-11-13 01:00 | 11 | 1 | 0.69682 | 773.3314
2017-11-13 02:00 | 11 | 2 | 0.65147 | 723.0068
2017-11-13 03:00 | 11 | 3 | 0.64424 | 714.9836
2017-11-13 04:00 | 11 | 4 | 0.6464 | 717.3781
2017-11-13 05:00 | 11 | 5 | 0.70276 | 779.9252
2017-11-13 06:00 | 11 | 6 | 0.86749 | 962.7383
2017-11-13 07:00 | 11 | 7 | 1.1164 | 1238.9578
2017-11-13 08:00 | 11 | 8 | 1.0841 | 1203.0925
2017-11-13 09:00 | 11 | 9 | 0.9585 | 1063.7397
2017-11-13 10:00 | 11 | 10 | 0.97056 | 1077.1252
2017-11-13 11:00 | 11 | 11 | 0.95905 | 1064.355
2017-11-13 12:00 | 11 | 12 | 0.93278 | 1035.198
2017-11-13 13:00 | 11 | 13 | 0.90593 | 1005.4002
2017-11-13 14:00 | 11 | 14 | 0.91059 | 1010.571
2017-11-13 15:00 | 11 | 15 | 0.99892 | 1108.6018
2017-11-13 16:00 | 11 | 16 | 1.2908 | 1432.5061
2017-11-13 17:00 | 11 | 17 | 1.7913 | 1987.9483
2017-11-13 18:00 | 11 | 18 | 2.0423 | 2266.505
2017-11-13 19:00 | 11 | 19 | 1.9451 | 2158.6506
2017-11-13 20:00 | 11 | 20 | 1.8508 | 2054.0419
2017-11-13 21:00 | 11 | 21 | 1.6871 | 1872.3146
2017-11-13 22:00 | 11 | 22 | 1.3758 | 1526.8467
2017-11-13 23:00 | 11 | 23 | 1.0829 | 1201.8538
2017-11-14 | 11 | 0 | 0.78429 | 870.4024
2017-11-14 01:00 | 11 | 1 | 0.67008 | 743.659
2017-11-14 02:00 | 11 | 2 | 0.61279 | 680.0799
2017-11-14 03:00 | 11 | 3 | 0.59867 | 664.3998
2017-11-14 04:00 | 11 | 4 | 0.59648 | 661.9736
2017-11-14 05:00 | 11 | 5 | 0.64874 | 719.9781
2017-11-14 06:00 | 11 | 6 | 0.82072 | 910.8407
2017-11-14 07:00 | 11 | 7 | 1.0596 | 1175.8927
2017-11-14 08:00 | 11 | 8 | 1.0213 | 1133.4256
2017-11-14 09:00 | 11 | 9 | 0.88519 | 982.3845
2017-11-14 10:00 | 11 | 10 | 0.88129 | 978.056
2017-11-14 11:00 | 11 | 11 | 0.86376 | 958.6032
2017-11-14 12:00 | 11 | 12 | 0.83141 | 922.6958
2017-11-14 13:00 | 11 | 13 | 0.79704 | 884.5596
2017-11-14 14:00 | 11 | 14 | 0.80794 | 896.6497
2017-11-14 15:00 | 11 | 15 | 0.90183 | 1000.8524
2017-11-14 16:00 | 11 | 16 | 1.1908 | 1321.6027
2017-11-14 17:00 | 11 | 17 | 1.6756 | 1859.5839
2017-11-14 18:00 | 11 | 18 | 1.9458 | 2159.4258
2017-11-14 19:00 | 11 | 19 | 1.8488 | 2051.8146
2017-11-14 20:00 | 11 | 20 | 1.7602 | 1953.4959
2017-11-14 21:00 | 11 | 21 | 1.5996 | 1775.2416
2017-11-14 22:00 | 11 | 22 | 1.2892 | 1430.7961
2017-11-14 23:00 | 11 | 23 | 0.99676 | 1106.2072
2017-11-15 | 11 | 0 | 0.6996 | 776.4125
2017-11-15 01:00 | 11 | 1 | 0.58319 | 647.2254
2017-11-15 02:00 | 11 | 2 | 0.53693 | 595.8888
2017-11-15 03:00 | 11 | 3 | 0.53362 | 592.2104
2017-11-15 04:00 | 11 | 4 | 0.53979 | 599.0558
2017-11-15 05:00 | 11 | 5 | 0.60196 | 668.0559
2017-11-15 06:00 | 11 | 6 | 0.78402 | 870.1093
2017-11-15 07:00 | 11 | 7 | 1.0308 | 1143.9865
2017-11-15 08:00 | 11 | 8 | 0.98853 | 1097.0734
2017-11-15 09:00 | 11 | 9 | 0.86124 | 955.8056
2017-11-15 10:00 | 11 | 10 | 0.86587 | 960.9472
2017-11-15 11:00 | 11 | 11 | 0.85096 | 944.4006
2017-11-15 12:00 | 11 | 12 | 0.82682 | 917.6089
2017-11-15 13:00 | 11 | 13 | 0.80137 | 889.3609
2017-11-15 14:00 | 11 | 14 | 0.81382 | 903.1834
2017-11-15 15:00 | 11 | 15 | 0.91451 | 1014.928
2017-11-15 16:00 | 11 | 16 | 1.2098 | 1342.5942
2017-11-15 17:00 | 11 | 17 | 1.7093 | 1897.0145
2017-11-15 18:00 | 11 | 18 | 1.9751 | 2191.9222
2017-11-15 19:00 | 11 | 19 | 1.8839 | 2090.781
2017-11-15 20:00 | 11 | 20 | 1.8003 | 1998.0205
2017-11-15 21:00 | 11 | 21 | 1.6437 | 1824.1636
2017-11-15 22:00 | 11 | 22 | 1.3378 | 1484.6871
2017-11-15 23:00 | 11 | 23 | 1.0494 | 1164.6631
2017-11-16 | 11 | 0 | 0.75761 | 840.8008
2017-11-16 01:00 | 11 | 1 | 0.64832 | 719.5056
2017-11-16 02:00 | 11 | 2 | 0.59883 | 664.5863
2017-11-16 03:00 | 11 | 3 | 0.59482 | 660.1365
2017-11-16 04:00 | 11 | 4 | 0.59718 | 662.7497
2017-11-16 05:00 | 11 | 5 | 0.65129 | 722.8043
2017-11-16 06:00 | 11 | 6 | 0.81504 | 904.5351
2017-11-16 07:00 | 11 | 7 | 1.0678 | 1185.0606
2017-11-16 08:00 | 11 | 8 | 1.0215 | 1133.6238
2017-11-16 09:00 | 11 | 9 | 0.89283 | 990.8665
2017-11-16 10:00 | 11 | 10 | 0.89471 | 992.9561
2017-11-16 11:00 | 11 | 11 | 0.87623 | 972.4409
2017-11-16 12:00 | 11 | 12 | 0.84691 | 939.9021
2017-11-16 13:00 | 11 | 13 | 0.81684 | 906.525
2017-11-16 14:00 | 11 | 14 | 0.82845 | 919.4122
2017-11-16 15:00 | 11 | 15 | 0.9308 | 1033.0028
2017-11-16 16:00 | 11 | 16 | 1.2299 | 1364.9915
2017-11-16 17:00 | 11 | 17 | 1.7393 | 1930.2885
2017-11-16 18:00 | 11 | 18 | 1.9978 | 2217.1176
2017-11-16 19:00 | 11 | 19 | 1.9097 | 2119.4072
2017-11-16 20:00 | 11 | 20 | 1.8293 | 2030.1102
2017-11-16 21:00 | 11 | 21 | 1.6776 | 1861.8377
2017-11-16 22:00 | 11 | 22 | 1.3746 | 1525.5677
2017-11-16 23:00 | 11 | 23 | 1.0904 | 1210.1289
2017-11-17 | 11 | 0 | 0.79668 | 884.1548
2017-11-17 01:00 | 11 | 1 | 0.6841 | 759.2136
2017-11-17 02:00 | 11 | 2 | 0.634 | 703.6094
2017-11-17 03:00 | 11 | 3 | 0.62783 | 696.7676
2017-11-17 04:00 | 11 | 4 | 0.63071 | 699.9683
2017-11-17 05:00 | 11 | 5 | 0.68621 | 761.5546
2017-11-17 06:00 | 11 | 6 | 0.84988 | 943.2025
2017-11-17 07:00 | 11 | 7 | 1.0922 | 1212.1204
2017-11-17 08:00 | 11 | 8 | 1.059 | 1175.2361
2017-11-17 09:00 | 11 | 9 | 0.93883 | 1041.9136
2017-11-17 10:00 | 11 | 10 | 0.95168 | 1056.1708
2017-11-17 11:00 | 11 | 11 | 0.94076 | 1044.0575
2017-11-17 12:00 | 11 | 12 | 0.91748 | 1018.2179
2017-11-17 13:00 | 11 | 13 | 0.8908 | 988.613
2017-11-17 14:00 | 11 | 14 | 0.89642 | 994.8455
2017-11-17 15:00 | 11 | 15 | 0.98576 | 1093.9927
2017-11-17 16:00 | 11 | 16 | 1.2683 | 1407.5372
2017-11-17 17:00 | 11 | 17 | 1.763 | 1956.5985
2017-11-17 18:00 | 11 | 18 | 2.0161 | 2237.5028
2017-11-17 19:00 | 11 | 19 | 1.917 | 2127.5374
2017-11-17 20:00 | 11 | 20 | 1.8267 | 2027.32
2017-11-17 21:00 | 11 | 21 | 1.6564 | 1838.2894
2017-11-17 22:00 | 11 | 22 | 1.3393 | 1486.3317
2017-11-17 23:00 | 11 | 23 | 1.0456 | 1160.4494
2017-11-18 | 11 | 0 | 0.74705 | 829.0815
2017-11-18 01:00 | 11 | 1 | 0.61808 | 685.9449
2017-11-18 02:00 | 11 | 2 | 0.55702 | 618.1814
2017-11-18 03:00 | 11 | 3 | 0.54158 | 601.0459
2017-11-18 04:00 | 11 | 4 | 0.53773 | 596.7788
2017-11-18 05:00 | 11 | 5 | 0.589 | 653.6725
2017-11-18 06:00 | 11 | 6 | 0.75394 | 836.7231
2017-11-18 07:00 | 11 | 7 | 1.0139 | 1125.2146
2017-11-18 08:00 | 11 | 8 | 0.9831 | 1091.0408
2017-11-18 09:00 | 11 | 9 | 0.86426 | 959.1548
2017-11-18 10:00 | 11 | 10 | 0.85716 | 951.2784
2017-11-18 11:00 | 11 | 11 | 0.87281 | 968.6494
2017-11-18 12:00 | 11 | 12 | 0.85385 | 947.6048
2017-11-18 13:00 | 11 | 13 | 0.82615 | 916.8597
2017-11-18 14:00 | 11 | 14 | 0.82965 | 920.746
2017-11-18 15:00 | 11 | 15 | 0.91894 | 1019.8425
2017-11-18 16:00 | 11 | 16 | 1.2128 | 1345.9848
2017-11-18 17:00 | 11 | 17 | 1.7122 | 1900.2573
2017-11-18 18:00 | 11 | 18 | 1.9808 | 2198.2453
2017-11-18 19:00 | 11 | 19 | 1.8956 | 2103.7345
2017-11-18 20:00 | 11 | 20 | 1.8162 | 2015.6739
2017-11-18 21:00 | 11 | 21 | 1.6629 | 1845.5208
2017-11-18 22:00 | 11 | 22 | 1.3541 | 1502.7871
2017-11-18 23:00 | 11 | 23 | 1.0561 | 1172.0873
2017-11-19 | 11 | 0 | 0.75525 | 838.1753
2017-11-19 01:00 | 11 | 1 | 0.64272 | 713.2889
2017-11-19 02:00 | 11 | 2 | 0.5948 | 660.1109
2017-11-19 03:00 | 11 | 3 | 0.58667 | 651.0891
2017-11-19 04:00 | 11 | 4 | 0.59028 | 655.094
2017-11-19 05:00 | 11 | 5 | 0.64896 | 720.2223
2017-11-19 06:00 | 11 | 6 | 0.81998 | 910.0178
2017-11-19 07:00 | 11 | 7 | 1.0766 | 1194.7717
2017-11-19 08:00 | 11 | 8 | 1.0382 | 1152.1662
2017-11-19 09:00 | 11 | 9 | 0.91423 | 1014.617
2017-11-19 10:00 | 11 | 10 | 0.91883 | 1019.7199
2017-11-19 11:00 | 11 | 11 | 0.904 | 1003.2592
2017-11-19 12:00 | 11 | 12 | 0.87444 | 970.4534
2017-11-19 13:00 | 11 | 13 | 0.84406 | 936.7432
2017-11-19 14:00 | 11 | 14 | 0.85134 | 944.8229
2017-11-19 15:00 | 11 | 15 | 0.95003 | 1054.3429
2017-11-19 16:00 | 11 | 16 | 1.2465 | 1383.3295
2017-11-19 17:00 | 11 | 17 | 1.7497 | 1941.8109
2017-11-19 18:00 | 11 | 18 | 2.0124 | 2233.3462
2017-11-19 19:00 | 11 | 19 | 1.9232 | 2134.3612
2017-11-19 20:00 | 11 | 20 | 1.8413 | 2043.5216
2017-11-19 21:00 | 11 | 21 | 1.6874 | 1872.706
2017-11-19 22:00 | 11 | 22 | 1.3748 | 1525.7266
2017-11-19 23:00 | 11 | 23 | 1.0769 | 1195.0936
2017-11-20 | 11 | 0 | 0.7693 | 853.7657
2017-11-20 01:00 | 11 | 1 | 0.65944 | 731.8482
2017-11-20 02:00 | 11 | 2 | 0.61147 | 678.6148
2017-11-20 03:00 | 11 | 3 | 0.6057 | 672.2065
2017-11-20 04:00 | 11 | 4 | 0.60916 | 676.0451
2017-11-20 05:00 | 11 | 5 | 0.66407 | 736.9872
2017-11-20 06:00 | 11 | 6 | 0.84885 | 942.0498
2017-11-20 07:00 | 11 | 7 | 1.0827 | 1201.6066
2017-11-20 08:00 | 11 | 8 | 1.0392 | 1153.3357
2017-11-20 09:00 | 11 | 9 | 0.90107 | 1000.0117
2017-11-20 10:00 | 11 | 10 | 0.90583 | 1005.297
2017-11-20 11:00 | 11 | 11 | 0.88282 | 979.7502
2017-11-20 12:00 | 11 | 12 | 0.85282 | 946.4639
2017-11-20 13:00 | 11 | 13 | 0.82488 | 915.4585
2017-11-20 14:00 | 11 | 14 | 0.84081 | 933.1373
2017-11-20 15:00 | 11 | 15 | 0.94771 | 1051.775
2017-11-20 16:00 | 11 | 16 | 1.2489 | 1386.0839
2017-11-20 17:00 | 11 | 17 | 1.762 | 1955.5031
2017-11-20 18:00 | 11 | 18 | 2.0202 | 2242.0258
2017-11-20 19:00 | 11 | 19 | 1.9305 | 2142.5243
2017-11-20 20:00 | 11 | 20 | 1.8476 | 2050.5114
2017-11-20 21:00 | 11 | 21 | 1.6915 | 1877.2773
2017-11-20 22:00 | 11 | 22 | 1.3848 | 1536.8565
2017-11-20 23:00 | 11 | 23 | 1.0983 | 1218.8483
2017-11-21 | 11 | 0 | 0.81003 | 898.9748
2017-11-21 01:00 | 11 | 1 | 0.69751 | 774.0968
2017-11-21 02:00 | 11 | 2 | 0.65175 | 723.3135
2017-11-21 03:00 | 11 | 3 | 0.65148 | 723.0123
2017-11-21 04:00 | 11 | 4 | 0.65496 | 726.8797
2017-11-21 05:00 | 11 | 5 | 0.71164 | 789.7783
2017-11-21 06:00 | 11 | 6 | 0.87733 | 973.663
2017-11-21 07:00 | 11 | 7 | 1.151 | 1277.3755
2017-11-21 08:00 | 11 | 8 | 1.1153 | 1237.7622
2017-11-21 09:00 | 11 | 9 | 0.99845 | 1108.0845
2017-11-21 10:00 | 11 | 10 | 1.0296 | 1142.6554
2017-11-21 11:00 | 11 | 11 | 1.0101 | 1120.9662
2017-11-21 12:00 | 11 | 12 | 0.98251 | 1090.3935
2017-11-21 13:00 | 11 | 13 | 0.95365 | 1058.3575
2017-11-21 14:00 | 11 | 14 | 0.96602 | 1072.0869
2017-11-21 15:00 | 11 | 15 | 1.0561 | 1172.0327
2017-11-21 16:00 | 11 | 16 | 1.3435 | 1491.0445
2017-11-21 17:00 | 11 | 17 | 1.8498 | 2052.865
2017-11-21 18:00 | 11 | 18 | 2.0941 | 2323.993
2017-11-21 19:00 | 11 | 19 | 1.9966 | 2215.8609
2017-11-21 20:00 | 11 | 20 | 1.9121 | 2122.0281
2017-11-21 21:00 | 11 | 21 | 1.7516 | 1943.9226
2017-11-21 22:00 | 11 | 22 | 1.4355 | 1593.0726
2017-11-21 23:00 | 11 | 23 | 1.1478 | 1273.7954
2017-11-22 | 11 | 0 | 0.8481 | 941.228
2017-11-22 01:00 | 11 | 1 | 0.7348 | 815.4848
2017-11-22 02:00 | 11 | 2 | 0.68217 | 757.0748
2017-11-22 03:00 | 11 | 3 | 0.67649 | 750.7683
2017-11-22 04:00 | 11 | 4 | 0.67296 | 746.8513
2017-11-22 05:00 | 11 | 5 | 0.72589 | 805.5992
2017-11-22 06:00 | 11 | 6 | 0.8898 | 987.5004
2017-11-22 07:00 | 11 | 7 | 1.1555 | 1282.4163
2017-11-22 08:00 | 11 | 8 | 1.1176 | 1240.2704
2017-11-22 09:00 | 11 | 9 | 1.0013 | 1111.269
2017-11-22 10:00 | 11 | 10 | 1.0284 | 1141.2702
2017-11-22 11:00 | 11 | 11 | 1.0097 | 1120.6189
2017-11-22 12:00 | 11 | 12 | 0.98515 | 1093.3155
2017-11-22 13:00 | 11 | 13 | 0.95631 | 1061.3164
2017-11-22 14:00 | 11 | 14 | 0.96379 | 1069.6146
2017-11-22 15:00 | 11 | 15 | 1.0555 | 1171.4388
2017-11-22 16:00 | 11 | 16 | 1.3403 | 1487.4958
2017-11-22 17:00 | 11 | 17 | 1.8463 | 2049.0382
2017-11-22 18:00 | 11 | 18 | 2.09 | 2319.4927
2017-11-22 19:00 | 11 | 19 | 1.9899 | 2208.429
2017-11-22 20:00 | 11 | 20 | 1.8994 | 2107.9521
2017-11-22 21:00 | 11 | 21 | 1.7358 | 1926.4101
2017-11-22 22:00 | 11 | 22 | 1.4244 | 1580.8514
2017-11-22 23:00 | 11 | 23 | 1.1312 | 1255.3924
2017-11-23 | 11 | 0 | 0.83883 | 930.9371
2017-11-23 01:00 | 11 | 1 | 0.7255 | 805.1646
2017-11-23 02:00 | 11 | 2 | 0.6731 | 747.0065
2017-11-23 03:00 | 11 | 3 | 0.66537 | 738.4334
2017-11-23 04:00 | 11 | 4 | 0.66358 | 736.4408
2017-11-23 05:00 | 11 | 5 | 0.71914 | 798.1038
2017-11-23 06:00 | 11 | 6 | 0.87999 | 976.6172
2017-11-23 07:00 | 11 | 7 | 1.1509 | 1277.2718
2017-11-23 08:00 | 11 | 8 | 1.1096 | 1231.4304
2017-11-23 09:00 | 11 | 9 | 0.98452 | 1092.6253
2017-11-23 10:00 | 11 | 10 | 1.0112 | 1122.225
2017-11-23 11:00 | 11 | 11 | 0.98827 | 1096.7884
2017-11-23 12:00 | 11 | 12 | 0.96028 | 1065.7227
2017-11-23 13:00 | 11 | 13 | 0.93092 | 1033.1323
2017-11-23 14:00 | 11 | 14 | 0.93531 | 1038.0113
2017-11-23 15:00 | 11 | 15 | 1.0256 | 1138.1946
2017-11-23 16:00 | 11 | 16 | 1.3122 | 1456.2946
2017-11-23 17:00 | 11 | 17 | 1.8152 | 2014.4665
2017-11-23 18:00 | 11 | 18 | 2.0621 | 2288.4745
2017-11-23 19:00 | 11 | 19 | 1.9627 | 2178.2424
2017-11-23 20:00 | 11 | 20 | 1.8719 | 2077.4627
2017-11-23 21:00 | 11 | 21 | 1.7164 | 1904.8924
2017-11-23 22:00 | 11 | 22 | 1.4062 | 1560.5854
2017-11-23 23:00 | 11 | 23 | 1.1105 | 1232.4759
2017-11-24 | 11 | 0 | 0.81143 | 900.5268
2017-11-24 01:00 | 11 | 1 | 0.68827 | 763.8431
2017-11-24 02:00 | 11 | 2 | 0.63239 | 701.8327
2017-11-24 03:00 | 11 | 3 | 0.6177 | 685.5278
2017-11-24 04:00 | 11 | 4 | 0.61266 | 679.9358
2017-11-24 05:00 | 11 | 5 | 0.66362 | 736.4834
2017-11-24 06:00 | 11 | 6 | 0.82041 | 910.4936
2017-11-24 07:00 | 11 | 7 | 1.0838 | 1202.8433
2017-11-24 08:00 | 11 | 8 | 1.0448 | 1159.5317
2017-11-24 09:00 | 11 | 9 | 0.92566 | 1027.3036
2017-11-24 10:00 | 11 | 10 | 0.94451 | 1048.2236
2017-11-24 11:00 | 11 | 11 | 0.93656 | 1039.3917
2017-11-24 12:00 | 11 | 12 | 0.91267 | 1012.8777
2017-11-24 13:00 | 11 | 13 | 0.90123 | 1000.1891
2017-11-24 14:00 | 11 | 14 | 0.91544 | 1015.9563
2017-11-24 15:00 | 11 | 15 | 1.0037 | 1113.9348
2017-11-24 16:00 | 11 | 16 | 1.2872 | 1428.5103
2017-11-24 17:00 | 11 | 17 | 1.7863 | 1982.4565
2017-11-24 18:00 | 11 | 18 | 2.034 | 2257.3277
2017-11-24 19:00 | 11 | 19 | 1.9343 | 2146.7324
2017-11-24 20:00 | 11 | 20 | 1.8453 | 2047.935
2017-11-24 21:00 | 11 | 21 | 1.6825 | 1867.2526
2017-11-24 22:00 | 11 | 22 | 1.3728 | 1523.5596
2017-11-24 23:00 | 11 | 23 | 1.0839 | 1202.953
2017-11-25 | 11 | 0 | 0.79289 | 879.9559
2017-11-25 01:00 | 11 | 1 | 0.67471 | 748.7936
2017-11-25 02:00 | 11 | 2 | 0.62353 | 691.9956
2017-11-25 03:00 | 11 | 3 | 0.61556 | 683.1469
2017-11-25 04:00 | 11 | 4 | 0.61766 | 685.4825
2017-11-25 05:00 | 11 | 5 | 0.67838 | 752.862
2017-11-25 06:00 | 11 | 6 | 0.87122 | 966.8839
2017-11-25 07:00 | 11 | 7 | 1.1327 | 1257.0964
2017-11-25 08:00 | 11 | 8 | 1.1002 | 1221.0002
2017-11-25 09:00 | 11 | 9 | 0.98974 | 1098.4191
2017-11-25 10:00 | 11 | 10 | 1.007 | 1117.5805
2017-11-25 11:00 | 11 | 11 | 0.98954 | 1098.1887
2017-11-25 12:00 | 11 | 12 | 0.96899 | 1075.3909
2017-11-25 13:00 | 11 | 13 | 0.93266 | 1035.0692
2017-11-25 14:00 | 11 | 14 | 0.93527 | 1037.9634
2017-11-25 15:00 | 11 | 15 | 1.0388 | 1152.9055
2017-11-25 16:00 | 11 | 16 | 1.3297 | 1475.696
2017-11-25 17:00 | 11 | 17 | 1.8412 | 2043.3379
2017-11-25 18:00 | 11 | 18 | 2.0918 | 2321.4379
2017-11-25 19:00 | 11 | 19 | 2.0065 | 2226.8661
2017-11-25 20:00 | 11 | 20 | 1.9258 | 2137.2823
2017-11-25 21:00 | 11 | 21 | 1.77 | 1964.381
2017-11-25 22:00 | 11 | 22 | 1.4596 | 1619.8433
2017-11-25 23:00 | 11 | 23 | 1.1719 | 1300.5587
2017-11-26 | 11 | 0 | 0.87618 | 972.385
2017-11-26 01:00 | 11 | 1 | 0.75728 | 840.4281
2017-11-26 02:00 | 11 | 2 | 0.71344 | 791.7755
2017-11-26 03:00 | 11 | 3 | 0.7168 | 795.5027
2017-11-26 04:00 | 11 | 4 | 0.72492 | 804.5168
2017-11-26 05:00 | 11 | 5 | 0.77378 | 858.743
2017-11-26 06:00 | 11 | 6 | 0.96352 | 1069.3213
2017-11-26 07:00 | 11 | 7 | 1.2071 | 1339.6951
2017-11-26 08:00 | 11 | 8 | 1.1697 | 1298.1444
2017-11-26 09:00 | 11 | 9 | 1.0418 | 1156.1642
2017-11-26 10:00 | 11 | 10 | 1.0603 | 1176.7064
2017-11-26 11:00 | 11 | 11 | 1.0334 | 1146.8676
2017-11-26 12:00 | 11 | 12 | 0.99589 | 1105.2405
2017-11-26 13:00 | 11 | 13 | 0.95954 | 1064.8944
2017-11-26 14:00 | 11 | 14 | 0.96597 | 1072.0313
2017-11-26 15:00 | 11 | 15 | 1.0653 | 1182.3207
2017-11-26 16:00 | 11 | 16 | 1.3624 | 1511.9556
2017-11-26 17:00 | 11 | 17 | 1.8865 | 2093.6872
2017-11-26 18:00 | 11 | 18 | 2.1396 | 2374.5589
2017-11-26 19:00 | 11 | 19 | 2.0492 | 2274.1858
2017-11-26 20:00 | 11 | 20 | 1.9753 | 2192.1394
2017-11-26 21:00 | 11 | 21 | 1.8213 | 2021.2793
2017-11-26 22:00 | 11 | 22 | 1.5115 | 1677.4675
2017-11-26 23:00 | 11 | 23 | 1.2108 | 1343.7369
2017-11-27 | 11 | 0 | 0.90325 | 1002.426
2017-11-27 01:00 | 11 | 1 | 0.7902 | 876.9652
2017-11-27 02:00 | 11 | 2 | 0.73574 | 816.5255
2017-11-27 03:00 | 11 | 3 | 0.72624 | 805.9847
2017-11-27 04:00 | 11 | 4 | 0.72525 | 804.8855
2017-11-27 05:00 | 11 | 5 | 0.77646 | 861.7218
2017-11-27 06:00 | 11 | 6 | 0.93825 | 1041.2725
2017-11-27 07:00 | 11 | 7 | 1.2107 | 1343.6169
2017-11-27 08:00 | 11 | 8 | 1.1647 | 1292.6397
2017-11-27 09:00 | 11 | 9 | 1.0423 | 1156.7923
2017-11-27 10:00 | 11 | 10 | 1.0793 | 1197.821
2017-11-27 11:00 | 11 | 11 | 1.0547 | 1170.4862
2017-11-27 12:00 | 11 | 12 | 1.0248 | 1137.3026
2017-11-27 13:00 | 11 | 13 | 0.99069 | 1099.467
2017-11-27 14:00 | 11 | 14 | 0.99088 | 1099.6844
2017-11-27 15:00 | 11 | 15 | 1.0784 | 1196.7785
2017-11-27 16:00 | 11 | 16 | 1.3622 | 1511.7984
2017-11-27 17:00 | 11 | 17 | 1.8711 | 2076.531
2017-11-27 18:00 | 11 | 18 | 2.1449 | 2380.4275
2017-11-27 19:00 | 11 | 19 | 2.0226 | 2244.6683
2017-11-27 20:00 | 11 | 20 | 1.9168 | 2127.297
2017-11-27 21:00 | 11 | 21 | 1.7506 | 1942.833
2017-11-27 22:00 | 11 | 22 | 1.4339 | 1591.3294
2017-11-27 23:00 | 11 | 23 | 1.1258 | 1249.3763
2017-11-28 | 11 | 0 | 0.825 | 915.5894
2017-11-28 01:00 | 11 | 1 | 0.70521 | 782.6461
2017-11-28 02:00 | 11 | 2 | 0.66209 | 734.7876
2017-11-28 03:00 | 11 | 3 | 0.66458 | 737.551
2017-11-28 04:00 | 11 | 4 | 0.66613 | 739.2719
2017-11-28 05:00 | 11 | 5 | 0.72325 | 802.6673
2017-11-28 06:00 | 11 | 6 | 0.90563 | 1005.0654
2017-11-28 07:00 | 11 | 7 | 1.1497 | 1275.9198
2017-11-28 08:00 | 11 | 8 | 1.1219 | 1245.1046
2017-11-28 09:00 | 11 | 9 | 1.0083 | 1118.9694
2017-11-28 10:00 | 11 | 10 | 1.0422 | 1156.6676
2017-11-28 11:00 | 11 | 11 | 1.0227 | 1134.983
2017-11-28 12:00 | 11 | 12 | 0.99535 | 1104.636
2017-11-28 13:00 | 11 | 13 | 0.95536 | 1060.2596
2017-11-28 14:00 | 11 | 14 | 0.95145 | 1055.9231
2017-11-28 15:00 | 11 | 15 | 1.0378 | 1151.7344
2017-11-28 16:00 | 11 | 16 | 1.3212 | 1466.3235
2017-11-28 17:00 | 11 | 17 | 1.7911 | 1987.8032
2017-11-28 18:00 | 11 | 18 | 2.0876 | 2316.7744
2017-11-28 19:00 | 11 | 19 | 1.9712 | 2187.6226
2017-11-28 20:00 | 11 | 20 | 1.8797 | 2086.1416
2017-11-28 21:00 | 11 | 21 | 1.7176 | 1906.2021
2017-11-28 22:00 | 11 | 22 | 1.4066 | 1561.0091
2017-11-28 23:00 | 11 | 23 | 1.1146 | 1236.9489
2017-11-29 | 11 | 0 | 0.81766 | 907.4432
2017-11-29 01:00 | 11 | 1 | 0.69702 | 773.555
2017-11-29 02:00 | 11 | 2 | 0.64494 | 715.7506
2017-11-29 03:00 | 11 | 3 | 0.64149 | 711.9231
2017-11-29 04:00 | 11 | 4 | 0.64341 | 714.0546
2017-11-29 05:00 | 11 | 5 | 0.69721 | 773.764
2017-11-29 06:00 | 11 | 6 | 0.85947 | 953.8439
2017-11-29 07:00 | 11 | 7 | 1.1041 | 1225.3065
2017-11-29 08:00 | 11 | 8 | 1.053 | 1168.6188
2017-11-29 09:00 | 11 | 9 | 0.91182 | 1011.9352
2017-11-29 10:00 | 11 | 10 | 0.91367 | 1013.9912
2017-11-29 11:00 | 11 | 11 | 0.88752 | 984.9717
2017-11-29 12:00 | 11 | 12 | 0.85928 | 953.6309
2017-11-29 13:00 | 11 | 13 | 0.83146 | 922.7506
2017-11-29 14:00 | 11 | 14 | 0.84818 | 941.3159
2017-11-29 15:00 | 11 | 15 | 0.95433 | 1059.1187
2017-11-29 16:00 | 11 | 16 | 1.2556 | 1393.4135
2017-11-29 17:00 | 11 | 17 | 1.7648 | 1958.5996
2017-11-29 18:00 | 11 | 18 | 2.0256 | 2247.9739
2017-11-29 19:00 | 11 | 19 | 1.9369 | 2149.5794
2017-11-29 20:00 | 11 | 20 | 1.8503 | 2053.4533
2017-11-29 21:00 | 11 | 21 | 1.6853 | 1870.3153
2017-11-29 22:00 | 11 | 22 | 1.3741 | 1525.0002
2017-11-29 23:00 | 11 | 23 | 1.0832 | 1202.0955
2017-11-30 | 11 | 0 | 0.78677 | 873.155
2017-11-30 01:00 | 11 | 1 | 0.67202 | 745.8131
2017-11-30 02:00 | 11 | 2 | 0.61974 | 687.7836
2017-11-30 03:00 | 11 | 3 | 0.6103 | 677.3122
2017-11-30 04:00 | 11 | 4 | 0.61272 | 679.9995
2017-11-30 05:00 | 11 | 5 | 0.66915 | 742.6247
2017-11-30 06:00 | 11 | 6 | 0.83016 | 921.3115
2017-11-30 07:00 | 11 | 7 | 1.0842 | 1203.2472
2017-11-30 08:00 | 11 | 8 | 1.0513 | 1166.7344
2017-11-30 09:00 | 11 | 9 | 0.91128 | 1011.344
2017-11-30 10:00 | 11 | 10 | 0.90766 | 1007.322
2017-11-30 11:00 | 11 | 11 | 0.88706 | 984.4644
2017-11-30 12:00 | 11 | 12 | 0.86352 | 958.3348
2017-11-30 13:00 | 11 | 13 | 0.83641 | 928.251
2017-11-30 14:00 | 11 | 14 | 0.84993 | 943.2534
2017-11-30 15:00 | 11 | 15 | 0.95197 | 1056.5015
2017-11-30 16:00 | 11 | 16 | 1.2431 | 1379.5389
2017-11-30 17:00 | 11 | 17 | 1.7443 | 1935.8688
2017-11-30 18:00 | 11 | 18 | 2.0026 | 2222.4789
2017-11-30 19:00 | 11 | 19 | 1.9131 | 2123.1389
2017-11-30 20:00 | 11 | 20 | 1.8298 | 2030.7096
2017-11-30 21:00 | 11 | 21 | 1.6707 | 1854.1117
2017-11-30 22:00 | 11 | 22 | 1.3617 | 1511.2445
2017-11-30 23:00 | 11 | 23 | 1.0709 | 1188.4945
2017-12-01 | 12 | 0 | 0.83119 | 922.4524
2017-12-01 01:00 | 12 | 1 | 0.71298 | 791.2664
2017-12-01 02:00 | 12 | 2 | 0.65599 | 728.0241
2017-12-01 03:00 | 12 | 3 | 0.64373 | 714.413
2017-12-01 04:00 | 12 | 4 | 0.64162 | 712.0727
2017-12-01 05:00 | 12 | 5 | 0.70097 | 777.9418
2017-12-01 06:00 | 12 | 6 | 0.90301 | 1002.1635
2017-12-01 07:00 | 12 | 7 | 1.2147 | 1348.032
2017-12-01 08:00 | 12 | 8 | 1.1679 | 1296.1733
2017-12-01 09:00 | 12 | 9 | 1.0092 | 1120.0358
2017-12-01 10:00 | 12 | 10 | 1.0154 | 1126.8428
2017-12-01 11:00 | 12 | 11 | 0.98955 | 1098.2004
2017-12-01 12:00 | 12 | 12 | 0.96239 | 1068.0672
2017-12-01 13:00 | 12 | 13 | 0.92683 | 1028.592
2017-12-01 14:00 | 12 | 14 | 0.9579 | 1063.0735
2017-12-01 15:00 | 12 | 15 | 1.0706 | 1188.1481
2017-12-01 16:00 | 12 | 16 | 1.3947 | 1547.8042
2017-12-01 17:00 | 12 | 17 | 1.9394 | 2152.3946
2017-12-01 18:00 | 12 | 18 | 2.2045 | 2446.5125
2017-12-01 19:00 | 12 | 19 | 2.0516 | 2276.8552
2017-12-01 20:00 | 12 | 20 | 1.9561 | 2170.8657
2017-12-01 21:00 | 12 | 21 | 1.7973 | 1994.6355
2017-12-01 22:00 | 12 | 22 | 1.4832 | 1646.112
2017-12-01 23:00 | 12 | 23 | 1.1857 | 1315.9059
2017-12-02 | 12 | 0 | 0.88346 | 980.4709
2017-12-02 01:00 | 12 | 1 | 0.76955 | 854.0456
2017-12-02 02:00 | 12 | 2 | 0.7143 | 792.7364
2017-12-02 03:00 | 12 | 3 | 0.70497 | 782.3777
2017-12-02 04:00 | 12 | 4 | 0.70738 | 785.0487
2017-12-02 05:00 | 12 | 5 | 0.77722 | 862.5654
2017-12-02 06:00 | 12 | 6 | 1.0034 | 1113.5927
2017-12-02 07:00 | 12 | 7 | 1.3035 | 1446.5795
2017-12-02 08:00 | 12 | 8 | 1.2442 | 1380.7642
2017-12-02 09:00 | 12 | 9 | 1.103 | 1224.1264
2017-12-02 10:00 | 12 | 10 | 1.1197 | 1242.6639
2017-12-02 11:00 | 12 | 11 | 1.1113 | 1233.3116
2017-12-02 12:00 | 12 | 12 | 1.1089 | 1230.6154
2017-12-02 13:00 | 12 | 13 | 1.0847 | 1203.771
2017-12-02 14:00 | 12 | 14 | 1.0982 | 1218.7705
2017-12-02 15:00 | 12 | 15 | 1.2104 | 1343.2999
2017-12-02 16:00 | 12 | 16 | 1.5379 | 1706.7513
2017-12-02 17:00 | 12 | 17 | 2.0999 | 2330.4906
2017-12-02 18:00 | 12 | 18 | 2.3554 | 2613.974
2017-12-02 19:00 | 12 | 19 | 2.2127 | 2455.6864
2017-12-02 20:00 | 12 | 20 | 2.1207 | 2353.6035
2017-12-02 21:00 | 12 | 21 | 1.9495 | 2163.6082
2017-12-02 22:00 | 12 | 22 | 1.6147 | 1792.0049
2017-12-02 23:00 | 12 | 23 | 1.3072 | 1450.6935
2017-12-03 | 12 | 0 | 0.99511 | 1104.3722
2017-12-03 01:00 | 12 | 1 | 0.87857 | 975.042
2017-12-03 02:00 | 12 | 2 | 0.82627 | 916.9926
2017-12-03 03:00 | 12 | 3 | 0.81887 | 908.7814
2017-12-03 04:00 | 12 | 4 | 0.81405 | 903.4311
2017-12-03 05:00 | 12 | 5 | 0.87156 | 967.2531
2017-12-03 06:00 | 12 | 6 | 1.0782 | 1196.5512
2017-12-03 07:00 | 12 | 7 | 1.4075 | 1562.0779
2017-12-03 08:00 | 12 | 8 | 1.3401 | 1487.2808
2017-12-03 09:00 | 12 | 9 | 1.1618 | 1289.3387
2017-12-03 10:00 | 12 | 10 | 1.1682 | 1296.5087
2017-12-03 11:00 | 12 | 11 | 1.1346 | 1259.2012
2017-12-03 12:00 | 12 | 12 | 1.088 | 1207.429
2017-12-03 13:00 | 12 | 13 | 1.051 | 1166.4435
2017-12-03 14:00 | 12 | 14 | 1.0609 | 1177.3452
2017-12-03 15:00 | 12 | 15 | 1.1684 | 1296.6688
2017-12-03 16:00 | 12 | 16 | 1.5091 | 1674.7817
2017-12-03 17:00 | 12 | 17 | 2.0716 | 2299.0989
2017-12-03 18:00 | 12 | 18 | 2.311 | 2564.7236
2017-12-03 19:00 | 12 | 19 | 2.1557 | 2392.3802
2017-12-03 20:00 | 12 | 20 | 2.0654 | 2292.2024
2017-12-03 21:00 | 12 | 21 | 1.9055 | 2114.6979
2017-12-03 22:00 | 12 | 22 | 1.5781 | 1751.4101
2017-12-03 23:00 | 12 | 23 | 1.2706 | 1410.1008
2017-12-04 | 12 | 0 | 0.94519 | 1048.9721
2017-12-04 01:00 | 12 | 1 | 0.8286 | 919.5866
2017-12-04 02:00 | 12 | 2 | 0.77388 | 858.8576
2017-12-04 03:00 | 12 | 3 | 0.76282 | 846.5819
2017-12-04 04:00 | 12 | 4 | 0.76422 | 848.1376
2017-12-04 05:00 | 12 | 5 | 0.82006 | 910.1025
2017-12-04 06:00 | 12 | 6 | 1.0203 | 1132.3554
2017-12-04 07:00 | 12 | 7 | 1.3132 | 1457.367
2017-12-04 08:00 | 12 | 8 | 1.2446 | 1381.2482
2017-12-04 09:00 | 12 | 9 | 1.0581 | 1174.3332
2017-12-04 10:00 | 12 | 10 | 1.0606 | 1177.083
2017-12-04 11:00 | 12 | 11 | 1.0427 | 1157.1685
2017-12-04 12:00 | 12 | 12 | 1.0252 | 1137.8233
2017-12-04 13:00 | 12 | 13 | 1.0058 | 1116.2493
2017-12-04 14:00 | 12 | 14 | 1.0205 | 1132.592
2017-12-04 15:00 | 12 | 15 | 1.1291 | 1253.0542
2017-12-04 16:00 | 12 | 16 | 1.4545 | 1614.2058
2017-12-04 17:00 | 12 | 17 | 2.0139 | 2234.9862
2017-12-04 18:00 | 12 | 18 | 2.2622 | 2510.6029
2017-12-04 19:00 | 12 | 19 | 2.1047 | 2335.7663
2017-12-04 20:00 | 12 | 20 | 2.0086 | 2229.0989
2017-12-04 21:00 | 12 | 21 | 1.8495 | 2052.5902
2017-12-04 22:00 | 12 | 22 | 1.5387 | 1707.6858
2017-12-04 23:00 | 12 | 23 | 1.2455 | 1382.2925
2017-12-05 | 12 | 0 | 0.9381 | 1041.1098
2017-12-05 01:00 | 12 | 1 | 0.82505 | 915.6449
2017-12-05 02:00 | 12 | 2 | 0.77526 | 860.3805
2017-12-05 03:00 | 12 | 3 | 0.76872 | 853.1304
2017-12-05 04:00 | 12 | 4 | 0.76893 | 853.3578
2017-12-05 05:00 | 12 | 5 | 0.83407 | 925.6475
2017-12-05 06:00 | 12 | 6 | 1.0405 | 1154.7785
2017-12-05 07:00 | 12 | 7 | 1.3616 | 1511.1506
2017-12-05 08:00 | 12 | 8 | 1.2933 | 1435.3573
2017-12-05 09:00 | 12 | 9 | 1.1088 | 1230.5129
2017-12-05 10:00 | 12 | 10 | 1.1151 | 1237.5657
2017-12-05 11:00 | 12 | 11 | 1.0755 | 1193.5983
2017-12-05 12:00 | 12 | 12 | 1.0451 | 1159.8184
2017-12-05 13:00 | 12 | 13 | 1.0191 | 1131.0538
2017-12-05 14:00 | 12 | 14 | 1.036 | 1149.737
2017-12-05 15:00 | 12 | 15 | 1.1389 | 1263.9649
2017-12-05 16:00 | 12 | 16 | 1.4603 | 1620.5967
2017-12-05 17:00 | 12 | 17 | 2.0199 | 2241.7092
2017-12-05 18:00 | 12 | 18 | 2.2774 | 2527.4865
2017-12-05 19:00 | 12 | 19 | 2.1155 | 2347.7467
2017-12-05 20:00 | 12 | 20 | 2.01 | 2230.661
2017-12-05 21:00 | 12 | 21 | 1.8464 | 2049.1146
2017-12-05 22:00 | 12 | 22 | 1.5372 | 1705.9928
2017-12-05 23:00 | 12 | 23 | 1.2391 | 1375.177
2017-12-06 | 12 | 0 | 0.92377 | 1025.1964
2017-12-06 01:00 | 12 | 1 | 0.81909 | 909.0228
2017-12-06 02:00 | 12 | 2 | 0.7562 | 839.2298
2017-12-06 03:00 | 12 | 3 | 0.74426 | 825.9854
2017-12-06 04:00 | 12 | 4 | 0.73837 | 819.4423
2017-12-06 05:00 | 12 | 5 | 0.82052 | 910.6095
2017-12-06 06:00 | 12 | 6 | 1.0168 | 1128.4966
2017-12-06 07:00 | 12 | 7 | 1.325 | 1470.4934
2017-12-06 08:00 | 12 | 8 | 1.267 | 1406.0706
2017-12-06 09:00 | 12 | 9 | 1.102 | 1222.9622
2017-12-06 10:00 | 12 | 10 | 1.0976 | 1218.1617
2017-12-06 11:00 | 12 | 11 | 1.1585 | 1285.7228
2017-12-06 12:00 | 12 | 12 | 1.109 | 1230.7804
2017-12-06 13:00 | 12 | 13 | 1.0937 | 1213.7822
2017-12-06 14:00 | 12 | 14 | 1.101 | 1221.93
2017-12-06 15:00 | 12 | 15 | 1.2113 | 1344.3023
2017-12-06 16:00 | 12 | 16 | 1.5345 | 1703.0283
2017-12-06 17:00 | 12 | 17 | 2.0548 | 2280.3839
2017-12-06 18:00 | 12 | 18 | 2.3116 | 2565.3701
2017-12-06 19:00 | 12 | 19 | 2.1429 | 2378.1976
2017-12-06 20:00 | 12 | 20 | 2.0402 | 2264.1811
2017-12-06 21:00 | 12 | 21 | 1.8791 | 2085.4675
2017-12-06 22:00 | 12 | 22 | 1.559 | 1730.1695
2017-12-06 23:00 | 12 | 23 | 1.2616 | 1400.1033
2017-12-07 | 12 | 0 | 0.94877 | 1052.9477
2017-12-07 01:00 | 12 | 1 | 0.83378 | 925.3325
2017-12-07 02:00 | 12 | 2 | 0.77323 | 858.1319
2017-12-07 03:00 | 12 | 3 | 0.7621 | 845.785
2017-12-07 04:00 | 12 | 4 | 0.76048 | 843.9804
2017-12-07 05:00 | 12 | 5 | 0.82345 | 913.8709
2017-12-07 06:00 | 12 | 6 | 1.0213 | 1133.4078
2017-12-07 07:00 | 12 | 7 | 1.3316 | 1477.7877
2017-12-07 08:00 | 12 | 8 | 1.2799 | 1420.4066
2017-12-07 09:00 | 12 | 9 | 1.1166 | 1239.189
2017-12-07 10:00 | 12 | 10 | 1.1343 | 1258.8931
2017-12-07 11:00 | 12 | 11 | 1.0909 | 1210.6446
2017-12-07 12:00 | 12 | 12 | 1.0666 | 1183.7164
2017-12-07 13:00 | 12 | 13 | 1.0568 | 1172.877
2017-12-07 14:00 | 12 | 14 | 1.069 | 1186.3329
2017-12-07 15:00 | 12 | 15 | 1.1702 | 1298.7108
2017-12-07 16:00 | 12 | 16 | 1.4919 | 1655.6646
2017-12-07 17:00 | 12 | 17 | 2.0461 | 2270.7347
2017-12-07 18:00 | 12 | 18 | 2.2877 | 2538.8736
2017-12-07 19:00 | 12 | 19 | 2.1247 | 2357.9756
2017-12-07 20:00 | 12 | 20 | 2.0237 | 2245.863
2017-12-07 21:00 | 12 | 21 | 1.8648 | 2069.6024
2017-12-07 22:00 | 12 | 22 | 1.5404 | 1709.5202
2017-12-07 23:00 | 12 | 23 | 1.2428 | 1379.2841
2017-12-08 | 12 | 0 | 0.92556 | 1027.1854
2017-12-08 01:00 | 12 | 1 | 0.80891 | 897.7242
2017-12-08 02:00 | 12 | 2 | 0.75372 | 836.479
2017-12-08 03:00 | 12 | 3 | 0.74612 | 828.0482
2017-12-08 04:00 | 12 | 4 | 0.74507 | 826.8804
2017-12-08 05:00 | 12 | 5 | 0.80887 | 897.6825
2017-12-08 06:00 | 12 | 6 | 1.0127 | 1123.8463
2017-12-08 07:00 | 12 | 7 | 1.3306 | 1476.6511
2017-12-08 08:00 | 12 | 8 | 1.2502 | 1387.4261
2017-12-08 09:00 | 12 | 9 | 1.0593 | 1175.6435
2017-12-08 10:00 | 12 | 10 | 1.0584 | 1174.6305
2017-12-08 11:00 | 12 | 11 | 1.0418 | 1156.1605
2017-12-08 12:00 | 12 | 12 | 0.99958 | 1109.3358
2017-12-08 13:00 | 12 | 13 | 0.96701 | 1073.192
2017-12-08 14:00 | 12 | 14 | 0.97848 | 1085.9145
2017-12-08 15:00 | 12 | 15 | 1.0906 | 1210.3288
2017-12-08 16:00 | 12 | 16 | 1.4223 | 1578.4465
2017-12-08 17:00 | 12 | 17 | 1.9864 | 2204.5493
2017-12-08 18:00 | 12 | 18 | 2.2416 | 2487.6819
2017-12-08 19:00 | 12 | 19 | 2.0838 | 2312.6003
2017-12-08 20:00 | 12 | 20 | 1.9922 | 2210.9275
2017-12-08 21:00 | 12 | 21 | 1.8331 | 2034.3911
2017-12-08 22:00 | 12 | 22 | 1.5154 | 1681.8323
2017-12-08 23:00 | 12 | 23 | 1.2199 | 1353.8458
2017-12-09 | 12 | 0 | 0.91735 | 1018.0738
2017-12-09 01:00 | 12 | 1 | 0.80447 | 892.8012
2017-12-09 02:00 | 12 | 2 | 0.75044 | 832.8448
2017-12-09 03:00 | 12 | 3 | 0.74453 | 826.2831
2017-12-09 04:00 | 12 | 4 | 0.74697 | 828.9873
2017-12-09 05:00 | 12 | 5 | 0.81127 | 900.344
2017-12-09 06:00 | 12 | 6 | 1.0222 | 1134.3934
2017-12-09 07:00 | 12 | 7 | 1.3539 | 1502.5982
2017-12-09 08:00 | 12 | 8 | 1.2828 | 1423.6622
2017-12-09 09:00 | 12 | 9 | 1.104 | 1225.2572
2017-12-09 10:00 | 12 | 10 | 1.1065 | 1228.0436
2017-12-09 11:00 | 12 | 11 | 1.0879 | 1207.3978
2017-12-09 12:00 | 12 | 12 | 1.0444 | 1159.0978
2017-12-09 13:00 | 12 | 13 | 1.0073 | 1117.9499
2017-12-09 14:00 | 12 | 14 | 1.0159 | 1127.5012
2017-12-09 15:00 | 12 | 15 | 1.1267 | 1250.426
2017-12-09 16:00 | 12 | 16 | 1.4523 | 1611.7463
2017-12-09 17:00 | 12 | 17 | 2.0161 | 2237.426
2017-12-09 18:00 | 12 | 18 | 2.264 | 2512.5607
2017-12-09 19:00 | 12 | 19 | 2.1044 | 2335.503
2017-12-09 20:00 | 12 | 20 | 2.0116 | 2232.5076
2017-12-09 21:00 | 12 | 21 | 1.8488 | 2051.7838
2017-12-09 22:00 | 12 | 22 | 1.5247 | 1692.1482
2017-12-09 23:00 | 12 | 23 | 1.2139 | 1347.1554
2017-12-10 | 12 | 0 | 0.89272 | 990.7381
2017-12-10 01:00 | 12 | 1 | 0.77505 | 860.1529
2017-12-10 02:00 | 12 | 2 | 0.7173 | 796.0594
2017-12-10 03:00 | 12 | 3 | 0.71147 | 789.589
2017-12-10 04:00 | 12 | 4 | 0.70954 | 787.4443
2017-12-10 05:00 | 12 | 5 | 0.76785 | 852.1583
2017-12-10 06:00 | 12 | 6 | 0.99192 | 1100.8303
2017-12-10 07:00 | 12 | 7 | 1.2902 | 1431.918
2017-12-10 08:00 | 12 | 8 | 1.2534 | 1391.0144
2017-12-10 09:00 | 12 | 9 | 1.1075 | 1229.1396
2017-12-10 10:00 | 12 | 10 | 1.1336 | 1258.1195
2017-12-10 11:00 | 12 | 11 | 1.1226 | 1245.9153
2017-12-10 12:00 | 12 | 12 | 1.0931 | 1213.1445
2017-12-10 13:00 | 12 | 13 | 1.0618 | 1178.4417
2017-12-10 14:00 | 12 | 14 | 1.0641 | 1180.9778
2017-12-10 15:00 | 12 | 15 | 1.1578 | 1284.9539
2017-12-10 16:00 | 12 | 16 | 1.4728 | 1634.5524
2017-12-10 17:00 | 12 | 17 | 2.0198 | 2241.5991
2017-12-10 18:00 | 12 | 18 | 2.2618 | 2510.1238
2017-12-10 19:00 | 12 | 19 | 2.0994 | 2329.8649
2017-12-10 20:00 | 12 | 20 | 1.9978 | 2217.1776
2017-12-10 21:00 | 12 | 21 | 1.8313 | 2032.3435
2017-12-10 22:00 | 12 | 22 | 1.5033 | 1668.3946
2017-12-10 23:00 | 12 | 23 | 1.1916 | 1322.4068
2017-12-11 | 12 | 0 | 0.8592 | 953.5425
2017-12-11 01:00 | 12 | 1 | 0.74308 | 824.6764
2017-12-11 02:00 | 12 | 2 | 0.68657 | 761.9579
2017-12-11 03:00 | 12 | 3 | 0.67589 | 750.1047
2017-12-11 04:00 | 12 | 4 | 0.67287 | 746.7527
2017-12-11 05:00 | 12 | 5 | 0.73314 | 813.6381
2017-12-11 06:00 | 12 | 6 | 0.9327 | 1035.1127
2017-12-11 07:00 | 12 | 7 | 1.2442 | 1380.814
2017-12-11 08:00 | 12 | 8 | 1.1913 | 1322.0818
2017-12-11 09:00 | 12 | 9 | 1.0332 | 1146.698
2017-12-11 10:00 | 12 | 10 | 1.0488 | 1163.9654
2017-12-11 11:00 | 12 | 11 | 1.0696 | 1187.0044
2017-12-11 12:00 | 12 | 12 | 1.0312 | 1144.4172
2017-12-11 13:00 | 12 | 13 | 1.0066 | 1117.178
2017-12-11 14:00 | 12 | 14 | 1.0106 | 1121.548
2017-12-11 15:00 | 12 | 15 | 1.0997 | 1220.498
2017-12-11 16:00 | 12 | 16 | 1.4162 | 1571.6936
2017-12-11 17:00 | 12 | 17 | 1.9479 | 2161.7862
2017-12-11 18:00 | 12 | 18 | 2.1996 | 2441.0782
2017-12-11 19:00 | 12 | 19 | 2.0365 | 2260.148
2017-12-11 20:00 | 12 | 20 | 1.9352 | 2147.6541
2017-12-11 21:00 | 12 | 21 | 1.7663 | 1960.2323
2017-12-11 22:00 | 12 | 22 | 1.447 | 1605.9326
2017-12-11 23:00 | 12 | 23 | 1.1614 | 1288.9767
2017-12-12 | 12 | 0 | 0.86933 | 964.7843
2017-12-12 01:00 | 12 | 1 | 0.76205 | 845.7224
2017-12-12 02:00 | 12 | 2 | 0.69777 | 774.384
2017-12-12 03:00 | 12 | 3 | 0.68639 | 761.7593
2017-12-12 04:00 | 12 | 4 | 0.68791 | 763.4402
2017-12-12 05:00 | 12 | 5 | 0.76967 | 854.1756
2017-12-12 06:00 | 12 | 6 | 0.9774 | 1084.719
2017-12-12 07:00 | 12 | 7 | 1.2713 | 1410.8597
2017-12-12 08:00 | 12 | 8 | 1.203 | 1335.0807
2017-12-12 09:00 | 12 | 9 | 1.0225 | 1134.8051
2017-12-12 10:00 | 12 | 10 | 1.0159 | 1127.4304
2017-12-12 11:00 | 12 | 11 | 1.0027 | 1112.7902
2017-12-12 12:00 | 12 | 12 | 0.97683 | 1084.0921
2017-12-12 13:00 | 12 | 13 | 0.95138 | 1055.8402
2017-12-12 14:00 | 12 | 14 | 0.96743 | 1073.6514
2017-12-12 15:00 | 12 | 15 | 1.0729 | 1190.67
2017-12-12 16:00 | 12 | 16 | 1.4109 | 1565.7945
2017-12-12 17:00 | 12 | 17 | 1.9669 | 2182.9018
2017-12-12 18:00 | 12 | 18 | 2.226 | 2470.4548
2017-12-12 19:00 | 12 | 19 | 2.0715 | 2298.9305
2017-12-12 20:00 | 12 | 20 | 1.9785 | 2195.7546
2017-12-12 21:00 | 12 | 21 | 1.8212 | 2021.1927
2017-12-12 22:00 | 12 | 22 | 1.5053 | 1670.5913
2017-12-12 23:00 | 12 | 23 | 1.2089 | 1341.6919
2017-12-13 | 12 | 0 | 0.90127 | 1000.2329
2017-12-13 01:00 | 12 | 1 | 0.78445 | 870.5787
2017-12-13 02:00 | 12 | 2 | 0.73266 | 813.1121
2017-12-13 03:00 | 12 | 3 | 0.72472 | 804.2921
2017-12-13 04:00 | 12 | 4 | 0.73022 | 810.3987
2017-12-13 05:00 | 12 | 5 | 0.79252 | 879.5417
2017-12-13 06:00 | 12 | 6 | 0.99696 | 1106.4323
2017-12-13 07:00 | 12 | 7 | 1.3203 | 1465.2171
2017-12-13 08:00 | 12 | 8 | 1.2516 | 1389.0515
2017-12-13 09:00 | 12 | 9 | 1.0735 | 1191.3686
2017-12-13 10:00 | 12 | 10 | 1.0736 | 1191.5149
2017-12-13 11:00 | 12 | 11 | 1.0578 | 1173.9768
2017-12-13 12:00 | 12 | 12 | 1.0193 | 1131.1965
2017-12-13 13:00 | 12 | 13 | 0.9868 | 1095.1477
2017-12-13 14:00 | 12 | 14 | 1.0069 | 1117.4953
2017-12-13 15:00 | 12 | 15 | 1.1244 | 1247.8813
2017-12-13 16:00 | 12 | 16 | 1.4526 | 1612.1527
2017-12-13 17:00 | 12 | 17 | 2.0249 | 2247.2692
2017-12-13 18:00 | 12 | 18 | 2.2763 | 2526.2954
2017-12-13 19:00 | 12 | 19 | 2.1195 | 2352.279
2017-12-13 20:00 | 12 | 20 | 2.0274 | 2250.0105
2017-12-13 21:00 | 12 | 21 | 1.8712 | 2076.6235
2017-12-13 22:00 | 12 | 22 | 1.5579 | 1728.9749
2017-12-13 23:00 | 12 | 23 | 1.2652 | 1404.0982
2017-12-14 | 12 | 0 | 0.95687 | 1061.9358
2017-12-14 01:00 | 12 | 1 | 0.84319 | 935.7787
2017-12-14 02:00 | 12 | 2 | 0.79349 | 880.6149
2017-12-14 03:00 | 12 | 3 | 0.7909 | 877.7457
2017-12-14 04:00 | 12 | 4 | 0.79101 | 877.8652
2017-12-14 05:00 | 12 | 5 | 0.85214 | 945.7087
2017-12-14 06:00 | 12 | 6 | 1.0551 | 1170.9851
2017-12-14 07:00 | 12 | 7 | 1.3775 | 1528.7585
2017-12-14 08:00 | 12 | 8 | 1.3203 | 1465.3224
2017-12-14 09:00 | 12 | 9 | 1.1508 | 1277.1783
2017-12-14 10:00 | 12 | 10 | 1.1747 | 1303.7382
2017-12-14 11:00 | 12 | 11 | 1.1486 | 1274.7716
2017-12-14 12:00 | 12 | 12 | 1.1132 | 1235.3963
2017-12-14 13:00 | 12 | 13 | 1.0825 | 1201.4072
2017-12-14 14:00 | 12 | 14 | 1.091 | 1210.7538
2017-12-14 15:00 | 12 | 15 | 1.1898 | 1320.4291
2017-12-14 16:00 | 12 | 16 | 1.5126 | 1678.688
2017-12-14 17:00 | 12 | 17 | 2.0247 | 2247.0533
2017-12-14 18:00 | 12 | 18 | 2.3001 | 2552.6327
2017-12-14 19:00 | 12 | 19 | 2.1362 | 2370.7386
2017-12-14 20:00 | 12 | 20 | 2.0443 | 2268.7612
2017-12-14 21:00 | 12 | 21 | 1.8617 | 2066.0872
2017-12-14 22:00 | 12 | 22 | 1.5311 | 1699.2141
2017-12-14 23:00 | 12 | 23 | 1.2352 | 1370.7945
2017-12-15 | 12 | 0 | 0.89999 | 998.8117
2017-12-15 01:00 | 12 | 1 | 0.77026 | 854.8344
2017-12-15 02:00 | 12 | 2 | 0.70557 | 783.0461
2017-12-15 03:00 | 12 | 3 | 0.69355 | 769.7001
2017-12-15 04:00 | 12 | 4 | 0.69288 | 768.9545
2017-12-15 05:00 | 12 | 5 | 0.75482 | 837.7035
2017-12-15 06:00 | 12 | 6 | 0.9621 | 1067.7384
2017-12-15 07:00 | 12 | 7 | 1.2728 | 1412.5422
2017-12-15 08:00 | 12 | 8 | 1.2379 | 1373.8425
2017-12-15 09:00 | 12 | 9 | 1.0936 | 1213.6673
2017-12-15 10:00 | 12 | 10 | 1.0869 | 1206.269
2017-12-15 11:00 | 12 | 11 | 1.0882 | 1207.7363
2017-12-15 12:00 | 12 | 12 | 1.0697 | 1187.1573
2017-12-15 13:00 | 12 | 13 | 1.0477 | 1162.7722
2017-12-15 14:00 | 12 | 14 | 1.0648 | 1181.6648
2017-12-15 15:00 | 12 | 15 | 1.1783 | 1307.6983
2017-12-15 16:00 | 12 | 16 | 1.4859 | 1649.0421
2017-12-15 17:00 | 12 | 17 | 2.0431 | 2267.4822
2017-12-15 18:00 | 12 | 18 | 2.3017 | 2554.3981
2017-12-15 19:00 | 12 | 19 | 2.1346 | 2368.9657
2017-12-15 20:00 | 12 | 20 | 2.0349 | 2258.2906
2017-12-15 21:00 | 12 | 21 | 1.8726 | 2078.1974
2017-12-15 22:00 | 12 | 22 | 1.5431 | 1712.5047
2017-12-15 23:00 | 12 | 23 | 1.2435 | 1380.0597
2017-12-16 | 12 | 0 | 0.92724 | 1029.0532
2017-12-16 01:00 | 12 | 1 | 0.80342 | 891.6313
2017-12-16 02:00 | 12 | 2 | 0.74629 | 828.2337
2017-12-16 03:00 | 12 | 3 | 0.73624 | 817.0776
2017-12-16 04:00 | 12 | 4 | 0.73582 | 816.6155
2017-12-16 05:00 | 12 | 5 | 0.79812 | 885.7595
2017-12-16 06:00 | 12 | 6 | 1.0082 | 1118.9561
2017-12-16 07:00 | 12 | 7 | 1.3268 | 1472.5184
2017-12-16 08:00 | 12 | 8 | 1.2747 | 1414.6992
2017-12-16 09:00 | 12 | 9 | 1.1044 | 1225.6507
2017-12-16 10:00 | 12 | 10 | 1.105 | 1226.3526
2017-12-16 11:00 | 12 | 11 | 1.0786 | 1197.0276
2017-12-16 12:00 | 12 | 12 | 1.0302 | 1143.3478
2017-12-16 13:00 | 12 | 13 | 0.98863 | 1097.1849
2017-12-16 14:00 | 12 | 14 | 0.99171 | 1100.6068
2017-12-16 15:00 | 12 | 15 | 1.0997 | 1220.4153
2017-12-16 16:00 | 12 | 16 | 1.4288 | 1585.6996
2017-12-16 17:00 | 12 | 17 | 1.9929 | 2211.7058
2017-12-16 18:00 | 12 | 18 | 2.2459 | 2492.4729
2017-12-16 19:00 | 12 | 19 | 2.0895 | 2318.911
2017-12-16 20:00 | 12 | 20 | 2.0006 | 2220.2511
2017-12-16 21:00 | 12 | 21 | 1.8398 | 2041.8341
2017-12-16 22:00 | 12 | 22 | 1.5135 | 1679.6501
2017-12-16 23:00 | 12 | 23 | 1.2055 | 1337.856
2017-12-17 | 12 | 0 | 0.89149 | 989.3752
2017-12-17 01:00 | 12 | 1 | 0.77065 | 855.2736
2017-12-17 02:00 | 12 | 2 | 0.71306 | 791.358
2017-12-17 03:00 | 12 | 3 | 0.69763 | 774.2303
2017-12-17 04:00 | 12 | 4 | 0.69309 | 769.1935
2017-12-17 05:00 | 12 | 5 | 0.7528 | 835.4622
2017-12-17 06:00 | 12 | 6 | 0.9708 | 1077.4004
2017-12-17 07:00 | 12 | 7 | 1.2835 | 1424.4227
2017-12-17 08:00 | 12 | 8 | 1.2251 | 1359.6552
2017-12-17 09:00 | 12 | 9 | 1.0674 | 1184.6372
2017-12-17 10:00 | 12 | 10 | 1.0785 | 1196.9011
2017-12-17 11:00 | 12 | 11 | 1.0706 | 1188.1316
2017-12-17 12:00 | 12 | 12 | 1.0451 | 1159.8185
2017-12-17 13:00 | 12 | 13 | 1.0101 | 1121.0561
2017-12-17 14:00 | 12 | 14 | 1.0153 | 1126.7303
2017-12-17 15:00 | 12 | 15 | 1.1163 | 1238.8576
2017-12-17 16:00 | 12 | 16 | 1.4344 | 1591.9406
2017-12-17 17:00 | 12 | 17 | 1.9488 | 2162.7395
2017-12-17 18:00 | 12 | 18 | 2.2331 | 2478.26
2017-12-17 19:00 | 12 | 19 | 2.0598 | 2285.9781
2017-12-17 20:00 | 12 | 20 | 1.9494 | 2163.4932
2017-12-17 21:00 | 12 | 21 | 1.785 | 1981.0078
2017-12-17 22:00 | 12 | 22 | 1.4511 | 1610.4404
2017-12-17 23:00 | 12 | 23 | 1.1611 | 1288.6055
2017-12-18 | 12 | 0 | 0.84311 | 935.6818
2017-12-18 01:00 | 12 | 1 | 0.73631 | 817.1551
2017-12-18 02:00 | 12 | 2 | 0.70867 | 786.4788
2017-12-18 03:00 | 12 | 3 | 0.69187 | 767.8402
2017-12-18 04:00 | 12 | 4 | 0.70092 | 777.8814
2017-12-18 05:00 | 12 | 5 | 0.77201 | 856.7806
2017-12-18 06:00 | 12 | 6 | 0.97977 | 1087.3519
2017-12-18 07:00 | 12 | 7 | 1.2922 | 1434.1083
2017-12-18 08:00 | 12 | 8 | 1.233 | 1368.3337
2017-12-18 09:00 | 12 | 9 | 1.0434 | 1157.9793
2017-12-18 10:00 | 12 | 10 | 1.0423 | 1156.6967
2017-12-18 11:00 | 12 | 11 | 1.019 | 1130.8803
2017-12-18 12:00 | 12 | 12 | 0.9923 | 1101.2517
2017-12-18 13:00 | 12 | 13 | 0.9663 | 1072.4011
2017-12-18 14:00 | 12 | 14 | 0.98697 | 1095.343
2017-12-18 15:00 | 12 | 15 | 1.0943 | 1214.4182
2017-12-18 16:00 | 12 | 16 | 1.423 | 1579.2256
2017-12-18 17:00 | 12 | 17 | 1.9768 | 2193.8987
2017-12-18 18:00 | 12 | 18 | 2.2363 | 2481.8304
2017-12-18 19:00 | 12 | 19 | 2.0728 | 2300.4355
2017-12-18 20:00 | 12 | 20 | 1.9835 | 2201.3263
2017-12-18 21:00 | 12 | 21 | 1.8215 | 2021.4606
2017-12-18 22:00 | 12 | 22 | 1.5003 | 1665.0456
2017-12-18 23:00 | 12 | 23 | 1.2055 | 1337.8921
2017-12-19 | 12 | 0 | 0.89817 | 996.7912
2017-12-19 01:00 | 12 | 1 | 0.78196 | 867.8189
2017-12-19 02:00 | 12 | 2 | 0.73119 | 811.4729
2017-12-19 03:00 | 12 | 3 | 0.72487 | 804.4593
2017-12-19 04:00 | 12 | 4 | 0.72404 | 803.5443
2017-12-19 05:00 | 12 | 5 | 0.78183 | 867.6762
2017-12-19 06:00 | 12 | 6 | 0.98732 | 1095.7278
2017-12-19 07:00 | 12 | 7 | 1.3077 | 1451.2845
2017-12-19 08:00 | 12 | 8 | 1.2288 | 1363.6723
2017-12-19 09:00 | 12 | 9 | 1.0439 | 1158.5606
2017-12-19 10:00 | 12 | 10 | 1.0399 | 1154.1023
2017-12-19 11:00 | 12 | 11 | 1.0097 | 1120.5991
2017-12-19 12:00 | 12 | 12 | 0.97078 | 1077.3698
2017-12-19 13:00 | 12 | 13 | 0.93882 | 1041.9041
2017-12-19 14:00 | 12 | 14 | 0.95186 | 1056.378
2017-12-19 15:00 | 12 | 15 | 1.0631 | 1179.8654
2017-12-19 16:00 | 12 | 16 | 1.3971 | 1550.5334
2017-12-19 17:00 | 12 | 17 | 1.9557 | 2170.393
2017-12-19 18:00 | 12 | 18 | 2.2115 | 2454.3121
2017-12-19 19:00 | 12 | 19 | 2.0571 | 2282.934
2017-12-19 20:00 | 12 | 20 | 1.9659 | 2181.799
2017-12-19 21:00 | 12 | 21 | 1.8065 | 2004.8843
2017-12-19 22:00 | 12 | 22 | 1.4909 | 1654.6177
2017-12-19 23:00 | 12 | 23 | 1.1963 | 1327.6726
2017-12-20 | 12 | 0 | 0.88635 | 983.6759
2017-12-20 01:00 | 12 | 1 | 0.77057 | 855.18
2017-12-20 02:00 | 12 | 2 | 0.71882 | 797.7447
2017-12-20 03:00 | 12 | 3 | 0.71229 | 790.504
2017-12-20 04:00 | 12 | 4 | 0.71159 | 789.7223
2017-12-20 05:00 | 12 | 5 | 0.77476 | 859.8243
2017-12-20 06:00 | 12 | 6 | 0.99659 | 1106.0162
2017-12-20 07:00 | 12 | 7 | 1.302 | 1444.9925
2017-12-20 08:00 | 12 | 8 | 1.2285 | 1363.4227
2017-12-20 09:00 | 12 | 9 | 1.0417 | 1156.0676
2017-12-20 10:00 | 12 | 10 | 1.0402 | 1154.3904
2017-12-20 11:00 | 12 | 11 | 1.012 | 1123.1133
2017-12-20 12:00 | 12 | 12 | 0.98953 | 1098.1863
2017-12-20 13:00 | 12 | 13 | 0.97224 | 1078.9965
2017-12-20 14:00 | 12 | 14 | 0.99494 | 1104.1817
2017-12-20 15:00 | 12 | 15 | 1.1014 | 1222.3077
2017-12-20 16:00 | 12 | 16 | 1.4277 | 1584.495
2017-12-20 17:00 | 12 | 17 | 1.9855 | 2203.5515
2017-12-20 18:00 | 12 | 18 | 2.2404 | 2486.3731
2017-12-20 19:00 | 12 | 19 | 2.0856 | 2314.6337
2017-12-20 20:00 | 12 | 20 | 1.9922 | 2210.9543
2017-12-20 21:00 | 12 | 21 | 1.8322 | 2033.3799
2017-12-20 22:00 | 12 | 22 | 1.5194 | 1686.2104
2017-12-20 23:00 | 12 | 23 | 1.2253 | 1359.855
2017-12-21 | 12 | 0 | 0.91573 | 1016.2806
2017-12-21 01:00 | 12 | 1 | 0.80374 | 891.996
2017-12-21 02:00 | 12 | 2 | 0.75386 | 836.6301
2017-12-21 03:00 | 12 | 3 | 0.74893 | 831.1679
2017-12-21 04:00 | 12 | 4 | 0.76113 | 844.7086
2017-12-21 05:00 | 12 | 5 | 0.82411 | 914.5983
2017-12-21 06:00 | 12 | 6 | 1.0267 | 1139.4196
2017-12-21 07:00 | 12 | 7 | 1.3482 | 1496.2477
2017-12-21 08:00 | 12 | 8 | 1.279 | 1419.4602
2017-12-21 09:00 | 12 | 9 | 1.0825 | 1201.3346
2017-12-21 10:00 | 12 | 10 | 1.0851 | 1204.2423
2017-12-21 11:00 | 12 | 11 | 1.0639 | 1180.7509
2017-12-21 12:00 | 12 | 12 | 1.0272 | 1139.9982
2017-12-21 13:00 | 12 | 13 | 1.013 | 1124.2344
2017-12-21 14:00 | 12 | 14 | 1.0303 | 1143.3821
2017-12-21 15:00 | 12 | 15 | 1.1294 | 1253.3657
2017-12-21 16:00 | 12 | 16 | 1.4542 | 1613.8787
2017-12-21 17:00 | 12 | 17 | 2.0062 | 2226.449
2017-12-21 18:00 | 12 | 18 | 2.2568 | 2504.6169
2017-12-21 19:00 | 12 | 19 | 2.0923 | 2322.0645
2017-12-21 20:00 | 12 | 20 | 1.9895 | 2207.9483
2017-12-21 21:00 | 12 | 21 | 1.8243 | 2024.5966
2017-12-21 22:00 | 12 | 22 | 1.5057 | 1671.0368
2017-12-21 23:00 | 12 | 23 | 1.2053 | 1337.6187
2017-12-22 | 12 | 0 | 0.86439 | 959.297
2017-12-22 01:00 | 12 | 1 | 0.76064 | 844.1603
2017-12-22 02:00 | 12 | 2 | 0.71111 | 789.1871
2017-12-22 03:00 | 12 | 3 | 0.706 | 783.5253
2017-12-22 04:00 | 12 | 4 | 0.69598 | 772.396
2017-12-22 05:00 | 12 | 5 | 0.74954 | 831.8461
2017-12-22 06:00 | 12 | 6 | 0.9232 | 1024.5726
2017-12-22 07:00 | 12 | 7 | 1.1767 | 1305.9188
2017-12-22 08:00 | 12 | 8 | 1.0558 | 1171.7677
2017-12-22 09:00 | 12 | 9 | 0.80216 | 890.2383
2017-12-22 10:00 | 12 | 10 | 0.77032 | 854.9071
2017-12-22 11:00 | 12 | 11 | 0.75626 | 839.3005
2017-12-22 12:00 | 12 | 12 | 0.75088 | 833.3249
2017-12-22 13:00 | 12 | 13 | 0.72949 | 809.5926
2017-12-22 14:00 | 12 | 14 | 0.76318 | 846.9749
2017-12-22 15:00 | 12 | 15 | 0.87678 | 973.0514
2017-12-22 16:00 | 12 | 16 | 1.2115 | 1344.5484
2017-12-22 17:00 | 12 | 17 | 1.7632 | 1956.7929
2017-12-22 18:00 | 12 | 18 | 2.0251 | 2247.5101
2017-12-22 19:00 | 12 | 19 | 1.8677 | 2072.7751
2017-12-22 20:00 | 12 | 20 | 1.7703 | 1964.6714
2017-12-22 21:00 | 12 | 21 | 1.6104 | 1787.2742
2017-12-22 22:00 | 12 | 22 | 1.3287 | 1474.5499
2017-12-22 23:00 | 12 | 23 | 1.09 | 1209.6601
2017-12-23 | 12 | 0 | 0.81877 | 908.676
2017-12-23 01:00 | 12 | 1 | 0.72005 | 799.1148
2017-12-23 02:00 | 12 | 2 | 0.67081 | 744.4635
2017-12-23 03:00 | 12 | 3 | 0.66862 | 742.0339
2017-12-23 04:00 | 12 | 4 | 0.66225 | 734.9626
2017-12-23 05:00 | 12 | 5 | 0.71782 | 796.6426
2017-12-23 06:00 | 12 | 6 | 0.89188 | 989.8134
2017-12-23 07:00 | 12 | 7 | 1.1421 | 1267.4861
2017-12-23 08:00 | 12 | 8 | 1.0437 | 1158.3346
2017-12-23 09:00 | 12 | 9 | 0.82285 | 913.2021
2017-12-23 10:00 | 12 | 10 | 0.80299 | 891.162
2017-12-23 11:00 | 12 | 11 | 0.77279 | 857.6426
2017-12-23 12:00 | 12 | 12 | 0.7453 | 827.1378
2017-12-23 13:00 | 12 | 13 | 0.71877 | 797.6932
2017-12-23 14:00 | 12 | 14 | 0.74401 | 825.7088
2017-12-23 15:00 | 12 | 15 | 0.86475 | 959.7052
2017-12-23 16:00 | 12 | 16 | 1.2017 | 1333.6141
2017-12-23 17:00 | 12 | 17 | 1.7572 | 1950.1253
2017-12-23 18:00 | 12 | 18 | 2.0143 | 2235.4662
2017-12-23 19:00 | 12 | 19 | 1.8541 | 2057.7173
2017-12-23 20:00 | 12 | 20 | 1.7583 | 1951.401
2017-12-23 21:00 | 12 | 21 | 1.5954 | 1770.5256
2017-12-23 22:00 | 12 | 22 | 1.3121 | 1456.2004
2017-12-23 23:00 | 12 | 23 | 1.0724 | 1190.1775
2017-12-24 | 12 | 0 | 0.80198 | 890.0418
2017-12-24 01:00 | 12 | 1 | 0.69503 | 771.3441
2017-12-24 02:00 | 12 | 2 | 0.64789 | 719.027
2017-12-24 03:00 | 12 | 3 | 0.64239 | 712.928
2017-12-24 04:00 | 12 | 4 | 0.637 | 706.9468
2017-12-24 05:00 | 12 | 5 | 0.69317 | 769.2764
2017-12-24 06:00 | 12 | 6 | 0.87201 | 967.7586
2017-12-24 07:00 | 12 | 7 | 1.1165 | 1239.0849
2017-12-24 08:00 | 12 | 8 | 1.0083 | 1119.0201
2017-12-24 09:00 | 12 | 9 | 0.7783 | 863.7549
2017-12-24 10:00 | 12 | 10 | 0.75631 | 839.3568
2017-12-24 11:00 | 12 | 11 | 0.75033 | 832.7205
2017-12-24 12:00 | 12 | 12 | 0.75434 | 837.1726
2017-12-24 13:00 | 12 | 13 | 0.74882 | 831.0421
2017-12-24 14:00 | 12 | 14 | 0.7787 | 864.2016
2017-12-24 15:00 | 12 | 15 | 0.88776 | 985.2321
2017-12-24 16:00 | 12 | 16 | 1.2104 | 1343.3134
2017-12-24 17:00 | 12 | 17 | 1.7466 | 1938.3746
2017-12-24 18:00 | 12 | 18 | 2.0189 | 2240.566
2017-12-24 19:00 | 12 | 19 | 1.8379 | 2039.7044
2017-12-24 20:00 | 12 | 20 | 1.7384 | 1929.235
2017-12-24 21:00 | 12 | 21 | 1.5721 | 1744.7511
2017-12-24 22:00 | 12 | 22 | 1.2869 | 1428.2169
2017-12-24 23:00 | 12 | 23 | 1.0447 | 1159.3671
2017-12-25 | 12 | 0 | 0.77213 | 856.9134
2017-12-25 01:00 | 12 | 1 | 0.66769 | 740.9994
2017-12-25 02:00 | 12 | 2 | 0.61988 | 687.9479
2017-12-25 03:00 | 12 | 3 | 0.61769 | 685.5097
2017-12-25 04:00 | 12 | 4 | 0.61535 | 682.9166
2017-12-25 05:00 | 12 | 5 | 0.67337 | 747.3056
2017-12-25 06:00 | 12 | 6 | 0.85973 | 954.1329
2017-12-25 07:00 | 12 | 7 | 1.1094 | 1231.211
2017-12-25 08:00 | 12 | 8 | 1.0002 | 1110.0432
2017-12-25 09:00 | 12 | 9 | 0.78525 | 871.4753
2017-12-25 10:00 | 12 | 10 | 0.77297 | 857.8475
2017-12-25 11:00 | 12 | 11 | 0.76459 | 848.5421
2017-12-25 12:00 | 12 | 12 | 0.73977 | 821.002
2017-12-25 13:00 | 12 | 13 | 0.74799 | 830.115
2017-12-25 14:00 | 12 | 14 | 0.78506 | 871.2629
2017-12-25 15:00 | 12 | 15 | 0.8968 | 995.2744
2017-12-25 16:00 | 12 | 16 | 1.2256 | 1360.1382
2017-12-25 17:00 | 12 | 17 | 1.7802 | 1975.6393
2017-12-25 18:00 | 12 | 18 | 2.0425 | 2266.783
2017-12-25 19:00 | 12 | 19 | 1.893 | 2100.8383
2017-12-25 20:00 | 12 | 20 | 1.8052 | 2003.4265
2017-12-25 21:00 | 12 | 21 | 1.6418 | 1822.0852
2017-12-25 22:00 | 12 | 22 | 1.3612 | 1510.6829
2017-12-25 23:00 | 12 | 23 | 1.1261 | 1249.7882
2017-12-26 | 12 | 0 | 0.88652 | 983.856
2017-12-26 01:00 | 12 | 1 | 0.76924 | 853.7022
2017-12-26 02:00 | 12 | 2 | 0.71774 | 796.547
2017-12-26 03:00 | 12 | 3 | 0.71324 | 791.5531
2017-12-26 04:00 | 12 | 4 | 0.71359 | 791.9425
2017-12-26 05:00 | 12 | 5 | 0.78152 | 867.3302
2017-12-26 06:00 | 12 | 6 | 0.98199 | 1089.8176
2017-12-26 07:00 | 12 | 7 | 1.2951 | 1437.2697
2017-12-26 08:00 | 12 | 8 | 1.2263 | 1360.9143
2017-12-26 09:00 | 12 | 9 | 1.0505 | 1165.8576
2017-12-26 10:00 | 12 | 10 | 1.0798 | 1198.3306
2017-12-26 11:00 | 12 | 11 | 1.0408 | 1155.0285
2017-12-26 12:00 | 12 | 12 | 1.0284 | 1141.2916
2017-12-26 13:00 | 12 | 13 | 1.0101 | 1121.0218
2017-12-26 14:00 | 12 | 14 | 1.0208 | 1132.8962
2017-12-26 15:00 | 12 | 15 | 1.118 | 1240.7314
2017-12-26 16:00 | 12 | 16 | 1.4367 | 1594.4373
2017-12-26 17:00 | 12 | 17 | 1.983 | 2200.7266
2017-12-26 18:00 | 12 | 18 | 2.2316 | 2476.5861
2017-12-26 19:00 | 12 | 19 | 2.0674 | 2294.4449
2017-12-26 20:00 | 12 | 20 | 1.9694 | 2185.6834
2017-12-26 21:00 | 12 | 21 | 1.8104 | 2009.1535
2017-12-26 22:00 | 12 | 22 | 1.4896 | 1653.164
2017-12-26 23:00 | 12 | 23 | 1.1892 | 1319.818
2017-12-27 | 12 | 0 | 0.87636 | 972.5841
2017-12-27 01:00 | 12 | 1 | 0.76277 | 846.5192
2017-12-27 02:00 | 12 | 2 | 0.7086 | 786.4091
2017-12-27 03:00 | 12 | 3 | 0.70007 | 776.9402
2017-12-27 04:00 | 12 | 4 | 0.69486 | 771.1563
2017-12-27 05:00 | 12 | 5 | 0.75633 | 839.3793
2017-12-27 06:00 | 12 | 6 | 0.9803 | 1087.9396
2017-12-27 07:00 | 12 | 7 | 1.2856 | 1426.72
2017-12-27 08:00 | 12 | 8 | 1.2118 | 1344.8764
2017-12-27 09:00 | 12 | 9 | 1.025 | 1137.5226
2017-12-27 10:00 | 12 | 10 | 1.0122 | 1123.3911
2017-12-27 11:00 | 12 | 11 | 0.98264 | 1090.5299
2017-12-27 12:00 | 12 | 12 | 0.94693 | 1050.9047
2017-12-27 13:00 | 12 | 13 | 0.91481 | 1015.2546
2017-12-27 14:00 | 12 | 14 | 0.92731 | 1029.1253
2017-12-27 15:00 | 12 | 15 | 1.0429 | 1157.401
2017-12-27 16:00 | 12 | 16 | 1.3787 | 1530.0553
2017-12-27 17:00 | 12 | 17 | 1.9383 | 2151.1562
2017-12-27 18:00 | 12 | 18 | 2.2002 | 2441.7314
2017-12-27 19:00 | 12 | 19 | 2.0445 | 2268.9597
2017-12-27 20:00 | 12 | 20 | 1.9539 | 2168.438
2017-12-27 21:00 | 12 | 21 | 1.7966 | 1993.8596
2017-12-27 22:00 | 12 | 22 | 1.4819 | 1644.5651
2017-12-27 23:00 | 12 | 23 | 1.1906 | 1321.3529
2017-12-28 | 12 | 0 | 0.88126 | 978.0225
2017-12-28 01:00 | 12 | 1 | 0.76716 | 851.394
2017-12-28 02:00 | 12 | 2 | 0.71445 | 792.9021
2017-12-28 03:00 | 12 | 3 | 0.70756 | 785.247
2017-12-28 04:00 | 12 | 4 | 0.70959 | 787.5087
2017-12-28 05:00 | 12 | 5 | 0.77215 | 856.9309
2017-12-28 06:00 | 12 | 6 | 0.99304 | 1102.0745
2017-12-28 07:00 | 12 | 7 | 1.283 | 1423.8519
2017-12-28 08:00 | 12 | 8 | 1.2141 | 1347.3864
2017-12-28 09:00 | 12 | 9 | 1.0204 | 1132.4081
2017-12-28 10:00 | 12 | 10 | 1.0009 | 1110.8142
2017-12-28 11:00 | 12 | 11 | 0.96798 | 1074.2629
2017-12-28 12:00 | 12 | 12 | 0.93048 | 1032.6464
2017-12-28 13:00 | 12 | 13 | 0.89643 | 994.8609
2017-12-28 14:00 | 12 | 14 | 0.90873 | 1008.5046
2017-12-28 15:00 | 12 | 15 | 1.0194 | 1131.3189
2017-12-28 16:00 | 12 | 16 | 1.3531 | 1501.6211
2017-12-28 17:00 | 12 | 17 | 1.9064 | 2115.7195
2017-12-28 18:00 | 12 | 18 | 2.1696 | 2407.849
2017-12-28 19:00 | 12 | 19 | 2.0197 | 2241.4393
2017-12-28 20:00 | 12 | 20 | 1.9255 | 2136.9373
2017-12-28 21:00 | 12 | 21 | 1.7718 | 1966.3963
2017-12-28 22:00 | 12 | 22 | 1.4558 | 1615.6304
2017-12-28 23:00 | 12 | 23 | 1.1647 | 1292.5709
2017-12-29 | 12 | 0 | 0.85784 | 952.0277
2017-12-29 01:00 | 12 | 1 | 0.74254 | 824.0716
2017-12-29 02:00 | 12 | 2 | 0.69068 | 766.5224
2017-12-29 03:00 | 12 | 3 | 0.68503 | 760.2523
2017-12-29 04:00 | 12 | 4 | 0.68324 | 758.2559
2017-12-29 05:00 | 12 | 5 | 0.74491 | 826.7052
2017-12-29 06:00 | 12 | 6 | 0.94795 | 1052.0355
2017-12-29 07:00 | 12 | 7 | 1.2666 | 1405.7062
2017-12-29 08:00 | 12 | 8 | 1.1903 | 1320.9934
2017-12-29 09:00 | 12 | 9 | 0.99675 | 1106.1997
2017-12-29 10:00 | 12 | 10 | 0.97697 | 1084.2384
2017-12-29 11:00 | 12 | 11 | 0.952 | 1056.526
2017-12-29 12:00 | 12 | 12 | 0.91414 | 1014.5175
2017-12-29 13:00 | 12 | 13 | 0.87804 | 974.4519
2017-12-29 14:00 | 12 | 14 | 0.89136 | 989.2283
2017-12-29 15:00 | 12 | 15 | 1.0019 | 1111.8733
2017-12-29 16:00 | 12 | 16 | 1.3354 | 1482.0476
2017-12-29 17:00 | 12 | 17 | 1.8852 | 2092.2238
2017-12-29 18:00 | 12 | 18 | 2.151 | 2387.1308
2017-12-29 19:00 | 12 | 19 | 1.9985 | 2217.9738
2017-12-29 20:00 | 12 | 20 | 1.9124 | 2122.4183
2017-12-29 21:00 | 12 | 21 | 1.7565 | 1949.3404
2017-12-29 22:00 | 12 | 22 | 1.443 | 1601.4387
2017-12-29 23:00 | 12 | 23 | 1.1489 | 1275.0221
2017-12-30 | 12 | 0 | 0.84858 | 941.7561
2017-12-30 01:00 | 12 | 1 | 0.73356 | 814.1064
2017-12-30 02:00 | 12 | 2 | 0.68248 | 757.4177
2017-12-30 03:00 | 12 | 3 | 0.67167 | 745.4181
2017-12-30 04:00 | 12 | 4 | 0.66895 | 742.3981
2017-12-30 05:00 | 12 | 5 | 0.72969 | 809.8128
2017-12-30 06:00 | 12 | 6 | 0.94109 | 1044.4199
2017-12-30 07:00 | 12 | 7 | 1.2467 | 1383.5509
2017-12-30 08:00 | 12 | 8 | 1.2062 | 1338.6066
2017-12-30 09:00 | 12 | 9 | 1.0352 | 1148.8733
2017-12-30 10:00 | 12 | 10 | 1.0484 | 1163.5223
2017-12-30 11:00 | 12 | 11 | 1.0473 | 1162.259
2017-12-30 12:00 | 12 | 12 | 1.0242 | 1136.6712
2017-12-30 13:00 | 12 | 13 | 0.98085 | 1088.5527
2017-12-30 14:00 | 12 | 14 | 1.011 | 1121.9946
2017-12-30 15:00 | 12 | 15 | 1.1157 | 1238.1955
2017-12-30 16:00 | 12 | 16 | 1.4322 | 1589.4482
2017-12-30 17:00 | 12 | 17 | 1.9798 | 2197.132
2017-12-30 18:00 | 12 | 18 | 2.2398 | 2485.7782
2017-12-30 19:00 | 12 | 19 | 2.0817 | 2310.2677
2017-12-30 20:00 | 12 | 20 | 1.9847 | 2202.6537
2017-12-30 21:00 | 12 | 21 | 1.8218 | 2021.8252
2017-12-30 22:00 | 12 | 22 | 1.5007 | 1665.4579
2017-12-30 23:00 | 12 | 23 | 1.1925 | 1323.4655
2017-12-31 | 12 | 0 | 0.86771 | 962.9862
2017-12-31 01:00 | 12 | 1 | 0.75039 | 832.7887
2017-12-31 02:00 | 12 | 2 | 0.69946 | 776.2655
2017-12-31 03:00 | 12 | 3 | 0.69277 | 768.8323
2017-12-31 04:00 | 12 | 4 | 0.68652 | 761.8973
2017-12-31 05:00 | 12 | 5 | 0.74876 | 830.9797
2017-12-31 06:00 | 12 | 6 | 0.97362 | 1080.5204
2017-12-31 07:00 | 12 | 7 | 1.2882 | 1429.6876
2017-12-31 08:00 | 12 | 8 | 1.2464 | 1383.2873
2017-12-31 09:00 | 12 | 9 | 1.0896 | 1209.2188
2017-12-31 10:00 | 12 | 10 | 1.0982 | 1218.7692
2017-12-31 11:00 | 12 | 11 | 1.0925 | 1212.4748
2017-12-31 12:00 | 12 | 12 | 1.0555 | 1171.4391
2017-12-31 13:00 | 12 | 13 | 1.0033 | 1113.4676
2017-12-31 14:00 | 12 | 14 | 1.0026 | 1112.6698
2017-12-31 15:00 | 12 | 15 | 1.1043 | 1225.5424
2017-12-31 16:00 | 12 | 16 | 1.4334 | 1590.8318
2017-12-31 17:00 | 12 | 17 | 1.9901 | 2208.595
2017-12-31 18:00 | 12 | 18 | 2.2448 | 2491.3203
2017-12-31 19:00 | 12 | 19 | 2.0813 | 2309.8063
2017-12-31 20:00 | 12 | 20 | 1.9933 | 2212.1394
2017-12-31 21:00 | 12 | 21 | 1.8329 | 2034.1153
2017-12-31 22:00 | 12 | 22 | 1.504 | 1669.1476
2017-12-31 23:00 | 12 | 23 | 1.192 | 1322.8506
|  |  | 9010.6197 | 10000000
Formulas:
Date = [Date, row above]+1/24

## Wind Output
From: | GridWorks:Raw Data:Weather Data:Suffolk County 2010-2019.xlsx |  |  |  | Source: | https://www.nrel.gov/gis/wind.html
Orig Source: | https://www.ncdc.noaa.gov/cdo-web/datatools/lcd |  |  |  | SiteID | 2379634 | Site Timezone | -5 | Data Timezone | -5 | Longitude | -71.0794 | Latitude | 42.3421
|  |  | Capacity Factor: | 23.87%
Name Plate (kW) | 10 |  |  | 20912113.3333 | GE 1.5sle | Power Curve
Date-time | month | hour | Wind Speed (MPH) | Power (W) | Bin | Wind speed (m/s) | Wind Speed (mph) | Power
2017-01-01 | 1 | 0 | 16.1 | 2773.3333 | 0 | 0 | 0 | 0
2017-01-01 01:00 | 1 | 1 | 17.825 | 4266.6667 | 1 | 0.5 | 1.1185 | 0
2017-01-01 02:00 | 1 | 2 | 16.1 | 2773.3333 | 2 | 1.5 | 3.3555 | 0
2017-01-01 03:00 | 1 | 3 | 18.975 | 4266.6667 | 3 | 2.5 | 5.5925 | 0
2017-01-01 04:00 | 1 | 4 | 19.55 | 6160 | 4 | 3.5 | 7.8295 | 43
2017-01-01 05:00 | 1 | 5 | 16.1 | 2773.3333 | 5 | 4.5 | 10.0665 | 131
2017-01-01 06:00 | 1 | 6 | 16.1 | 2773.3333 | 6 | 5.5 | 12.3035 | 250
2017-01-01 07:00 | 1 | 7 | 16.675 | 2773.3333 | 7 | 6.5 | 14.5405 | 416
2017-01-01 08:00 | 1 | 8 | 17.25 | 4266.6667 | 8 | 7.5 | 16.7775 | 640
2017-01-01 09:00 | 1 | 9 | 23 | 7873.3333 | 9 | 8.5 | 19.0145 | 924
2017-01-01 10:00 | 1 | 10 | 21.275 | 7873.3333 | 10 | 9.5 | 21.2515 | 1181
2017-01-01 11:00 | 1 | 11 | 26.45 | 9573.3333 | 11 | 10.5 | 23.4885 | 1359
2017-01-01 12:00 | 1 | 12 | 25.3 | 9060 | 12 | 11.5 | 25.7255 | 1436
2017-01-01 13:00 | 1 | 13 | 21.85 | 7873.3333 | 13 | 12.5 | 27.9625 | 1481
2017-01-01 14:00 | 1 | 14 | 24.15 | 9060 | 14 | 13.5 | 30.1995 | 1494
2017-01-01 15:00 | 1 | 15 | 12.65 | 1666.6667 | 15 | 14.5 | 32.4365 | 1500
2017-01-01 16:00 | 1 | 16 | 12.075 | 873.3333 | 16 | 15.5 | 34.6735 | 1500
2017-01-01 17:00 | 1 | 17 | 10.35 | 873.3333 | 17 | 16.5 | 36.9105 | 1500
2017-01-01 18:00 | 1 | 18 | 9.2 | 286.6667 | 18 | 17.5 | 39.1475 | 1500
2017-01-01 19:00 | 1 | 19 | 10.925 | 873.3333
2017-01-01 20:00 | 1 | 20 | 9.2 | 286.6667
2017-01-01 21:00 | 1 | 21 | 9.2 | 286.6667
2017-01-01 22:00 | 1 | 22 | 8.625 | 286.6667
2017-01-01 23:00 | 1 | 23 | 8.05 | 286.6667
2017-01-02 | 1 | 0 | 8.05 | 286.6667
2017-01-02 01:00 | 1 | 1 | 5.75 | 0
2017-01-02 02:00 | 1 | 2 | 0 | 0
2017-01-02 03:00 | 1 | 3 | 0 | 0
2017-01-02 04:00 | 1 | 4 | 0 | 0
2017-01-02 05:00 | 1 | 5 | 0 | 0
2017-01-02 06:00 | 1 | 6 | 3.45 | 0
2017-01-02 07:00 | 1 | 7 | 4.6 | 0
2017-01-02 08:00 | 1 | 8 | 3.45 | 0
2017-01-02 09:00 | 1 | 9 | 8.05 | 286.6667
2017-01-02 10:00 | 1 | 10 | 4.025 | 0
2017-01-02 11:00 | 1 | 11 | 0 | 0
2017-01-02 12:00 | 1 | 12 | 0 | 0
2017-01-02 13:00 | 1 | 13 | 0 | 0
2017-01-02 14:00 | 1 | 14 | 3.45 | 0
2017-01-02 15:00 | 1 | 15 | 5.75 | 0
2017-01-02 16:00 | 1 | 16 | 7.475 | 0
2017-01-02 17:00 | 1 | 17 | 9.2 | 286.6667
2017-01-02 18:00 | 1 | 18 | 10.35 | 873.3333
2017-01-02 19:00 | 1 | 19 | 9.2 | 286.6667
2017-01-02 20:00 | 1 | 20 | 8.05 | 286.6667
2017-01-02 21:00 | 1 | 21 | 9.2 | 286.6667
2017-01-02 22:00 | 1 | 22 | 10.35 | 873.3333
2017-01-02 23:00 | 1 | 23 | 12.075 | 873.3333
2017-01-03 | 1 | 0 | 13.8 | 1666.6667
2017-01-03 01:00 | 1 | 1 | 12.3625 | 1666.6667
2017-01-03 02:00 | 1 | 2 | 9.2 | 286.6667
2017-01-03 03:00 | 1 | 3 | 12.65 | 1666.6667
2017-01-03 04:00 | 1 | 4 | 15.525 | 2773.3333
2017-01-03 05:00 | 1 | 5 | 18.975 | 4266.6667
2017-01-03 06:00 | 1 | 6 | 21.85 | 7873.3333
2017-01-03 07:00 | 1 | 7 | 23.575 | 9060
2017-01-03 08:00 | 1 | 8 | 23 | 7873.3333
2017-01-03 09:00 | 1 | 9 | 21.85 | 7873.3333
2017-01-03 10:00 | 1 | 10 | 21.275 | 7873.3333
2017-01-03 11:00 | 1 | 11 | 21.85 | 7873.3333
2017-01-03 12:00 | 1 | 12 | 23 | 7873.3333
2017-01-03 13:00 | 1 | 13 | 23.2875 | 7873.3333
2017-01-03 14:00 | 1 | 14 | 21.4667 | 7873.3333
2017-01-03 15:00 | 1 | 15 | 25.3 | 9060
2017-01-03 16:00 | 1 | 16 | 26.0667 | 9573.3333
2017-01-03 17:00 | 1 | 17 | 25.0125 | 9060
2017-01-03 18:00 | 1 | 18 | 24.5333 | 9060
2017-01-03 19:00 | 1 | 19 | 20.125 | 6160
2017-01-03 20:00 | 1 | 20 | 23 | 7873.3333
2017-01-03 21:00 | 1 | 21 | 23.3833 | 7873.3333
2017-01-03 22:00 | 1 | 22 | 23.575 | 9060
2017-01-03 23:00 | 1 | 23 | 23.8625 | 9060
2017-01-04 | 1 | 0 | 14.95 | 2773.3333
2017-01-04 01:00 | 1 | 1 | 12.075 | 873.3333
2017-01-04 02:00 | 1 | 2 | 9.2 | 286.6667
2017-01-04 03:00 | 1 | 3 | 14.95 | 2773.3333
2017-01-04 04:00 | 1 | 4 | 13.8 | 1666.6667
2017-01-04 05:00 | 1 | 5 | 12.075 | 873.3333
2017-01-04 06:00 | 1 | 6 | 11.5 | 873.3333
2017-01-04 07:00 | 1 | 7 | 9.2 | 286.6667
2017-01-04 08:00 | 1 | 8 | 8.05 | 286.6667
2017-01-04 09:00 | 1 | 9 | 15.525 | 2773.3333
2017-01-04 10:00 | 1 | 10 | 15.3333 | 2773.3333
2017-01-04 11:00 | 1 | 11 | 18.4 | 4266.6667
2017-01-04 12:00 | 1 | 12 | 13.225 | 1666.6667
2017-01-04 13:00 | 1 | 13 | 16.1 | 2773.3333
2017-01-04 14:00 | 1 | 14 | 11.5 | 873.3333
2017-01-04 15:00 | 1 | 15 | 12.65 | 1666.6667
2017-01-04 16:00 | 1 | 16 | 11.5 | 873.3333
2017-01-04 17:00 | 1 | 17 | 14.375 | 1666.6667
2017-01-04 18:00 | 1 | 18 | 17.825 | 4266.6667
2017-01-04 19:00 | 1 | 19 | 20.7 | 6160
2017-01-04 20:00 | 1 | 20 | 23.3833 | 7873.3333
2017-01-04 21:00 | 1 | 21 | 19.55 | 6160
2017-01-04 22:00 | 1 | 22 | 21.85 | 7873.3333
2017-01-04 23:00 | 1 | 23 | 17.25 | 4266.6667
2017-01-05 | 1 | 0 | 23 | 7873.3333
2017-01-05 01:00 | 1 | 1 | 20.7 | 6160
2017-01-05 02:00 | 1 | 2 | 24.15 | 9060
2017-01-05 03:00 | 1 | 3 | 18.4 | 4266.6667
2017-01-05 04:00 | 1 | 4 | 20.7 | 6160
2017-01-05 05:00 | 1 | 5 | 23 | 7873.3333
2017-01-05 06:00 | 1 | 6 | 20.7 | 6160
2017-01-05 07:00 | 1 | 7 | 17.825 | 4266.6667
2017-01-05 08:00 | 1 | 8 | 20.7 | 6160
2017-01-05 09:00 | 1 | 9 | 23 | 7873.3333
2017-01-05 10:00 | 1 | 10 | 23 | 7873.3333
2017-01-05 11:00 | 1 | 11 | 24.15 | 9060
2017-01-05 12:00 | 1 | 12 | 17.25 | 4266.6667
2017-01-05 13:00 | 1 | 13 | 14.375 | 1666.6667
2017-01-05 14:00 | 1 | 14 | 19.55 | 6160
2017-01-05 15:00 | 1 | 15 | 14.95 | 2773.3333
2017-01-05 16:00 | 1 | 16 | 13.8 | 1666.6667
2017-01-05 17:00 | 1 | 17 | 9.2 | 286.6667
2017-01-05 18:00 | 1 | 18 | 10.35 | 873.3333
2017-01-05 19:00 | 1 | 19 | 10.925 | 873.3333
2017-01-05 20:00 | 1 | 20 | 11.5 | 873.3333
2017-01-05 21:00 | 1 | 21 | 8.05 | 286.6667
2017-01-05 22:00 | 1 | 22 | 9.775 | 286.6667
2017-01-05 23:00 | 1 | 23 | 12.65 | 1666.6667
2017-01-06 | 1 | 0 | 8.05 | 286.6667
2017-01-06 01:00 | 1 | 1 | 8.625 | 286.6667
2017-01-06 02:00 | 1 | 2 | 11.5 | 873.3333
2017-01-06 03:00 | 1 | 3 | 10.35 | 873.3333
2017-01-06 04:00 | 1 | 4 | 8.625 | 286.6667
2017-01-06 05:00 | 1 | 5 | 8.05 | 286.6667
2017-01-06 06:00 | 1 | 6 | 5.75 | 0
2017-01-06 07:00 | 1 | 7 | 6.67 | 0
2017-01-06 08:00 | 1 | 8 | 6.9 | 0
2017-01-06 09:00 | 1 | 9 | 6.9 | 0
2017-01-06 10:00 | 1 | 10 | 7.475 | 0
2017-01-06 11:00 | 1 | 11 | 8.625 | 286.6667
2017-01-06 12:00 | 1 | 12 | 8.05 | 286.6667
2017-01-06 13:00 | 1 | 13 | 8.625 | 286.6667
2017-01-06 14:00 | 1 | 14 | 11.5 | 873.3333
2017-01-06 15:00 | 1 | 15 | 10.35 | 873.3333
2017-01-06 16:00 | 1 | 16 | 10.35 | 873.3333
2017-01-06 17:00 | 1 | 17 | 12.65 | 1666.6667
2017-01-06 18:00 | 1 | 18 | 8.05 | 286.6667
2017-01-06 19:00 | 1 | 19 | 10.35 | 873.3333
2017-01-06 20:00 | 1 | 20 | 10.35 | 873.3333
2017-01-06 21:00 | 1 | 21 | 8.05 | 286.6667
2017-01-06 22:00 | 1 | 22 | 9.775 | 286.6667
2017-01-06 23:00 | 1 | 23 | 10.35 | 873.3333
2017-01-07 | 1 | 0 | 12.65 | 1666.6667
2017-01-07 01:00 | 1 | 1 | 11.5 | 873.3333
2017-01-07 02:00 | 1 | 2 | 10.35 | 873.3333
2017-01-07 03:00 | 1 | 3 | 9.2 | 286.6667
2017-01-07 04:00 | 1 | 4 | 9.775 | 286.6667
2017-01-07 05:00 | 1 | 5 | 9.2 | 286.6667
2017-01-07 06:00 | 1 | 6 | 11.5 | 873.3333
2017-01-07 07:00 | 1 | 7 | 12.075 | 873.3333
2017-01-07 08:00 | 1 | 8 | 11.5 | 873.3333
2017-01-07 09:00 | 1 | 9 | 14.95 | 2773.3333
2017-01-07 10:00 | 1 | 10 | 15.525 | 2773.3333
2017-01-07 11:00 | 1 | 11 | 13.5125 | 1666.6667
2017-01-07 12:00 | 1 | 12 | 14.95 | 2773.3333
2017-01-07 13:00 | 1 | 13 | 17.825 | 4266.6667
2017-01-07 14:00 | 1 | 14 | 20.125 | 6160
2017-01-07 15:00 | 1 | 15 | 18.4 | 4266.6667
2017-01-07 16:00 | 1 | 16 | 19.55 | 6160
2017-01-07 17:00 | 1 | 17 | 25.3 | 9060
2017-01-07 18:00 | 1 | 18 | 25.6833 | 9060
2017-01-07 19:00 | 1 | 19 | 26.0667 | 9573.3333
2017-01-07 20:00 | 1 | 20 | 25.3 | 9060
2017-01-07 21:00 | 1 | 21 | 19.1667 | 6160
2017-01-07 22:00 | 1 | 22 | 18.4 | 4266.6667
2017-01-07 23:00 | 1 | 23 | 17.25 | 4266.6667
2017-01-08 | 1 | 0 | 18.4 | 4266.6667
2017-01-08 01:00 | 1 | 1 | 17.25 | 4266.6667
2017-01-08 02:00 | 1 | 2 | 16.1 | 2773.3333
2017-01-08 03:00 | 1 | 3 | 14.95 | 2773.3333
2017-01-08 04:00 | 1 | 4 | 14.95 | 2773.3333
2017-01-08 05:00 | 1 | 5 | 14.95 | 2773.3333
2017-01-08 06:00 | 1 | 6 | 11.5 | 873.3333
2017-01-08 07:00 | 1 | 7 | 13.8 | 1666.6667
2017-01-08 08:00 | 1 | 8 | 17.25 | 4266.6667
2017-01-08 09:00 | 1 | 9 | 17.25 | 4266.6667
2017-01-08 10:00 | 1 | 10 | 16.675 | 2773.3333
2017-01-08 11:00 | 1 | 11 | 16.1 | 2773.3333
2017-01-08 12:00 | 1 | 12 | 18.4 | 4266.6667
2017-01-08 13:00 | 1 | 13 | 14.95 | 2773.3333
2017-01-08 14:00 | 1 | 14 | 16.1 | 2773.3333
2017-01-08 15:00 | 1 | 15 | 18.4 | 4266.6667
2017-01-08 16:00 | 1 | 16 | 15.525 | 2773.3333
2017-01-08 17:00 | 1 | 17 | 16.1 | 2773.3333
2017-01-08 18:00 | 1 | 18 | 14.95 | 2773.3333
2017-01-08 19:00 | 1 | 19 | 13.225 | 1666.6667
2017-01-08 20:00 | 1 | 20 | 16.1 | 2773.3333
2017-01-08 21:00 | 1 | 21 | 17.25 | 4266.6667
2017-01-08 22:00 | 1 | 22 | 14.95 | 2773.3333
2017-01-08 23:00 | 1 | 23 | 14.95 | 2773.3333
2017-01-09 | 1 | 0 | 11.5 | 873.3333
2017-01-09 01:00 | 1 | 1 | 13.8 | 1666.6667
2017-01-09 02:00 | 1 | 2 | 18.4 | 4266.6667
2017-01-09 03:00 | 1 | 3 | 16.1 | 2773.3333
2017-01-09 04:00 | 1 | 4 | 14.375 | 1666.6667
2017-01-09 05:00 | 1 | 5 | 17.25 | 4266.6667
2017-01-09 06:00 | 1 | 6 | 16.1 | 2773.3333
2017-01-09 07:00 | 1 | 7 | 15.525 | 2773.3333
2017-01-09 08:00 | 1 | 8 | 16.1 | 2773.3333
2017-01-09 09:00 | 1 | 9 | 9.2 | 286.6667
2017-01-09 10:00 | 1 | 10 | 12.075 | 873.3333
2017-01-09 11:00 | 1 | 11 | 8.05 | 286.6667
2017-01-09 12:00 | 1 | 12 | 3.45 | 0
2017-01-09 13:00 | 1 | 13 | 6.325 | 0
2017-01-09 14:00 | 1 | 14 | 11.5 | 873.3333
2017-01-09 15:00 | 1 | 15 | 12.65 | 1666.6667
2017-01-09 16:00 | 1 | 16 | 12.65 | 1666.6667
2017-01-09 17:00 | 1 | 17 | 16.1 | 2773.3333
2017-01-09 18:00 | 1 | 18 | 14.95 | 2773.3333
2017-01-09 19:00 | 1 | 19 | 13.225 | 1666.6667
2017-01-09 20:00 | 1 | 20 | 11.5 | 873.3333
2017-01-09 21:00 | 1 | 21 | 9.2 | 286.6667
2017-01-09 22:00 | 1 | 22 | 9.775 | 286.6667
2017-01-09 23:00 | 1 | 23 | 9.2 | 286.6667
2017-01-10 | 1 | 0 | 10.35 | 873.3333
2017-01-10 01:00 | 1 | 1 | 10.35 | 873.3333
2017-01-10 02:00 | 1 | 2 | 12.65 | 1666.6667
2017-01-10 03:00 | 1 | 3 | 10.35 | 873.3333
2017-01-10 04:00 | 1 | 4 | 9.2 | 286.6667
2017-01-10 05:00 | 1 | 5 | 5.75 | 0
2017-01-10 06:00 | 1 | 6 | 6.9 | 0
2017-01-10 07:00 | 1 | 7 | 6.9 | 0
2017-01-10 08:00 | 1 | 8 | 6.9 | 0
2017-01-10 09:00 | 1 | 9 | 8.05 | 286.6667
2017-01-10 10:00 | 1 | 10 | 6.9 | 0
2017-01-10 11:00 | 1 | 11 | 8.05 | 286.6667
2017-01-10 12:00 | 1 | 12 | 6.9 | 0
2017-01-10 13:00 | 1 | 13 | 6.9 | 0
2017-01-10 14:00 | 1 | 14 | 5.75 | 0
2017-01-10 15:00 | 1 | 15 | 0 | 0
2017-01-10 16:00 | 1 | 16 | 1.725 | 0
2017-01-10 17:00 | 1 | 17 | 16.1 | 2773.3333
2017-01-10 18:00 | 1 | 18 | 21.0833 | 6160
2017-01-10 19:00 | 1 | 19 | 23.575 | 9060
2017-01-10 20:00 | 1 | 20 | 17.825 | 4266.6667
2017-01-10 21:00 | 1 | 21 | 13.225 | 1666.6667
2017-01-10 22:00 | 1 | 22 | 16.1 | 2773.3333
2017-01-10 23:00 | 1 | 23 | 16.1 | 2773.3333
2017-01-11 | 1 | 0 | 11.5 | 873.3333
2017-01-11 01:00 | 1 | 1 | 14.5667 | 2773.3333
2017-01-11 02:00 | 1 | 2 | 17.25 | 4266.6667
2017-01-11 03:00 | 1 | 3 | 25.3 | 9060
2017-01-11 04:00 | 1 | 4 | 24.725 | 9060
2017-01-11 05:00 | 1 | 5 | 29.9 | 9873.3333
2017-01-11 06:00 | 1 | 6 | 32.2 | 9960
2017-01-11 07:00 | 1 | 7 | 28.3667 | 9873.3333
2017-01-11 08:00 | 1 | 8 | 24.15 | 9060
2017-01-11 09:00 | 1 | 9 | 24.15 | 9060
2017-01-11 10:00 | 1 | 10 | 24.725 | 9060
2017-01-11 11:00 | 1 | 11 | 18.4 | 4266.6667
2017-01-11 12:00 | 1 | 12 | 19.55 | 6160
2017-01-11 13:00 | 1 | 13 | 16.1 | 2773.3333
2017-01-11 14:00 | 1 | 14 | 18.4 | 4266.6667
2017-01-11 15:00 | 1 | 15 | 9.2 | 286.6667
2017-01-11 16:00 | 1 | 16 | 7.475 | 0
2017-01-11 17:00 | 1 | 17 | 10.35 | 873.3333
2017-01-11 18:00 | 1 | 18 | 9.2 | 286.6667
2017-01-11 19:00 | 1 | 19 | 10.35 | 873.3333
2017-01-11 20:00 | 1 | 20 | 11.5 | 873.3333
2017-01-11 21:00 | 1 | 21 | 10.35 | 873.3333
2017-01-11 22:00 | 1 | 22 | 10.7333 | 873.3333
2017-01-11 23:00 | 1 | 23 | 8.05 | 286.6667
2017-01-12 | 1 | 0 | 9.2 | 286.6667
2017-01-12 01:00 | 1 | 1 | 7.475 | 0
2017-01-12 02:00 | 1 | 2 | 8.05 | 286.6667
2017-01-12 03:00 | 1 | 3 | 10.12 | 873.3333
2017-01-12 04:00 | 1 | 4 | 19.1667 | 6160
2017-01-12 05:00 | 1 | 5 | 19.55 | 6160
2017-01-12 06:00 | 1 | 6 | 19.9333 | 6160
2017-01-12 07:00 | 1 | 7 | 22.425 | 7873.3333
2017-01-12 08:00 | 1 | 8 | 18.4 | 4266.6667
2017-01-12 09:00 | 1 | 9 | 23 | 7873.3333
2017-01-12 10:00 | 1 | 10 | 23.3833 | 7873.3333
2017-01-12 11:00 | 1 | 11 | 23 | 7873.3333
2017-01-12 12:00 | 1 | 12 | 17.25 | 4266.6667
2017-01-12 13:00 | 1 | 13 | 17.825 | 4266.6667
2017-01-12 14:00 | 1 | 14 | 16.1 | 2773.3333
2017-01-12 15:00 | 1 | 15 | 14.95 | 2773.3333
2017-01-12 16:00 | 1 | 16 | 11.5 | 873.3333
2017-01-12 17:00 | 1 | 17 | 9.2 | 286.6667
2017-01-12 18:00 | 1 | 18 | 12.65 | 1666.6667
2017-01-12 19:00 | 1 | 19 | 11.5 | 873.3333
2017-01-12 20:00 | 1 | 20 | 19.55 | 6160
2017-01-12 21:00 | 1 | 21 | 23 | 7873.3333
2017-01-12 22:00 | 1 | 22 | 20.7 | 6160
2017-01-12 23:00 | 1 | 23 | 17.25 | 4266.6667
2017-01-13 | 1 | 0 | 12.65 | 1666.6667
2017-01-13 01:00 | 1 | 1 | 15.525 | 2773.3333
2017-01-13 02:00 | 1 | 2 | 14.95 | 2773.3333
2017-01-13 03:00 | 1 | 3 | 17.25 | 4266.6667
2017-01-13 04:00 | 1 | 4 | 20.125 | 6160
2017-01-13 05:00 | 1 | 5 | 17.25 | 4266.6667
2017-01-13 06:00 | 1 | 6 | 27.6 | 9573.3333
2017-01-13 07:00 | 1 | 7 | 22.425 | 7873.3333
2017-01-13 08:00 | 1 | 8 | 19.55 | 6160
2017-01-13 09:00 | 1 | 9 | 26.45 | 9573.3333
2017-01-13 10:00 | 1 | 10 | 23.575 | 9060
2017-01-13 11:00 | 1 | 11 | 24.15 | 9060
2017-01-13 12:00 | 1 | 12 | 23 | 7873.3333
2017-01-13 13:00 | 1 | 13 | 23 | 7873.3333
2017-01-13 14:00 | 1 | 14 | 23 | 7873.3333
2017-01-13 15:00 | 1 | 15 | 20.7 | 6160
2017-01-13 16:00 | 1 | 16 | 20.125 | 6160
2017-01-13 17:00 | 1 | 17 | 14.95 | 2773.3333
2017-01-13 18:00 | 1 | 18 | 14.95 | 2773.3333
2017-01-13 19:00 | 1 | 19 | 13.8 | 1666.6667
2017-01-13 20:00 | 1 | 20 | 17.25 | 4266.6667
2017-01-13 21:00 | 1 | 21 | 14.95 | 2773.3333
2017-01-13 22:00 | 1 | 22 | 16.675 | 2773.3333
2017-01-13 23:00 | 1 | 23 | 11.5 | 873.3333
2017-01-14 | 1 | 0 | 17.25 | 4266.6667
2017-01-14 01:00 | 1 | 1 | 16.1 | 2773.3333
2017-01-14 02:00 | 1 | 2 | 12.65 | 1666.6667
2017-01-14 03:00 | 1 | 3 | 10.35 | 873.3333
2017-01-14 04:00 | 1 | 4 | 10.925 | 873.3333
2017-01-14 05:00 | 1 | 5 | 8.05 | 286.6667
2017-01-14 06:00 | 1 | 6 | 10.35 | 873.3333
2017-01-14 07:00 | 1 | 7 | 9.775 | 286.6667
2017-01-14 08:00 | 1 | 8 | 5.75 | 0
2017-01-14 09:00 | 1 | 9 | 5.75 | 0
2017-01-14 10:00 | 1 | 10 | 2.875 | 0
2017-01-14 11:00 | 1 | 11 | 5.75 | 0
2017-01-14 12:00 | 1 | 12 | 8.05 | 286.6667
2017-01-14 13:00 | 1 | 13 | 8.625 | 286.6667
2017-01-14 14:00 | 1 | 14 | 12.65 | 1666.6667
2017-01-14 15:00 | 1 | 15 | 11.5 | 873.3333
2017-01-14 16:00 | 1 | 16 | 12.075 | 873.3333
2017-01-14 17:00 | 1 | 17 | 14.95 | 2773.3333
2017-01-14 18:00 | 1 | 18 | 12.65 | 1666.6667
2017-01-14 19:00 | 1 | 19 | 12.075 | 873.3333
2017-01-14 20:00 | 1 | 20 | 16.1 | 2773.3333
2017-01-14 21:00 | 1 | 21 | 16.1 | 2773.3333
2017-01-14 22:00 | 1 | 22 | 13.8 | 1666.6667
2017-01-14 23:00 | 1 | 23 | 11.5 | 873.3333
2017-01-15 | 1 | 0 | 12.65 | 1666.6667
2017-01-15 01:00 | 1 | 1 | 12.075 | 873.3333
2017-01-15 02:00 | 1 | 2 | 8.05 | 286.6667
2017-01-15 03:00 | 1 | 3 | 17.25 | 4266.6667
2017-01-15 04:00 | 1 | 4 | 16.1 | 2773.3333
2017-01-15 05:00 | 1 | 5 | 11.5 | 873.3333
2017-01-15 06:00 | 1 | 6 | 11.5 | 873.3333
2017-01-15 07:00 | 1 | 7 | 10.925 | 873.3333
2017-01-15 08:00 | 1 | 8 | 9.2 | 286.6667
2017-01-15 09:00 | 1 | 9 | 10.35 | 873.3333
2017-01-15 10:00 | 1 | 10 | 10.925 | 873.3333
2017-01-15 11:00 | 1 | 11 | 11.5 | 873.3333
2017-01-15 12:00 | 1 | 12 | 14.95 | 2773.3333
2017-01-15 13:00 | 1 | 13 | 14.95 | 2773.3333
2017-01-15 14:00 | 1 | 14 | 11.5 | 873.3333
2017-01-15 15:00 | 1 | 15 | 10.35 | 873.3333
2017-01-15 16:00 | 1 | 16 | 10.35 | 873.3333
2017-01-15 17:00 | 1 | 17 | 8.05 | 286.6667
2017-01-15 18:00 | 1 | 18 | 8.05 | 286.6667
2017-01-15 19:00 | 1 | 19 | 8.05 | 286.6667
2017-01-15 20:00 | 1 | 20 | 6.9 | 0
2017-01-15 21:00 | 1 | 21 | 3.45 | 0
2017-01-15 22:00 | 1 | 22 | 5.175 | 0
2017-01-15 23:00 | 1 | 23 | 6.9 | 0
2017-01-16 | 1 | 0 | 5.75 | 0
2017-01-16 01:00 | 1 | 1 | 6.325 | 0
2017-01-16 02:00 | 1 | 2 | 0 | 0
2017-01-16 03:00 | 1 | 3 | 0 | 0
2017-01-16 04:00 | 1 | 4 | 0 | 0
2017-01-16 05:00 | 1 | 5 | 0 | 0
2017-01-16 06:00 | 1 | 6 | 0 | 0
2017-01-16 07:00 | 1 | 7 | 2.875 | 0
2017-01-16 08:00 | 1 | 8 | 6.9 | 0
2017-01-16 09:00 | 1 | 9 | 12.65 | 1666.6667
2017-01-16 10:00 | 1 | 10 | 12.65 | 1666.6667
2017-01-16 11:00 | 1 | 11 | 20.7 | 6160
2017-01-16 12:00 | 1 | 12 | 18.4 | 4266.6667
2017-01-16 13:00 | 1 | 13 | 17.825 | 4266.6667
2017-01-16 14:00 | 1 | 14 | 16.1 | 2773.3333
2017-01-16 15:00 | 1 | 15 | 17.25 | 4266.6667
2017-01-16 16:00 | 1 | 16 | 16.675 | 2773.3333
2017-01-16 17:00 | 1 | 17 | 14.95 | 2773.3333
2017-01-16 18:00 | 1 | 18 | 14.95 | 2773.3333
2017-01-16 19:00 | 1 | 19 | 15.525 | 2773.3333
2017-01-16 20:00 | 1 | 20 | 14.95 | 2773.3333
2017-01-16 21:00 | 1 | 21 | 16.1 | 2773.3333
2017-01-16 22:00 | 1 | 22 | 17.25 | 4266.6667
2017-01-16 23:00 | 1 | 23 | 16.1 | 2773.3333
2017-01-17 | 1 | 0 | 14.95 | 2773.3333
2017-01-17 01:00 | 1 | 1 | 12.075 | 873.3333
2017-01-17 02:00 | 1 | 2 | 10.35 | 873.3333
2017-01-17 03:00 | 1 | 3 | 6.9 | 0
2017-01-17 04:00 | 1 | 4 | 6.325 | 0
2017-01-17 05:00 | 1 | 5 | 9.2 | 286.6667
2017-01-17 06:00 | 1 | 6 | 6.9 | 0
2017-01-17 07:00 | 1 | 7 | 8.625 | 286.6667
2017-01-17 08:00 | 1 | 8 | 10.35 | 873.3333
2017-01-17 09:00 | 1 | 9 | 8.05 | 286.6667
2017-01-17 10:00 | 1 | 10 | 8.05 | 286.6667
2017-01-17 11:00 | 1 | 11 | 9.2 | 286.6667
2017-01-17 12:00 | 1 | 12 | 18.4 | 4266.6667
2017-01-17 13:00 | 1 | 13 | 16.675 | 2773.3333
2017-01-17 14:00 | 1 | 14 | 10.35 | 873.3333
2017-01-17 15:00 | 1 | 15 | 10.35 | 873.3333
2017-01-17 16:00 | 1 | 16 | 10.35 | 873.3333
2017-01-17 17:00 | 1 | 17 | 17.25 | 4266.6667
2017-01-17 18:00 | 1 | 18 | 17.825 | 4266.6667
2017-01-17 19:00 | 1 | 19 | 20.125 | 6160
2017-01-17 20:00 | 1 | 20 | 21.85 | 7873.3333
2017-01-17 21:00 | 1 | 21 | 18.4 | 4266.6667
2017-01-17 22:00 | 1 | 22 | 20.7 | 6160
2017-01-17 23:00 | 1 | 23 | 17.825 | 4266.6667
2017-01-18 | 1 | 0 | 17.25 | 4266.6667
2017-01-18 01:00 | 1 | 1 | 17.825 | 4266.6667
2017-01-18 02:00 | 1 | 2 | 24.15 | 9060
2017-01-18 03:00 | 1 | 3 | 23 | 7873.3333
2017-01-18 04:00 | 1 | 4 | 20.7 | 6160
2017-01-18 05:00 | 1 | 5 | 19.55 | 6160
2017-01-18 06:00 | 1 | 6 | 19.55 | 6160
2017-01-18 07:00 | 1 | 7 | 17.6333 | 4266.6667
2017-01-18 08:00 | 1 | 8 | 16.4833 | 2773.3333
2017-01-18 09:00 | 1 | 9 | 16.8667 | 4266.6667
2017-01-18 10:00 | 1 | 10 | 18.0167 | 4266.6667
2017-01-18 11:00 | 1 | 11 | 17.825 | 4266.6667
2017-01-18 12:00 | 1 | 12 | 19.9333 | 6160
2017-01-18 13:00 | 1 | 13 | 18.1125 | 4266.6667
2017-01-18 14:00 | 1 | 14 | 17.25 | 4266.6667
2017-01-18 15:00 | 1 | 15 | 12.65 | 1666.6667
2017-01-18 16:00 | 1 | 16 | 11.5 | 873.3333
2017-01-18 17:00 | 1 | 17 | 10.925 | 873.3333
2017-01-18 18:00 | 1 | 18 | 14.375 | 1666.6667
2017-01-18 19:00 | 1 | 19 | 10.925 | 873.3333
2017-01-18 20:00 | 1 | 20 | 6.9 | 0
2017-01-18 21:00 | 1 | 21 | 9.775 | 286.6667
2017-01-18 22:00 | 1 | 22 | 11.1167 | 873.3333
2017-01-18 23:00 | 1 | 23 | 9.2 | 286.6667
2017-01-19 | 1 | 0 | 10.35 | 873.3333
2017-01-19 01:00 | 1 | 1 | 9.2 | 286.6667
2017-01-19 02:00 | 1 | 2 | 9.2 | 286.6667
2017-01-19 03:00 | 1 | 3 | 6.9 | 0
2017-01-19 04:00 | 1 | 4 | 6.9 | 0
2017-01-19 05:00 | 1 | 5 | 5.75 | 0
2017-01-19 06:00 | 1 | 6 | 3.45 | 0
2017-01-19 07:00 | 1 | 7 | 4.2167 | 0
2017-01-19 08:00 | 1 | 8 | 0 | 0
2017-01-19 09:00 | 1 | 9 | 0 | 0
2017-01-19 10:00 | 1 | 10 | 4.6 | 0
2017-01-19 11:00 | 1 | 11 | 12.65 | 1666.6667
2017-01-19 12:00 | 1 | 12 | 12.65 | 1666.6667
2017-01-19 13:00 | 1 | 13 | 13.8 | 1666.6667
2017-01-19 14:00 | 1 | 14 | 14.95 | 2773.3333
2017-01-19 15:00 | 1 | 15 | 8.05 | 286.6667
2017-01-19 16:00 | 1 | 16 | 7.475 | 0
2017-01-19 17:00 | 1 | 17 | 10.35 | 873.3333
2017-01-19 18:00 | 1 | 18 | 12.65 | 1666.6667
2017-01-19 19:00 | 1 | 19 | 12.65 | 1666.6667
2017-01-19 20:00 | 1 | 20 | 11.5 | 873.3333
2017-01-19 21:00 | 1 | 21 | 12.65 | 1666.6667
2017-01-19 22:00 | 1 | 22 | 14.375 | 1666.6667
2017-01-19 23:00 | 1 | 23 | 9.2 | 286.6667
2017-01-20 | 1 | 0 | 6.9 | 0
2017-01-20 01:00 | 1 | 1 | 7.475 | 0
2017-01-20 02:00 | 1 | 2 | 8.05 | 286.6667
2017-01-20 03:00 | 1 | 3 | 10.35 | 873.3333
2017-01-20 04:00 | 1 | 4 | 9.2 | 286.6667
2017-01-20 05:00 | 1 | 5 | 6.9 | 0
2017-01-20 06:00 | 1 | 6 | 3.45 | 0
2017-01-20 07:00 | 1 | 7 | 4.6 | 0
2017-01-20 08:00 | 1 | 8 | 3.45 | 0
2017-01-20 09:00 | 1 | 9 | 0 | 0
2017-01-20 10:00 | 1 | 10 | 1.725 | 0
2017-01-20 11:00 | 1 | 11 | 0 | 0
2017-01-20 12:00 | 1 | 12 | 5.75 | 0
2017-01-20 13:00 | 1 | 13 | 2.875 | 0
2017-01-20 14:00 | 1 | 14 | 5.75 | 0
2017-01-20 15:00 | 1 | 15 | 7.475 | 0
2017-01-20 16:00 | 1 | 16 | 8.4333 | 286.6667
2017-01-20 17:00 | 1 | 17 | 9.2 | 286.6667
2017-01-20 18:00 | 1 | 18 | 9.2 | 286.6667
2017-01-20 19:00 | 1 | 19 | 7.6667 | 0
2017-01-20 20:00 | 1 | 20 | 8.05 | 286.6667
2017-01-20 21:00 | 1 | 21 | 6.9 | 0
2017-01-20 22:00 | 1 | 22 | 6.325 | 0
2017-01-20 23:00 | 1 | 23 | 9.2 | 286.6667
2017-01-21 | 1 | 0 | 11.5 | 873.3333
2017-01-21 01:00 | 1 | 1 | 8.05 | 286.6667
2017-01-21 02:00 | 1 | 2 | 5.175 | 0
2017-01-21 03:00 | 1 | 3 | 6.9 | 0
2017-01-21 04:00 | 1 | 4 | 5.3667 | 0
2017-01-21 05:00 | 1 | 5 | 5.75 | 0
2017-01-21 06:00 | 1 | 6 | 6.9 | 0
2017-01-21 07:00 | 1 | 7 | 9.775 | 286.6667
2017-01-21 08:00 | 1 | 8 | 12.075 | 873.3333
2017-01-21 09:00 | 1 | 9 | 6.9 | 0
2017-01-21 10:00 | 1 | 10 | 7.475 | 0
2017-01-21 11:00 | 1 | 11 | 8.05 | 286.6667
2017-01-21 12:00 | 1 | 12 | 14.95 | 2773.3333
2017-01-21 13:00 | 1 | 13 | 10.925 | 873.3333
2017-01-21 14:00 | 1 | 14 | 8.05 | 286.6667
2017-01-21 15:00 | 1 | 15 | 14.95 | 2773.3333
2017-01-21 16:00 | 1 | 16 | 13.225 | 1666.6667
2017-01-21 17:00 | 1 | 17 | 12.65 | 1666.6667
2017-01-21 18:00 | 1 | 18 | 9.2 | 286.6667
2017-01-21 19:00 | 1 | 19 | 9.2 | 286.6667
2017-01-21 20:00 | 1 | 20 | 8.05 | 286.6667
2017-01-21 21:00 | 1 | 21 | 9.2 | 286.6667
2017-01-21 22:00 | 1 | 22 | 7.475 | 0
2017-01-21 23:00 | 1 | 23 | 3.45 | 0
2017-01-22 | 1 | 0 | 0 | 0
2017-01-22 01:00 | 1 | 1 | 1.725 | 0
2017-01-22 02:00 | 1 | 2 | 0 | 0
2017-01-22 03:00 | 1 | 3 | 3.45 | 0
2017-01-22 04:00 | 1 | 4 | 4.6 | 0
2017-01-22 05:00 | 1 | 5 | 0 | 0
2017-01-22 06:00 | 1 | 6 | 5.75 | 0
2017-01-22 07:00 | 1 | 7 | 4.6 | 0
2017-01-22 08:00 | 1 | 8 | 0 | 0
2017-01-22 09:00 | 1 | 9 | 8.05 | 286.6667
2017-01-22 10:00 | 1 | 10 | 10.35 | 873.3333
2017-01-22 11:00 | 1 | 11 | 15.525 | 2773.3333
2017-01-22 12:00 | 1 | 12 | 16.675 | 2773.3333
2017-01-22 13:00 | 1 | 13 | 17.25 | 4266.6667
2017-01-22 14:00 | 1 | 14 | 20.4125 | 6160
2017-01-22 15:00 | 1 | 15 | 19.55 | 6160
2017-01-22 16:00 | 1 | 16 | 19.55 | 6160
2017-01-22 17:00 | 1 | 17 | 21.4667 | 7873.3333
2017-01-22 18:00 | 1 | 18 | 20.7 | 6160
2017-01-22 19:00 | 1 | 19 | 21.5625 | 7873.3333
2017-01-22 20:00 | 1 | 20 | 19.55 | 6160
2017-01-22 21:00 | 1 | 21 | 20.7 | 6160
2017-01-22 22:00 | 1 | 22 | 23 | 7873.3333
2017-01-22 23:00 | 1 | 23 | 22.2333 | 7873.3333
2017-01-23 | 1 | 0 | 23.575 | 9060
2017-01-23 01:00 | 1 | 1 | 25.3 | 9060
2017-01-23 02:00 | 1 | 2 | 24.725 | 9060
2017-01-23 03:00 | 1 | 3 | 27.83 | 9573.3333
2017-01-23 04:00 | 1 | 4 | 28.75 | 9873.3333
2017-01-23 05:00 | 1 | 5 | 22.425 | 7873.3333
2017-01-23 06:00 | 1 | 6 | 24.725 | 9060
2017-01-23 07:00 | 1 | 7 | 26.45 | 9573.3333
2017-01-23 08:00 | 1 | 8 | 27.6 | 9573.3333
2017-01-23 09:00 | 1 | 9 | 26.45 | 9573.3333
2017-01-23 10:00 | 1 | 10 | 24.15 | 9060
2017-01-23 11:00 | 1 | 11 | 30.475 | 9960
2017-01-23 12:00 | 1 | 12 | 26.45 | 9573.3333
2017-01-23 13:00 | 1 | 13 | 28.3667 | 9873.3333
2017-01-23 14:00 | 1 | 14 | 32.775 | 10000
2017-01-23 15:00 | 1 | 15 | 27.6 | 9573.3333
2017-01-23 16:00 | 1 | 16 | 29.325 | 9873.3333
2017-01-23 17:00 | 1 | 17 | 34.5 | 10000
2017-01-23 18:00 | 1 | 18 | 33.35 | 10000
2017-01-23 19:00 | 1 | 19 | 35.65 | 10000
2017-01-23 20:00 | 1 | 20 | 32.9667 | 10000
2017-01-23 21:00 | 1 | 21 | 34.2125 | 10000
2017-01-23 22:00 | 1 | 22 | 34.5 | 10000
2017-01-23 23:00 | 1 | 23 | 32.2 | 9960
2017-01-24 | 1 | 0 | 32.2 | 9960
2017-01-24 01:00 | 1 | 1 | 36.4167 | 10000
2017-01-24 02:00 | 1 | 2 | 37.95 | 10000
2017-01-24 03:00 | 1 | 3 | 41.0167 | 10000
2017-01-24 04:00 | 1 | 4 | 38.1417 | 10000
2017-01-24 05:00 | 1 | 5 | 33.35 | 10000
2017-01-24 06:00 | 1 | 6 | 35.075 | 10000
2017-01-24 07:00 | 1 | 7 | 33.81 | 10000
2017-01-24 08:00 | 1 | 8 | 31.05 | 9960
2017-01-24 09:00 | 1 | 9 | 31.05 | 9960
2017-01-24 10:00 | 1 | 10 | 32.5833 | 10000
2017-01-24 11:00 | 1 | 11 | 37.375 | 10000
2017-01-24 12:00 | 1 | 12 | 35.2667 | 10000
2017-01-24 13:00 | 1 | 13 | 31.05 | 9960
2017-01-24 14:00 | 1 | 14 | 27.3125 | 9573.3333
2017-01-24 15:00 | 1 | 15 | 24.15 | 9060
2017-01-24 16:00 | 1 | 16 | 26.1625 | 9573.3333
2017-01-24 17:00 | 1 | 17 | 19.55 | 6160
2017-01-24 18:00 | 1 | 18 | 18.0167 | 4266.6667
2017-01-24 19:00 | 1 | 19 | 16.1 | 2773.3333
2017-01-24 20:00 | 1 | 20 | 17.25 | 4266.6667
2017-01-24 21:00 | 1 | 21 | 20.7 | 6160
2017-01-24 22:00 | 1 | 22 | 18.4 | 4266.6667
2017-01-24 23:00 | 1 | 23 | 18.4 | 4266.6667
2017-01-25 | 1 | 0 | 16.1 | 2773.3333
2017-01-25 01:00 | 1 | 1 | 16.1 | 2773.3333
2017-01-25 02:00 | 1 | 2 | 15.525 | 2773.3333
2017-01-25 03:00 | 1 | 3 | 18.4 | 4266.6667
2017-01-25 04:00 | 1 | 4 | 16.9625 | 4266.6667
2017-01-25 05:00 | 1 | 5 | 14.95 | 2773.3333
2017-01-25 06:00 | 1 | 6 | 21.275 | 7873.3333
2017-01-25 07:00 | 1 | 7 | 21.85 | 7873.3333
2017-01-25 08:00 | 1 | 8 | 23 | 7873.3333
2017-01-25 09:00 | 1 | 9 | 25.3 | 9060
2017-01-25 10:00 | 1 | 10 | 25.3 | 9060
2017-01-25 11:00 | 1 | 11 | 26.45 | 9573.3333
2017-01-25 12:00 | 1 | 12 | 23 | 7873.3333
2017-01-25 13:00 | 1 | 13 | 13.225 | 1666.6667
2017-01-25 14:00 | 1 | 14 | 23 | 7873.3333
2017-01-25 15:00 | 1 | 15 | 17.25 | 4266.6667
2017-01-25 16:00 | 1 | 16 | 17.825 | 4266.6667
2017-01-25 17:00 | 1 | 17 | 16.1 | 2773.3333
2017-01-25 18:00 | 1 | 18 | 14.95 | 2773.3333
2017-01-25 19:00 | 1 | 19 | 12.65 | 1666.6667
2017-01-25 20:00 | 1 | 20 | 12.65 | 1666.6667
2017-01-25 21:00 | 1 | 21 | 11.5 | 873.3333
2017-01-25 22:00 | 1 | 22 | 9.775 | 286.6667
2017-01-25 23:00 | 1 | 23 | 8.05 | 286.6667
2017-01-26 | 1 | 0 | 11.5 | 873.3333
2017-01-26 01:00 | 1 | 1 | 10.925 | 873.3333
2017-01-26 02:00 | 1 | 2 | 11.5 | 873.3333
2017-01-26 03:00 | 1 | 3 | 10.35 | 873.3333
2017-01-26 04:00 | 1 | 4 | 9.775 | 286.6667
2017-01-26 05:00 | 1 | 5 | 11.5 | 873.3333
2017-01-26 06:00 | 1 | 6 | 6.9 | 0
2017-01-26 07:00 | 1 | 7 | 3.45 | 0
2017-01-26 08:00 | 1 | 8 | 10.35 | 873.3333
2017-01-26 09:00 | 1 | 9 | 10.35 | 873.3333
2017-01-26 10:00 | 1 | 10 | 17.25 | 4266.6667
2017-01-26 11:00 | 1 | 11 | 17.25 | 4266.6667
2017-01-26 12:00 | 1 | 12 | 18.4 | 4266.6667
2017-01-26 13:00 | 1 | 13 | 21.275 | 7873.3333
2017-01-26 14:00 | 1 | 14 | 20.7 | 6160
2017-01-26 15:00 | 1 | 15 | 23.575 | 9060
2017-01-26 16:00 | 1 | 16 | 17.25 | 4266.6667
2017-01-26 17:00 | 1 | 17 | 18.4 | 4266.6667
2017-01-26 18:00 | 1 | 18 | 18.4 | 4266.6667
2017-01-26 19:00 | 1 | 19 | 17.25 | 4266.6667
2017-01-26 20:00 | 1 | 20 | 17.25 | 4266.6667
2017-01-26 21:00 | 1 | 21 | 18.4 | 4266.6667
2017-01-26 22:00 | 1 | 22 | 21.275 | 7873.3333
2017-01-26 23:00 | 1 | 23 | 25.3 | 9060
2017-01-27 | 1 | 0 | 18.4 | 4266.6667
2017-01-27 01:00 | 1 | 1 | 14.95 | 2773.3333
2017-01-27 02:00 | 1 | 2 | 17.25 | 4266.6667
2017-01-27 03:00 | 1 | 3 | 23 | 7873.3333
2017-01-27 04:00 | 1 | 4 | 20.125 | 6160
2017-01-27 05:00 | 1 | 5 | 18.4 | 4266.6667
2017-01-27 06:00 | 1 | 6 | 11.5 | 873.3333
2017-01-27 07:00 | 1 | 7 | 14.95 | 2773.3333
2017-01-27 08:00 | 1 | 8 | 16.1 | 2773.3333
2017-01-27 09:00 | 1 | 9 | 29.9 | 9873.3333
2017-01-27 10:00 | 1 | 10 | 27.6 | 9573.3333
2017-01-27 11:00 | 1 | 11 | 32.2 | 9960
2017-01-27 12:00 | 1 | 12 | 24.15 | 9060
2017-01-27 13:00 | 1 | 13 | 25.3 | 9060
2017-01-27 14:00 | 1 | 14 | 24.15 | 9060
2017-01-27 15:00 | 1 | 15 | 19.55 | 6160
2017-01-27 16:00 | 1 | 16 | 19.55 | 6160
2017-01-27 17:00 | 1 | 17 | 19.55 | 6160
2017-01-27 18:00 | 1 | 18 | 17.25 | 4266.6667
2017-01-27 19:00 | 1 | 19 | 17.825 | 4266.6667
2017-01-27 20:00 | 1 | 20 | 17.25 | 4266.6667
2017-01-27 21:00 | 1 | 21 | 18.4 | 4266.6667
2017-01-27 22:00 | 1 | 22 | 18.4 | 4266.6667
2017-01-27 23:00 | 1 | 23 | 19.55 | 6160
2017-01-28 | 1 | 0 | 19.55 | 6160
2017-01-28 01:00 | 1 | 1 | 18.4 | 4266.6667
2017-01-28 02:00 | 1 | 2 | 19.55 | 6160
2017-01-28 03:00 | 1 | 3 | 17.25 | 4266.6667
2017-01-28 04:00 | 1 | 4 | 14.375 | 1666.6667
2017-01-28 05:00 | 1 | 5 | 10.35 | 873.3333
2017-01-28 06:00 | 1 | 6 | 11.5 | 873.3333
2017-01-28 07:00 | 1 | 7 | 14.95 | 2773.3333
2017-01-28 08:00 | 1 | 8 | 16.1 | 2773.3333
2017-01-28 09:00 | 1 | 9 | 24.15 | 9060
2017-01-28 10:00 | 1 | 10 | 21.85 | 7873.3333
2017-01-28 11:00 | 1 | 11 | 18.4 | 4266.6667
2017-01-28 12:00 | 1 | 12 | 23 | 7873.3333
2017-01-28 13:00 | 1 | 13 | 21.85 | 7873.3333
2017-01-28 14:00 | 1 | 14 | 24.15 | 9060
2017-01-28 15:00 | 1 | 15 | 18.4 | 4266.6667
2017-01-28 16:00 | 1 | 16 | 17.825 | 4266.6667
2017-01-28 17:00 | 1 | 17 | 17.25 | 4266.6667
2017-01-28 18:00 | 1 | 18 | 16.1 | 2773.3333
2017-01-28 19:00 | 1 | 19 | 14.375 | 1666.6667
2017-01-28 20:00 | 1 | 20 | 16.1 | 2773.3333
2017-01-28 21:00 | 1 | 21 | 14.95 | 2773.3333
2017-01-28 22:00 | 1 | 22 | 15.525 | 2773.3333
2017-01-28 23:00 | 1 | 23 | 16.1 | 2773.3333
2017-01-29 | 1 | 0 | 14.95 | 2773.3333
2017-01-29 01:00 | 1 | 1 | 13.225 | 1666.6667
2017-01-29 02:00 | 1 | 2 | 11.5 | 873.3333
2017-01-29 03:00 | 1 | 3 | 14.95 | 2773.3333
2017-01-29 04:00 | 1 | 4 | 13.8 | 1666.6667
2017-01-29 05:00 | 1 | 5 | 11.5 | 873.3333
2017-01-29 06:00 | 1 | 6 | 12.65 | 1666.6667
2017-01-29 07:00 | 1 | 7 | 12.65 | 1666.6667
2017-01-29 08:00 | 1 | 8 | 14.95 | 2773.3333
2017-01-29 09:00 | 1 | 9 | 17.25 | 4266.6667
2017-01-29 10:00 | 1 | 10 | 16.675 | 2773.3333
2017-01-29 11:00 | 1 | 11 | 16.1 | 2773.3333
2017-01-29 12:00 | 1 | 12 | 19.55 | 6160
2017-01-29 13:00 | 1 | 13 | 18.975 | 4266.6667
2017-01-29 14:00 | 1 | 14 | 11.5 | 873.3333
2017-01-29 15:00 | 1 | 15 | 16.1 | 2773.3333
2017-01-29 16:00 | 1 | 16 | 13.4167 | 1666.6667
2017-01-29 17:00 | 1 | 17 | 9.2 | 286.6667
2017-01-29 18:00 | 1 | 18 | 9.2 | 286.6667
2017-01-29 19:00 | 1 | 19 | 8.625 | 286.6667
2017-01-29 20:00 | 1 | 20 | 11.5 | 873.3333
2017-01-29 21:00 | 1 | 21 | 10.35 | 873.3333
2017-01-29 22:00 | 1 | 22 | 9.2 | 286.6667
2017-01-29 23:00 | 1 | 23 | 8.05 | 286.6667
2017-01-30 | 1 | 0 | 10.35 | 873.3333
2017-01-30 01:00 | 1 | 1 | 9.775 | 286.6667
2017-01-30 02:00 | 1 | 2 | 9.2 | 286.6667
2017-01-30 03:00 | 1 | 3 | 10.35 | 873.3333
2017-01-30 04:00 | 1 | 4 | 10.925 | 873.3333
2017-01-30 05:00 | 1 | 5 | 10.35 | 873.3333
2017-01-30 06:00 | 1 | 6 | 8.05 | 286.6667
2017-01-30 07:00 | 1 | 7 | 7.475 | 0
2017-01-30 08:00 | 1 | 8 | 11.5 | 873.3333
2017-01-30 09:00 | 1 | 9 | 9.2 | 286.6667
2017-01-30 10:00 | 1 | 10 | 6.325 | 0
2017-01-30 11:00 | 1 | 11 | 5.75 | 0
2017-01-30 12:00 | 1 | 12 | 9.2 | 286.6667
2017-01-30 13:00 | 1 | 13 | 10.35 | 873.3333
2017-01-30 14:00 | 1 | 14 | 12.65 | 1666.6667
2017-01-30 15:00 | 1 | 15 | 16.1 | 2773.3333
2017-01-30 16:00 | 1 | 16 | 12.075 | 873.3333
2017-01-30 17:00 | 1 | 17 | 9.2 | 286.6667
2017-01-30 18:00 | 1 | 18 | 17.25 | 4266.6667
2017-01-30 19:00 | 1 | 19 | 17.25 | 4266.6667
2017-01-30 20:00 | 1 | 20 | 16.1 | 2773.3333
2017-01-30 21:00 | 1 | 21 | 16.1 | 2773.3333
2017-01-30 22:00 | 1 | 22 | 16.1 | 2773.3333
2017-01-30 23:00 | 1 | 23 | 17.25 | 4266.6667
2017-01-31 | 1 | 0 | 17.25 | 4266.6667
2017-01-31 01:00 | 1 | 1 | 17.825 | 4266.6667
2017-01-31 02:00 | 1 | 2 | 17.25 | 4266.6667
2017-01-31 03:00 | 1 | 3 | 16.1 | 2773.3333
2017-01-31 04:00 | 1 | 4 | 14.375 | 1666.6667
2017-01-31 05:00 | 1 | 5 | 16.1 | 2773.3333
2017-01-31 06:00 | 1 | 6 | 12.65 | 1666.6667
2017-01-31 07:00 | 1 | 7 | 10.925 | 873.3333
2017-01-31 08:00 | 1 | 8 | 9.2 | 286.6667
2017-01-31 09:00 | 1 | 9 | 0 | 0
2017-01-31 10:00 | 1 | 10 | 2.875 | 0
2017-01-31 11:00 | 1 | 11 | 6.9 | 0
2017-01-31 12:00 | 1 | 12 | 6.9 | 0
2017-01-31 13:00 | 1 | 13 | 7.475 | 0
2017-01-31 14:00 | 1 | 14 | 5.75 | 0
2017-01-31 15:00 | 1 | 15 | 6.6125 | 0
2017-01-31 16:00 | 1 | 16 | 6.6125 | 0
2017-01-31 17:00 | 1 | 17 | 6.9 | 0
2017-01-31 18:00 | 1 | 18 | 3.22 | 0
2017-01-31 19:00 | 1 | 19 | 2.99 | 0
2017-01-31 20:00 | 1 | 20 | 1.725 | 0
2017-01-31 21:00 | 1 | 21 | 3.45 | 0
2017-01-31 22:00 | 1 | 22 | 4.2167 | 0
2017-01-31 23:00 | 1 | 23 | 6.9 | 0
2017-02-01 | 2 | 0 | 7.6667 | 0
2017-02-01 01:00 | 2 | 1 | 8.05 | 286.6667
2017-02-01 02:00 | 2 | 2 | 6.9 | 0
2017-02-01 03:00 | 2 | 3 | 9.2 | 286.6667
2017-02-01 04:00 | 2 | 4 | 6.9 | 0
2017-02-01 05:00 | 2 | 5 | 0 | 0
2017-02-01 06:00 | 2 | 6 | 1.725 | 0
2017-02-01 07:00 | 2 | 7 | 9.9667 | 286.6667
2017-02-01 08:00 | 2 | 8 | 13.225 | 1666.6667
2017-02-01 09:00 | 2 | 9 | 10.35 | 873.3333
2017-02-01 10:00 | 2 | 10 | 9.775 | 286.6667
2017-02-01 11:00 | 2 | 11 | 16.1 | 2773.3333
2017-02-01 12:00 | 2 | 12 | 19.55 | 6160
2017-02-01 13:00 | 2 | 13 | 18.975 | 4266.6667
2017-02-01 14:00 | 2 | 14 | 26.45 | 9573.3333
2017-02-01 15:00 | 2 | 15 | 27.6 | 9573.3333
2017-02-01 16:00 | 2 | 16 | 21.275 | 7873.3333
2017-02-01 17:00 | 2 | 17 | 12.65 | 1666.6667
2017-02-01 18:00 | 2 | 18 | 9.2 | 286.6667
2017-02-01 19:00 | 2 | 19 | 9.2 | 286.6667
2017-02-01 20:00 | 2 | 20 | 9.2 | 286.6667
2017-02-01 21:00 | 2 | 21 | 18.4 | 4266.6667
2017-02-01 22:00 | 2 | 22 | 16.675 | 2773.3333
2017-02-01 23:00 | 2 | 23 | 11.5 | 873.3333
2017-02-02 | 2 | 0 | 14.95 | 2773.3333
2017-02-02 01:00 | 2 | 1 | 13.8 | 1666.6667
2017-02-02 02:00 | 2 | 2 | 9.2 | 286.6667
2017-02-02 03:00 | 2 | 3 | 11.5 | 873.3333
2017-02-02 04:00 | 2 | 4 | 10.35 | 873.3333
2017-02-02 05:00 | 2 | 5 | 10.35 | 873.3333
2017-02-02 06:00 | 2 | 6 | 11.5 | 873.3333
2017-02-02 07:00 | 2 | 7 | 13.8 | 1666.6667
2017-02-02 08:00 | 2 | 8 | 11.5 | 873.3333
2017-02-02 09:00 | 2 | 9 | 11.5 | 873.3333
2017-02-02 10:00 | 2 | 10 | 13.8 | 1666.6667
2017-02-02 11:00 | 2 | 11 | 18.4 | 4266.6667
2017-02-02 12:00 | 2 | 12 | 20.7 | 6160
2017-02-02 13:00 | 2 | 13 | 19.55 | 6160
2017-02-02 14:00 | 2 | 14 | 19.55 | 6160
2017-02-02 15:00 | 2 | 15 | 17.25 | 4266.6667
2017-02-02 16:00 | 2 | 16 | 14.95 | 2773.3333
2017-02-02 17:00 | 2 | 17 | 23 | 7873.3333
2017-02-02 18:00 | 2 | 18 | 16.1 | 2773.3333
2017-02-02 19:00 | 2 | 19 | 14.375 | 1666.6667
2017-02-02 20:00 | 2 | 20 | 16.1 | 2773.3333
2017-02-02 21:00 | 2 | 21 | 19.55 | 6160
2017-02-02 22:00 | 2 | 22 | 21.275 | 7873.3333
2017-02-02 23:00 | 2 | 23 | 14.95 | 2773.3333
2017-02-03 | 2 | 0 | 18.4 | 4266.6667
2017-02-03 01:00 | 2 | 1 | 14.375 | 1666.6667
2017-02-03 02:00 | 2 | 2 | 18.4 | 4266.6667
2017-02-03 03:00 | 2 | 3 | 12.65 | 1666.6667
2017-02-03 04:00 | 2 | 4 | 12.65 | 1666.6667
2017-02-03 05:00 | 2 | 5 | 12.65 | 1666.6667
2017-02-03 06:00 | 2 | 6 | 12.65 | 1666.6667
2017-02-03 07:00 | 2 | 7 | 10.925 | 873.3333
2017-02-03 08:00 | 2 | 8 | 8.05 | 286.6667
2017-02-03 09:00 | 2 | 9 | 8.05 | 286.6667
2017-02-03 10:00 | 2 | 10 | 9.2 | 286.6667
2017-02-03 11:00 | 2 | 11 | 9.2 | 286.6667
2017-02-03 12:00 | 2 | 12 | 10.35 | 873.3333
2017-02-03 13:00 | 2 | 13 | 11.5 | 873.3333
2017-02-03 14:00 | 2 | 14 | 16.1 | 2773.3333
2017-02-03 15:00 | 2 | 15 | 16.1 | 2773.3333
2017-02-03 16:00 | 2 | 16 | 14.375 | 1666.6667
2017-02-03 17:00 | 2 | 17 | 12.65 | 1666.6667
2017-02-03 18:00 | 2 | 18 | 15.525 | 2773.3333
2017-02-03 19:00 | 2 | 19 | 17.25 | 4266.6667
2017-02-03 20:00 | 2 | 20 | 14.95 | 2773.3333
2017-02-03 21:00 | 2 | 21 | 14.95 | 2773.3333
2017-02-03 22:00 | 2 | 22 | 16.1 | 2773.3333
2017-02-03 23:00 | 2 | 23 | 16.1 | 2773.3333
2017-02-04 | 2 | 0 | 20.7 | 6160
2017-02-04 01:00 | 2 | 1 | 20.125 | 6160
2017-02-04 02:00 | 2 | 2 | 19.55 | 6160
2017-02-04 03:00 | 2 | 3 | 18.4 | 4266.6667
2017-02-04 04:00 | 2 | 4 | 17.25 | 4266.6667
2017-02-04 05:00 | 2 | 5 | 14.95 | 2773.3333
2017-02-04 06:00 | 2 | 6 | 18.4 | 4266.6667
2017-02-04 07:00 | 2 | 7 | 14.95 | 2773.3333
2017-02-04 08:00 | 2 | 8 | 16.1 | 2773.3333
2017-02-04 09:00 | 2 | 9 | 14.95 | 2773.3333
2017-02-04 10:00 | 2 | 10 | 16.675 | 2773.3333
2017-02-04 11:00 | 2 | 11 | 17.25 | 4266.6667
2017-02-04 12:00 | 2 | 12 | 18.4 | 4266.6667
2017-02-04 13:00 | 2 | 13 | 20.7 | 6160
2017-02-04 14:00 | 2 | 14 | 9.2 | 286.6667
2017-02-04 15:00 | 2 | 15 | 16.1 | 2773.3333
2017-02-04 16:00 | 2 | 16 | 13.8 | 1666.6667
2017-02-04 17:00 | 2 | 17 | 17.25 | 4266.6667
2017-02-04 18:00 | 2 | 18 | 10.35 | 873.3333
2017-02-04 19:00 | 2 | 19 | 9.775 | 286.6667
2017-02-04 20:00 | 2 | 20 | 9.2 | 286.6667
2017-02-04 21:00 | 2 | 21 | 8.05 | 286.6667
2017-02-04 22:00 | 2 | 22 | 11.5 | 873.3333
2017-02-04 23:00 | 2 | 23 | 11.5 | 873.3333
2017-02-05 | 2 | 0 | 9.2 | 286.6667
2017-02-05 01:00 | 2 | 1 | 9.2 | 286.6667
2017-02-05 02:00 | 2 | 2 | 10.35 | 873.3333
2017-02-05 03:00 | 2 | 3 | 10.35 | 873.3333
2017-02-05 04:00 | 2 | 4 | 9.775 | 286.6667
2017-02-05 05:00 | 2 | 5 | 11.5 | 873.3333
2017-02-05 06:00 | 2 | 6 | 17.25 | 4266.6667
2017-02-05 07:00 | 2 | 7 | 17.825 | 4266.6667
2017-02-05 08:00 | 2 | 8 | 16.1 | 2773.3333
2017-02-05 09:00 | 2 | 9 | 17.25 | 4266.6667
2017-02-05 10:00 | 2 | 10 | 14.375 | 1666.6667
2017-02-05 11:00 | 2 | 11 | 24.15 | 9060
2017-02-05 12:00 | 2 | 12 | 18.4 | 4266.6667
2017-02-05 13:00 | 2 | 13 | 22.425 | 7873.3333
2017-02-05 14:00 | 2 | 14 | 25.3 | 9060
2017-02-05 15:00 | 2 | 15 | 20.7 | 6160
2017-02-05 16:00 | 2 | 16 | 18.975 | 4266.6667
2017-02-05 17:00 | 2 | 17 | 19.55 | 6160
2017-02-05 18:00 | 2 | 18 | 14.95 | 2773.3333
2017-02-05 19:00 | 2 | 19 | 17.25 | 4266.6667
2017-02-05 20:00 | 2 | 20 | 9.2 | 286.6667
2017-02-05 21:00 | 2 | 21 | 12.65 | 1666.6667
2017-02-05 22:00 | 2 | 22 | 12.65 | 1666.6667
2017-02-05 23:00 | 2 | 23 | 14.95 | 2773.3333
2017-02-06 | 2 | 0 | 11.5 | 873.3333
2017-02-06 01:00 | 2 | 1 | 16.1 | 2773.3333
2017-02-06 02:00 | 2 | 2 | 20.7 | 6160
2017-02-06 03:00 | 2 | 3 | 27.6 | 9573.3333
2017-02-06 04:00 | 2 | 4 | 24.15 | 9060
2017-02-06 05:00 | 2 | 5 | 18.4 | 4266.6667
2017-02-06 06:00 | 2 | 6 | 18.4 | 4266.6667
2017-02-06 07:00 | 2 | 7 | 17.825 | 4266.6667
2017-02-06 08:00 | 2 | 8 | 12.65 | 1666.6667
2017-02-06 09:00 | 2 | 9 | 25.3 | 9060
2017-02-06 10:00 | 2 | 10 | 22.425 | 7873.3333
2017-02-06 11:00 | 2 | 11 | 23 | 7873.3333
2017-02-06 12:00 | 2 | 12 | 19.55 | 6160
2017-02-06 13:00 | 2 | 13 | 20.125 | 6160
2017-02-06 14:00 | 2 | 14 | 20.7 | 6160
2017-02-06 15:00 | 2 | 15 | 20.7 | 6160
2017-02-06 16:00 | 2 | 16 | 18.4 | 4266.6667
2017-02-06 17:00 | 2 | 17 | 12.65 | 1666.6667
2017-02-06 18:00 | 2 | 18 | 11.5 | 873.3333
2017-02-06 19:00 | 2 | 19 | 10.925 | 873.3333
2017-02-06 20:00 | 2 | 20 | 5.75 | 0
2017-02-06 21:00 | 2 | 21 | 5.75 | 0
2017-02-06 22:00 | 2 | 22 | 2.875 | 0
2017-02-06 23:00 | 2 | 23 | 3.45 | 0
2017-02-07 | 2 | 0 | 5.75 | 0
2017-02-07 01:00 | 2 | 1 | 6.9 | 0
2017-02-07 02:00 | 2 | 2 | 10.35 | 873.3333
2017-02-07 03:00 | 2 | 3 | 11.5 | 873.3333
2017-02-07 04:00 | 2 | 4 | 15.525 | 2773.3333
2017-02-07 05:00 | 2 | 5 | 18.4 | 4266.6667
2017-02-07 06:00 | 2 | 6 | 20.7 | 6160
2017-02-07 07:00 | 2 | 7 | 18.7833 | 4266.6667
2017-02-07 08:00 | 2 | 8 | 19.55 | 6160
2017-02-07 09:00 | 2 | 9 | 20.125 | 6160
2017-02-07 10:00 | 2 | 10 | 21.85 | 7873.3333
2017-02-07 11:00 | 2 | 11 | 22.425 | 7873.3333
2017-02-07 12:00 | 2 | 12 | 27.6 | 9573.3333
2017-02-07 13:00 | 2 | 13 | 26.45 | 9573.3333
2017-02-07 14:00 | 2 | 14 | 25.3 | 9060
2017-02-07 15:00 | 2 | 15 | 27.025 | 9573.3333
2017-02-07 16:00 | 2 | 16 | 26.45 | 9573.3333
2017-02-07 17:00 | 2 | 17 | 23 | 7873.3333
2017-02-07 18:00 | 2 | 18 | 20.7 | 6160
2017-02-07 19:00 | 2 | 19 | 23.92 | 9060
2017-02-07 20:00 | 2 | 20 | 20.7 | 6160
2017-02-07 21:00 | 2 | 21 | 18.4 | 4266.6667
2017-02-07 22:00 | 2 | 22 | 17.25 | 4266.6667
2017-02-07 23:00 | 2 | 23 | 10.35 | 873.3333
2017-02-08 | 2 | 0 | 10.35 | 873.3333
2017-02-08 01:00 | 2 | 1 | 13.0333 | 1666.6667
2017-02-08 02:00 | 2 | 2 | 9.2 | 286.6667
2017-02-08 03:00 | 2 | 3 | 8.05 | 286.6667
2017-02-08 04:00 | 2 | 4 | 10.7333 | 873.3333
2017-02-08 05:00 | 2 | 5 | 4.2167 | 0
2017-02-08 06:00 | 2 | 6 | 6.1333 | 0
2017-02-08 07:00 | 2 | 7 | 4.6 | 0
2017-02-08 08:00 | 2 | 8 | 8.05 | 286.6667
2017-02-08 09:00 | 2 | 9 | 5.75 | 0
2017-02-08 10:00 | 2 | 10 | 8.3375 | 286.6667
2017-02-08 11:00 | 2 | 11 | 10.6375 | 873.3333
2017-02-08 12:00 | 2 | 12 | 12.65 | 1666.6667
2017-02-08 13:00 | 2 | 13 | 11.5 | 873.3333
2017-02-08 14:00 | 2 | 14 | 18.4 | 4266.6667
2017-02-08 15:00 | 2 | 15 | 14.95 | 2773.3333
2017-02-08 16:00 | 2 | 16 | 12.075 | 873.3333
2017-02-08 17:00 | 2 | 17 | 10.35 | 873.3333
2017-02-08 18:00 | 2 | 18 | 12.65 | 1666.6667
2017-02-08 19:00 | 2 | 19 | 12.075 | 873.3333
2017-02-08 20:00 | 2 | 20 | 16.1 | 2773.3333
2017-02-08 21:00 | 2 | 21 | 14.95 | 2773.3333
2017-02-08 22:00 | 2 | 22 | 12.65 | 1666.6667
2017-02-08 23:00 | 2 | 23 | 8.05 | 286.6667
2017-02-09 | 2 | 0 | 3.45 | 0
2017-02-09 01:00 | 2 | 1 | 4.6 | 0
2017-02-09 02:00 | 2 | 2 | 5.75 | 0
2017-02-09 03:00 | 2 | 3 | 6.9 | 0
2017-02-09 04:00 | 2 | 4 | 13.8 | 1666.6667
2017-02-09 05:00 | 2 | 5 | 22.425 | 7873.3333
2017-02-09 06:00 | 2 | 6 | 24.15 | 9060
2017-02-09 07:00 | 2 | 7 | 26.45 | 9573.3333
2017-02-09 08:00 | 2 | 8 | 25.5875 | 9060
2017-02-09 09:00 | 2 | 9 | 35.2667 | 10000
2017-02-09 10:00 | 2 | 10 | 37.6625 | 10000
2017-02-09 11:00 | 2 | 11 | 35.65 | 10000
2017-02-09 12:00 | 2 | 12 | 28.75 | 9873.3333
2017-02-09 13:00 | 2 | 13 | 31.3375 | 9960
2017-02-09 14:00 | 2 | 14 | 27.6 | 9573.3333
2017-02-09 15:00 | 2 | 15 | 22.425 | 7873.3333
2017-02-09 16:00 | 2 | 16 | 22.2333 | 7873.3333
2017-02-09 17:00 | 2 | 17 | 18.7833 | 4266.6667
2017-02-09 18:00 | 2 | 18 | 28.175 | 9873.3333
2017-02-09 19:00 | 2 | 19 | 25.99 | 9573.3333
2017-02-09 20:00 | 2 | 20 | 27.2167 | 9573.3333
2017-02-09 21:00 | 2 | 21 | 29.9 | 9873.3333
2017-02-09 22:00 | 2 | 22 | 33.35 | 10000
2017-02-09 23:00 | 2 | 23 | 25.3 | 9060
2017-02-10 | 2 | 0 | 23 | 7873.3333
2017-02-10 01:00 | 2 | 1 | 21.0833 | 6160
2017-02-10 02:00 | 2 | 2 | 17.25 | 4266.6667
2017-02-10 03:00 | 2 | 3 | 16.1 | 2773.3333
2017-02-10 04:00 | 2 | 4 | 16.675 | 2773.3333
2017-02-10 05:00 | 2 | 5 | 11.5 | 873.3333
2017-02-10 06:00 | 2 | 6 | 12.65 | 1666.6667
2017-02-10 07:00 | 2 | 7 | 14.95 | 2773.3333
2017-02-10 08:00 | 2 | 8 | 14.95 | 2773.3333
2017-02-10 09:00 | 2 | 9 | 18.4 | 4266.6667
2017-02-10 10:00 | 2 | 10 | 22.425 | 7873.3333
2017-02-10 11:00 | 2 | 11 | 18.4 | 4266.6667
2017-02-10 12:00 | 2 | 12 | 20.7 | 6160
2017-02-10 13:00 | 2 | 13 | 19.55 | 6160
2017-02-10 14:00 | 2 | 14 | 14.95 | 2773.3333
2017-02-10 15:00 | 2 | 15 | 17.25 | 4266.6667
2017-02-10 16:00 | 2 | 16 | 16.1 | 2773.3333
2017-02-10 17:00 | 2 | 17 | 8.05 | 286.6667
2017-02-10 18:00 | 2 | 18 | 9.2 | 286.6667
2017-02-10 19:00 | 2 | 19 | 8.625 | 286.6667
2017-02-10 20:00 | 2 | 20 | 8.05 | 286.6667
2017-02-10 21:00 | 2 | 21 | 9.2 | 286.6667
2017-02-10 22:00 | 2 | 22 | 8.625 | 286.6667
2017-02-10 23:00 | 2 | 23 | 7.475 | 0
2017-02-11 | 2 | 0 | 6.9 | 0
2017-02-11 01:00 | 2 | 1 | 3.22 | 0
2017-02-11 02:00 | 2 | 2 | 6.1333 | 0
2017-02-11 03:00 | 2 | 3 | 11.3083 | 873.3333
2017-02-11 04:00 | 2 | 4 | 9.3917 | 286.6667
2017-02-11 05:00 | 2 | 5 | 11.8833 | 873.3333
2017-02-11 06:00 | 2 | 6 | 10.58 | 873.3333
2017-02-11 07:00 | 2 | 7 | 6.9 | 0
2017-02-11 08:00 | 2 | 8 | 0 | 0
2017-02-11 09:00 | 2 | 9 | 4.2167 | 0
2017-02-11 10:00 | 2 | 10 | 10.6375 | 873.3333
2017-02-11 11:00 | 2 | 11 | 11.5 | 873.3333
2017-02-11 12:00 | 2 | 12 | 12.65 | 1666.6667
2017-02-11 13:00 | 2 | 13 | 13.8 | 1666.6667
2017-02-11 14:00 | 2 | 14 | 12.65 | 1666.6667
2017-02-11 15:00 | 2 | 15 | 11.5 | 873.3333
2017-02-11 16:00 | 2 | 16 | 10.925 | 873.3333
2017-02-11 17:00 | 2 | 17 | 9.2 | 286.6667
2017-02-11 18:00 | 2 | 18 | 11.5 | 873.3333
2017-02-11 19:00 | 2 | 19 | 11.5 | 873.3333
2017-02-11 20:00 | 2 | 20 | 11.5 | 873.3333
2017-02-11 21:00 | 2 | 21 | 11.5 | 873.3333
2017-02-11 22:00 | 2 | 22 | 12.65 | 1666.6667
2017-02-11 23:00 | 2 | 23 | 11.5 | 873.3333
2017-02-12 | 2 | 0 | 9.775 | 286.6667
2017-02-12 01:00 | 2 | 1 | 10.7333 | 873.3333
2017-02-12 02:00 | 2 | 2 | 12.65 | 1666.6667
2017-02-12 03:00 | 2 | 3 | 12.65 | 1666.6667
2017-02-12 04:00 | 2 | 4 | 11.8833 | 873.3333
2017-02-12 05:00 | 2 | 5 | 11.5 | 873.3333
2017-02-12 06:00 | 2 | 6 | 11.1167 | 873.3333
2017-02-12 07:00 | 2 | 7 | 13.225 | 1666.6667
2017-02-12 08:00 | 2 | 8 | 10.35 | 873.3333
2017-02-12 09:00 | 2 | 9 | 6.9 | 0
2017-02-12 10:00 | 2 | 10 | 16.4833 | 2773.3333
2017-02-12 11:00 | 2 | 11 | 26.45 | 9573.3333
2017-02-12 12:00 | 2 | 12 | 25.3 | 9060
2017-02-12 13:00 | 2 | 13 | 25.875 | 9573.3333
2017-02-12 14:00 | 2 | 14 | 25.99 | 9573.3333
2017-02-12 15:00 | 2 | 15 | 19.55 | 6160
2017-02-12 16:00 | 2 | 16 | 18.975 | 4266.6667
2017-02-12 17:00 | 2 | 17 | 17.25 | 4266.6667
2017-02-12 18:00 | 2 | 18 | 17.5375 | 4266.6667
2017-02-12 19:00 | 2 | 19 | 15.8125 | 2773.3333
2017-02-12 20:00 | 2 | 20 | 19.55 | 6160
2017-02-12 21:00 | 2 | 21 | 20.125 | 6160
2017-02-12 22:00 | 2 | 22 | 17.6333 | 4266.6667
2017-02-12 23:00 | 2 | 23 | 10.35 | 873.3333
2017-02-13 | 2 | 0 | 9.775 | 286.6667
2017-02-13 01:00 | 2 | 1 | 16.675 | 2773.3333
2017-02-13 02:00 | 2 | 2 | 20.4125 | 6160
2017-02-13 03:00 | 2 | 3 | 19.55 | 6160
2017-02-13 04:00 | 2 | 4 | 22.6167 | 7873.3333
2017-02-13 05:00 | 2 | 5 | 18.4 | 4266.6667
2017-02-13 06:00 | 2 | 6 | 19.55 | 6160
2017-02-13 07:00 | 2 | 7 | 23.46 | 7873.3333
2017-02-13 08:00 | 2 | 8 | 18.6875 | 4266.6667
2017-02-13 09:00 | 2 | 9 | 17.25 | 4266.6667
2017-02-13 10:00 | 2 | 10 | 25.3 | 9060
2017-02-13 11:00 | 2 | 11 | 29.9 | 9873.3333
2017-02-13 12:00 | 2 | 12 | 32.2 | 9960
2017-02-13 13:00 | 2 | 13 | 31.05 | 9960
2017-02-13 14:00 | 2 | 14 | 28.75 | 9873.3333
2017-02-13 15:00 | 2 | 15 | 27.6 | 9573.3333
2017-02-13 16:00 | 2 | 16 | 26.45 | 9573.3333
2017-02-13 17:00 | 2 | 17 | 25.3 | 9060
2017-02-13 18:00 | 2 | 18 | 24.15 | 9060
2017-02-13 19:00 | 2 | 19 | 23.575 | 9060
2017-02-13 20:00 | 2 | 20 | 24.15 | 9060
2017-02-13 21:00 | 2 | 21 | 23 | 7873.3333
2017-02-13 22:00 | 2 | 22 | 20.7 | 6160
2017-02-13 23:00 | 2 | 23 | 19.55 | 6160
2017-02-14 | 2 | 0 | 17.25 | 4266.6667
2017-02-14 01:00 | 2 | 1 | 16.1 | 2773.3333
2017-02-14 02:00 | 2 | 2 | 14.95 | 2773.3333
2017-02-14 03:00 | 2 | 3 | 16.1 | 2773.3333
2017-02-14 04:00 | 2 | 4 | 17.25 | 4266.6667
2017-02-14 05:00 | 2 | 5 | 14.95 | 2773.3333
2017-02-14 06:00 | 2 | 6 | 14.95 | 2773.3333
2017-02-14 07:00 | 2 | 7 | 13.225 | 1666.6667
2017-02-14 08:00 | 2 | 8 | 10.35 | 873.3333
2017-02-14 09:00 | 2 | 9 | 10.35 | 873.3333
2017-02-14 10:00 | 2 | 10 | 10.35 | 873.3333
2017-02-14 11:00 | 2 | 11 | 6.9 | 0
2017-02-14 12:00 | 2 | 12 | 0 | 0
2017-02-14 13:00 | 2 | 13 | 4.6 | 0
2017-02-14 14:00 | 2 | 14 | 5.75 | 0
2017-02-14 15:00 | 2 | 15 | 8.05 | 286.6667
2017-02-14 16:00 | 2 | 16 | 10.35 | 873.3333
2017-02-14 17:00 | 2 | 17 | 10.35 | 873.3333
2017-02-14 18:00 | 2 | 18 | 9.2 | 286.6667
2017-02-14 19:00 | 2 | 19 | 8.05 | 286.6667
2017-02-14 20:00 | 2 | 20 | 11.5 | 873.3333
2017-02-14 21:00 | 2 | 21 | 12.65 | 1666.6667
2017-02-14 22:00 | 2 | 22 | 10.925 | 873.3333
2017-02-14 23:00 | 2 | 23 | 6.9 | 0
2017-02-15 | 2 | 0 | 9.2 | 286.6667
2017-02-15 01:00 | 2 | 1 | 8.625 | 286.6667
2017-02-15 02:00 | 2 | 2 | 12.65 | 1666.6667
2017-02-15 03:00 | 2 | 3 | 10.35 | 873.3333
2017-02-15 04:00 | 2 | 4 | 10.35 | 873.3333
2017-02-15 05:00 | 2 | 5 | 8.05 | 286.6667
2017-02-15 06:00 | 2 | 6 | 0 | 0
2017-02-15 07:00 | 2 | 7 | 4.9833 | 0
2017-02-15 08:00 | 2 | 8 | 3.45 | 0
2017-02-15 09:00 | 2 | 9 | 3.45 | 0
2017-02-15 10:00 | 2 | 10 | 6.325 | 0
2017-02-15 11:00 | 2 | 11 | 5.75 | 0
2017-02-15 12:00 | 2 | 12 | 6.325 | 0
2017-02-15 13:00 | 2 | 13 | 6.9 | 0
2017-02-15 14:00 | 2 | 14 | 9.2 | 286.6667
2017-02-15 15:00 | 2 | 15 | 3.45 | 0
2017-02-15 16:00 | 2 | 16 | 5.175 | 0
2017-02-15 17:00 | 2 | 17 | 8.625 | 286.6667
2017-02-15 18:00 | 2 | 18 | 4.9833 | 0
2017-02-15 19:00 | 2 | 19 | 1.15 | 0
2017-02-15 20:00 | 2 | 20 | 10.35 | 873.3333
2017-02-15 21:00 | 2 | 21 | 15.525 | 2773.3333
2017-02-15 22:00 | 2 | 22 | 13.8 | 1666.6667
2017-02-15 23:00 | 2 | 23 | 18.0167 | 4266.6667
2017-02-16 | 2 | 0 | 18.975 | 4266.6667
2017-02-16 01:00 | 2 | 1 | 20.3167 | 6160
2017-02-16 02:00 | 2 | 2 | 16.675 | 2773.3333
2017-02-16 03:00 | 2 | 3 | 17.825 | 4266.6667
2017-02-16 04:00 | 2 | 4 | 15.525 | 2773.3333
2017-02-16 05:00 | 2 | 5 | 15.525 | 2773.3333
2017-02-16 06:00 | 2 | 6 | 14.72 | 2773.3333
2017-02-16 07:00 | 2 | 7 | 16.3875 | 2773.3333
2017-02-16 08:00 | 2 | 8 | 16.3875 | 2773.3333
2017-02-16 09:00 | 2 | 9 | 16.1 | 2773.3333
2017-02-16 10:00 | 2 | 10 | 18.0167 | 4266.6667
2017-02-16 11:00 | 2 | 11 | 18.4 | 4266.6667
2017-02-16 12:00 | 2 | 12 | 18.4 | 4266.6667
2017-02-16 13:00 | 2 | 13 | 17.825 | 4266.6667
2017-02-16 14:00 | 2 | 14 | 20.7 | 6160
2017-02-16 15:00 | 2 | 15 | 21.85 | 7873.3333
2017-02-16 16:00 | 2 | 16 | 20.7 | 6160
2017-02-16 17:00 | 2 | 17 | 23 | 7873.3333
2017-02-16 18:00 | 2 | 18 | 24.15 | 9060
2017-02-16 19:00 | 2 | 19 | 24.725 | 9060
2017-02-16 20:00 | 2 | 20 | 23 | 7873.3333
2017-02-16 21:00 | 2 | 21 | 19.55 | 6160
2017-02-16 22:00 | 2 | 22 | 18.975 | 4266.6667
2017-02-16 23:00 | 2 | 23 | 16.1 | 2773.3333
2017-02-17 | 2 | 0 | 17.25 | 4266.6667
2017-02-17 01:00 | 2 | 1 | 16.675 | 2773.3333
2017-02-17 02:00 | 2 | 2 | 14.95 | 2773.3333
2017-02-17 03:00 | 2 | 3 | 17.25 | 4266.6667
2017-02-17 04:00 | 2 | 4 | 17.825 | 4266.6667
2017-02-17 05:00 | 2 | 5 | 12.65 | 1666.6667
2017-02-17 06:00 | 2 | 6 | 11.5 | 873.3333
2017-02-17 07:00 | 2 | 7 | 13.225 | 1666.6667
2017-02-17 08:00 | 2 | 8 | 20.7 | 6160
2017-02-17 09:00 | 2 | 9 | 16.1 | 2773.3333
2017-02-17 10:00 | 2 | 10 | 17.825 | 4266.6667
2017-02-17 11:00 | 2 | 11 | 23 | 7873.3333
2017-02-17 12:00 | 2 | 12 | 17.25 | 4266.6667
2017-02-17 13:00 | 2 | 13 | 14.95 | 2773.3333
2017-02-17 14:00 | 2 | 14 | 12.65 | 1666.6667
2017-02-17 15:00 | 2 | 15 | 19.55 | 6160
2017-02-17 16:00 | 2 | 16 | 17.825 | 4266.6667
2017-02-17 17:00 | 2 | 17 | 17.25 | 4266.6667
2017-02-17 18:00 | 2 | 18 | 18.4 | 4266.6667
2017-02-17 19:00 | 2 | 19 | 15.525 | 2773.3333
2017-02-17 20:00 | 2 | 20 | 14.95 | 2773.3333
2017-02-17 21:00 | 2 | 21 | 11.5 | 873.3333
2017-02-17 22:00 | 2 | 22 | 11.5 | 873.3333
2017-02-17 23:00 | 2 | 23 | 16.1 | 2773.3333
2017-02-18 | 2 | 0 | 11.5 | 873.3333
2017-02-18 01:00 | 2 | 1 | 12.075 | 873.3333
2017-02-18 02:00 | 2 | 2 | 12.65 | 1666.6667
2017-02-18 03:00 | 2 | 3 | 8.05 | 286.6667
2017-02-18 04:00 | 2 | 4 | 8.05 | 286.6667
2017-02-18 05:00 | 2 | 5 | 10.35 | 873.3333
2017-02-18 06:00 | 2 | 6 | 9.2 | 286.6667
2017-02-18 07:00 | 2 | 7 | 10.35 | 873.3333
2017-02-18 08:00 | 2 | 8 | 9.2 | 286.6667
2017-02-18 09:00 | 2 | 9 | 11.5 | 873.3333
2017-02-18 10:00 | 2 | 10 | 14.95 | 2773.3333
2017-02-18 11:00 | 2 | 11 | 19.55 | 6160
2017-02-18 12:00 | 2 | 12 | 23 | 7873.3333
2017-02-18 13:00 | 2 | 13 | 21.85 | 7873.3333
2017-02-18 14:00 | 2 | 14 | 24.15 | 9060
2017-02-18 15:00 | 2 | 15 | 17.25 | 4266.6667
2017-02-18 16:00 | 2 | 16 | 16.675 | 2773.3333
2017-02-18 17:00 | 2 | 17 | 17.25 | 4266.6667
2017-02-18 18:00 | 2 | 18 | 20.7 | 6160
2017-02-18 19:00 | 2 | 19 | 20.125 | 6160
2017-02-18 20:00 | 2 | 20 | 16.1 | 2773.3333
2017-02-18 21:00 | 2 | 21 | 19.55 | 6160
2017-02-18 22:00 | 2 | 22 | 18.975 | 4266.6667
2017-02-18 23:00 | 2 | 23 | 17.25 | 4266.6667
2017-02-19 | 2 | 0 | 16.1 | 2773.3333
2017-02-19 01:00 | 2 | 1 | 14.375 | 1666.6667
2017-02-19 02:00 | 2 | 2 | 14.95 | 2773.3333
2017-02-19 03:00 | 2 | 3 | 11.5 | 873.3333
2017-02-19 04:00 | 2 | 4 | 9.775 | 286.6667
2017-02-19 05:00 | 2 | 5 | 11.5 | 873.3333
2017-02-19 06:00 | 2 | 6 | 12.65 | 1666.6667
2017-02-19 07:00 | 2 | 7 | 11.5 | 873.3333
2017-02-19 08:00 | 2 | 8 | 12.65 | 1666.6667
2017-02-19 09:00 | 2 | 9 | 12.65 | 1666.6667
2017-02-19 10:00 | 2 | 10 | 12.075 | 873.3333
2017-02-19 11:00 | 2 | 11 | 16.1 | 2773.3333
2017-02-19 12:00 | 2 | 12 | 25.3 | 9060
2017-02-19 13:00 | 2 | 13 | 20.125 | 6160
2017-02-19 14:00 | 2 | 14 | 19.55 | 6160
2017-02-19 15:00 | 2 | 15 | 16.1 | 2773.3333
2017-02-19 16:00 | 2 | 16 | 13.225 | 1666.6667
2017-02-19 17:00 | 2 | 17 | 8.05 | 286.6667
2017-02-19 18:00 | 2 | 18 | 5.75 | 0
2017-02-19 19:00 | 2 | 19 | 7.475 | 0
2017-02-19 20:00 | 2 | 20 | 8.05 | 286.6667
2017-02-19 21:00 | 2 | 21 | 11.5 | 873.3333
2017-02-19 22:00 | 2 | 22 | 10.35 | 873.3333
2017-02-19 23:00 | 2 | 23 | 8.05 | 286.6667
2017-02-20 | 2 | 0 | 8.05 | 286.6667
2017-02-20 01:00 | 2 | 1 | 10.35 | 873.3333
2017-02-20 02:00 | 2 | 2 | 10.35 | 873.3333
2017-02-20 03:00 | 2 | 3 | 12.65 | 1666.6667
2017-02-20 04:00 | 2 | 4 | 11.5 | 873.3333
2017-02-20 05:00 | 2 | 5 | 12.65 | 1666.6667
2017-02-20 06:00 | 2 | 6 | 12.65 | 1666.6667
2017-02-20 07:00 | 2 | 7 | 13.8 | 1666.6667
2017-02-20 08:00 | 2 | 8 | 17.25 | 4266.6667
2017-02-20 09:00 | 2 | 9 | 12.65 | 1666.6667
2017-02-20 10:00 | 2 | 10 | 11.5 | 873.3333
2017-02-20 11:00 | 2 | 11 | 10.35 | 873.3333
2017-02-20 12:00 | 2 | 12 | 16.1 | 2773.3333
2017-02-20 13:00 | 2 | 13 | 16.675 | 2773.3333
2017-02-20 14:00 | 2 | 14 | 14.95 | 2773.3333
2017-02-20 15:00 | 2 | 15 | 18.4 | 4266.6667
2017-02-20 16:00 | 2 | 16 | 16.675 | 2773.3333
2017-02-20 17:00 | 2 | 17 | 11.5 | 873.3333
2017-02-20 18:00 | 2 | 18 | 12.65 | 1666.6667
2017-02-20 19:00 | 2 | 19 | 11.5 | 873.3333
2017-02-20 20:00 | 2 | 20 | 10.35 | 873.3333
2017-02-20 21:00 | 2 | 21 | 11.5 | 873.3333
2017-02-20 22:00 | 2 | 22 | 11.5 | 873.3333
2017-02-20 23:00 | 2 | 23 | 9.2 | 286.6667
2017-02-21 | 2 | 0 | 9.2 | 286.6667
2017-02-21 01:00 | 2 | 1 | 8.625 | 286.6667
2017-02-21 02:00 | 2 | 2 | 8.05 | 286.6667
2017-02-21 03:00 | 2 | 3 | 8.05 | 286.6667
2017-02-21 04:00 | 2 | 4 | 8.05 | 286.6667
2017-02-21 05:00 | 2 | 5 | 9.2 | 286.6667
2017-02-21 06:00 | 2 | 6 | 8.05 | 286.6667
2017-02-21 07:00 | 2 | 7 | 8.05 | 286.6667
2017-02-21 08:00 | 2 | 8 | 6.9 | 0
2017-02-21 09:00 | 2 | 9 | 9.2 | 286.6667
2017-02-21 10:00 | 2 | 10 | 8.625 | 286.6667
2017-02-21 11:00 | 2 | 11 | 5.75 | 0
2017-02-21 12:00 | 2 | 12 | 10.35 | 873.3333
2017-02-21 13:00 | 2 | 13 | 13.225 | 1666.6667
2017-02-21 14:00 | 2 | 14 | 16.1 | 2773.3333
2017-02-21 15:00 | 2 | 15 | 16.1 | 2773.3333
2017-02-21 16:00 | 2 | 16 | 13.8 | 1666.6667
2017-02-21 17:00 | 2 | 17 | 11.5 | 873.3333
2017-02-21 18:00 | 2 | 18 | 10.35 | 873.3333
2017-02-21 19:00 | 2 | 19 | 10.925 | 873.3333
2017-02-21 20:00 | 2 | 20 | 11.5 | 873.3333
2017-02-21 21:00 | 2 | 21 | 11.5 | 873.3333
2017-02-21 22:00 | 2 | 22 | 13.225 | 1666.6667
2017-02-21 23:00 | 2 | 23 | 11.5 | 873.3333
2017-02-22 | 2 | 0 | 12.65 | 1666.6667
2017-02-22 01:00 | 2 | 1 | 12.075 | 873.3333
2017-02-22 02:00 | 2 | 2 | 12.65 | 1666.6667
2017-02-22 03:00 | 2 | 3 | 16.1 | 2773.3333
2017-02-22 04:00 | 2 | 4 | 14.375 | 1666.6667
2017-02-22 05:00 | 2 | 5 | 10.35 | 873.3333
2017-02-22 06:00 | 2 | 6 | 10.35 | 873.3333
2017-02-22 07:00 | 2 | 7 | 11.5 | 873.3333
2017-02-22 08:00 | 2 | 8 | 8.05 | 286.6667
2017-02-22 09:00 | 2 | 9 | 6.9 | 0
2017-02-22 10:00 | 2 | 10 | 8.05 | 286.6667
2017-02-22 11:00 | 2 | 11 | 3.45 | 0
2017-02-22 12:00 | 2 | 12 | 6.9 | 0
2017-02-22 13:00 | 2 | 13 | 7.475 | 0
2017-02-22 14:00 | 2 | 14 | 12.65 | 1666.6667
2017-02-22 15:00 | 2 | 15 | 9.2 | 286.6667
2017-02-22 16:00 | 2 | 16 | 7.475 | 0
2017-02-22 17:00 | 2 | 17 | 9.2 | 286.6667
2017-02-22 18:00 | 2 | 18 | 8.05 | 286.6667
2017-02-22 19:00 | 2 | 19 | 6.9 | 0
2017-02-22 20:00 | 2 | 20 | 3.45 | 0
2017-02-22 21:00 | 2 | 21 | 6.9 | 0
2017-02-22 22:00 | 2 | 22 | 6.9 | 0
2017-02-22 23:00 | 2 | 23 | 8.05 | 286.6667
2017-02-23 | 2 | 0 | 5.75 | 0
2017-02-23 01:00 | 2 | 1 | 5.75 | 0
2017-02-23 02:00 | 2 | 2 | 10.35 | 873.3333
2017-02-23 03:00 | 2 | 3 | 0 | 0
2017-02-23 04:00 | 2 | 4 | 4.6 | 0
2017-02-23 05:00 | 2 | 5 | 10.35 | 873.3333
2017-02-23 06:00 | 2 | 6 | 6.9 | 0
2017-02-23 07:00 | 2 | 7 | 6.9 | 0
2017-02-23 08:00 | 2 | 8 | 8.05 | 286.6667
2017-02-23 09:00 | 2 | 9 | 8.05 | 286.6667
2017-02-23 10:00 | 2 | 10 | 10.35 | 873.3333
2017-02-23 11:00 | 2 | 11 | 12.65 | 1666.6667
2017-02-23 12:00 | 2 | 12 | 18.4 | 4266.6667
2017-02-23 13:00 | 2 | 13 | 21.275 | 7873.3333
2017-02-23 14:00 | 2 | 14 | 24.15 | 9060
2017-02-23 15:00 | 2 | 15 | 18.4 | 4266.6667
2017-02-23 16:00 | 2 | 16 | 17.825 | 4266.6667
2017-02-23 17:00 | 2 | 17 | 23 | 7873.3333
2017-02-23 18:00 | 2 | 18 | 23 | 7873.3333
2017-02-23 19:00 | 2 | 19 | 21.85 | 7873.3333
2017-02-23 20:00 | 2 | 20 | 20.7 | 6160
2017-02-23 21:00 | 2 | 21 | 19.55 | 6160
2017-02-23 22:00 | 2 | 22 | 20.125 | 6160
2017-02-23 23:00 | 2 | 23 | 14.95 | 2773.3333
2017-02-24 | 2 | 0 | 9.2 | 286.6667
2017-02-24 01:00 | 2 | 1 | 9.775 | 286.6667
2017-02-24 02:00 | 2 | 2 | 8.05 | 286.6667
2017-02-24 03:00 | 2 | 3 | 0 | 0
2017-02-24 04:00 | 2 | 4 | 2.875 | 0
2017-02-24 05:00 | 2 | 5 | 6.9 | 0
2017-02-24 06:00 | 2 | 6 | 5.75 | 0
2017-02-24 07:00 | 2 | 7 | 6.325 | 0
2017-02-24 08:00 | 2 | 8 | 11.5 | 873.3333
2017-02-24 09:00 | 2 | 9 | 11.5 | 873.3333
2017-02-24 10:00 | 2 | 10 | 12.075 | 873.3333
2017-02-24 11:00 | 2 | 11 | 12.65 | 1666.6667
2017-02-24 12:00 | 2 | 12 | 23 | 7873.3333
2017-02-24 13:00 | 2 | 13 | 24.725 | 9060
2017-02-24 14:00 | 2 | 14 | 24.15 | 9060
2017-02-24 15:00 | 2 | 15 | 23 | 7873.3333
2017-02-24 16:00 | 2 | 16 | 21.275 | 7873.3333
2017-02-24 17:00 | 2 | 17 | 19.55 | 6160
2017-02-24 18:00 | 2 | 18 | 17.25 | 4266.6667
2017-02-24 19:00 | 2 | 19 | 14.95 | 2773.3333
2017-02-24 20:00 | 2 | 20 | 14.95 | 2773.3333
2017-02-24 21:00 | 2 | 21 | 11.5 | 873.3333
2017-02-24 22:00 | 2 | 22 | 11.5 | 873.3333
2017-02-24 23:00 | 2 | 23 | 18.4 | 4266.6667
2017-02-25 | 2 | 0 | 12.65 | 1666.6667
2017-02-25 01:00 | 2 | 1 | 10.35 | 873.3333
2017-02-25 02:00 | 2 | 2 | 9.2 | 286.6667
2017-02-25 03:00 | 2 | 3 | 9.2 | 286.6667
2017-02-25 04:00 | 2 | 4 | 9.2 | 286.6667
2017-02-25 05:00 | 2 | 5 | 9.775 | 286.6667
2017-02-25 06:00 | 2 | 6 | 9.2 | 286.6667
2017-02-25 07:00 | 2 | 7 | 11.2125 | 873.3333
2017-02-25 08:00 | 2 | 8 | 11.5 | 873.3333
2017-02-25 09:00 | 2 | 9 | 9.2 | 286.6667
2017-02-25 10:00 | 2 | 10 | 12.075 | 873.3333
2017-02-25 11:00 | 2 | 11 | 10.35 | 873.3333
2017-02-25 12:00 | 2 | 12 | 19.55 | 6160
2017-02-25 13:00 | 2 | 13 | 18.975 | 4266.6667
2017-02-25 14:00 | 2 | 14 | 12.65 | 1666.6667
2017-02-25 15:00 | 2 | 15 | 20.7 | 6160
2017-02-25 16:00 | 2 | 16 | 15.525 | 2773.3333
2017-02-25 17:00 | 2 | 17 | 20.125 | 6160
2017-02-25 18:00 | 2 | 18 | 11.5 | 873.3333
2017-02-25 19:00 | 2 | 19 | 9.2 | 286.6667
2017-02-25 20:00 | 2 | 20 | 12.2667 | 873.3333
2017-02-25 21:00 | 2 | 21 | 11.5 | 873.3333
2017-02-25 22:00 | 2 | 22 | 17.4417 | 4266.6667
2017-02-25 23:00 | 2 | 23 | 18.4 | 4266.6667
2017-02-26 | 2 | 0 | 23 | 7873.3333
2017-02-26 01:00 | 2 | 1 | 20.125 | 6160
2017-02-26 02:00 | 2 | 2 | 19.55 | 6160
2017-02-26 03:00 | 2 | 3 | 23 | 7873.3333
2017-02-26 04:00 | 2 | 4 | 23 | 7873.3333
2017-02-26 05:00 | 2 | 5 | 20.7 | 6160
2017-02-26 06:00 | 2 | 6 | 20.7 | 6160
2017-02-26 07:00 | 2 | 7 | 20.7 | 6160
2017-02-26 08:00 | 2 | 8 | 18.4 | 4266.6667
2017-02-26 09:00 | 2 | 9 | 14.95 | 2773.3333
2017-02-26 10:00 | 2 | 10 | 19.55 | 6160
2017-02-26 11:00 | 2 | 11 | 24.15 | 9060
2017-02-26 12:00 | 2 | 12 | 19.55 | 6160
2017-02-26 13:00 | 2 | 13 | 22.425 | 7873.3333
2017-02-26 14:00 | 2 | 14 | 23 | 7873.3333
2017-02-26 15:00 | 2 | 15 | 23 | 7873.3333
2017-02-26 16:00 | 2 | 16 | 23.575 | 9060
2017-02-26 17:00 | 2 | 17 | 20.7 | 6160
2017-02-26 18:00 | 2 | 18 | 20.7 | 6160
2017-02-26 19:00 | 2 | 19 | 20.7 | 6160
2017-02-26 20:00 | 2 | 20 | 11.5 | 873.3333
2017-02-26 21:00 | 2 | 21 | 16.1 | 2773.3333
2017-02-26 22:00 | 2 | 22 | 14.375 | 1666.6667
2017-02-26 23:00 | 2 | 23 | 14.95 | 2773.3333
2017-02-27 | 2 | 0 | 11.5 | 873.3333
2017-02-27 01:00 | 2 | 1 | 11.5 | 873.3333
2017-02-27 02:00 | 2 | 2 | 14.95 | 2773.3333
2017-02-27 03:00 | 2 | 3 | 10.35 | 873.3333
2017-02-27 04:00 | 2 | 4 | 13.8 | 1666.6667
2017-02-27 05:00 | 2 | 5 | 19.55 | 6160
2017-02-27 06:00 | 2 | 6 | 24.15 | 9060
2017-02-27 07:00 | 2 | 7 | 24.15 | 9060
2017-02-27 08:00 | 2 | 8 | 20.7 | 6160
2017-02-27 09:00 | 2 | 9 | 17.25 | 4266.6667
2017-02-27 10:00 | 2 | 10 | 18.4 | 4266.6667
2017-02-27 11:00 | 2 | 11 | 16.1 | 2773.3333
2017-02-27 12:00 | 2 | 12 | 26.45 | 9573.3333
2017-02-27 13:00 | 2 | 13 | 26.45 | 9573.3333
2017-02-27 14:00 | 2 | 14 | 25.3 | 9060
2017-02-27 15:00 | 2 | 15 | 26.45 | 9573.3333
2017-02-27 16:00 | 2 | 16 | 27.6 | 9573.3333
2017-02-27 17:00 | 2 | 17 | 26.45 | 9573.3333
2017-02-27 18:00 | 2 | 18 | 23 | 7873.3333
2017-02-27 19:00 | 2 | 19 | 20.7 | 6160
2017-02-27 20:00 | 2 | 20 | 14.95 | 2773.3333
2017-02-27 21:00 | 2 | 21 | 12.65 | 1666.6667
2017-02-27 22:00 | 2 | 22 | 12.65 | 1666.6667
2017-02-27 23:00 | 2 | 23 | 14.95 | 2773.3333
2017-02-28 | 2 | 0 | 14.95 | 2773.3333
2017-02-28 01:00 | 2 | 1 | 13.8 | 1666.6667
2017-02-28 02:00 | 2 | 2 | 10.35 | 873.3333
2017-02-28 03:00 | 2 | 3 | 11.5 | 873.3333
2017-02-28 04:00 | 2 | 4 | 12.075 | 873.3333
2017-02-28 05:00 | 2 | 5 | 9.2 | 286.6667
2017-02-28 06:00 | 2 | 6 | 3.45 | 0
2017-02-28 07:00 | 2 | 7 | 1.725 | 0
2017-02-28 08:00 | 2 | 8 | 6.9 | 0
2017-02-28 09:00 | 2 | 9 | 5.75 | 0
2017-02-28 10:00 | 2 | 10 | 2.875 | 0
2017-02-28 11:00 | 2 | 11 | 8.05 | 286.6667
2017-02-28 12:00 | 2 | 12 | 9.2 | 286.6667
2017-02-28 13:00 | 2 | 13 | 12.075 | 873.3333
2017-02-28 14:00 | 2 | 14 | 12.65 | 1666.6667
2017-02-28 15:00 | 2 | 15 | 9.2 | 286.6667
2017-02-28 16:00 | 2 | 16 | 9.5833 | 286.6667
2017-02-28 17:00 | 2 | 17 | 8.05 | 286.6667
2017-02-28 18:00 | 2 | 18 | 6.9 | 0
2017-02-28 19:00 | 2 | 19 | 8.4333 | 286.6667
2017-02-28 20:00 | 2 | 20 | 9.2 | 286.6667
2017-02-28 21:00 | 2 | 21 | 8.05 | 286.6667
2017-02-28 22:00 | 2 | 22 | 9.2 | 286.6667
2017-02-28 23:00 | 2 | 23 | 9.2 | 286.6667
2017-03-01 | 3 | 0 | 9.775 | 286.6667
2017-03-01 01:00 | 3 | 1 | 9.775 | 286.6667
2017-03-01 02:00 | 3 | 2 | 9.2 | 286.6667
2017-03-01 03:00 | 3 | 3 | 10.35 | 873.3333
2017-03-01 04:00 | 3 | 4 | 10.35 | 873.3333
2017-03-01 05:00 | 3 | 5 | 11.5 | 873.3333
2017-03-01 06:00 | 3 | 6 | 14.95 | 2773.3333
2017-03-01 07:00 | 3 | 7 | 16.1 | 2773.3333
2017-03-01 08:00 | 3 | 8 | 16.1 | 2773.3333
2017-03-01 09:00 | 3 | 9 | 15.525 | 2773.3333
2017-03-01 10:00 | 3 | 10 | 13.225 | 1666.6667
2017-03-01 11:00 | 3 | 11 | 17.825 | 4266.6667
2017-03-01 12:00 | 3 | 12 | 18.4 | 4266.6667
2017-03-01 13:00 | 3 | 13 | 20.7 | 6160
2017-03-01 14:00 | 3 | 14 | 21.85 | 7873.3333
2017-03-01 15:00 | 3 | 15 | 20.125 | 6160
2017-03-01 16:00 | 3 | 16 | 17.25 | 4266.6667
2017-03-01 17:00 | 3 | 17 | 20.7 | 6160
2017-03-01 18:00 | 3 | 18 | 23 | 7873.3333
2017-03-01 19:00 | 3 | 19 | 19.8375 | 6160
2017-03-01 20:00 | 3 | 20 | 24.15 | 9060
2017-03-01 21:00 | 3 | 21 | 25.3 | 9060
2017-03-01 22:00 | 3 | 22 | 25.3 | 9060
2017-03-01 23:00 | 3 | 23 | 17.25 | 4266.6667
2017-03-02 | 3 | 0 | 19.55 | 6160
2017-03-02 01:00 | 3 | 1 | 18.975 | 4266.6667
2017-03-02 02:00 | 3 | 2 | 16.1 | 2773.3333
2017-03-02 03:00 | 3 | 3 | 17.25 | 4266.6667
2017-03-02 04:00 | 3 | 4 | 17.25 | 4266.6667
2017-03-02 05:00 | 3 | 5 | 31.625 | 9960
2017-03-02 06:00 | 3 | 6 | 25.3 | 9060
2017-03-02 07:00 | 3 | 7 | 24.15 | 9060
2017-03-02 08:00 | 3 | 8 | 25.3 | 9060
2017-03-02 09:00 | 3 | 9 | 34.5 | 10000
2017-03-02 10:00 | 3 | 10 | 35.075 | 10000
2017-03-02 11:00 | 3 | 11 | 34.5 | 10000
2017-03-02 12:00 | 3 | 12 | 29.9 | 9873.3333
2017-03-02 13:00 | 3 | 13 | 29.325 | 9873.3333
2017-03-02 14:00 | 3 | 14 | 34.5 | 10000
2017-03-02 15:00 | 3 | 15 | 26.45 | 9573.3333
2017-03-02 16:00 | 3 | 16 | 29.325 | 9873.3333
2017-03-02 17:00 | 3 | 17 | 29.9 | 9873.3333
2017-03-02 18:00 | 3 | 18 | 25.3 | 9060
2017-03-02 19:00 | 3 | 19 | 24.15 | 9060
2017-03-02 20:00 | 3 | 20 | 23 | 7873.3333
2017-03-02 21:00 | 3 | 21 | 17.25 | 4266.6667
2017-03-02 22:00 | 3 | 22 | 16.1 | 2773.3333
2017-03-02 23:00 | 3 | 23 | 20.7 | 6160
2017-03-03 | 3 | 0 | 17.25 | 4266.6667
2017-03-03 01:00 | 3 | 1 | 14.95 | 2773.3333
2017-03-03 02:00 | 3 | 2 | 12.65 | 1666.6667
2017-03-03 03:00 | 3 | 3 | 12.65 | 1666.6667
2017-03-03 04:00 | 3 | 4 | 12.075 | 873.3333
2017-03-03 05:00 | 3 | 5 | 17.25 | 4266.6667
2017-03-03 06:00 | 3 | 6 | 18.4 | 4266.6667
2017-03-03 07:00 | 3 | 7 | 20.7 | 6160
2017-03-03 08:00 | 3 | 8 | 23 | 7873.3333
2017-03-03 09:00 | 3 | 9 | 17.25 | 4266.6667
2017-03-03 10:00 | 3 | 10 | 16.1 | 2773.3333
2017-03-03 11:00 | 3 | 11 | 18.4 | 4266.6667
2017-03-03 12:00 | 3 | 12 | 11.5 | 873.3333
2017-03-03 13:00 | 3 | 13 | 11.5 | 873.3333
2017-03-03 14:00 | 3 | 14 | 10.35 | 873.3333
2017-03-03 15:00 | 3 | 15 | 6.9 | 0
2017-03-03 16:00 | 3 | 16 | 12.075 | 873.3333
2017-03-03 17:00 | 3 | 17 | 16.1 | 2773.3333
2017-03-03 18:00 | 3 | 18 | 12.65 | 1666.6667
2017-03-03 19:00 | 3 | 19 | 20.125 | 6160
2017-03-03 20:00 | 3 | 20 | 19.55 | 6160
2017-03-03 21:00 | 3 | 21 | 26.45 | 9573.3333
2017-03-03 22:00 | 3 | 22 | 24.15 | 9060
2017-03-03 23:00 | 3 | 23 | 19.9333 | 6160
2017-03-04 | 3 | 0 | 24.15 | 9060
2017-03-04 01:00 | 3 | 1 | 21.85 | 7873.3333
2017-03-04 02:00 | 3 | 2 | 27.6 | 9573.3333
2017-03-04 03:00 | 3 | 3 | 20.7 | 6160
2017-03-04 04:00 | 3 | 4 | 21.85 | 7873.3333
2017-03-04 05:00 | 3 | 5 | 16.1 | 2773.3333
2017-03-04 06:00 | 3 | 6 | 14.95 | 2773.3333
2017-03-04 07:00 | 3 | 7 | 15.525 | 2773.3333
2017-03-04 08:00 | 3 | 8 | 16.1 | 2773.3333
2017-03-04 09:00 | 3 | 9 | 19.55 | 6160
2017-03-04 10:00 | 3 | 10 | 18.4 | 4266.6667
2017-03-04 11:00 | 3 | 11 | 26.45 | 9573.3333
2017-03-04 12:00 | 3 | 12 | 26.45 | 9573.3333
2017-03-04 13:00 | 3 | 13 | 27.025 | 9573.3333
2017-03-04 14:00 | 3 | 14 | 24.15 | 9060
2017-03-04 15:00 | 3 | 15 | 26.45 | 9573.3333
2017-03-04 16:00 | 3 | 16 | 27.6 | 9573.3333
2017-03-04 17:00 | 3 | 17 | 24.15 | 9060
2017-03-04 18:00 | 3 | 18 | 23 | 7873.3333
2017-03-04 19:00 | 3 | 19 | 24.15 | 9060
2017-03-04 20:00 | 3 | 20 | 25.3 | 9060
2017-03-04 21:00 | 3 | 21 | 23 | 7873.3333
2017-03-04 22:00 | 3 | 22 | 25.3 | 9060
2017-03-04 23:00 | 3 | 23 | 17.25 | 4266.6667
2017-03-05 | 3 | 0 | 24.15 | 9060
2017-03-05 01:00 | 3 | 1 | 24.15 | 9060
2017-03-05 02:00 | 3 | 2 | 29.9 | 9873.3333
2017-03-05 03:00 | 3 | 3 | 26.45 | 9573.3333
2017-03-05 04:00 | 3 | 4 | 27.025 | 9573.3333
2017-03-05 05:00 | 3 | 5 | 23 | 7873.3333
2017-03-05 06:00 | 3 | 6 | 18.4 | 4266.6667
2017-03-05 07:00 | 3 | 7 | 17.825 | 4266.6667
2017-03-05 08:00 | 3 | 8 | 18.4 | 4266.6667
2017-03-05 09:00 | 3 | 9 | 19.55 | 6160
2017-03-05 10:00 | 3 | 10 | 21.275 | 7873.3333
2017-03-05 11:00 | 3 | 11 | 19.55 | 6160
2017-03-05 12:00 | 3 | 12 | 23 | 7873.3333
2017-03-05 13:00 | 3 | 13 | 21.275 | 7873.3333
2017-03-05 14:00 | 3 | 14 | 17.25 | 4266.6667
2017-03-05 15:00 | 3 | 15 | 25.3 | 9060
2017-03-05 16:00 | 3 | 16 | 21.275 | 7873.3333
2017-03-05 17:00 | 3 | 17 | 18.4 | 4266.6667
2017-03-05 18:00 | 3 | 18 | 19.55 | 6160
2017-03-05 19:00 | 3 | 19 | 17.825 | 4266.6667
2017-03-05 20:00 | 3 | 20 | 17.25 | 4266.6667
2017-03-05 21:00 | 3 | 21 | 12.65 | 1666.6667
2017-03-05 22:00 | 3 | 22 | 14.375 | 1666.6667
2017-03-05 23:00 | 3 | 23 | 11.5 | 873.3333
2017-03-06 | 3 | 0 | 14.95 | 2773.3333
2017-03-06 01:00 | 3 | 1 | 16.1 | 2773.3333
2017-03-06 02:00 | 3 | 2 | 9.2 | 286.6667
2017-03-06 03:00 | 3 | 3 | 12.65 | 1666.6667
2017-03-06 04:00 | 3 | 4 | 14.375 | 1666.6667
2017-03-06 05:00 | 3 | 5 | 10.35 | 873.3333
2017-03-06 06:00 | 3 | 6 | 6.9 | 0
2017-03-06 07:00 | 3 | 7 | 7.475 | 0
2017-03-06 08:00 | 3 | 8 | 5.75 | 0
2017-03-06 09:00 | 3 | 9 | 0 | 0
2017-03-06 10:00 | 3 | 10 | 2.875 | 0
2017-03-06 11:00 | 3 | 11 | 6.9 | 0
2017-03-06 12:00 | 3 | 12 | 5.75 | 0
2017-03-06 13:00 | 3 | 13 | 5.75 | 0
2017-03-06 14:00 | 3 | 14 | 11.5 | 873.3333
2017-03-06 15:00 | 3 | 15 | 11.5 | 873.3333
2017-03-06 16:00 | 3 | 16 | 11.5 | 873.3333
2017-03-06 17:00 | 3 | 17 | 11.5 | 873.3333
2017-03-06 18:00 | 3 | 18 | 9.2 | 286.6667
2017-03-06 19:00 | 3 | 19 | 8.625 | 286.6667
2017-03-06 20:00 | 3 | 20 | 8.05 | 286.6667
2017-03-06 21:00 | 3 | 21 | 9.2 | 286.6667
2017-03-06 22:00 | 3 | 22 | 8.625 | 286.6667
2017-03-06 23:00 | 3 | 23 | 8.05 | 286.6667
2017-03-07 | 3 | 0 | 9.2 | 286.6667
2017-03-07 01:00 | 3 | 1 | 8.625 | 286.6667
2017-03-07 02:00 | 3 | 2 | 8.05 | 286.6667
2017-03-07 03:00 | 3 | 3 | 8.05 | 286.6667
2017-03-07 04:00 | 3 | 4 | 8.05 | 286.6667
2017-03-07 05:00 | 3 | 5 | 6.9 | 0
2017-03-07 06:00 | 3 | 6 | 9.2 | 286.6667
2017-03-07 07:00 | 3 | 7 | 9.2 | 286.6667
2017-03-07 08:00 | 3 | 8 | 12.65 | 1666.6667
2017-03-07 09:00 | 3 | 9 | 14.95 | 2773.3333
2017-03-07 10:00 | 3 | 10 | 13.8 | 1666.6667
2017-03-07 11:00 | 3 | 11 | 11.5 | 873.3333
2017-03-07 12:00 | 3 | 12 | 11.5 | 873.3333
2017-03-07 13:00 | 3 | 13 | 13.8 | 1666.6667
2017-03-07 14:00 | 3 | 14 | 17.25 | 4266.6667
2017-03-07 15:00 | 3 | 15 | 14.95 | 2773.3333
2017-03-07 16:00 | 3 | 16 | 11.5 | 873.3333
2017-03-07 17:00 | 3 | 17 | 10.35 | 873.3333
2017-03-07 18:00 | 3 | 18 | 10.35 | 873.3333
2017-03-07 19:00 | 3 | 19 | 10.925 | 873.3333
2017-03-07 20:00 | 3 | 20 | 10.925 | 873.3333
2017-03-07 21:00 | 3 | 21 | 11.5 | 873.3333
2017-03-07 22:00 | 3 | 22 | 12.075 | 873.3333
2017-03-07 23:00 | 3 | 23 | 11.5 | 873.3333
2017-03-08 | 3 | 0 | 14.95 | 2773.3333
2017-03-08 01:00 | 3 | 1 | 13.8 | 1666.6667
2017-03-08 02:00 | 3 | 2 | 12.65 | 1666.6667
2017-03-08 03:00 | 3 | 3 | 16.1 | 2773.3333
2017-03-08 04:00 | 3 | 4 | 15.525 | 2773.3333
2017-03-08 05:00 | 3 | 5 | 15.7167 | 2773.3333
2017-03-08 06:00 | 3 | 6 | 18.975 | 4266.6667
2017-03-08 07:00 | 3 | 7 | 17.25 | 4266.6667
2017-03-08 08:00 | 3 | 8 | 18.975 | 4266.6667
2017-03-08 09:00 | 3 | 9 | 17.25 | 4266.6667
2017-03-08 10:00 | 3 | 10 | 12.65 | 1666.6667
2017-03-08 11:00 | 3 | 11 | 17.25 | 4266.6667
2017-03-08 12:00 | 3 | 12 | 19.55 | 6160
2017-03-08 13:00 | 3 | 13 | 18.975 | 4266.6667
2017-03-08 14:00 | 3 | 14 | 19.55 | 6160
2017-03-08 15:00 | 3 | 15 | 20.7 | 6160
2017-03-08 16:00 | 3 | 16 | 18.4 | 4266.6667
2017-03-08 17:00 | 3 | 17 | 16.1 | 2773.3333
2017-03-08 18:00 | 3 | 18 | 10.35 | 873.3333
2017-03-08 19:00 | 3 | 19 | 12.65 | 1666.6667
2017-03-08 20:00 | 3 | 20 | 16.1 | 2773.3333
2017-03-08 21:00 | 3 | 21 | 18.4 | 4266.6667
2017-03-08 22:00 | 3 | 22 | 17.25 | 4266.6667
2017-03-08 23:00 | 3 | 23 | 19.55 | 6160
2017-03-09 | 3 | 0 | 12.65 | 1666.6667
2017-03-09 01:00 | 3 | 1 | 12.65 | 1666.6667
2017-03-09 02:00 | 3 | 2 | 12.65 | 1666.6667
2017-03-09 03:00 | 3 | 3 | 12.65 | 1666.6667
2017-03-09 04:00 | 3 | 4 | 12.65 | 1666.6667
2017-03-09 05:00 | 3 | 5 | 12.65 | 1666.6667
2017-03-09 06:00 | 3 | 6 | 11.5 | 873.3333
2017-03-09 07:00 | 3 | 7 | 13.8 | 1666.6667
2017-03-09 08:00 | 3 | 8 | 28.75 | 9873.3333
2017-03-09 09:00 | 3 | 9 | 34.5 | 10000
2017-03-09 10:00 | 3 | 10 | 28.75 | 9873.3333
2017-03-09 11:00 | 3 | 11 | 27.6 | 9573.3333
2017-03-09 12:00 | 3 | 12 | 39.1 | 10000
2017-03-09 13:00 | 3 | 13 | 32.775 | 10000
2017-03-09 14:00 | 3 | 14 | 27.6 | 9573.3333
2017-03-09 15:00 | 3 | 15 | 32.2 | 9960
2017-03-09 16:00 | 3 | 16 | 27.6 | 9573.3333
2017-03-09 17:00 | 3 | 17 | 14.95 | 2773.3333
2017-03-09 18:00 | 3 | 18 | 17.25 | 4266.6667
2017-03-09 19:00 | 3 | 19 | 17.25 | 4266.6667
2017-03-09 20:00 | 3 | 20 | 20.7 | 6160
2017-03-09 21:00 | 3 | 21 | 20.7 | 6160
2017-03-09 22:00 | 3 | 22 | 18.4 | 4266.6667
2017-03-09 23:00 | 3 | 23 | 18.4 | 4266.6667
2017-03-10 | 3 | 0 | 12.65 | 1666.6667
2017-03-10 01:00 | 3 | 1 | 10.925 | 873.3333
2017-03-10 02:00 | 3 | 2 | 6.9 | 0
2017-03-10 03:00 | 3 | 3 | 6.9 | 0
2017-03-10 04:00 | 3 | 4 | 5.175 | 0
2017-03-10 05:00 | 3 | 5 | 5.75 | 0
2017-03-10 06:00 | 3 | 6 | 9.2 | 286.6667
2017-03-10 07:00 | 3 | 7 | 6.9 | 0
2017-03-10 08:00 | 3 | 8 | 6.9 | 0
2017-03-10 09:00 | 3 | 9 | 3.45 | 0
2017-03-10 10:00 | 3 | 10 | 4.6 | 0
2017-03-10 11:00 | 3 | 11 | 3.8333 | 0
2017-03-10 12:00 | 3 | 12 | 5.175 | 0
2017-03-10 13:00 | 3 | 13 | 7.475 | 0
2017-03-10 14:00 | 3 | 14 | 7.475 | 0
2017-03-10 15:00 | 3 | 15 | 6.325 | 0
2017-03-10 16:00 | 3 | 16 | 2.7929 | 0
2017-03-10 17:00 | 3 | 17 | 7.1875 | 0
2017-03-10 18:00 | 3 | 18 | 6.9 | 0
2017-03-10 19:00 | 3 | 19 | 14.375 | 1666.6667
2017-03-10 20:00 | 3 | 20 | 25.875 | 9573.3333
2017-03-10 21:00 | 3 | 21 | 25.99 | 9573.3333
2017-03-10 22:00 | 3 | 22 | 19.7417 | 6160
2017-03-10 23:00 | 3 | 23 | 18.4 | 4266.6667
2017-03-11 | 3 | 0 | 15.7167 | 2773.3333
2017-03-11 01:00 | 3 | 1 | 15.3333 | 2773.3333
2017-03-11 02:00 | 3 | 2 | 19.9333 | 6160
2017-03-11 03:00 | 3 | 3 | 21.6583 | 7873.3333
2017-03-11 04:00 | 3 | 4 | 27.9833 | 9873.3333
2017-03-11 05:00 | 3 | 5 | 26.7375 | 9573.3333
2017-03-11 06:00 | 3 | 6 | 20.7 | 6160
2017-03-11 07:00 | 3 | 7 | 25.3 | 9060
2017-03-11 08:00 | 3 | 8 | 24.15 | 9060
2017-03-11 09:00 | 3 | 9 | 20.7 | 6160
2017-03-11 10:00 | 3 | 10 | 20.7 | 6160
2017-03-11 11:00 | 3 | 11 | 26.45 | 9573.3333
2017-03-11 12:00 | 3 | 12 | 20.7 | 6160
2017-03-11 13:00 | 3 | 13 | 20.7 | 6160
2017-03-11 14:00 | 3 | 14 | 24.15 | 9060
2017-03-11 15:00 | 3 | 15 | 28.75 | 9873.3333
2017-03-11 16:00 | 3 | 16 | 24.15 | 9060
2017-03-11 17:00 | 3 | 17 | 24.15 | 9060
2017-03-11 18:00 | 3 | 18 | 17.25 | 4266.6667
2017-03-11 19:00 | 3 | 19 | 18.4 | 4266.6667
2017-03-11 20:00 | 3 | 20 | 19.55 | 6160
2017-03-11 21:00 | 3 | 21 | 26.45 | 9573.3333
2017-03-11 22:00 | 3 | 22 | 24.725 | 9060
2017-03-11 23:00 | 3 | 23 | 16.1 | 2773.3333
2017-03-12 | 3 | 0 | 11.5 | 873.3333
2017-03-12 01:00 | 3 | 1 | 13.8 | 1666.6667
2017-03-12 02:00 | 3 | 2 | 24.15 | 9060
2017-03-12 03:00 | 3 | 3 | 14.95 | 2773.3333
2017-03-12 04:00 | 3 | 4 | 14.95 | 2773.3333
2017-03-12 05:00 | 3 | 5 | 20.7 | 6160
2017-03-12 06:00 | 3 | 6 | 12.65 | 1666.6667
2017-03-12 07:00 | 3 | 7 | 18.975 | 4266.6667
2017-03-12 08:00 | 3 | 8 | 25.3 | 9060
2017-03-12 09:00 | 3 | 9 | 19.55 | 6160
2017-03-12 10:00 | 3 | 10 | 17.825 | 4266.6667
2017-03-12 11:00 | 3 | 11 | 19.55 | 6160
2017-03-12 12:00 | 3 | 12 | 17.25 | 4266.6667
2017-03-12 13:00 | 3 | 13 | 18.4 | 4266.6667
2017-03-12 14:00 | 3 | 14 | 24.15 | 9060
2017-03-12 15:00 | 3 | 15 | 23 | 7873.3333
2017-03-12 16:00 | 3 | 16 | 23 | 7873.3333
2017-03-12 17:00 | 3 | 17 | 18.4 | 4266.6667
2017-03-12 18:00 | 3 | 18 | 19.55 | 6160
2017-03-12 19:00 | 3 | 19 | 19.55 | 6160
2017-03-12 20:00 | 3 | 20 | 17.25 | 4266.6667
2017-03-12 21:00 | 3 | 21 | 16.1 | 2773.3333
2017-03-12 22:00 | 3 | 22 | 16.1 | 2773.3333
2017-03-12 23:00 | 3 | 23 | 20.7 | 6160
2017-03-13 | 3 | 0 | 19.55 | 6160
2017-03-13 01:00 | 3 | 1 | 15.525 | 2773.3333
2017-03-13 02:00 | 3 | 2 | 18.4 | 4266.6667
2017-03-13 03:00 | 3 | 3 | 16.1 | 2773.3333
2017-03-13 04:00 | 3 | 4 | 14.375 | 1666.6667
2017-03-13 05:00 | 3 | 5 | 18.4 | 4266.6667
2017-03-13 06:00 | 3 | 6 | 17.25 | 4266.6667
2017-03-13 07:00 | 3 | 7 | 16.675 | 2773.3333
2017-03-13 08:00 | 3 | 8 | 14.95 | 2773.3333
2017-03-13 09:00 | 3 | 9 | 10.35 | 873.3333
2017-03-13 10:00 | 3 | 10 | 9.775 | 286.6667
2017-03-13 11:00 | 3 | 11 | 6.9 | 0
2017-03-13 12:00 | 3 | 12 | 0 | 0
2017-03-13 13:00 | 3 | 13 | 1.725 | 0
2017-03-13 14:00 | 3 | 14 | 5.75 | 0
2017-03-13 15:00 | 3 | 15 | 18.4 | 4266.6667
2017-03-13 16:00 | 3 | 16 | 17.825 | 4266.6667
2017-03-13 17:00 | 3 | 17 | 14.95 | 2773.3333
2017-03-13 18:00 | 3 | 18 | 10.35 | 873.3333
2017-03-13 19:00 | 3 | 19 | 10.35 | 873.3333
2017-03-13 20:00 | 3 | 20 | 11.5 | 873.3333
2017-03-13 21:00 | 3 | 21 | 10.35 | 873.3333
2017-03-13 22:00 | 3 | 22 | 10.35 | 873.3333
2017-03-13 23:00 | 3 | 23 | 8.05 | 286.6667
2017-03-14 | 3 | 0 | 8.05 | 286.6667
2017-03-14 01:00 | 3 | 1 | 8.05 | 286.6667
2017-03-14 02:00 | 3 | 2 | 9.2 | 286.6667
2017-03-14 03:00 | 3 | 3 | 11.5 | 873.3333
2017-03-14 04:00 | 3 | 4 | 9.4875 | 286.6667
2017-03-14 05:00 | 3 | 5 | 14.95 | 2773.3333
2017-03-14 06:00 | 3 | 6 | 19.55 | 6160
2017-03-14 07:00 | 3 | 7 | 22.8083 | 7873.3333
2017-03-14 08:00 | 3 | 8 | 33.0625 | 10000
2017-03-14 09:00 | 3 | 9 | 36.8 | 10000
2017-03-14 10:00 | 3 | 10 | 38.2375 | 10000
2017-03-14 11:00 | 3 | 11 | 40.6333 | 10000
2017-03-14 12:00 | 3 | 12 | 40.825 | 10000
2017-03-14 13:00 | 3 | 13 | 40.825 | 10000
2017-03-14 14:00 | 3 | 14 | 39.1 | 10000
2017-03-14 15:00 | 3 | 15 | 41.7833 | 10000
2017-03-14 16:00 | 3 | 16 | 44.85 | 10000
2017-03-14 17:00 | 3 | 17 | 35.65 | 10000
2017-03-14 18:00 | 3 | 18 | 16.9625 | 4266.6667
2017-03-14 19:00 | 3 | 19 | 12.075 | 873.3333
2017-03-14 20:00 | 3 | 20 | 32.5833 | 10000
2017-03-14 21:00 | 3 | 21 | 26.8333 | 9573.3333
2017-03-14 22:00 | 3 | 22 | 26.45 | 9573.3333
2017-03-14 23:00 | 3 | 23 | 25.3 | 9060
2017-03-15 | 3 | 0 | 24.725 | 9060
2017-03-15 01:00 | 3 | 1 | 27.6 | 9573.3333
2017-03-15 02:00 | 3 | 2 | 19.55 | 6160
2017-03-15 03:00 | 3 | 3 | 20.7 | 6160
2017-03-15 04:00 | 3 | 4 | 20.7 | 6160
2017-03-15 05:00 | 3 | 5 | 19.55 | 6160
2017-03-15 06:00 | 3 | 6 | 19.55 | 6160
2017-03-15 07:00 | 3 | 7 | 21.275 | 7873.3333
2017-03-15 08:00 | 3 | 8 | 17.25 | 4266.6667
2017-03-15 09:00 | 3 | 9 | 20.7 | 6160
2017-03-15 10:00 | 3 | 10 | 20.125 | 6160
2017-03-15 11:00 | 3 | 11 | 24.15 | 9060
2017-03-15 12:00 | 3 | 12 | 23 | 7873.3333
2017-03-15 13:00 | 3 | 13 | 20.7 | 6160
2017-03-15 14:00 | 3 | 14 | 23 | 7873.3333
2017-03-15 15:00 | 3 | 15 | 19.55 | 6160
2017-03-15 16:00 | 3 | 16 | 19.55 | 6160
2017-03-15 17:00 | 3 | 17 | 26.45 | 9573.3333
2017-03-15 18:00 | 3 | 18 | 23 | 7873.3333
2017-03-15 19:00 | 3 | 19 | 21.85 | 7873.3333
2017-03-15 20:00 | 3 | 20 | 20.7 | 6160
2017-03-15 21:00 | 3 | 21 | 27.6 | 9573.3333
2017-03-15 22:00 | 3 | 22 | 27.025 | 9573.3333
2017-03-15 23:00 | 3 | 23 | 25.3 | 9060
2017-03-16 | 3 | 0 | 20.7 | 6160
2017-03-16 01:00 | 3 | 1 | 18.975 | 4266.6667
2017-03-16 02:00 | 3 | 2 | 20.7 | 6160
2017-03-16 03:00 | 3 | 3 | 16.1 | 2773.3333
2017-03-16 04:00 | 3 | 4 | 17.25 | 4266.6667
2017-03-16 05:00 | 3 | 5 | 20.7 | 6160
2017-03-16 06:00 | 3 | 6 | 20.7 | 6160
2017-03-16 07:00 | 3 | 7 | 22.425 | 7873.3333
2017-03-16 08:00 | 3 | 8 | 24.15 | 9060
2017-03-16 09:00 | 3 | 9 | 19.55 | 6160
2017-03-16 10:00 | 3 | 10 | 18.4 | 4266.6667
2017-03-16 11:00 | 3 | 11 | 18.4 | 4266.6667
2017-03-16 12:00 | 3 | 12 | 18.4 | 4266.6667
2017-03-16 13:00 | 3 | 13 | 21.275 | 7873.3333
2017-03-16 14:00 | 3 | 14 | 27.6 | 9573.3333
2017-03-16 15:00 | 3 | 15 | 20.7 | 6160
2017-03-16 16:00 | 3 | 16 | 19.55 | 6160
2017-03-16 17:00 | 3 | 17 | 16.1 | 2773.3333
2017-03-16 18:00 | 3 | 18 | 10.35 | 873.3333
2017-03-16 19:00 | 3 | 19 | 14.95 | 2773.3333
2017-03-16 20:00 | 3 | 20 | 12.65 | 1666.6667
2017-03-16 21:00 | 3 | 21 | 16.1 | 2773.3333
2017-03-16 22:00 | 3 | 22 | 14.375 | 1666.6667
2017-03-16 23:00 | 3 | 23 | 9.2 | 286.6667
2017-03-17 | 3 | 0 | 0 | 0
2017-03-17 01:00 | 3 | 1 | 2.875 | 0
2017-03-17 02:00 | 3 | 2 | 16.1 | 2773.3333
2017-03-17 03:00 | 3 | 3 | 11.5 | 873.3333
2017-03-17 04:00 | 3 | 4 | 13.225 | 1666.6667
2017-03-17 05:00 | 3 | 5 | 11.5 | 873.3333
2017-03-17 06:00 | 3 | 6 | 12.65 | 1666.6667
2017-03-17 07:00 | 3 | 7 | 14.95 | 2773.3333
2017-03-17 08:00 | 3 | 8 | 16.1 | 2773.3333
2017-03-17 09:00 | 3 | 9 | 14.95 | 2773.3333
2017-03-17 10:00 | 3 | 10 | 15.525 | 2773.3333
2017-03-17 11:00 | 3 | 11 | 14.95 | 2773.3333
2017-03-17 12:00 | 3 | 12 | 17.25 | 4266.6667
2017-03-17 13:00 | 3 | 13 | 16.1 | 2773.3333
2017-03-17 14:00 | 3 | 14 | 14.95 | 2773.3333
2017-03-17 15:00 | 3 | 15 | 9.2 | 286.6667
2017-03-17 16:00 | 3 | 16 | 9.2 | 286.6667
2017-03-17 17:00 | 3 | 17 | 11.5 | 873.3333
2017-03-17 18:00 | 3 | 18 | 8.05 | 286.6667
2017-03-17 19:00 | 3 | 19 | 8.05 | 286.6667
2017-03-17 20:00 | 3 | 20 | 5.75 | 0
2017-03-17 21:00 | 3 | 21 | 8.05 | 286.6667
2017-03-17 22:00 | 3 | 22 | 6.9 | 0
2017-03-17 23:00 | 3 | 23 | 3.45 | 0
2017-03-18 | 3 | 0 | 0 | 0
2017-03-18 01:00 | 3 | 1 | 4.025 | 0
2017-03-18 02:00 | 3 | 2 | 10.35 | 873.3333
2017-03-18 03:00 | 3 | 3 | 10.35 | 873.3333
2017-03-18 04:00 | 3 | 4 | 10.35 | 873.3333
2017-03-18 05:00 | 3 | 5 | 10.35 | 873.3333
2017-03-18 06:00 | 3 | 6 | 9.2 | 286.6667
2017-03-18 07:00 | 3 | 7 | 12.65 | 1666.6667
2017-03-18 08:00 | 3 | 8 | 10.35 | 873.3333
2017-03-18 09:00 | 3 | 9 | 17.25 | 4266.6667
2017-03-18 10:00 | 3 | 10 | 16.675 | 2773.3333
2017-03-18 11:00 | 3 | 11 | 14.95 | 2773.3333
2017-03-18 12:00 | 3 | 12 | 16.1 | 2773.3333
2017-03-18 13:00 | 3 | 13 | 15.525 | 2773.3333
2017-03-18 14:00 | 3 | 14 | 16.1 | 2773.3333
2017-03-18 15:00 | 3 | 15 | 16.1 | 2773.3333
2017-03-18 16:00 | 3 | 16 | 16.675 | 2773.3333
2017-03-18 17:00 | 3 | 17 | 12.65 | 1666.6667
2017-03-18 18:00 | 3 | 18 | 11.5 | 873.3333
2017-03-18 19:00 | 3 | 19 | 13.225 | 1666.6667
2017-03-18 20:00 | 3 | 20 | 16.1 | 2773.3333
2017-03-18 21:00 | 3 | 21 | 17.25 | 4266.6667
2017-03-18 22:00 | 3 | 22 | 16.675 | 2773.3333
2017-03-18 23:00 | 3 | 23 | 19.55 | 6160
2017-03-19 | 3 | 0 | 19.55 | 6160
2017-03-19 01:00 | 3 | 1 | 20.125 | 6160
2017-03-19 02:00 | 3 | 2 | 18.0167 | 4266.6667
2017-03-19 03:00 | 3 | 3 | 14.95 | 2773.3333
2017-03-19 04:00 | 3 | 4 | 14.5667 | 2773.3333
2017-03-19 05:00 | 3 | 5 | 16.675 | 2773.3333
2017-03-19 06:00 | 3 | 6 | 16.1 | 2773.3333
2017-03-19 07:00 | 3 | 7 | 12.65 | 1666.6667
2017-03-19 08:00 | 3 | 8 | 14.95 | 2773.3333
2017-03-19 09:00 | 3 | 9 | 20.7 | 6160
2017-03-19 10:00 | 3 | 10 | 23.7667 | 9060
2017-03-19 11:00 | 3 | 11 | 25.3 | 9060
2017-03-19 12:00 | 3 | 12 | 28.75 | 9873.3333
2017-03-19 13:00 | 3 | 13 | 28.75 | 9873.3333
2017-03-19 14:00 | 3 | 14 | 26.45 | 9573.3333
2017-03-19 15:00 | 3 | 15 | 20.7 | 6160
2017-03-19 16:00 | 3 | 16 | 18.975 | 4266.6667
2017-03-19 17:00 | 3 | 17 | 18.4 | 4266.6667
2017-03-19 18:00 | 3 | 18 | 14.95 | 2773.3333
2017-03-19 19:00 | 3 | 19 | 14.95 | 2773.3333
2017-03-19 20:00 | 3 | 20 | 12.65 | 1666.6667
2017-03-19 21:00 | 3 | 21 | 11.5 | 873.3333
2017-03-19 22:00 | 3 | 22 | 13.225 | 1666.6667
2017-03-19 23:00 | 3 | 23 | 14.95 | 2773.3333
2017-03-20 | 3 | 0 | 12.65 | 1666.6667
2017-03-20 01:00 | 3 | 1 | 12.65 | 1666.6667
2017-03-20 02:00 | 3 | 2 | 12.65 | 1666.6667
2017-03-20 03:00 | 3 | 3 | 16.1 | 2773.3333
2017-03-20 04:00 | 3 | 4 | 16.1 | 2773.3333
2017-03-20 05:00 | 3 | 5 | 16.1 | 2773.3333
2017-03-20 06:00 | 3 | 6 | 16.1 | 2773.3333
2017-03-20 07:00 | 3 | 7 | 16.1 | 2773.3333
2017-03-20 08:00 | 3 | 8 | 20.7 | 6160
2017-03-20 09:00 | 3 | 9 | 24.15 | 9060
2017-03-20 10:00 | 3 | 10 | 20.7 | 6160
2017-03-20 11:00 | 3 | 11 | 16.1 | 2773.3333
2017-03-20 12:00 | 3 | 12 | 11.5 | 873.3333
2017-03-20 13:00 | 3 | 13 | 13.8 | 1666.6667
2017-03-20 14:00 | 3 | 14 | 16.1 | 2773.3333
2017-03-20 15:00 | 3 | 15 | 10.35 | 873.3333
2017-03-20 16:00 | 3 | 16 | 10.925 | 873.3333
2017-03-20 17:00 | 3 | 17 | 6.9 | 0
2017-03-20 18:00 | 3 | 18 | 5.75 | 0
2017-03-20 19:00 | 3 | 19 | 5.75 | 0
2017-03-20 20:00 | 3 | 20 | 3.45 | 0
2017-03-20 21:00 | 3 | 21 | 6.9 | 0
2017-03-20 22:00 | 3 | 22 | 9.775 | 286.6667
2017-03-20 23:00 | 3 | 23 | 11.5 | 873.3333
2017-03-21 | 3 | 0 | 11.5 | 873.3333
2017-03-21 01:00 | 3 | 1 | 9.775 | 286.6667
2017-03-21 02:00 | 3 | 2 | 11.5 | 873.3333
2017-03-21 03:00 | 3 | 3 | 10.35 | 873.3333
2017-03-21 04:00 | 3 | 4 | 9.775 | 286.6667
2017-03-21 05:00 | 3 | 5 | 8.05 | 286.6667
2017-03-21 06:00 | 3 | 6 | 8.05 | 286.6667
2017-03-21 07:00 | 3 | 7 | 8.05 | 286.6667
2017-03-21 08:00 | 3 | 8 | 9.2 | 286.6667
2017-03-21 09:00 | 3 | 9 | 5.75 | 0
2017-03-21 10:00 | 3 | 10 | 9.2 | 286.6667
2017-03-21 11:00 | 3 | 11 | 9.2 | 286.6667
2017-03-21 12:00 | 3 | 12 | 8.05 | 286.6667
2017-03-21 13:00 | 3 | 13 | 9.775 | 286.6667
2017-03-21 14:00 | 3 | 14 | 8.05 | 286.6667
2017-03-21 15:00 | 3 | 15 | 5.75 | 0
2017-03-21 16:00 | 3 | 16 | 7.475 | 0
2017-03-21 17:00 | 3 | 17 | 10.35 | 873.3333
2017-03-21 18:00 | 3 | 18 | 17.25 | 4266.6667
2017-03-21 19:00 | 3 | 19 | 13.8 | 1666.6667
2017-03-21 20:00 | 3 | 20 | 16.1 | 2773.3333
2017-03-21 21:00 | 3 | 21 | 14.95 | 2773.3333
2017-03-21 22:00 | 3 | 22 | 13.8 | 1666.6667
2017-03-21 23:00 | 3 | 23 | 12.65 | 1666.6667
2017-03-22 | 3 | 0 | 8.05 | 286.6667
2017-03-22 01:00 | 3 | 1 | 7.475 | 0
2017-03-22 02:00 | 3 | 2 | 19.55 | 6160
2017-03-22 03:00 | 3 | 3 | 12.65 | 1666.6667
2017-03-22 04:00 | 3 | 4 | 18.4 | 4266.6667
2017-03-22 05:00 | 3 | 5 | 17.25 | 4266.6667
2017-03-22 06:00 | 3 | 6 | 17.25 | 4266.6667
2017-03-22 07:00 | 3 | 7 | 23 | 7873.3333
2017-03-22 08:00 | 3 | 8 | 25.3 | 9060
2017-03-22 09:00 | 3 | 9 | 24.15 | 9060
2017-03-22 10:00 | 3 | 10 | 25.3 | 9060
2017-03-22 11:00 | 3 | 11 | 25.3 | 9060
2017-03-22 12:00 | 3 | 12 | 25.3 | 9060
2017-03-22 13:00 | 3 | 13 | 27.025 | 9573.3333
2017-03-22 14:00 | 3 | 14 | 35.65 | 10000
2017-03-22 15:00 | 3 | 15 | 32.2 | 9960
2017-03-22 16:00 | 3 | 16 | 29.325 | 9873.3333
2017-03-22 17:00 | 3 | 17 | 28.75 | 9873.3333
2017-03-22 18:00 | 3 | 18 | 29.9 | 9873.3333
2017-03-22 19:00 | 3 | 19 | 25.3 | 9060
2017-03-22 20:00 | 3 | 20 | 26.45 | 9573.3333
2017-03-22 21:00 | 3 | 21 | 29.9 | 9873.3333
2017-03-22 22:00 | 3 | 22 | 29.9 | 9873.3333
2017-03-22 23:00 | 3 | 23 | 24.15 | 9060
2017-03-23 | 3 | 0 | 23 | 7873.3333
2017-03-23 01:00 | 3 | 1 | 19.55 | 6160
2017-03-23 02:00 | 3 | 2 | 19.55 | 6160
2017-03-23 03:00 | 3 | 3 | 14.95 | 2773.3333
2017-03-23 04:00 | 3 | 4 | 13.225 | 1666.6667
2017-03-23 05:00 | 3 | 5 | 14.95 | 2773.3333
2017-03-23 06:00 | 3 | 6 | 23 | 7873.3333
2017-03-23 07:00 | 3 | 7 | 19.55 | 6160
2017-03-23 08:00 | 3 | 8 | 16.1 | 2773.3333
2017-03-23 09:00 | 3 | 9 | 19.55 | 6160
2017-03-23 10:00 | 3 | 10 | 17.825 | 4266.6667
2017-03-23 11:00 | 3 | 11 | 12.65 | 1666.6667
2017-03-23 12:00 | 3 | 12 | 14.95 | 2773.3333
2017-03-23 13:00 | 3 | 13 | 16.675 | 2773.3333
2017-03-23 14:00 | 3 | 14 | 19.55 | 6160
2017-03-23 15:00 | 3 | 15 | 24.15 | 9060
2017-03-23 16:00 | 3 | 16 | 21.85 | 7873.3333
2017-03-23 17:00 | 3 | 17 | 10.35 | 873.3333
2017-03-23 18:00 | 3 | 18 | 14.95 | 2773.3333
2017-03-23 19:00 | 3 | 19 | 12.65 | 1666.6667
2017-03-23 20:00 | 3 | 20 | 9.2 | 286.6667
2017-03-23 21:00 | 3 | 21 | 6.9 | 0
2017-03-23 22:00 | 3 | 22 | 8.625 | 286.6667
2017-03-23 23:00 | 3 | 23 | 10.35 | 873.3333
2017-03-24 | 3 | 0 | 5.75 | 0
2017-03-24 01:00 | 3 | 1 | 2.875 | 0
2017-03-24 02:00 | 3 | 2 | 5.75 | 0
2017-03-24 03:00 | 3 | 3 | 5.75 | 0
2017-03-24 04:00 | 3 | 4 | 7.475 | 0
2017-03-24 05:00 | 3 | 5 | 9.2 | 286.6667
2017-03-24 06:00 | 3 | 6 | 9.2 | 286.6667
2017-03-24 07:00 | 3 | 7 | 9.775 | 286.6667
2017-03-24 08:00 | 3 | 8 | 11.5 | 873.3333
2017-03-24 09:00 | 3 | 9 | 11.5 | 873.3333
2017-03-24 10:00 | 3 | 10 | 13.8 | 1666.6667
2017-03-24 11:00 | 3 | 11 | 20.7 | 6160
2017-03-24 12:00 | 3 | 12 | 24.15 | 9060
2017-03-24 13:00 | 3 | 13 | 19.1667 | 6160
2017-03-24 14:00 | 3 | 14 | 10.35 | 873.3333
2017-03-24 15:00 | 3 | 15 | 20.7 | 6160
2017-03-24 16:00 | 3 | 16 | 18.4 | 4266.6667
2017-03-24 17:00 | 3 | 17 | 17.25 | 4266.6667
2017-03-24 18:00 | 3 | 18 | 18.4 | 4266.6667
2017-03-24 19:00 | 3 | 19 | 16.675 | 2773.3333
2017-03-24 20:00 | 3 | 20 | 11.5 | 873.3333
2017-03-24 21:00 | 3 | 21 | 9.2 | 286.6667
2017-03-24 22:00 | 3 | 22 | 9.2 | 286.6667
2017-03-24 23:00 | 3 | 23 | 9.2 | 286.6667
2017-03-25 | 3 | 0 | 5.75 | 0
2017-03-25 01:00 | 3 | 1 | 6.325 | 0
2017-03-25 02:00 | 3 | 2 | 8.05 | 286.6667
2017-03-25 03:00 | 3 | 3 | 10.35 | 873.3333
2017-03-25 04:00 | 3 | 4 | 6.9 | 0
2017-03-25 05:00 | 3 | 5 | 7.475 | 0
2017-03-25 06:00 | 3 | 6 | 5.75 | 0
2017-03-25 07:00 | 3 | 7 | 9.5833 | 286.6667
2017-03-25 08:00 | 3 | 8 | 9.2 | 286.6667
2017-03-25 09:00 | 3 | 9 | 10.35 | 873.3333
2017-03-25 10:00 | 3 | 10 | 9.2 | 286.6667
2017-03-25 11:00 | 3 | 11 | 9.2 | 286.6667
2017-03-25 12:00 | 3 | 12 | 8.8167 | 286.6667
2017-03-25 13:00 | 3 | 13 | 9.9667 | 286.6667
2017-03-25 14:00 | 3 | 14 | 6.325 | 0
2017-03-25 15:00 | 3 | 15 | 5.75 | 0
2017-03-25 16:00 | 3 | 16 | 8.625 | 286.6667
2017-03-25 17:00 | 3 | 17 | 5.75 | 0
2017-03-25 18:00 | 3 | 18 | 8.05 | 286.6667
2017-03-25 19:00 | 3 | 19 | 6.325 | 0
2017-03-25 20:00 | 3 | 20 | 6.9 | 0
2017-03-25 21:00 | 3 | 21 | 9.2 | 286.6667
2017-03-25 22:00 | 3 | 22 | 8.625 | 286.6667
2017-03-25 23:00 | 3 | 23 | 10.35 | 873.3333
2017-03-26 | 3 | 0 | 6.9 | 0
2017-03-26 01:00 | 3 | 1 | 8.05 | 286.6667
2017-03-26 02:00 | 3 | 2 | 10.35 | 873.3333
2017-03-26 03:00 | 3 | 3 | 10.35 | 873.3333
2017-03-26 04:00 | 3 | 4 | 10.925 | 873.3333
2017-03-26 05:00 | 3 | 5 | 10.35 | 873.3333
2017-03-26 06:00 | 3 | 6 | 10.35 | 873.3333
2017-03-26 07:00 | 3 | 7 | 14.375 | 1666.6667
2017-03-26 08:00 | 3 | 8 | 17.25 | 4266.6667
2017-03-26 09:00 | 3 | 9 | 16.1 | 2773.3333
2017-03-26 10:00 | 3 | 10 | 17.25 | 4266.6667
2017-03-26 11:00 | 3 | 11 | 17.25 | 4266.6667
2017-03-26 12:00 | 3 | 12 | 16.1 | 2773.3333
2017-03-26 13:00 | 3 | 13 | 14.375 | 1666.6667
2017-03-26 14:00 | 3 | 14 | 14.95 | 2773.3333
2017-03-26 15:00 | 3 | 15 | 12.65 | 1666.6667
2017-03-26 16:00 | 3 | 16 | 12.65 | 1666.6667
2017-03-26 17:00 | 3 | 17 | 11.5 | 873.3333
2017-03-26 18:00 | 3 | 18 | 14.95 | 2773.3333
2017-03-26 19:00 | 3 | 19 | 14.95 | 2773.3333
2017-03-26 20:00 | 3 | 20 | 14.95 | 2773.3333
2017-03-26 21:00 | 3 | 21 | 12.65 | 1666.6667
2017-03-26 22:00 | 3 | 22 | 10.35 | 873.3333
2017-03-26 23:00 | 3 | 23 | 9.2 | 286.6667
2017-03-27 | 3 | 0 | 10.35 | 873.3333
2017-03-27 01:00 | 3 | 1 | 10.7333 | 873.3333
2017-03-27 02:00 | 3 | 2 | 12.65 | 1666.6667
2017-03-27 03:00 | 3 | 3 | 11.5 | 873.3333
2017-03-27 04:00 | 3 | 4 | 13.3071 | 1666.6667
2017-03-27 05:00 | 3 | 5 | 11.5 | 873.3333
2017-03-27 06:00 | 3 | 6 | 14.95 | 2773.3333
2017-03-27 07:00 | 3 | 7 | 14.95 | 2773.3333
2017-03-27 08:00 | 3 | 8 | 10.925 | 873.3333
2017-03-27 09:00 | 3 | 9 | 8.05 | 286.6667
2017-03-27 10:00 | 3 | 10 | 7.475 | 0
2017-03-27 11:00 | 3 | 11 | 4.9833 | 0
2017-03-27 12:00 | 3 | 12 | 7.2833 | 0
2017-03-27 13:00 | 3 | 13 | 8.05 | 286.6667
2017-03-27 14:00 | 3 | 14 | 6.9 | 0
2017-03-27 15:00 | 3 | 15 | 6.9 | 0
2017-03-27 16:00 | 3 | 16 | 6.9 | 0
2017-03-27 17:00 | 3 | 17 | 11.5 | 873.3333
2017-03-27 18:00 | 3 | 18 | 11.5 | 873.3333
2017-03-27 19:00 | 3 | 19 | 10.925 | 873.3333
2017-03-27 20:00 | 3 | 20 | 11.5 | 873.3333
2017-03-27 21:00 | 3 | 21 | 8.05 | 286.6667
2017-03-27 22:00 | 3 | 22 | 6.9 | 0
2017-03-27 23:00 | 3 | 23 | 3.45 | 0
2017-03-28 | 3 | 0 | 6.9 | 0
2017-03-28 01:00 | 3 | 1 | 6.9 | 0
2017-03-28 02:00 | 3 | 2 | 6.325 | 0
2017-03-28 03:00 | 3 | 3 | 6.9 | 0
2017-03-28 04:00 | 3 | 4 | 3.45 | 0
2017-03-28 05:00 | 3 | 5 | 3.45 | 0
2017-03-28 06:00 | 3 | 6 | 6.9 | 0
2017-03-28 07:00 | 3 | 7 | 6.9 | 0
2017-03-28 08:00 | 3 | 8 | 8.05 | 286.6667
2017-03-28 09:00 | 3 | 9 | 6.9 | 0
2017-03-28 10:00 | 3 | 10 | 8.05 | 286.6667
2017-03-28 11:00 | 3 | 11 | 9.2 | 286.6667
2017-03-28 12:00 | 3 | 12 | 10.35 | 873.3333
2017-03-28 13:00 | 3 | 13 | 9.5833 | 286.6667
2017-03-28 14:00 | 3 | 14 | 8.8167 | 286.6667
2017-03-28 15:00 | 3 | 15 | 9.9667 | 286.6667
2017-03-28 16:00 | 3 | 16 | 9.5833 | 286.6667
2017-03-28 17:00 | 3 | 17 | 9.5833 | 286.6667
2017-03-28 18:00 | 3 | 18 | 8.05 | 286.6667
2017-03-28 19:00 | 3 | 19 | 7.59 | 0
2017-03-28 20:00 | 3 | 20 | 8.28 | 286.6667
2017-03-28 21:00 | 3 | 21 | 6.9 | 0
2017-03-28 22:00 | 3 | 22 | 8.625 | 286.6667
2017-03-28 23:00 | 3 | 23 | 9.775 | 286.6667
2017-03-29 | 3 | 0 | 8.4333 | 286.6667
2017-03-29 01:00 | 3 | 1 | 9.5833 | 286.6667
2017-03-29 02:00 | 3 | 2 | 11.5 | 873.3333
2017-03-29 03:00 | 3 | 3 | 10.35 | 873.3333
2017-03-29 04:00 | 3 | 4 | 10.35 | 873.3333
2017-03-29 05:00 | 3 | 5 | 11.2125 | 873.3333
2017-03-29 06:00 | 3 | 6 | 10.925 | 873.3333
2017-03-29 07:00 | 3 | 7 | 11.5 | 873.3333
2017-03-29 08:00 | 3 | 8 | 13.225 | 1666.6667
2017-03-29 09:00 | 3 | 9 | 13.8 | 1666.6667
2017-03-29 10:00 | 3 | 10 | 10.925 | 873.3333
2017-03-29 11:00 | 3 | 11 | 10.35 | 873.3333
2017-03-29 12:00 | 3 | 12 | 10.35 | 873.3333
2017-03-29 13:00 | 3 | 13 | 14.95 | 2773.3333
2017-03-29 14:00 | 3 | 14 | 18.4 | 4266.6667
2017-03-29 15:00 | 3 | 15 | 24.15 | 9060
2017-03-29 16:00 | 3 | 16 | 24.15 | 9060
2017-03-29 17:00 | 3 | 17 | 24.15 | 9060
2017-03-29 18:00 | 3 | 18 | 19.55 | 6160
2017-03-29 19:00 | 3 | 19 | 17.825 | 4266.6667
2017-03-29 20:00 | 3 | 20 | 17.25 | 4266.6667
2017-03-29 21:00 | 3 | 21 | 17.25 | 4266.6667
2017-03-29 22:00 | 3 | 22 | 17.25 | 4266.6667
2017-03-29 23:00 | 3 | 23 | 18.4 | 4266.6667
2017-03-30 | 3 | 0 | 17.25 | 4266.6667
2017-03-30 01:00 | 3 | 1 | 14.375 | 1666.6667
2017-03-30 02:00 | 3 | 2 | 16.1 | 2773.3333
2017-03-30 03:00 | 3 | 3 | 14.95 | 2773.3333
2017-03-30 04:00 | 3 | 4 | 13.225 | 1666.6667
2017-03-30 05:00 | 3 | 5 | 11.5 | 873.3333
2017-03-30 06:00 | 3 | 6 | 16.1 | 2773.3333
2017-03-30 07:00 | 3 | 7 | 15.525 | 2773.3333
2017-03-30 08:00 | 3 | 8 | 14.95 | 2773.3333
2017-03-30 09:00 | 3 | 9 | 10.35 | 873.3333
2017-03-30 10:00 | 3 | 10 | 10.35 | 873.3333
2017-03-30 11:00 | 3 | 11 | 12.65 | 1666.6667
2017-03-30 12:00 | 3 | 12 | 9.2 | 286.6667
2017-03-30 13:00 | 3 | 13 | 12.65 | 1666.6667
2017-03-30 14:00 | 3 | 14 | 12.65 | 1666.6667
2017-03-30 15:00 | 3 | 15 | 10.35 | 873.3333
2017-03-30 16:00 | 3 | 16 | 10.925 | 873.3333
2017-03-30 17:00 | 3 | 17 | 12.65 | 1666.6667
2017-03-30 18:00 | 3 | 18 | 10.35 | 873.3333
2017-03-30 19:00 | 3 | 19 | 10.35 | 873.3333
2017-03-30 20:00 | 3 | 20 | 9.2 | 286.6667
2017-03-30 21:00 | 3 | 21 | 9.2 | 286.6667
2017-03-30 22:00 | 3 | 22 | 8.625 | 286.6667
2017-03-30 23:00 | 3 | 23 | 6.9 | 0
2017-03-31 | 3 | 0 | 3.45 | 0
2017-03-31 01:00 | 3 | 1 | 4.6 | 0
2017-03-31 02:00 | 3 | 2 | 5.75 | 0
2017-03-31 03:00 | 3 | 3 | 6.9 | 0
2017-03-31 04:00 | 3 | 4 | 5.175 | 0
2017-03-31 05:00 | 3 | 5 | 6.9 | 0
2017-03-31 06:00 | 3 | 6 | 9.2 | 286.6667
2017-03-31 07:00 | 3 | 7 | 13.225 | 1666.6667
2017-03-31 08:00 | 3 | 8 | 18.4 | 4266.6667
2017-03-31 09:00 | 3 | 9 | 17.25 | 4266.6667
2017-03-31 10:00 | 3 | 10 | 17.25 | 4266.6667
2017-03-31 11:00 | 3 | 11 | 14.95 | 2773.3333
2017-03-31 12:00 | 3 | 12 | 13.8 | 1666.6667
2017-03-31 13:00 | 3 | 13 | 13.225 | 1666.6667
2017-03-31 14:00 | 3 | 14 | 10.925 | 873.3333
2017-03-31 15:00 | 3 | 15 | 10.35 | 873.3333
2017-03-31 16:00 | 3 | 16 | 12.3625 | 1666.6667
2017-03-31 17:00 | 3 | 17 | 16.1 | 2773.3333
2017-03-31 18:00 | 3 | 18 | 18.4 | 4266.6667
2017-03-31 19:00 | 3 | 19 | 20.4125 | 6160
2017-03-31 20:00 | 3 | 20 | 19.55 | 6160
2017-03-31 21:00 | 3 | 21 | 24.9167 | 9060
2017-03-31 22:00 | 3 | 22 | 27.6 | 9573.3333
2017-03-31 23:00 | 3 | 23 | 25.3 | 9060
2017-04-01 | 4 | 0 | 28.175 | 9873.3333
2017-04-01 01:00 | 4 | 1 | 26.8333 | 9573.3333
2017-04-01 02:00 | 4 | 2 | 27.9833 | 9873.3333
2017-04-01 03:00 | 4 | 3 | 27.3125 | 9573.3333
2017-04-01 04:00 | 4 | 4 | 27.025 | 9573.3333
2017-04-01 05:00 | 4 | 5 | 26.45 | 9573.3333
2017-04-01 06:00 | 4 | 6 | 27.025 | 9573.3333
2017-04-01 07:00 | 4 | 7 | 27.025 | 9573.3333
2017-04-01 08:00 | 4 | 8 | 24.15 | 9060
2017-04-01 09:00 | 4 | 9 | 20.7 | 6160
2017-04-01 10:00 | 4 | 10 | 23 | 7873.3333
2017-04-01 11:00 | 4 | 11 | 26.45 | 9573.3333
2017-04-01 12:00 | 4 | 12 | 28.75 | 9873.3333
2017-04-01 13:00 | 4 | 13 | 28.29 | 9873.3333
2017-04-01 14:00 | 4 | 14 | 27.6 | 9573.3333
2017-04-01 15:00 | 4 | 15 | 25.3 | 9060
2017-04-01 16:00 | 4 | 16 | 22.425 | 7873.3333
2017-04-01 17:00 | 4 | 17 | 15.525 | 2773.3333
2017-04-01 18:00 | 4 | 18 | 14.5667 | 2773.3333
2017-04-01 19:00 | 4 | 19 | 14.95 | 2773.3333
2017-04-01 20:00 | 4 | 20 | 14.95 | 2773.3333
2017-04-01 21:00 | 4 | 21 | 14.95 | 2773.3333
2017-04-01 22:00 | 4 | 22 | 13.8 | 1666.6667
2017-04-01 23:00 | 4 | 23 | 10.925 | 873.3333
2017-04-02 | 4 | 0 | 10.35 | 873.3333
2017-04-02 01:00 | 4 | 1 | 9.2 | 286.6667
2017-04-02 02:00 | 4 | 2 | 8.05 | 286.6667
2017-04-02 03:00 | 4 | 3 | 8.05 | 286.6667
2017-04-02 04:00 | 4 | 4 | 8.05 | 286.6667
2017-04-02 05:00 | 4 | 5 | 6.9 | 0
2017-04-02 06:00 | 4 | 6 | 9.2 | 286.6667
2017-04-02 07:00 | 4 | 7 | 9.775 | 286.6667
2017-04-02 08:00 | 4 | 8 | 13.8 | 1666.6667
2017-04-02 09:00 | 4 | 9 | 19.55 | 6160
2017-04-02 10:00 | 4 | 10 | 14.1833 | 1666.6667
2017-04-02 11:00 | 4 | 11 | 10.35 | 873.3333
2017-04-02 12:00 | 4 | 12 | 12.65 | 1666.6667
2017-04-02 13:00 | 4 | 13 | 12.075 | 873.3333
2017-04-02 14:00 | 4 | 14 | 14.95 | 2773.3333
2017-04-02 15:00 | 4 | 15 | 6.9 | 0
2017-04-02 16:00 | 4 | 16 | 8.625 | 286.6667
2017-04-02 17:00 | 4 | 17 | 16.1 | 2773.3333
2017-04-02 18:00 | 4 | 18 | 10.35 | 873.3333
2017-04-02 19:00 | 4 | 19 | 10.35 | 873.3333
2017-04-02 20:00 | 4 | 20 | 8.05 | 286.6667
2017-04-02 21:00 | 4 | 21 | 10.35 | 873.3333
2017-04-02 22:00 | 4 | 22 | 10.925 | 873.3333
2017-04-02 23:00 | 4 | 23 | 8.05 | 286.6667
2017-04-03 | 4 | 0 | 11.5 | 873.3333
2017-04-03 01:00 | 4 | 1 | 9.775 | 286.6667
2017-04-03 02:00 | 4 | 2 | 8.05 | 286.6667
2017-04-03 03:00 | 4 | 3 | 6.9 | 0
2017-04-03 04:00 | 4 | 4 | 6.9 | 0
2017-04-03 05:00 | 4 | 5 | 10.35 | 873.3333
2017-04-03 06:00 | 4 | 6 | 5.75 | 0
2017-04-03 07:00 | 4 | 7 | 6.9 | 0
2017-04-03 08:00 | 4 | 8 | 8.05 | 286.6667
2017-04-03 09:00 | 4 | 9 | 10.35 | 873.3333
2017-04-03 10:00 | 4 | 10 | 8.625 | 286.6667
2017-04-03 11:00 | 4 | 11 | 14.95 | 2773.3333
2017-04-03 12:00 | 4 | 12 | 12.65 | 1666.6667
2017-04-03 13:00 | 4 | 13 | 14.375 | 1666.6667
2017-04-03 14:00 | 4 | 14 | 16.1 | 2773.3333
2017-04-03 15:00 | 4 | 15 | 12.65 | 1666.6667
2017-04-03 16:00 | 4 | 16 | 13.8 | 1666.6667
2017-04-03 17:00 | 4 | 17 | 11.5 | 873.3333
2017-04-03 18:00 | 4 | 18 | 10.35 | 873.3333
2017-04-03 19:00 | 4 | 19 | 9.775 | 286.6667
2017-04-03 20:00 | 4 | 20 | 10.35 | 873.3333
2017-04-03 21:00 | 4 | 21 | 9.2 | 286.6667
2017-04-03 22:00 | 4 | 22 | 9.2 | 286.6667
2017-04-03 23:00 | 4 | 23 | 8.05 | 286.6667
2017-04-04 | 4 | 0 | 10.35 | 873.3333
2017-04-04 01:00 | 4 | 1 | 9.2 | 286.6667
2017-04-04 02:00 | 4 | 2 | 5.75 | 0
2017-04-04 03:00 | 4 | 3 | 6.9 | 0
2017-04-04 04:00 | 4 | 4 | 12.65 | 1666.6667
2017-04-04 05:00 | 4 | 5 | 23 | 7873.3333
2017-04-04 06:00 | 4 | 6 | 24.15 | 9060
2017-04-04 07:00 | 4 | 7 | 27.025 | 9573.3333
2017-04-04 08:00 | 4 | 8 | 26.45 | 9573.3333
2017-04-04 09:00 | 4 | 9 | 29.5167 | 9873.3333
2017-04-04 10:00 | 4 | 10 | 25.99 | 9573.3333
2017-04-04 11:00 | 4 | 11 | 25.3 | 9060
2017-04-04 12:00 | 4 | 12 | 20.4125 | 6160
2017-04-04 13:00 | 4 | 13 | 20.7 | 6160
2017-04-04 14:00 | 4 | 14 | 24.15 | 9060
2017-04-04 15:00 | 4 | 15 | 24.15 | 9060
2017-04-04 16:00 | 4 | 16 | 20.7 | 6160
2017-04-04 17:00 | 4 | 17 | 24.15 | 9060
2017-04-04 18:00 | 4 | 18 | 23.575 | 9060
2017-04-04 19:00 | 4 | 19 | 21.85 | 7873.3333
2017-04-04 20:00 | 4 | 20 | 17.25 | 4266.6667
2017-04-04 21:00 | 4 | 21 | 10.35 | 873.3333
2017-04-04 22:00 | 4 | 22 | 12.88 | 1666.6667
2017-04-04 23:00 | 4 | 23 | 12.65 | 1666.6667
2017-04-05 | 4 | 0 | 10.35 | 873.3333
2017-04-05 01:00 | 4 | 1 | 11.5 | 873.3333
2017-04-05 02:00 | 4 | 2 | 10.35 | 873.3333
2017-04-05 03:00 | 4 | 3 | 12.65 | 1666.6667
2017-04-05 04:00 | 4 | 4 | 12.65 | 1666.6667
2017-04-05 05:00 | 4 | 5 | 12.65 | 1666.6667
2017-04-05 06:00 | 4 | 6 | 9.2 | 286.6667
2017-04-05 07:00 | 4 | 7 | 9.2 | 286.6667
2017-04-05 08:00 | 4 | 8 | 6.9 | 0
2017-04-05 09:00 | 4 | 9 | 9.2 | 286.6667
2017-04-05 10:00 | 4 | 10 | 8.05 | 286.6667
2017-04-05 11:00 | 4 | 11 | 9.2 | 286.6667
2017-04-05 12:00 | 4 | 12 | 10.35 | 873.3333
2017-04-05 13:00 | 4 | 13 | 10.7333 | 873.3333
2017-04-05 14:00 | 4 | 14 | 10.35 | 873.3333
2017-04-05 15:00 | 4 | 15 | 10.35 | 873.3333
2017-04-05 16:00 | 4 | 16 | 10.925 | 873.3333
2017-04-05 17:00 | 4 | 17 | 9.2 | 286.6667
2017-04-05 18:00 | 4 | 18 | 6.9 | 0
2017-04-05 19:00 | 4 | 19 | 8.05 | 286.6667
2017-04-05 20:00 | 4 | 20 | 10.35 | 873.3333
2017-04-05 21:00 | 4 | 21 | 3.45 | 0
2017-04-05 22:00 | 4 | 22 | 1.725 | 0
2017-04-05 23:00 | 4 | 23 | 6.9 | 0
2017-04-06 | 4 | 0 | 11.5 | 873.3333
2017-04-06 01:00 | 4 | 1 | 12.075 | 873.3333
2017-04-06 02:00 | 4 | 2 | 13.8 | 1666.6667
2017-04-06 03:00 | 4 | 3 | 10.35 | 873.3333
2017-04-06 04:00 | 4 | 4 | 10.925 | 873.3333
2017-04-06 05:00 | 4 | 5 | 12.65 | 1666.6667
2017-04-06 06:00 | 4 | 6 | 16.3875 | 2773.3333
2017-04-06 07:00 | 4 | 7 | 15.8125 | 2773.3333
2017-04-06 08:00 | 4 | 8 | 16.1 | 2773.3333
2017-04-06 09:00 | 4 | 9 | 16.675 | 2773.3333
2017-04-06 10:00 | 4 | 10 | 17.5375 | 4266.6667
2017-04-06 11:00 | 4 | 11 | 18.4 | 4266.6667
2017-04-06 12:00 | 4 | 12 | 18.975 | 4266.6667
2017-04-06 13:00 | 4 | 13 | 18.975 | 4266.6667
2017-04-06 14:00 | 4 | 14 | 20.125 | 6160
2017-04-06 15:00 | 4 | 15 | 18.4 | 4266.6667
2017-04-06 16:00 | 4 | 16 | 19.55 | 6160
2017-04-06 17:00 | 4 | 17 | 19.55 | 6160
2017-04-06 18:00 | 4 | 18 | 24.4375 | 9060
2017-04-06 19:00 | 4 | 19 | 26.1625 | 9573.3333
2017-04-06 20:00 | 4 | 20 | 8.05 | 286.6667
2017-04-06 21:00 | 4 | 21 | 6.5167 | 0
2017-04-06 22:00 | 4 | 22 | 16.8667 | 4266.6667
2017-04-06 23:00 | 4 | 23 | 19.55 | 6160
2017-04-07 | 4 | 0 | 16.1 | 2773.3333
2017-04-07 01:00 | 4 | 1 | 16.4833 | 2773.3333
2017-04-07 02:00 | 4 | 2 | 11.5 | 873.3333
2017-04-07 03:00 | 4 | 3 | 10.35 | 873.3333
2017-04-07 04:00 | 4 | 4 | 10.7333 | 873.3333
2017-04-07 05:00 | 4 | 5 | 14.95 | 2773.3333
2017-04-07 06:00 | 4 | 6 | 14.95 | 2773.3333
2017-04-07 07:00 | 4 | 7 | 18.975 | 4266.6667
2017-04-07 08:00 | 4 | 8 | 23 | 7873.3333
2017-04-07 09:00 | 4 | 9 | 25.3 | 9060
2017-04-07 10:00 | 4 | 10 | 27.6 | 9573.3333
2017-04-07 11:00 | 4 | 11 | 20.7 | 6160
2017-04-07 12:00 | 4 | 12 | 23 | 7873.3333
2017-04-07 13:00 | 4 | 13 | 23.575 | 9060
2017-04-07 14:00 | 4 | 14 | 23 | 7873.3333
2017-04-07 15:00 | 4 | 15 | 20.7 | 6160
2017-04-07 16:00 | 4 | 16 | 20.125 | 6160
2017-04-07 17:00 | 4 | 17 | 16.1 | 2773.3333
2017-04-07 18:00 | 4 | 18 | 19.55 | 6160
2017-04-07 19:00 | 4 | 19 | 18.4 | 4266.6667
2017-04-07 20:00 | 4 | 20 | 17.25 | 4266.6667
2017-04-07 21:00 | 4 | 21 | 19.55 | 6160
2017-04-07 22:00 | 4 | 22 | 21.275 | 7873.3333
2017-04-07 23:00 | 4 | 23 | 18.4 | 4266.6667
2017-04-08 | 4 | 0 | 19.55 | 6160
2017-04-08 01:00 | 4 | 1 | 19.55 | 6160
2017-04-08 02:00 | 4 | 2 | 18.4 | 4266.6667
2017-04-08 03:00 | 4 | 3 | 18.4 | 4266.6667
2017-04-08 04:00 | 4 | 4 | 18.975 | 4266.6667
2017-04-08 05:00 | 4 | 5 | 19.55 | 6160
2017-04-08 06:00 | 4 | 6 | 25.3 | 9060
2017-04-08 07:00 | 4 | 7 | 24.725 | 9060
2017-04-08 08:00 | 4 | 8 | 18.4 | 4266.6667
2017-04-08 09:00 | 4 | 9 | 23 | 7873.3333
2017-04-08 10:00 | 4 | 10 | 24.15 | 9060
2017-04-08 11:00 | 4 | 11 | 23 | 7873.3333
2017-04-08 12:00 | 4 | 12 | 24.15 | 9060
2017-04-08 13:00 | 4 | 13 | 25.875 | 9573.3333
2017-04-08 14:00 | 4 | 14 | 23 | 7873.3333
2017-04-08 15:00 | 4 | 15 | 20.7 | 6160
2017-04-08 16:00 | 4 | 16 | 18.975 | 4266.6667
2017-04-08 17:00 | 4 | 17 | 16.1 | 2773.3333
2017-04-08 18:00 | 4 | 18 | 10.35 | 873.3333
2017-04-08 19:00 | 4 | 19 | 10.35 | 873.3333
2017-04-08 20:00 | 4 | 20 | 8.05 | 286.6667
2017-04-08 21:00 | 4 | 21 | 10.35 | 873.3333
2017-04-08 22:00 | 4 | 22 | 11.5 | 873.3333
2017-04-08 23:00 | 4 | 23 | 11.5 | 873.3333
2017-04-09 | 4 | 0 | 5.75 | 0
2017-04-09 01:00 | 4 | 1 | 10.35 | 873.3333
2017-04-09 02:00 | 4 | 2 | 12.65 | 1666.6667
2017-04-09 03:00 | 4 | 3 | 10.35 | 873.3333
2017-04-09 04:00 | 4 | 4 | 12.65 | 1666.6667
2017-04-09 05:00 | 4 | 5 | 10.35 | 873.3333
2017-04-09 06:00 | 4 | 6 | 10.35 | 873.3333
2017-04-09 07:00 | 4 | 7 | 12.65 | 1666.6667
2017-04-09 08:00 | 4 | 8 | 16.1 | 2773.3333
2017-04-09 09:00 | 4 | 9 | 16.1 | 2773.3333
2017-04-09 10:00 | 4 | 10 | 14.375 | 1666.6667
2017-04-09 11:00 | 4 | 11 | 10.35 | 873.3333
2017-04-09 12:00 | 4 | 12 | 10.35 | 873.3333
2017-04-09 13:00 | 4 | 13 | 10.35 | 873.3333
2017-04-09 14:00 | 4 | 14 | 5.75 | 0
2017-04-09 15:00 | 4 | 15 | 9.2 | 286.6667
2017-04-09 16:00 | 4 | 16 | 9.2 | 286.6667
2017-04-09 17:00 | 4 | 17 | 8.05 | 286.6667
2017-04-09 18:00 | 4 | 18 | 6.9 | 0
2017-04-09 19:00 | 4 | 19 | 6.9 | 0
2017-04-09 20:00 | 4 | 20 | 14.95 | 2773.3333
2017-04-09 21:00 | 4 | 21 | 10.35 | 873.3333
2017-04-09 22:00 | 4 | 22 | 12.65 | 1666.6667
2017-04-09 23:00 | 4 | 23 | 12.65 | 1666.6667
2017-04-10 | 4 | 0 | 14.95 | 2773.3333
2017-04-10 01:00 | 4 | 1 | 11.5 | 873.3333
2017-04-10 02:00 | 4 | 2 | 10.35 | 873.3333
2017-04-10 03:00 | 4 | 3 | 8.05 | 286.6667
2017-04-10 04:00 | 4 | 4 | 6.9 | 0
2017-04-10 05:00 | 4 | 5 | 3.45 | 0
2017-04-10 06:00 | 4 | 6 | 9.2 | 286.6667
2017-04-10 07:00 | 4 | 7 | 10.925 | 873.3333
2017-04-10 08:00 | 4 | 8 | 14.95 | 2773.3333
2017-04-10 09:00 | 4 | 9 | 19.55 | 6160
2017-04-10 10:00 | 4 | 10 | 18.4 | 4266.6667
2017-04-10 11:00 | 4 | 11 | 18.4 | 4266.6667
2017-04-10 12:00 | 4 | 12 | 19.55 | 6160
2017-04-10 13:00 | 4 | 13 | 24.15 | 9060
2017-04-10 14:00 | 4 | 14 | 20.7 | 6160
2017-04-10 15:00 | 4 | 15 | 19.55 | 6160
2017-04-10 16:00 | 4 | 16 | 18.4 | 4266.6667
2017-04-10 17:00 | 4 | 17 | 18.4 | 4266.6667
2017-04-10 18:00 | 4 | 18 | 11.5 | 873.3333
2017-04-10 19:00 | 4 | 19 | 12.075 | 873.3333
2017-04-10 20:00 | 4 | 20 | 10.35 | 873.3333
2017-04-10 21:00 | 4 | 21 | 10.35 | 873.3333
2017-04-10 22:00 | 4 | 22 | 12.65 | 1666.6667
2017-04-10 23:00 | 4 | 23 | 17.25 | 4266.6667
2017-04-11 | 4 | 0 | 11.5 | 873.3333
2017-04-11 01:00 | 4 | 1 | 11.5 | 873.3333
2017-04-11 02:00 | 4 | 2 | 9.2 | 286.6667
2017-04-11 03:00 | 4 | 3 | 9.2 | 286.6667
2017-04-11 04:00 | 4 | 4 | 10.35 | 873.3333
2017-04-11 05:00 | 4 | 5 | 16.1 | 2773.3333
2017-04-11 06:00 | 4 | 6 | 16.1 | 2773.3333
2017-04-11 07:00 | 4 | 7 | 13.225 | 1666.6667
2017-04-11 08:00 | 4 | 8 | 8.05 | 286.6667
2017-04-11 09:00 | 4 | 9 | 11.5 | 873.3333
2017-04-11 10:00 | 4 | 10 | 10.925 | 873.3333
2017-04-11 11:00 | 4 | 11 | 9.2 | 286.6667
2017-04-11 12:00 | 4 | 12 | 11.5 | 873.3333
2017-04-11 13:00 | 4 | 13 | 13.225 | 1666.6667
2017-04-11 14:00 | 4 | 14 | 16.1 | 2773.3333
2017-04-11 15:00 | 4 | 15 | 17.25 | 4266.6667
2017-04-11 16:00 | 4 | 16 | 17.825 | 4266.6667
2017-04-11 17:00 | 4 | 17 | 14.95 | 2773.3333
2017-04-11 18:00 | 4 | 18 | 16.1 | 2773.3333
2017-04-11 19:00 | 4 | 19 | 13.8 | 1666.6667
2017-04-11 20:00 | 4 | 20 | 12.65 | 1666.6667
2017-04-11 21:00 | 4 | 21 | 14.95 | 2773.3333
2017-04-11 22:00 | 4 | 22 | 12.075 | 873.3333
2017-04-11 23:00 | 4 | 23 | 11.5 | 873.3333
2017-04-12 | 4 | 0 | 10.35 | 873.3333
2017-04-12 01:00 | 4 | 1 | 8.625 | 286.6667
2017-04-12 02:00 | 4 | 2 | 3.45 | 0
2017-04-12 03:00 | 4 | 3 | 0 | 0
2017-04-12 04:00 | 4 | 4 | 2.875 | 0
2017-04-12 05:00 | 4 | 5 | 0 | 0
2017-04-12 06:00 | 4 | 6 | 6.9 | 0
2017-04-12 07:00 | 4 | 7 | 8.625 | 286.6667
2017-04-12 08:00 | 4 | 8 | 9.2 | 286.6667
2017-04-12 09:00 | 4 | 9 | 12.65 | 1666.6667
2017-04-12 10:00 | 4 | 10 | 12.075 | 873.3333
2017-04-12 11:00 | 4 | 11 | 12.65 | 1666.6667
2017-04-12 12:00 | 4 | 12 | 8.05 | 286.6667
2017-04-12 13:00 | 4 | 13 | 7.475 | 0
2017-04-12 14:00 | 4 | 14 | 0 | 0
2017-04-12 15:00 | 4 | 15 | 9.2 | 286.6667
2017-04-12 16:00 | 4 | 16 | 8.05 | 286.6667
2017-04-12 17:00 | 4 | 17 | 5.75 | 0
2017-04-12 18:00 | 4 | 18 | 14.95 | 2773.3333
2017-04-12 19:00 | 4 | 19 | 15.525 | 2773.3333
2017-04-12 20:00 | 4 | 20 | 11.5 | 873.3333
2017-04-12 21:00 | 4 | 21 | 16.1 | 2773.3333
2017-04-12 22:00 | 4 | 22 | 13.8 | 1666.6667
2017-04-12 23:00 | 4 | 23 | 18.4 | 4266.6667
2017-04-13 | 4 | 0 | 17.25 | 4266.6667
2017-04-13 01:00 | 4 | 1 | 16.675 | 2773.3333
2017-04-13 02:00 | 4 | 2 | 9.2 | 286.6667
2017-04-13 03:00 | 4 | 3 | 8.05 | 286.6667
2017-04-13 04:00 | 4 | 4 | 9.2 | 286.6667
2017-04-13 05:00 | 4 | 5 | 17.25 | 4266.6667
2017-04-13 06:00 | 4 | 6 | 17.25 | 4266.6667
2017-04-13 07:00 | 4 | 7 | 14.95 | 2773.3333
2017-04-13 08:00 | 4 | 8 | 12.65 | 1666.6667
2017-04-13 09:00 | 4 | 9 | 12.65 | 1666.6667
2017-04-13 10:00 | 4 | 10 | 13.8 | 1666.6667
2017-04-13 11:00 | 4 | 11 | 18.4 | 4266.6667
2017-04-13 12:00 | 4 | 12 | 12.65 | 1666.6667
2017-04-13 13:00 | 4 | 13 | 13.8 | 1666.6667
2017-04-13 14:00 | 4 | 14 | 19.55 | 6160
2017-04-13 15:00 | 4 | 15 | 18.4 | 4266.6667
2017-04-13 16:00 | 4 | 16 | 18.4 | 4266.6667
2017-04-13 17:00 | 4 | 17 | 17.25 | 4266.6667
2017-04-13 18:00 | 4 | 18 | 14.95 | 2773.3333
2017-04-13 19:00 | 4 | 19 | 12.075 | 873.3333
2017-04-13 20:00 | 4 | 20 | 6.9 | 0
2017-04-13 21:00 | 4 | 21 | 5.75 | 0
2017-04-13 22:00 | 4 | 22 | 4.6 | 0
2017-04-13 23:00 | 4 | 23 | 0 | 0
2017-04-14 | 4 | 0 | 6.9 | 0
2017-04-14 01:00 | 4 | 1 | 8.05 | 286.6667
2017-04-14 02:00 | 4 | 2 | 10.35 | 873.3333
2017-04-14 03:00 | 4 | 3 | 9.2 | 286.6667
2017-04-14 04:00 | 4 | 4 | 9.775 | 286.6667
2017-04-14 05:00 | 4 | 5 | 10.35 | 873.3333
2017-04-14 06:00 | 4 | 6 | 9.2 | 286.6667
2017-04-14 07:00 | 4 | 7 | 7.475 | 0
2017-04-14 08:00 | 4 | 8 | 6.9 | 0
2017-04-14 09:00 | 4 | 9 | 9.2 | 286.6667
2017-04-14 10:00 | 4 | 10 | 9.2 | 286.6667
2017-04-14 11:00 | 4 | 11 | 17.25 | 4266.6667
2017-04-14 12:00 | 4 | 12 | 18.4 | 4266.6667
2017-04-14 13:00 | 4 | 13 | 17.825 | 4266.6667
2017-04-14 14:00 | 4 | 14 | 17.25 | 4266.6667
2017-04-14 15:00 | 4 | 15 | 16.1 | 2773.3333
2017-04-14 16:00 | 4 | 16 | 13.225 | 1666.6667
2017-04-14 17:00 | 4 | 17 | 10.35 | 873.3333
2017-04-14 18:00 | 4 | 18 | 9.2 | 286.6667
2017-04-14 19:00 | 4 | 19 | 8.625 | 286.6667
2017-04-14 20:00 | 4 | 20 | 9.2 | 286.6667
2017-04-14 21:00 | 4 | 21 | 11.5 | 873.3333
2017-04-14 22:00 | 4 | 22 | 9.775 | 286.6667
2017-04-14 23:00 | 4 | 23 | 8.05 | 286.6667
2017-04-15 | 4 | 0 | 8.05 | 286.6667
2017-04-15 01:00 | 4 | 1 | 9.775 | 286.6667
2017-04-15 02:00 | 4 | 2 | 10.35 | 873.3333
2017-04-15 03:00 | 4 | 3 | 5.75 | 0
2017-04-15 04:00 | 4 | 4 | 5.75 | 0
2017-04-15 05:00 | 4 | 5 | 9.2 | 286.6667
2017-04-15 06:00 | 4 | 6 | 8.05 | 286.6667
2017-04-15 07:00 | 4 | 7 | 8.05 | 286.6667
2017-04-15 08:00 | 4 | 8 | 9.2 | 286.6667
2017-04-15 09:00 | 4 | 9 | 17.25 | 4266.6667
2017-04-15 10:00 | 4 | 10 | 16.675 | 2773.3333
2017-04-15 11:00 | 4 | 11 | 19.55 | 6160
2017-04-15 12:00 | 4 | 12 | 20.7 | 6160
2017-04-15 13:00 | 4 | 13 | 25.3 | 9060
2017-04-15 14:00 | 4 | 14 | 24.15 | 9060
2017-04-15 15:00 | 4 | 15 | 29.9 | 9873.3333
2017-04-15 16:00 | 4 | 16 | 32.775 | 10000
2017-04-15 17:00 | 4 | 17 | 20.7 | 6160
2017-04-15 18:00 | 4 | 18 | 28.75 | 9873.3333
2017-04-15 19:00 | 4 | 19 | 25.875 | 9573.3333
2017-04-15 20:00 | 4 | 20 | 21.85 | 7873.3333
2017-04-15 21:00 | 4 | 21 | 27.6 | 9573.3333
2017-04-15 22:00 | 4 | 22 | 25.3 | 9060
2017-04-15 23:00 | 4 | 23 | 22.425 | 7873.3333
2017-04-16 | 4 | 0 | 26.45 | 9573.3333
2017-04-16 01:00 | 4 | 1 | 22.425 | 7873.3333
2017-04-16 02:00 | 4 | 2 | 19.55 | 6160
2017-04-16 03:00 | 4 | 3 | 18.4 | 4266.6667
2017-04-16 04:00 | 4 | 4 | 17.25 | 4266.6667
2017-04-16 05:00 | 4 | 5 | 18.4 | 4266.6667
2017-04-16 06:00 | 4 | 6 | 16.1 | 2773.3333
2017-04-16 07:00 | 4 | 7 | 15.525 | 2773.3333
2017-04-16 08:00 | 4 | 8 | 14.95 | 2773.3333
2017-04-16 09:00 | 4 | 9 | 20.7 | 6160
2017-04-16 10:00 | 4 | 10 | 20.7 | 6160
2017-04-16 11:00 | 4 | 11 | 26.45 | 9573.3333
2017-04-16 12:00 | 4 | 12 | 23 | 7873.3333
2017-04-16 13:00 | 4 | 13 | 24.15 | 9060
2017-04-16 14:00 | 4 | 14 | 25.3 | 9060
2017-04-16 15:00 | 4 | 15 | 24.15 | 9060
2017-04-16 16:00 | 4 | 16 | 23.575 | 9060
2017-04-16 17:00 | 4 | 17 | 23 | 7873.3333
2017-04-16 18:00 | 4 | 18 | 23 | 7873.3333
2017-04-16 19:00 | 4 | 19 | 23 | 7873.3333
2017-04-16 20:00 | 4 | 20 | 19.55 | 6160
2017-04-16 21:00 | 4 | 21 | 16.1 | 2773.3333
2017-04-16 22:00 | 4 | 22 | 16.675 | 2773.3333
2017-04-16 23:00 | 4 | 23 | 14.95 | 2773.3333
2017-04-17 | 4 | 0 | 16.1 | 2773.3333
2017-04-17 01:00 | 4 | 1 | 15.525 | 2773.3333
2017-04-17 02:00 | 4 | 2 | 16.1 | 2773.3333
2017-04-17 03:00 | 4 | 3 | 12.65 | 1666.6667
2017-04-17 04:00 | 4 | 4 | 12.65 | 1666.6667
2017-04-17 05:00 | 4 | 5 | 10.35 | 873.3333
2017-04-17 06:00 | 4 | 6 | 14.95 | 2773.3333
2017-04-17 07:00 | 4 | 7 | 17.25 | 4266.6667
2017-04-17 08:00 | 4 | 8 | 17.25 | 4266.6667
2017-04-17 09:00 | 4 | 9 | 18.4 | 4266.6667
2017-04-17 10:00 | 4 | 10 | 21.85 | 7873.3333
2017-04-17 11:00 | 4 | 11 | 16.1 | 2773.3333
2017-04-17 12:00 | 4 | 12 | 24.15 | 9060
2017-04-17 13:00 | 4 | 13 | 19.55 | 6160
2017-04-17 14:00 | 4 | 14 | 14.95 | 2773.3333
2017-04-17 15:00 | 4 | 15 | 18.4 | 4266.6667
2017-04-17 16:00 | 4 | 16 | 14.375 | 1666.6667
2017-04-17 17:00 | 4 | 17 | 11.5 | 873.3333
2017-04-17 18:00 | 4 | 18 | 18.4 | 4266.6667
2017-04-17 19:00 | 4 | 19 | 17.825 | 4266.6667
2017-04-17 20:00 | 4 | 20 | 11.5 | 873.3333
2017-04-17 21:00 | 4 | 21 | 20.7 | 6160
2017-04-17 22:00 | 4 | 22 | 19.55 | 6160
2017-04-17 23:00 | 4 | 23 | 17.25 | 4266.6667
2017-04-18 | 4 | 0 | 12.65 | 1666.6667
2017-04-18 01:00 | 4 | 1 | 12.65 | 1666.6667
2017-04-18 02:00 | 4 | 2 | 16.1 | 2773.3333
2017-04-18 03:00 | 4 | 3 | 12.65 | 1666.6667
2017-04-18 04:00 | 4 | 4 | 13.8 | 1666.6667
2017-04-18 05:00 | 4 | 5 | 16.1 | 2773.3333
2017-04-18 06:00 | 4 | 6 | 11.5 | 873.3333
2017-04-18 07:00 | 4 | 7 | 11.5 | 873.3333
2017-04-18 08:00 | 4 | 8 | 14.95 | 2773.3333
2017-04-18 09:00 | 4 | 9 | 19.55 | 6160
2017-04-18 10:00 | 4 | 10 | 19.55 | 6160
2017-04-18 11:00 | 4 | 11 | 20.7 | 6160
2017-04-18 12:00 | 4 | 12 | 19.55 | 6160
2017-04-18 13:00 | 4 | 13 | 20.125 | 6160
2017-04-18 14:00 | 4 | 14 | 18.4 | 4266.6667
2017-04-18 15:00 | 4 | 15 | 18.4 | 4266.6667
2017-04-18 16:00 | 4 | 16 | 18.975 | 4266.6667
2017-04-18 17:00 | 4 | 17 | 18.4 | 4266.6667
2017-04-18 18:00 | 4 | 18 | 18.4 | 4266.6667
2017-04-18 19:00 | 4 | 19 | 14.375 | 1666.6667
2017-04-18 20:00 | 4 | 20 | 12.075 | 873.3333
2017-04-18 21:00 | 4 | 21 | 9.2 | 286.6667
2017-04-18 22:00 | 4 | 22 | 8.05 | 286.6667
2017-04-18 23:00 | 4 | 23 | 11.5 | 873.3333
2017-04-19 | 4 | 0 | 12.65 | 1666.6667
2017-04-19 01:00 | 4 | 1 | 10.925 | 873.3333
2017-04-19 02:00 | 4 | 2 | 10.35 | 873.3333
2017-04-19 03:00 | 4 | 3 | 10.35 | 873.3333
2017-04-19 04:00 | 4 | 4 | 9.9667 | 286.6667
2017-04-19 05:00 | 4 | 5 | 6.9 | 0
2017-04-19 06:00 | 4 | 6 | 8.05 | 286.6667
2017-04-19 07:00 | 4 | 7 | 8.625 | 286.6667
2017-04-19 08:00 | 4 | 8 | 10.35 | 873.3333
2017-04-19 09:00 | 4 | 9 | 13.225 | 1666.6667
2017-04-19 10:00 | 4 | 10 | 15.525 | 2773.3333
2017-04-19 11:00 | 4 | 11 | 18.4 | 4266.6667
2017-04-19 12:00 | 4 | 12 | 19.55 | 6160
2017-04-19 13:00 | 4 | 13 | 21.275 | 7873.3333
2017-04-19 14:00 | 4 | 14 | 24.15 | 9060
2017-04-19 15:00 | 4 | 15 | 19.55 | 6160
2017-04-19 16:00 | 4 | 16 | 18.4 | 4266.6667
2017-04-19 17:00 | 4 | 17 | 18.4 | 4266.6667
2017-04-19 18:00 | 4 | 18 | 17.25 | 4266.6667
2017-04-19 19:00 | 4 | 19 | 16.1 | 2773.3333
2017-04-19 20:00 | 4 | 20 | 16.675 | 2773.3333
2017-04-19 21:00 | 4 | 21 | 16.1 | 2773.3333
2017-04-19 22:00 | 4 | 22 | 15.525 | 2773.3333
2017-04-19 23:00 | 4 | 23 | 11.5 | 873.3333
2017-04-20 | 4 | 0 | 14.95 | 2773.3333
2017-04-20 01:00 | 4 | 1 | 13.8 | 1666.6667
2017-04-20 02:00 | 4 | 2 | 9.2 | 286.6667
2017-04-20 03:00 | 4 | 3 | 8.05 | 286.6667
2017-04-20 04:00 | 4 | 4 | 7.6667 | 0
2017-04-20 05:00 | 4 | 5 | 6.325 | 0
2017-04-20 06:00 | 4 | 6 | 5.75 | 0
2017-04-20 07:00 | 4 | 7 | 5.75 | 0
2017-04-20 08:00 | 4 | 8 | 1.725 | 0
2017-04-20 09:00 | 4 | 9 | 8.05 | 286.6667
2017-04-20 10:00 | 4 | 10 | 7.2833 | 0
2017-04-20 11:00 | 4 | 11 | 10.35 | 873.3333
2017-04-20 12:00 | 4 | 12 | 12.65 | 1666.6667
2017-04-20 13:00 | 4 | 13 | 14.375 | 1666.6667
2017-04-20 14:00 | 4 | 14 | 18.4 | 4266.6667
2017-04-20 15:00 | 4 | 15 | 15.525 | 2773.3333
2017-04-20 16:00 | 4 | 16 | 13.8 | 1666.6667
2017-04-20 17:00 | 4 | 17 | 17.6333 | 4266.6667
2017-04-20 18:00 | 4 | 18 | 14.375 | 1666.6667
2017-04-20 19:00 | 4 | 19 | 12.2667 | 873.3333
2017-04-20 20:00 | 4 | 20 | 14.95 | 2773.3333
2017-04-20 21:00 | 4 | 21 | 18.4 | 4266.6667
2017-04-20 22:00 | 4 | 22 | 16.1 | 2773.3333
2017-04-20 23:00 | 4 | 23 | 11.5 | 873.3333
2017-04-21 | 4 | 0 | 16.1 | 2773.3333
2017-04-21 01:00 | 4 | 1 | 16.1 | 2773.3333
2017-04-21 02:00 | 4 | 2 | 18.4 | 4266.6667
2017-04-21 03:00 | 4 | 3 | 18.7833 | 4266.6667
2017-04-21 04:00 | 4 | 4 | 14.95 | 2773.3333
2017-04-21 05:00 | 4 | 5 | 14.95 | 2773.3333
2017-04-21 06:00 | 4 | 6 | 18.4 | 4266.6667
2017-04-21 07:00 | 4 | 7 | 18.7833 | 4266.6667
2017-04-21 08:00 | 4 | 8 | 18.4 | 4266.6667
2017-04-21 09:00 | 4 | 9 | 20.125 | 6160
2017-04-21 10:00 | 4 | 10 | 19.8375 | 6160
2017-04-21 11:00 | 4 | 11 | 18.975 | 4266.6667
2017-04-21 12:00 | 4 | 12 | 19.55 | 6160
2017-04-21 13:00 | 4 | 13 | 19.1667 | 6160
2017-04-21 14:00 | 4 | 14 | 19.55 | 6160
2017-04-21 15:00 | 4 | 15 | 17.6333 | 4266.6667
2017-04-21 16:00 | 4 | 16 | 18.4 | 4266.6667
2017-04-21 17:00 | 4 | 17 | 16.675 | 2773.3333
2017-04-21 18:00 | 4 | 18 | 15.8125 | 2773.3333
2017-04-21 19:00 | 4 | 19 | 11.5 | 873.3333
2017-04-21 20:00 | 4 | 20 | 11.5 | 873.3333
2017-04-21 21:00 | 4 | 21 | 11.5 | 873.3333
2017-04-21 22:00 | 4 | 22 | 12.65 | 1666.6667
2017-04-21 23:00 | 4 | 23 | 11.5 | 873.3333
2017-04-22 | 4 | 0 | 13.4167 | 1666.6667
2017-04-22 01:00 | 4 | 1 | 14.1833 | 1666.6667
2017-04-22 02:00 | 4 | 2 | 12.65 | 1666.6667
2017-04-22 03:00 | 4 | 3 | 12.65 | 1666.6667
2017-04-22 04:00 | 4 | 4 | 12.65 | 1666.6667
2017-04-22 05:00 | 4 | 5 | 12.65 | 1666.6667
2017-04-22 06:00 | 4 | 6 | 11.1167 | 873.3333
2017-04-22 07:00 | 4 | 7 | 10.925 | 873.3333
2017-04-22 08:00 | 4 | 8 | 6.9 | 0
2017-04-22 09:00 | 4 | 9 | 14.95 | 2773.3333
2017-04-22 10:00 | 4 | 10 | 13.8 | 1666.6667
2017-04-22 11:00 | 4 | 11 | 11.5 | 873.3333
2017-04-22 12:00 | 4 | 12 | 10.925 | 873.3333
2017-04-22 13:00 | 4 | 13 | 11.5 | 873.3333
2017-04-22 14:00 | 4 | 14 | 12.65 | 1666.6667
2017-04-22 15:00 | 4 | 15 | 10.35 | 873.3333
2017-04-22 16:00 | 4 | 16 | 10.7333 | 873.3333
2017-04-22 17:00 | 4 | 17 | 10.35 | 873.3333
2017-04-22 18:00 | 4 | 18 | 10.35 | 873.3333
2017-04-22 19:00 | 4 | 19 | 6.9 | 0
2017-04-22 20:00 | 4 | 20 | 5.175 | 0
2017-04-22 21:00 | 4 | 21 | 5.75 | 0
2017-04-22 22:00 | 4 | 22 | 5.75 | 0
2017-04-22 23:00 | 4 | 23 | 0 | 0
2017-04-23 | 4 | 0 | 3.0667 | 0
2017-04-23 01:00 | 4 | 1 | 6.9 | 0
2017-04-23 02:00 | 4 | 2 | 11.5 | 873.3333
2017-04-23 03:00 | 4 | 3 | 10.35 | 873.3333
2017-04-23 04:00 | 4 | 4 | 12.65 | 1666.6667
2017-04-23 05:00 | 4 | 5 | 11.5 | 873.3333
2017-04-23 06:00 | 4 | 6 | 12.65 | 1666.6667
2017-04-23 07:00 | 4 | 7 | 10.925 | 873.3333
2017-04-23 08:00 | 4 | 8 | 8.05 | 286.6667
2017-04-23 09:00 | 4 | 9 | 11.5 | 873.3333
2017-04-23 10:00 | 4 | 10 | 12.075 | 873.3333
2017-04-23 11:00 | 4 | 11 | 12.65 | 1666.6667
2017-04-23 12:00 | 4 | 12 | 16.1 | 2773.3333
2017-04-23 13:00 | 4 | 13 | 17.25 | 4266.6667
2017-04-23 14:00 | 4 | 14 | 16.1 | 2773.3333
2017-04-23 15:00 | 4 | 15 | 23 | 7873.3333
2017-04-23 16:00 | 4 | 16 | 21.275 | 7873.3333
2017-04-23 17:00 | 4 | 17 | 24.15 | 9060
2017-04-23 18:00 | 4 | 18 | 17.25 | 4266.6667
2017-04-23 19:00 | 4 | 19 | 16.1 | 2773.3333
2017-04-23 20:00 | 4 | 20 | 12.65 | 1666.6667
2017-04-23 21:00 | 4 | 21 | 12.65 | 1666.6667
2017-04-23 22:00 | 4 | 22 | 11.5 | 873.3333
2017-04-23 23:00 | 4 | 23 | 11.5 | 873.3333
2017-04-24 | 4 | 0 | 9.2 | 286.6667
2017-04-24 01:00 | 4 | 1 | 8.625 | 286.6667
2017-04-24 02:00 | 4 | 2 | 9.2 | 286.6667
2017-04-24 03:00 | 4 | 3 | 11.5 | 873.3333
2017-04-24 04:00 | 4 | 4 | 13.225 | 1666.6667
2017-04-24 05:00 | 4 | 5 | 12.65 | 1666.6667
2017-04-24 06:00 | 4 | 6 | 5.75 | 0
2017-04-24 07:00 | 4 | 7 | 6.325 | 0
2017-04-24 08:00 | 4 | 8 | 5.75 | 0
2017-04-24 09:00 | 4 | 9 | 10.35 | 873.3333
2017-04-24 10:00 | 4 | 10 | 8.05 | 286.6667
2017-04-24 11:00 | 4 | 11 | 9.2 | 286.6667
2017-04-24 12:00 | 4 | 12 | 10.35 | 873.3333
2017-04-24 13:00 | 4 | 13 | 10.35 | 873.3333
2017-04-24 14:00 | 4 | 14 | 14.95 | 2773.3333
2017-04-24 15:00 | 4 | 15 | 17.25 | 4266.6667
2017-04-24 16:00 | 4 | 16 | 14.375 | 1666.6667
2017-04-24 17:00 | 4 | 17 | 12.65 | 1666.6667
2017-04-24 18:00 | 4 | 18 | 11.5 | 873.3333
2017-04-24 19:00 | 4 | 19 | 10.35 | 873.3333
2017-04-24 20:00 | 4 | 20 | 6.9 | 0
2017-04-24 21:00 | 4 | 21 | 5.75 | 0
2017-04-24 22:00 | 4 | 22 | 6.325 | 0
2017-04-24 23:00 | 4 | 23 | 8.05 | 286.6667
2017-04-25 | 4 | 0 | 10.35 | 873.3333
2017-04-25 01:00 | 4 | 1 | 16.1 | 2773.3333
2017-04-25 02:00 | 4 | 2 | 11.5 | 873.3333
2017-04-25 03:00 | 4 | 3 | 12.65 | 1666.6667
2017-04-25 04:00 | 4 | 4 | 13.4167 | 1666.6667
2017-04-25 05:00 | 4 | 5 | 13.8 | 1666.6667
2017-04-25 06:00 | 4 | 6 | 18.4 | 4266.6667
2017-04-25 07:00 | 4 | 7 | 18.4 | 4266.6667
2017-04-25 08:00 | 4 | 8 | 20.7 | 6160
2017-04-25 09:00 | 4 | 9 | 23 | 7873.3333
2017-04-25 10:00 | 4 | 10 | 23.575 | 9060
2017-04-25 11:00 | 4 | 11 | 23 | 7873.3333
2017-04-25 12:00 | 4 | 12 | 25.3 | 9060
2017-04-25 13:00 | 4 | 13 | 21.85 | 7873.3333
2017-04-25 14:00 | 4 | 14 | 21.275 | 7873.3333
2017-04-25 15:00 | 4 | 15 | 23 | 7873.3333
2017-04-25 16:00 | 4 | 16 | 24.15 | 9060
2017-04-25 17:00 | 4 | 17 | 23 | 7873.3333
2017-04-25 18:00 | 4 | 18 | 20.125 | 6160
2017-04-25 19:00 | 4 | 19 | 17.825 | 4266.6667
2017-04-25 20:00 | 4 | 20 | 18.4 | 4266.6667
2017-04-25 21:00 | 4 | 21 | 16.1 | 2773.3333
2017-04-25 22:00 | 4 | 22 | 15.525 | 2773.3333
2017-04-25 23:00 | 4 | 23 | 10.35 | 873.3333
2017-04-26 | 4 | 0 | 13.6083 | 1666.6667
2017-04-26 01:00 | 4 | 1 | 13.8 | 1666.6667
2017-04-26 02:00 | 4 | 2 | 14.95 | 2773.3333
2017-04-26 03:00 | 4 | 3 | 23 | 7873.3333
2017-04-26 04:00 | 4 | 4 | 18.7833 | 4266.6667
2017-04-26 05:00 | 4 | 5 | 15.3333 | 2773.3333
2017-04-26 06:00 | 4 | 6 | 11.5 | 873.3333
2017-04-26 07:00 | 4 | 7 | 11.5 | 873.3333
2017-04-26 08:00 | 4 | 8 | 12.65 | 1666.6667
2017-04-26 09:00 | 4 | 9 | 12.65 | 1666.6667
2017-04-26 10:00 | 4 | 10 | 12.2667 | 873.3333
2017-04-26 11:00 | 4 | 11 | 10.35 | 873.3333
2017-04-26 12:00 | 4 | 12 | 12.65 | 1666.6667
2017-04-26 13:00 | 4 | 13 | 9.2 | 286.6667
2017-04-26 14:00 | 4 | 14 | 6.9 | 0
2017-04-26 15:00 | 4 | 15 | 8.05 | 286.6667
2017-04-26 16:00 | 4 | 16 | 8.4333 | 286.6667
2017-04-26 17:00 | 4 | 17 | 9.2 | 286.6667
2017-04-26 18:00 | 4 | 18 | 11.5 | 873.3333
2017-04-26 19:00 | 4 | 19 | 9.775 | 286.6667
2017-04-26 20:00 | 4 | 20 | 9.2 | 286.6667
2017-04-26 21:00 | 4 | 21 | 5.75 | 0
2017-04-26 22:00 | 4 | 22 | 6.1333 | 0
2017-04-26 23:00 | 4 | 23 | 7.475 | 0
2017-04-27 | 4 | 0 | 5.75 | 0
2017-04-27 01:00 | 4 | 1 | 4.6 | 0
2017-04-27 02:00 | 4 | 2 | 3.45 | 0
2017-04-27 03:00 | 4 | 3 | 5.75 | 0
2017-04-27 04:00 | 4 | 4 | 7.475 | 0
2017-04-27 05:00 | 4 | 5 | 6.9 | 0
2017-04-27 06:00 | 4 | 6 | 5.75 | 0
2017-04-27 07:00 | 4 | 7 | 6.325 | 0
2017-04-27 08:00 | 4 | 8 | 6.9 | 0
2017-04-27 09:00 | 4 | 9 | 6.325 | 0
2017-04-27 10:00 | 4 | 10 | 6.9 | 0
2017-04-27 11:00 | 4 | 11 | 10.35 | 873.3333
2017-04-27 12:00 | 4 | 12 | 10.35 | 873.3333
2017-04-27 13:00 | 4 | 13 | 11.5 | 873.3333
2017-04-27 14:00 | 4 | 14 | 10.35 | 873.3333
2017-04-27 15:00 | 4 | 15 | 14.95 | 2773.3333
2017-04-27 16:00 | 4 | 16 | 13.225 | 1666.6667
2017-04-27 17:00 | 4 | 17 | 9.2 | 286.6667
2017-04-27 18:00 | 4 | 18 | 9.775 | 286.6667
2017-04-27 19:00 | 4 | 19 | 9.2 | 286.6667
2017-04-27 20:00 | 4 | 20 | 0 | 0
2017-04-27 21:00 | 4 | 21 | 3.45 | 0
2017-04-27 22:00 | 4 | 22 | 5.75 | 0
2017-04-27 23:00 | 4 | 23 | 8.05 | 286.6667
2017-04-28 | 4 | 0 | 6.9 | 0
2017-04-28 01:00 | 4 | 1 | 6.9 | 0
2017-04-28 02:00 | 4 | 2 | 5.75 | 0
2017-04-28 03:00 | 4 | 3 | 3.45 | 0
2017-04-28 04:00 | 4 | 4 | 6.325 | 0
2017-04-28 05:00 | 4 | 5 | 6.325 | 0
2017-04-28 06:00 | 4 | 6 | 5.75 | 0
2017-04-28 07:00 | 4 | 7 | 7.7625 | 0
2017-04-28 08:00 | 4 | 8 | 9.2 | 286.6667
2017-04-28 09:00 | 4 | 9 | 9.2 | 286.6667
2017-04-28 10:00 | 4 | 10 | 9.5833 | 286.6667
2017-04-28 11:00 | 4 | 11 | 11.5 | 873.3333
2017-04-28 12:00 | 4 | 12 | 9.2 | 286.6667
2017-04-28 13:00 | 4 | 13 | 8.05 | 286.6667
2017-04-28 14:00 | 4 | 14 | 8.05 | 286.6667
2017-04-28 15:00 | 4 | 15 | 10.35 | 873.3333
2017-04-28 16:00 | 4 | 16 | 12.65 | 1666.6667
2017-04-28 17:00 | 4 | 17 | 14.95 | 2773.3333
2017-04-28 18:00 | 4 | 18 | 9.2 | 286.6667
2017-04-28 19:00 | 4 | 19 | 9.2 | 286.6667
2017-04-28 20:00 | 4 | 20 | 11.5 | 873.3333
2017-04-28 21:00 | 4 | 21 | 6.9 | 0
2017-04-28 22:00 | 4 | 22 | 8.625 | 286.6667
2017-04-28 23:00 | 4 | 23 | 11.5 | 873.3333
2017-04-29 | 4 | 0 | 8.05 | 286.6667
2017-04-29 01:00 | 4 | 1 | 9.2 | 286.6667
2017-04-29 02:00 | 4 | 2 | 6.9 | 0
2017-04-29 03:00 | 4 | 3 | 9.2 | 286.6667
2017-04-29 04:00 | 4 | 4 | 8.05 | 286.6667
2017-04-29 05:00 | 4 | 5 | 8.05 | 286.6667
2017-04-29 06:00 | 4 | 6 | 5.75 | 0
2017-04-29 07:00 | 4 | 7 | 6.325 | 0
2017-04-29 08:00 | 4 | 8 | 9.2 | 286.6667
2017-04-29 09:00 | 4 | 9 | 14.95 | 2773.3333
2017-04-29 10:00 | 4 | 10 | 17.25 | 4266.6667
2017-04-29 11:00 | 4 | 11 | 18.4 | 4266.6667
2017-04-29 12:00 | 4 | 12 | 20.7 | 6160
2017-04-29 13:00 | 4 | 13 | 21.85 | 7873.3333
2017-04-29 14:00 | 4 | 14 | 24.15 | 9060
2017-04-29 15:00 | 4 | 15 | 19.55 | 6160
2017-04-29 16:00 | 4 | 16 | 23.575 | 9060
2017-04-29 17:00 | 4 | 17 | 19.55 | 6160
2017-04-29 18:00 | 4 | 18 | 17.25 | 4266.6667
2017-04-29 19:00 | 4 | 19 | 20.7 | 6160
2017-04-29 20:00 | 4 | 20 | 16.1 | 2773.3333
2017-04-29 21:00 | 4 | 21 | 17.25 | 4266.6667
2017-04-29 22:00 | 4 | 22 | 16.1 | 2773.3333
2017-04-29 23:00 | 4 | 23 | 16.1 | 2773.3333
2017-04-30 | 4 | 0 | 16.1 | 2773.3333
2017-04-30 01:00 | 4 | 1 | 18.4 | 4266.6667
2017-04-30 02:00 | 4 | 2 | 14.95 | 2773.3333
2017-04-30 03:00 | 4 | 3 | 16.1 | 2773.3333
2017-04-30 04:00 | 4 | 4 | 14.375 | 1666.6667
2017-04-30 05:00 | 4 | 5 | 14.95 | 2773.3333
2017-04-30 06:00 | 4 | 6 | 10.35 | 873.3333
2017-04-30 07:00 | 4 | 7 | 14.375 | 1666.6667
2017-04-30 08:00 | 4 | 8 | 19.55 | 6160
2017-04-30 09:00 | 4 | 9 | 18.4 | 4266.6667
2017-04-30 10:00 | 4 | 10 | 17.25 | 4266.6667
2017-04-30 11:00 | 4 | 11 | 16.1 | 2773.3333
2017-04-30 12:00 | 4 | 12 | 14.95 | 2773.3333
2017-04-30 13:00 | 4 | 13 | 16.675 | 2773.3333
2017-04-30 14:00 | 4 | 14 | 10.35 | 873.3333
2017-04-30 15:00 | 4 | 15 | 11.5 | 873.3333
2017-04-30 16:00 | 4 | 16 | 10.35 | 873.3333
2017-04-30 17:00 | 4 | 17 | 11.5 | 873.3333
2017-04-30 18:00 | 4 | 18 | 6.9 | 0
2017-04-30 19:00 | 4 | 19 | 8.05 | 286.6667
2017-04-30 20:00 | 4 | 20 | 9.2 | 286.6667
2017-04-30 21:00 | 4 | 21 | 9.2 | 286.6667
2017-04-30 22:00 | 4 | 22 | 9.2 | 286.6667
2017-04-30 23:00 | 4 | 23 | 9.2 | 286.6667
2017-05-01 | 5 | 0 | 12.65 | 1666.6667
2017-05-01 01:00 | 5 | 1 | 12.65 | 1666.6667
2017-05-01 02:00 | 5 | 2 | 10.35 | 873.3333
2017-05-01 03:00 | 5 | 3 | 9.2 | 286.6667
2017-05-01 04:00 | 5 | 4 | 9.2 | 286.6667
2017-05-01 05:00 | 5 | 5 | 6.9 | 0
2017-05-01 06:00 | 5 | 6 | 6.9 | 0
2017-05-01 07:00 | 5 | 7 | 8.05 | 286.6667
2017-05-01 08:00 | 5 | 8 | 11.5 | 873.3333
2017-05-01 09:00 | 5 | 9 | 12.65 | 1666.6667
2017-05-01 10:00 | 5 | 10 | 12.65 | 1666.6667
2017-05-01 11:00 | 5 | 11 | 10.925 | 873.3333
2017-05-01 12:00 | 5 | 12 | 10.35 | 873.3333
2017-05-01 13:00 | 5 | 13 | 10.35 | 873.3333
2017-05-01 14:00 | 5 | 14 | 9.2 | 286.6667
2017-05-01 15:00 | 5 | 15 | 10.35 | 873.3333
2017-05-01 16:00 | 5 | 16 | 10.35 | 873.3333
2017-05-01 17:00 | 5 | 17 | 10.35 | 873.3333
2017-05-01 18:00 | 5 | 18 | 12.075 | 873.3333
2017-05-01 19:00 | 5 | 19 | 12.075 | 873.3333
2017-05-01 20:00 | 5 | 20 | 10.35 | 873.3333
2017-05-01 21:00 | 5 | 21 | 11.5 | 873.3333
2017-05-01 22:00 | 5 | 22 | 8.625 | 286.6667
2017-05-01 23:00 | 5 | 23 | 14.95 | 2773.3333
2017-05-02 | 5 | 0 | 14.1833 | 1666.6667
2017-05-02 01:00 | 5 | 1 | 11.1167 | 873.3333
2017-05-02 02:00 | 5 | 2 | 9.2 | 286.6667
2017-05-02 03:00 | 5 | 3 | 14.95 | 2773.3333
2017-05-02 04:00 | 5 | 4 | 12.88 | 1666.6667
2017-05-02 05:00 | 5 | 5 | 14.95 | 2773.3333
2017-05-02 06:00 | 5 | 6 | 5.75 | 0
2017-05-02 07:00 | 5 | 7 | 5.3667 | 0
2017-05-02 08:00 | 5 | 8 | 0 | 0
2017-05-02 09:00 | 5 | 9 | 5.75 | 0
2017-05-02 10:00 | 5 | 10 | 5.3667 | 0
2017-05-02 11:00 | 5 | 11 | 7.6667 | 0
2017-05-02 12:00 | 5 | 12 | 10.35 | 873.3333
2017-05-02 13:00 | 5 | 13 | 4.6 | 0
2017-05-02 14:00 | 5 | 14 | 4.6 | 0
2017-05-02 15:00 | 5 | 15 | 8.05 | 286.6667
2017-05-02 16:00 | 5 | 16 | 6.9 | 0
2017-05-02 17:00 | 5 | 17 | 3.45 | 0
2017-05-02 18:00 | 5 | 18 | 6.9 | 0
2017-05-02 19:00 | 5 | 19 | 6.325 | 0
2017-05-02 20:00 | 5 | 20 | 26.45 | 9573.3333
2017-05-02 21:00 | 5 | 21 | 24.15 | 9060
2017-05-02 22:00 | 5 | 22 | 20.7 | 6160
2017-05-02 23:00 | 5 | 23 | 11.5 | 873.3333
2017-05-03 | 5 | 0 | 11.5 | 873.3333
2017-05-03 01:00 | 5 | 1 | 9.775 | 286.6667
2017-05-03 02:00 | 5 | 2 | 9.2 | 286.6667
2017-05-03 03:00 | 5 | 3 | 11.5 | 873.3333
2017-05-03 04:00 | 5 | 4 | 12.075 | 873.3333
2017-05-03 05:00 | 5 | 5 | 16.1 | 2773.3333
2017-05-03 06:00 | 5 | 6 | 19.55 | 6160
2017-05-03 07:00 | 5 | 7 | 21.275 | 7873.3333
2017-05-03 08:00 | 5 | 8 | 25.3 | 9060
2017-05-03 09:00 | 5 | 9 | 19.55 | 6160
2017-05-03 10:00 | 5 | 10 | 18.975 | 4266.6667
2017-05-03 11:00 | 5 | 11 | 14.95 | 2773.3333
2017-05-03 12:00 | 5 | 12 | 20.7 | 6160
2017-05-03 13:00 | 5 | 13 | 20.7 | 6160
2017-05-03 14:00 | 5 | 14 | 20.7 | 6160
2017-05-03 15:00 | 5 | 15 | 23 | 7873.3333
2017-05-03 16:00 | 5 | 16 | 21.85 | 7873.3333
2017-05-03 17:00 | 5 | 17 | 20.7 | 6160
2017-05-03 18:00 | 5 | 18 | 17.25 | 4266.6667
2017-05-03 19:00 | 5 | 19 | 18.975 | 4266.6667
2017-05-03 20:00 | 5 | 20 | 12.65 | 1666.6667
2017-05-03 21:00 | 5 | 21 | 11.5 | 873.3333
2017-05-03 22:00 | 5 | 22 | 13.225 | 1666.6667
2017-05-03 23:00 | 5 | 23 | 10.35 | 873.3333
2017-05-04 | 5 | 0 | 11.5 | 873.3333
2017-05-04 01:00 | 5 | 1 | 12.075 | 873.3333
2017-05-04 02:00 | 5 | 2 | 10.35 | 873.3333
2017-05-04 03:00 | 5 | 3 | 12.65 | 1666.6667
2017-05-04 04:00 | 5 | 4 | 11.5 | 873.3333
2017-05-04 05:00 | 5 | 5 | 8.05 | 286.6667
2017-05-04 06:00 | 5 | 6 | 8.05 | 286.6667
2017-05-04 07:00 | 5 | 7 | 9.2 | 286.6667
2017-05-04 08:00 | 5 | 8 | 9.2 | 286.6667
2017-05-04 09:00 | 5 | 9 | 11.5 | 873.3333
2017-05-04 10:00 | 5 | 10 | 12.075 | 873.3333
2017-05-04 11:00 | 5 | 11 | 14.95 | 2773.3333
2017-05-04 12:00 | 5 | 12 | 17.25 | 4266.6667
2017-05-04 13:00 | 5 | 13 | 17.25 | 4266.6667
2017-05-04 14:00 | 5 | 14 | 20.7 | 6160
2017-05-04 15:00 | 5 | 15 | 24.15 | 9060
2017-05-04 16:00 | 5 | 16 | 24.725 | 9060
2017-05-04 17:00 | 5 | 17 | 19.55 | 6160
2017-05-04 18:00 | 5 | 18 | 16.675 | 2773.3333
2017-05-04 19:00 | 5 | 19 | 13.225 | 1666.6667
2017-05-04 20:00 | 5 | 20 | 11.5 | 873.3333
2017-05-04 21:00 | 5 | 21 | 10.35 | 873.3333
2017-05-04 22:00 | 5 | 22 | 9.2 | 286.6667
2017-05-04 23:00 | 5 | 23 | 10.35 | 873.3333
2017-05-05 | 5 | 0 | 10.35 | 873.3333
2017-05-05 01:00 | 5 | 1 | 9.2 | 286.6667
2017-05-05 02:00 | 5 | 2 | 11.5 | 873.3333
2017-05-05 03:00 | 5 | 3 | 10.35 | 873.3333
2017-05-05 04:00 | 5 | 4 | 9.775 | 286.6667
2017-05-05 05:00 | 5 | 5 | 11.5 | 873.3333
2017-05-05 06:00 | 5 | 6 | 8.05 | 286.6667
2017-05-05 07:00 | 5 | 7 | 6.9 | 0
2017-05-05 08:00 | 5 | 8 | 16.1 | 2773.3333
2017-05-05 09:00 | 5 | 9 | 16.1 | 2773.3333
2017-05-05 10:00 | 5 | 10 | 17.25 | 4266.6667
2017-05-05 11:00 | 5 | 11 | 21.275 | 7873.3333
2017-05-05 12:00 | 5 | 12 | 20.125 | 6160
2017-05-05 13:00 | 5 | 13 | 20.125 | 6160
2017-05-05 14:00 | 5 | 14 | 20.3167 | 6160
2017-05-05 15:00 | 5 | 15 | 14.95 | 2773.3333
2017-05-05 16:00 | 5 | 16 | 15.8125 | 2773.3333
2017-05-05 17:00 | 5 | 17 | 22.2333 | 7873.3333
2017-05-05 18:00 | 5 | 18 | 19.55 | 6160
2017-05-05 19:00 | 5 | 19 | 16.4833 | 2773.3333
2017-05-05 20:00 | 5 | 20 | 10.35 | 873.3333
2017-05-05 21:00 | 5 | 21 | 5.75 | 0
2017-05-05 22:00 | 5 | 22 | 7.475 | 0
2017-05-05 23:00 | 5 | 23 | 4.6 | 0
2017-05-06 | 5 | 0 | 3.1625 | 0
2017-05-06 01:00 | 5 | 1 | 3.45 | 0
2017-05-06 02:00 | 5 | 2 | 4.6 | 0
2017-05-06 03:00 | 5 | 3 | 8.05 | 286.6667
2017-05-06 04:00 | 5 | 4 | 8.625 | 286.6667
2017-05-06 05:00 | 5 | 5 | 11.04 | 873.3333
2017-05-06 06:00 | 5 | 6 | 15.525 | 2773.3333
2017-05-06 07:00 | 5 | 7 | 18.7833 | 4266.6667
2017-05-06 08:00 | 5 | 8 | 0 | 0
2017-05-06 09:00 | 5 | 9 | 5.75 | 0
2017-05-06 10:00 | 5 | 10 | 9.775 | 286.6667
2017-05-06 11:00 | 5 | 11 | 17.25 | 4266.6667
2017-05-06 12:00 | 5 | 12 | 16.1 | 2773.3333
2017-05-06 13:00 | 5 | 13 | 17.825 | 4266.6667
2017-05-06 14:00 | 5 | 14 | 21.85 | 7873.3333
2017-05-06 15:00 | 5 | 15 | 18.4 | 4266.6667
2017-05-06 16:00 | 5 | 16 | 18.975 | 4266.6667
2017-05-06 17:00 | 5 | 17 | 10.35 | 873.3333
2017-05-06 18:00 | 5 | 18 | 14.95 | 2773.3333
2017-05-06 19:00 | 5 | 19 | 12.65 | 1666.6667
2017-05-06 20:00 | 5 | 20 | 11.5 | 873.3333
2017-05-06 21:00 | 5 | 21 | 12.65 | 1666.6667
2017-05-06 22:00 | 5 | 22 | 15.3333 | 2773.3333
2017-05-06 23:00 | 5 | 23 | 16.1 | 2773.3333
2017-05-07 | 5 | 0 | 13.4167 | 1666.6667
2017-05-07 01:00 | 5 | 1 | 13.8 | 1666.6667
2017-05-07 02:00 | 5 | 2 | 11.5 | 873.3333
2017-05-07 03:00 | 5 | 3 | 10.35 | 873.3333
2017-05-07 04:00 | 5 | 4 | 13.8 | 1666.6667
2017-05-07 05:00 | 5 | 5 | 18.4 | 4266.6667
2017-05-07 06:00 | 5 | 6 | 18.4 | 4266.6667
2017-05-07 07:00 | 5 | 7 | 17.25 | 4266.6667
2017-05-07 08:00 | 5 | 8 | 20.7 | 6160
2017-05-07 09:00 | 5 | 9 | 20.7 | 6160
2017-05-07 10:00 | 5 | 10 | 20.7 | 6160
2017-05-07 11:00 | 5 | 11 | 24.15 | 9060
2017-05-07 12:00 | 5 | 12 | 20.7 | 6160
2017-05-07 13:00 | 5 | 13 | 23.575 | 9060
2017-05-07 14:00 | 5 | 14 | 25.3 | 9060
2017-05-07 15:00 | 5 | 15 | 24.15 | 9060
2017-05-07 16:00 | 5 | 16 | 23.575 | 9060
2017-05-07 17:00 | 5 | 17 | 24.15 | 9060
2017-05-07 18:00 | 5 | 18 | 20.7 | 6160
2017-05-07 19:00 | 5 | 19 | 18.4 | 4266.6667
2017-05-07 20:00 | 5 | 20 | 12.65 | 1666.6667
2017-05-07 21:00 | 5 | 21 | 10.35 | 873.3333
2017-05-07 22:00 | 5 | 22 | 9.775 | 286.6667
2017-05-07 23:00 | 5 | 23 | 12.65 | 1666.6667
2017-05-08 | 5 | 0 | 18.4 | 4266.6667
2017-05-08 01:00 | 5 | 1 | 17.825 | 4266.6667
2017-05-08 02:00 | 5 | 2 | 19.55 | 6160
2017-05-08 03:00 | 5 | 3 | 18.4 | 4266.6667
2017-05-08 04:00 | 5 | 4 | 17.25 | 4266.6667
2017-05-08 05:00 | 5 | 5 | 16.1 | 2773.3333
2017-05-08 06:00 | 5 | 6 | 17.25 | 4266.6667
2017-05-08 07:00 | 5 | 7 | 16.1 | 2773.3333
2017-05-08 08:00 | 5 | 8 | 18.4 | 4266.6667
2017-05-08 09:00 | 5 | 9 | 16.1 | 2773.3333
2017-05-08 10:00 | 5 | 10 | 16.1 | 2773.3333
2017-05-08 11:00 | 5 | 11 | 17.25 | 4266.6667
2017-05-08 12:00 | 5 | 12 | 16.1 | 2773.3333
2017-05-08 13:00 | 5 | 13 | 16.675 | 2773.3333
2017-05-08 14:00 | 5 | 14 | 17.25 | 4266.6667
2017-05-08 15:00 | 5 | 15 | 17.825 | 4266.6667
2017-05-08 16:00 | 5 | 16 | 16.675 | 2773.3333
2017-05-08 17:00 | 5 | 17 | 16.1 | 2773.3333
2017-05-08 18:00 | 5 | 18 | 12.65 | 1666.6667
2017-05-08 19:00 | 5 | 19 | 10.925 | 873.3333
2017-05-08 20:00 | 5 | 20 | 12.65 | 1666.6667
2017-05-08 21:00 | 5 | 21 | 14.95 | 2773.3333
2017-05-08 22:00 | 5 | 22 | 13.225 | 1666.6667
2017-05-08 23:00 | 5 | 23 | 6.9 | 0
2017-05-09 | 5 | 0 | 9.2 | 286.6667
2017-05-09 01:00 | 5 | 1 | 8.05 | 286.6667
2017-05-09 02:00 | 5 | 2 | 9.2 | 286.6667
2017-05-09 03:00 | 5 | 3 | 8.05 | 286.6667
2017-05-09 04:00 | 5 | 4 | 5.75 | 0
2017-05-09 05:00 | 5 | 5 | 8.05 | 286.6667
2017-05-09 06:00 | 5 | 6 | 8.05 | 286.6667
2017-05-09 07:00 | 5 | 7 | 8.05 | 286.6667
2017-05-09 08:00 | 5 | 8 | 9.2 | 286.6667
2017-05-09 09:00 | 5 | 9 | 16.1 | 2773.3333
2017-05-09 10:00 | 5 | 10 | 17.25 | 4266.6667
2017-05-09 11:00 | 5 | 11 | 11.5 | 873.3333
2017-05-09 12:00 | 5 | 12 | 16.1 | 2773.3333
2017-05-09 13:00 | 5 | 13 | 14.375 | 1666.6667
2017-05-09 14:00 | 5 | 14 | 10.35 | 873.3333
2017-05-09 15:00 | 5 | 15 | 9.2 | 286.6667
2017-05-09 16:00 | 5 | 16 | 8.625 | 286.6667
2017-05-09 17:00 | 5 | 17 | 8.05 | 286.6667
2017-05-09 18:00 | 5 | 18 | 5.75 | 0
2017-05-09 19:00 | 5 | 19 | 6.325 | 0
2017-05-09 20:00 | 5 | 20 | 5.75 | 0
2017-05-09 21:00 | 5 | 21 | 0 | 0
2017-05-09 22:00 | 5 | 22 | 1.725 | 0
2017-05-09 23:00 | 5 | 23 | 0 | 0
2017-05-10 | 5 | 0 | 6.9 | 0
2017-05-10 01:00 | 5 | 1 | 8.625 | 286.6667
2017-05-10 02:00 | 5 | 2 | 9.2 | 286.6667
2017-05-10 03:00 | 5 | 3 | 10.35 | 873.3333
2017-05-10 04:00 | 5 | 4 | 10.35 | 873.3333
2017-05-10 05:00 | 5 | 5 | 10.35 | 873.3333
2017-05-10 06:00 | 5 | 6 | 11.5 | 873.3333
2017-05-10 07:00 | 5 | 7 | 9.2 | 286.6667
2017-05-10 08:00 | 5 | 8 | 5.75 | 0
2017-05-10 09:00 | 5 | 9 | 11.5 | 873.3333
2017-05-10 10:00 | 5 | 10 | 12.075 | 873.3333
2017-05-10 11:00 | 5 | 11 | 11.5 | 873.3333
2017-05-10 12:00 | 5 | 12 | 12.65 | 1666.6667
2017-05-10 13:00 | 5 | 13 | 14.375 | 1666.6667
2017-05-10 14:00 | 5 | 14 | 14.95 | 2773.3333
2017-05-10 15:00 | 5 | 15 | 11.5 | 873.3333
2017-05-10 16:00 | 5 | 16 | 10.925 | 873.3333
2017-05-10 17:00 | 5 | 17 | 9.2 | 286.6667
2017-05-10 18:00 | 5 | 18 | 5.75 | 0
2017-05-10 19:00 | 5 | 19 | 9.2 | 286.6667
2017-05-10 20:00 | 5 | 20 | 11.5 | 873.3333
2017-05-10 21:00 | 5 | 21 | 10.35 | 873.3333
2017-05-10 22:00 | 5 | 22 | 9.2 | 286.6667
2017-05-10 23:00 | 5 | 23 | 6.9 | 0
2017-05-11 | 5 | 0 | 9.2 | 286.6667
2017-05-11 01:00 | 5 | 1 | 8.05 | 286.6667
2017-05-11 02:00 | 5 | 2 | 6.9 | 0
2017-05-11 03:00 | 5 | 3 | 10.35 | 873.3333
2017-05-11 04:00 | 5 | 4 | 9.775 | 286.6667
2017-05-11 05:00 | 5 | 5 | 12.65 | 1666.6667
2017-05-11 06:00 | 5 | 6 | 11.5 | 873.3333
2017-05-11 07:00 | 5 | 7 | 11.5 | 873.3333
2017-05-11 08:00 | 5 | 8 | 15.7167 | 2773.3333
2017-05-11 09:00 | 5 | 9 | 14.95 | 2773.3333
2017-05-11 10:00 | 5 | 10 | 16.8667 | 4266.6667
2017-05-11 11:00 | 5 | 11 | 18.4 | 4266.6667
2017-05-11 12:00 | 5 | 12 | 14.95 | 2773.3333
2017-05-11 13:00 | 5 | 13 | 16.1 | 2773.3333
2017-05-11 14:00 | 5 | 14 | 18.4 | 4266.6667
2017-05-11 15:00 | 5 | 15 | 12.65 | 1666.6667
2017-05-11 16:00 | 5 | 16 | 10.925 | 873.3333
2017-05-11 17:00 | 5 | 17 | 9.2 | 286.6667
2017-05-11 18:00 | 5 | 18 | 6.9 | 0
2017-05-11 19:00 | 5 | 19 | 9.2 | 286.6667
2017-05-11 20:00 | 5 | 20 | 10.35 | 873.3333
2017-05-11 21:00 | 5 | 21 | 8.05 | 286.6667
2017-05-11 22:00 | 5 | 22 | 8.625 | 286.6667
2017-05-11 23:00 | 5 | 23 | 8.05 | 286.6667
2017-05-12 | 5 | 0 | 6.9 | 0
2017-05-12 01:00 | 5 | 1 | 6.9 | 0
2017-05-12 02:00 | 5 | 2 | 3.45 | 0
2017-05-12 03:00 | 5 | 3 | 8.05 | 286.6667
2017-05-12 04:00 | 5 | 4 | 8.8167 | 286.6667
2017-05-12 05:00 | 5 | 5 | 9.2 | 286.6667
2017-05-12 06:00 | 5 | 6 | 9.2 | 286.6667
2017-05-12 07:00 | 5 | 7 | 13.6083 | 1666.6667
2017-05-12 08:00 | 5 | 8 | 10.35 | 873.3333
2017-05-12 09:00 | 5 | 9 | 13.8 | 1666.6667
2017-05-12 10:00 | 5 | 10 | 13.225 | 1666.6667
2017-05-12 11:00 | 5 | 11 | 10.925 | 873.3333
2017-05-12 12:00 | 5 | 12 | 12.65 | 1666.6667
2017-05-12 13:00 | 5 | 13 | 12.65 | 1666.6667
2017-05-12 14:00 | 5 | 14 | 16.675 | 2773.3333
2017-05-12 15:00 | 5 | 15 | 10.35 | 873.3333
2017-05-12 16:00 | 5 | 16 | 10.925 | 873.3333
2017-05-12 17:00 | 5 | 17 | 8.05 | 286.6667
2017-05-12 18:00 | 5 | 18 | 3.45 | 0
2017-05-12 19:00 | 5 | 19 | 5.75 | 0
2017-05-12 20:00 | 5 | 20 | 6.9 | 0
2017-05-12 21:00 | 5 | 21 | 8.05 | 286.6667
2017-05-12 22:00 | 5 | 22 | 7.475 | 0
2017-05-12 23:00 | 5 | 23 | 5.75 | 0
2017-05-13 | 5 | 0 | 3.45 | 0
2017-05-13 01:00 | 5 | 1 | 3.45 | 0
2017-05-13 02:00 | 5 | 2 | 5.75 | 0
2017-05-13 03:00 | 5 | 3 | 6.9 | 0
2017-05-13 04:00 | 5 | 4 | 9.2 | 286.6667
2017-05-13 05:00 | 5 | 5 | 11.5 | 873.3333
2017-05-13 06:00 | 5 | 6 | 10.35 | 873.3333
2017-05-13 07:00 | 5 | 7 | 9.775 | 286.6667
2017-05-13 08:00 | 5 | 8 | 8.05 | 286.6667
2017-05-13 09:00 | 5 | 9 | 11.5 | 873.3333
2017-05-13 10:00 | 5 | 10 | 15.8125 | 2773.3333
2017-05-13 11:00 | 5 | 11 | 17.25 | 4266.6667
2017-05-13 12:00 | 5 | 12 | 19.55 | 6160
2017-05-13 13:00 | 5 | 13 | 21.275 | 7873.3333
2017-05-13 14:00 | 5 | 14 | 19.55 | 6160
2017-05-13 15:00 | 5 | 15 | 17.25 | 4266.6667
2017-05-13 16:00 | 5 | 16 | 16.1 | 2773.3333
2017-05-13 17:00 | 5 | 17 | 17.25 | 4266.6667
2017-05-13 18:00 | 5 | 18 | 16.675 | 2773.3333
2017-05-13 19:00 | 5 | 19 | 17.25 | 4266.6667
2017-05-13 20:00 | 5 | 20 | 14.95 | 2773.3333
2017-05-13 21:00 | 5 | 21 | 17.25 | 4266.6667
2017-05-13 22:00 | 5 | 22 | 17.25 | 4266.6667
2017-05-13 23:00 | 5 | 23 | 17.825 | 4266.6667
2017-05-14 | 5 | 0 | 17.25 | 4266.6667
2017-05-14 01:00 | 5 | 1 | 16.1 | 2773.3333
2017-05-14 02:00 | 5 | 2 | 24.15 | 9060
2017-05-14 03:00 | 5 | 3 | 24.15 | 9060
2017-05-14 04:00 | 5 | 4 | 22.425 | 7873.3333
2017-05-14 05:00 | 5 | 5 | 24.15 | 9060
2017-05-14 06:00 | 5 | 6 | 24.15 | 9060
2017-05-14 07:00 | 5 | 7 | 25.3 | 9060
2017-05-14 08:00 | 5 | 8 | 26.45 | 9573.3333
2017-05-14 09:00 | 5 | 9 | 24.15 | 9060
2017-05-14 10:00 | 5 | 10 | 25.3 | 9060
2017-05-14 11:00 | 5 | 11 | 21.85 | 7873.3333
2017-05-14 12:00 | 5 | 12 | 18.4 | 4266.6667
2017-05-14 13:00 | 5 | 13 | 19.6778 | 6160
2017-05-14 14:00 | 5 | 14 | 20.01 | 6160
2017-05-14 15:00 | 5 | 15 | 21.0833 | 6160
2017-05-14 16:00 | 5 | 16 | 20.9875 | 6160
2017-05-14 17:00 | 5 | 17 | 18.4 | 4266.6667
2017-05-14 18:00 | 5 | 18 | 18.4 | 4266.6667
2017-05-14 19:00 | 5 | 19 | 17.25 | 4266.6667
2017-05-14 20:00 | 5 | 20 | 19.55 | 6160
2017-05-14 21:00 | 5 | 21 | 16.1 | 2773.3333
2017-05-14 22:00 | 5 | 22 | 16.1 | 2773.3333
2017-05-14 23:00 | 5 | 23 | 12.65 | 1666.6667
2017-05-15 | 5 | 0 | 14.95 | 2773.3333
2017-05-15 01:00 | 5 | 1 | 15.525 | 2773.3333
2017-05-15 02:00 | 5 | 2 | 18.4 | 4266.6667
2017-05-15 03:00 | 5 | 3 | 18.4 | 4266.6667
2017-05-15 04:00 | 5 | 4 | 17.825 | 4266.6667
2017-05-15 05:00 | 5 | 5 | 19.55 | 6160
2017-05-15 06:00 | 5 | 6 | 23 | 7873.3333
2017-05-15 07:00 | 5 | 7 | 21.275 | 7873.3333
2017-05-15 08:00 | 5 | 8 | 17.25 | 4266.6667
2017-05-15 09:00 | 5 | 9 | 12.65 | 1666.6667
2017-05-15 10:00 | 5 | 10 | 13.0333 | 1666.6667
2017-05-15 11:00 | 5 | 11 | 18.4 | 4266.6667
2017-05-15 12:00 | 5 | 12 | 21.275 | 7873.3333
2017-05-15 13:00 | 5 | 13 | 16.675 | 2773.3333
2017-05-15 14:00 | 5 | 14 | 18.4 | 4266.6667
2017-05-15 15:00 | 5 | 15 | 23 | 7873.3333
2017-05-15 16:00 | 5 | 16 | 23.575 | 9060
2017-05-15 17:00 | 5 | 17 | 17.25 | 4266.6667
2017-05-15 18:00 | 5 | 18 | 12.65 | 1666.6667
2017-05-15 19:00 | 5 | 19 | 10.35 | 873.3333
2017-05-15 20:00 | 5 | 20 | 9.2 | 286.6667
2017-05-15 21:00 | 5 | 21 | 11.5 | 873.3333
2017-05-15 22:00 | 5 | 22 | 11.5 | 873.3333
2017-05-15 23:00 | 5 | 23 | 11.5 | 873.3333
2017-05-16 | 5 | 0 | 11.5 | 873.3333
2017-05-16 01:00 | 5 | 1 | 12.075 | 873.3333
2017-05-16 02:00 | 5 | 2 | 16.1 | 2773.3333
2017-05-16 03:00 | 5 | 3 | 17.25 | 4266.6667
2017-05-16 04:00 | 5 | 4 | 17.25 | 4266.6667
2017-05-16 05:00 | 5 | 5 | 14.95 | 2773.3333
2017-05-16 06:00 | 5 | 6 | 18.4 | 4266.6667
2017-05-16 07:00 | 5 | 7 | 18.4 | 4266.6667
2017-05-16 08:00 | 5 | 8 | 18.4 | 4266.6667
2017-05-16 09:00 | 5 | 9 | 14.95 | 2773.3333
2017-05-16 10:00 | 5 | 10 | 15.525 | 2773.3333
2017-05-16 11:00 | 5 | 11 | 12.65 | 1666.6667
2017-05-16 12:00 | 5 | 12 | 11.5 | 873.3333
2017-05-16 13:00 | 5 | 13 | 13.8 | 1666.6667
2017-05-16 14:00 | 5 | 14 | 19.55 | 6160
2017-05-16 15:00 | 5 | 15 | 11.5 | 873.3333
2017-05-16 16:00 | 5 | 16 | 14.95 | 2773.3333
2017-05-16 17:00 | 5 | 17 | 14.95 | 2773.3333
2017-05-16 18:00 | 5 | 18 | 11.5 | 873.3333
2017-05-16 19:00 | 5 | 19 | 10.925 | 873.3333
2017-05-16 20:00 | 5 | 20 | 8.05 | 286.6667
2017-05-16 21:00 | 5 | 21 | 10.35 | 873.3333
2017-05-16 22:00 | 5 | 22 | 9.2 | 286.6667
2017-05-16 23:00 | 5 | 23 | 5.75 | 0
2017-05-17 | 5 | 0 | 8.05 | 286.6667
2017-05-17 01:00 | 5 | 1 | 4.025 | 0
2017-05-17 02:00 | 5 | 2 | 6.9 | 0
2017-05-17 03:00 | 5 | 3 | 0 | 0
2017-05-17 04:00 | 5 | 4 | 4.025 | 0
2017-05-17 05:00 | 5 | 5 | 8.05 | 286.6667
2017-05-17 06:00 | 5 | 6 | 9.2 | 286.6667
2017-05-17 07:00 | 5 | 7 | 8.625 | 286.6667
2017-05-17 08:00 | 5 | 8 | 9.2 | 286.6667
2017-05-17 09:00 | 5 | 9 | 9.2 | 286.6667
2017-05-17 10:00 | 5 | 10 | 10.925 | 873.3333
2017-05-17 11:00 | 5 | 11 | 18.4 | 4266.6667
2017-05-17 12:00 | 5 | 12 | 11.5 | 873.3333
2017-05-17 13:00 | 5 | 13 | 14.375 | 1666.6667
2017-05-17 14:00 | 5 | 14 | 19.55 | 6160
2017-05-17 15:00 | 5 | 15 | 12.65 | 1666.6667
2017-05-17 16:00 | 5 | 16 | 12.65 | 1666.6667
2017-05-17 17:00 | 5 | 17 | 20.125 | 6160
2017-05-17 18:00 | 5 | 18 | 20.7 | 6160
2017-05-17 19:00 | 5 | 19 | 19.55 | 6160
2017-05-17 20:00 | 5 | 20 | 16.1 | 2773.3333
2017-05-17 21:00 | 5 | 21 | 14.95 | 2773.3333
2017-05-17 22:00 | 5 | 22 | 13.8 | 1666.6667
2017-05-17 23:00 | 5 | 23 | 18.4 | 4266.6667
2017-05-18 | 5 | 0 | 19.55 | 6160
2017-05-18 01:00 | 5 | 1 | 18.4 | 4266.6667
2017-05-18 02:00 | 5 | 2 | 17.25 | 4266.6667
2017-05-18 03:00 | 5 | 3 | 11.5 | 873.3333
2017-05-18 04:00 | 5 | 4 | 13.225 | 1666.6667
2017-05-18 05:00 | 5 | 5 | 10.35 | 873.3333
2017-05-18 06:00 | 5 | 6 | 12.65 | 1666.6667
2017-05-18 07:00 | 5 | 7 | 11.5 | 873.3333
2017-05-18 08:00 | 5 | 8 | 16.1 | 2773.3333
2017-05-18 09:00 | 5 | 9 | 16.1 | 2773.3333
2017-05-18 10:00 | 5 | 10 | 16.1 | 2773.3333
2017-05-18 11:00 | 5 | 11 | 17.25 | 4266.6667
2017-05-18 12:00 | 5 | 12 | 18.4 | 4266.6667
2017-05-18 13:00 | 5 | 13 | 15.525 | 2773.3333
2017-05-18 14:00 | 5 | 14 | 16.1 | 2773.3333
2017-05-18 15:00 | 5 | 15 | 20.7 | 6160
2017-05-18 16:00 | 5 | 16 | 16.1 | 2773.3333
2017-05-18 17:00 | 5 | 17 | 18.4 | 4266.6667
2017-05-18 18:00 | 5 | 18 | 24.15 | 9060
2017-05-18 19:00 | 5 | 19 | 24.15 | 9060
2017-05-18 20:00 | 5 | 20 | 24.15 | 9060
2017-05-18 21:00 | 5 | 21 | 23 | 7873.3333
2017-05-18 22:00 | 5 | 22 | 21.275 | 7873.3333
2017-05-18 23:00 | 5 | 23 | 16.1 | 2773.3333
2017-05-19 | 5 | 0 | 18.4 | 4266.6667
2017-05-19 01:00 | 5 | 1 | 19.55 | 6160
2017-05-19 02:00 | 5 | 2 | 17.25 | 4266.6667
2017-05-19 03:00 | 5 | 3 | 14.95 | 2773.3333
2017-05-19 04:00 | 5 | 4 | 15.525 | 2773.3333
2017-05-19 05:00 | 5 | 5 | 12.65 | 1666.6667
2017-05-19 06:00 | 5 | 6 | 10.35 | 873.3333
2017-05-19 07:00 | 5 | 7 | 13.225 | 1666.6667
2017-05-19 08:00 | 5 | 8 | 20.7 | 6160
2017-05-19 09:00 | 5 | 9 | 19.55 | 6160
2017-05-19 10:00 | 5 | 10 | 20.125 | 6160
2017-05-19 11:00 | 5 | 11 | 20.7 | 6160
2017-05-19 12:00 | 5 | 12 | 24.15 | 9060
2017-05-19 13:00 | 5 | 13 | 24.15 | 9060
2017-05-19 14:00 | 5 | 14 | 18.4 | 4266.6667
2017-05-19 15:00 | 5 | 15 | 25.3 | 9060
2017-05-19 16:00 | 5 | 16 | 23 | 7873.3333
2017-05-19 17:00 | 5 | 17 | 17.25 | 4266.6667
2017-05-19 18:00 | 5 | 18 | 24.15 | 9060
2017-05-19 19:00 | 5 | 19 | 16.1 | 2773.3333
2017-05-19 20:00 | 5 | 20 | 17.25 | 4266.6667
2017-05-19 21:00 | 5 | 21 | 12.65 | 1666.6667
2017-05-19 22:00 | 5 | 22 | 14.375 | 1666.6667
2017-05-19 23:00 | 5 | 23 | 10.35 | 873.3333
2017-05-20 | 5 | 0 | 9.2 | 286.6667
2017-05-20 01:00 | 5 | 1 | 9.775 | 286.6667
2017-05-20 02:00 | 5 | 2 | 6.9 | 0
2017-05-20 03:00 | 5 | 3 | 10.35 | 873.3333
2017-05-20 04:00 | 5 | 4 | 10.35 | 873.3333
2017-05-20 05:00 | 5 | 5 | 12.65 | 1666.6667
2017-05-20 06:00 | 5 | 6 | 18.4 | 4266.6667
2017-05-20 07:00 | 5 | 7 | 17.825 | 4266.6667
2017-05-20 08:00 | 5 | 8 | 17.25 | 4266.6667
2017-05-20 09:00 | 5 | 9 | 17.25 | 4266.6667
2017-05-20 10:00 | 5 | 10 | 18.975 | 4266.6667
2017-05-20 11:00 | 5 | 11 | 16.1 | 2773.3333
2017-05-20 12:00 | 5 | 12 | 16.1 | 2773.3333
2017-05-20 13:00 | 5 | 13 | 15.525 | 2773.3333
2017-05-20 14:00 | 5 | 14 | 12.65 | 1666.6667
2017-05-20 15:00 | 5 | 15 | 11.5 | 873.3333
2017-05-20 16:00 | 5 | 16 | 11.5 | 873.3333
2017-05-20 17:00 | 5 | 17 | 12.65 | 1666.6667
2017-05-20 18:00 | 5 | 18 | 8.05 | 286.6667
2017-05-20 19:00 | 5 | 19 | 8.05 | 286.6667
2017-05-20 20:00 | 5 | 20 | 11.5 | 873.3333
2017-05-20 21:00 | 5 | 21 | 9.2 | 286.6667
2017-05-20 22:00 | 5 | 22 | 8.625 | 286.6667
2017-05-20 23:00 | 5 | 23 | 10.35 | 873.3333
2017-05-21 | 5 | 0 | 11.5 | 873.3333
2017-05-21 01:00 | 5 | 1 | 10.35 | 873.3333
2017-05-21 02:00 | 5 | 2 | 8.05 | 286.6667
2017-05-21 03:00 | 5 | 3 | 3.45 | 0
2017-05-21 04:00 | 5 | 4 | 4.6 | 0
2017-05-21 05:00 | 5 | 5 | 5.75 | 0
2017-05-21 06:00 | 5 | 6 | 11.5 | 873.3333
2017-05-21 07:00 | 5 | 7 | 13.225 | 1666.6667
2017-05-21 08:00 | 5 | 8 | 12.65 | 1666.6667
2017-05-21 09:00 | 5 | 9 | 11.5 | 873.3333
2017-05-21 10:00 | 5 | 10 | 12.075 | 873.3333
2017-05-21 11:00 | 5 | 11 | 12.65 | 1666.6667
2017-05-21 12:00 | 5 | 12 | 16.1 | 2773.3333
2017-05-21 13:00 | 5 | 13 | 16.675 | 2773.3333
2017-05-21 14:00 | 5 | 14 | 17.25 | 4266.6667
2017-05-21 15:00 | 5 | 15 | 14.95 | 2773.3333
2017-05-21 16:00 | 5 | 16 | 15.525 | 2773.3333
2017-05-21 17:00 | 5 | 17 | 16.1 | 2773.3333
2017-05-21 18:00 | 5 | 18 | 12.65 | 1666.6667
2017-05-21 19:00 | 5 | 19 | 11.5 | 873.3333
2017-05-21 20:00 | 5 | 20 | 9.2 | 286.6667
2017-05-21 21:00 | 5 | 21 | 12.65 | 1666.6667
2017-05-21 22:00 | 5 | 22 | 10.925 | 873.3333
2017-05-21 23:00 | 5 | 23 | 11.5 | 873.3333
2017-05-22 | 5 | 0 | 9.2 | 286.6667
2017-05-22 01:00 | 5 | 1 | 10.35 | 873.3333
2017-05-22 02:00 | 5 | 2 | 6.9 | 0
2017-05-22 03:00 | 5 | 3 | 8.05 | 286.6667
2017-05-22 04:00 | 5 | 4 | 9.2 | 286.6667
2017-05-22 05:00 | 5 | 5 | 8.05 | 286.6667
2017-05-22 06:00 | 5 | 6 | 10.35 | 873.3333
2017-05-22 07:00 | 5 | 7 | 9.775 | 286.6667
2017-05-22 08:00 | 5 | 8 | 11.5 | 873.3333
2017-05-22 09:00 | 5 | 9 | 9.2 | 286.6667
2017-05-22 10:00 | 5 | 10 | 8.05 | 286.6667
2017-05-22 11:00 | 5 | 11 | 9.2 | 286.6667
2017-05-22 12:00 | 5 | 12 | 10.925 | 873.3333
2017-05-22 13:00 | 5 | 13 | 9.5833 | 286.6667
2017-05-22 14:00 | 5 | 14 | 11.8833 | 873.3333
2017-05-22 15:00 | 5 | 15 | 13.8 | 1666.6667
2017-05-22 16:00 | 5 | 16 | 13.8 | 1666.6667
2017-05-22 17:00 | 5 | 17 | 10.35 | 873.3333
2017-05-22 18:00 | 5 | 18 | 8.625 | 286.6667
2017-05-22 19:00 | 5 | 19 | 6.325 | 0
2017-05-22 20:00 | 5 | 20 | 3.45 | 0
2017-05-22 21:00 | 5 | 21 | 7.475 | 0
2017-05-22 22:00 | 5 | 22 | 8.05 | 286.6667
2017-05-22 23:00 | 5 | 23 | 6.9 | 0
2017-05-23 | 5 | 0 | 6.9 | 0
2017-05-23 01:00 | 5 | 1 | 6.9 | 0
2017-05-23 02:00 | 5 | 2 | 6.325 | 0
2017-05-23 03:00 | 5 | 3 | 6.9 | 0
2017-05-23 04:00 | 5 | 4 | 7.475 | 0
2017-05-23 05:00 | 5 | 5 | 5.75 | 0
2017-05-23 06:00 | 5 | 6 | 9.2 | 286.6667
2017-05-23 07:00 | 5 | 7 | 9.775 | 286.6667
2017-05-23 08:00 | 5 | 8 | 11.5 | 873.3333
2017-05-23 09:00 | 5 | 9 | 9.2 | 286.6667
2017-05-23 10:00 | 5 | 10 | 9.2 | 286.6667
2017-05-23 11:00 | 5 | 11 | 11.5 | 873.3333
2017-05-23 12:00 | 5 | 12 | 9.2 | 286.6667
2017-05-23 13:00 | 5 | 13 | 9.2 | 286.6667
2017-05-23 14:00 | 5 | 14 | 10.35 | 873.3333
2017-05-23 15:00 | 5 | 15 | 8.05 | 286.6667
2017-05-23 16:00 | 5 | 16 | 8.05 | 286.6667
2017-05-23 17:00 | 5 | 17 | 6.9 | 0
2017-05-23 18:00 | 5 | 18 | 0 | 0
2017-05-23 19:00 | 5 | 19 | 0 | 0
2017-05-23 20:00 | 5 | 20 | 5.75 | 0
2017-05-23 21:00 | 5 | 21 | 8.05 | 286.6667
2017-05-23 22:00 | 5 | 22 | 7.475 | 0
2017-05-23 23:00 | 5 | 23 | 6.9 | 0
2017-05-24 | 5 | 0 | 6.9 | 0
2017-05-24 01:00 | 5 | 1 | 7.475 | 0
2017-05-24 02:00 | 5 | 2 | 3.45 | 0
2017-05-24 03:00 | 5 | 3 | 3.45 | 0
2017-05-24 04:00 | 5 | 4 | 4.6 | 0
2017-05-24 05:00 | 5 | 5 | 5.75 | 0
2017-05-24 06:00 | 5 | 6 | 5.75 | 0
2017-05-24 07:00 | 5 | 7 | 6.9 | 0
2017-05-24 08:00 | 5 | 8 | 6.9 | 0
2017-05-24 09:00 | 5 | 9 | 6.9 | 0
2017-05-24 10:00 | 5 | 10 | 6.9 | 0
2017-05-24 11:00 | 5 | 11 | 8.05 | 286.6667
2017-05-24 12:00 | 5 | 12 | 5.75 | 0
2017-05-24 13:00 | 5 | 13 | 6.9 | 0
2017-05-24 14:00 | 5 | 14 | 9.2 | 286.6667
2017-05-24 15:00 | 5 | 15 | 11.5 | 873.3333
2017-05-24 16:00 | 5 | 16 | 10.35 | 873.3333
2017-05-24 17:00 | 5 | 17 | 10.35 | 873.3333
2017-05-24 18:00 | 5 | 18 | 9.2 | 286.6667
2017-05-24 19:00 | 5 | 19 | 8.05 | 286.6667
2017-05-24 20:00 | 5 | 20 | 5.75 | 0
2017-05-24 21:00 | 5 | 21 | 3.45 | 0
2017-05-24 22:00 | 5 | 22 | 3.45 | 0
2017-05-24 23:00 | 5 | 23 | 3.45 | 0
2017-05-25 | 5 | 0 | 5.75 | 0
2017-05-25 01:00 | 5 | 1 | 2.875 | 0
2017-05-25 02:00 | 5 | 2 | 9.2 | 286.6667
2017-05-25 03:00 | 5 | 3 | 11.5 | 873.3333
2017-05-25 04:00 | 5 | 4 | 12.075 | 873.3333
2017-05-25 05:00 | 5 | 5 | 14.95 | 2773.3333
2017-05-25 06:00 | 5 | 6 | 17.25 | 4266.6667
2017-05-25 07:00 | 5 | 7 | 17.25 | 4266.6667
2017-05-25 08:00 | 5 | 8 | 18.4 | 4266.6667
2017-05-25 09:00 | 5 | 9 | 21.85 | 7873.3333
2017-05-25 10:00 | 5 | 10 | 23 | 7873.3333
2017-05-25 11:00 | 5 | 11 | 23.46 | 7873.3333
2017-05-25 12:00 | 5 | 12 | 21.275 | 7873.3333
2017-05-25 13:00 | 5 | 13 | 21.275 | 7873.3333
2017-05-25 14:00 | 5 | 14 | 23 | 7873.3333
2017-05-25 15:00 | 5 | 15 | 20.125 | 6160
2017-05-25 16:00 | 5 | 16 | 19.1667 | 6160
2017-05-25 17:00 | 5 | 17 | 18.4 | 4266.6667
2017-05-25 18:00 | 5 | 18 | 19.9333 | 6160
2017-05-25 19:00 | 5 | 19 | 19.2625 | 6160
2017-05-25 20:00 | 5 | 20 | 20.125 | 6160
2017-05-25 21:00 | 5 | 21 | 17.25 | 4266.6667
2017-05-25 22:00 | 5 | 22 | 18.4 | 4266.6667
2017-05-25 23:00 | 5 | 23 | 16.8667 | 4266.6667
2017-05-26 | 5 | 0 | 13.8 | 1666.6667
2017-05-26 01:00 | 5 | 1 | 9.775 | 286.6667
2017-05-26 02:00 | 5 | 2 | 23 | 7873.3333
2017-05-26 03:00 | 5 | 3 | 14.95 | 2773.3333
2017-05-26 04:00 | 5 | 4 | 13.225 | 1666.6667
2017-05-26 05:00 | 5 | 5 | 12.65 | 1666.6667
2017-05-26 06:00 | 5 | 6 | 15.525 | 2773.3333
2017-05-26 07:00 | 5 | 7 | 13.225 | 1666.6667
2017-05-26 08:00 | 5 | 8 | 14.95 | 2773.3333
2017-05-26 09:00 | 5 | 9 | 12.65 | 1666.6667
2017-05-26 10:00 | 5 | 10 | 15.3333 | 2773.3333
2017-05-26 11:00 | 5 | 11 | 15.525 | 2773.3333
2017-05-26 12:00 | 5 | 12 | 12.65 | 1666.6667
2017-05-26 13:00 | 5 | 13 | 17.25 | 4266.6667
2017-05-26 14:00 | 5 | 14 | 14.375 | 1666.6667
2017-05-26 15:00 | 5 | 15 | 10.35 | 873.3333
2017-05-26 16:00 | 5 | 16 | 10.7333 | 873.3333
2017-05-26 17:00 | 5 | 17 | 11.5 | 873.3333
2017-05-26 18:00 | 5 | 18 | 9.9667 | 286.6667
2017-05-26 19:00 | 5 | 19 | 9.5833 | 286.6667
2017-05-26 20:00 | 5 | 20 | 6.0375 | 0
2017-05-26 21:00 | 5 | 21 | 0 | 0
2017-05-26 22:00 | 5 | 22 | 3.45 | 0
2017-05-26 23:00 | 5 | 23 | 7.2833 | 0
2017-05-27 | 5 | 0 | 8.05 | 286.6667
2017-05-27 01:00 | 5 | 1 | 8.05 | 286.6667
2017-05-27 02:00 | 5 | 2 | 9.2 | 286.6667
2017-05-27 03:00 | 5 | 3 | 8.05 | 286.6667
2017-05-27 04:00 | 5 | 4 | 7.475 | 0
2017-05-27 05:00 | 5 | 5 | 3.45 | 0
2017-05-27 06:00 | 5 | 6 | 8.05 | 286.6667
2017-05-27 07:00 | 5 | 7 | 8.05 | 286.6667
2017-05-27 08:00 | 5 | 8 | 8.05 | 286.6667
2017-05-27 09:00 | 5 | 9 | 8.625 | 286.6667
2017-05-27 10:00 | 5 | 10 | 14.5667 | 2773.3333
2017-05-27 11:00 | 5 | 11 | 14.95 | 2773.3333
2017-05-27 12:00 | 5 | 12 | 12.65 | 1666.6667
2017-05-27 13:00 | 5 | 13 | 14.375 | 1666.6667
2017-05-27 14:00 | 5 | 14 | 12.65 | 1666.6667
2017-05-27 15:00 | 5 | 15 | 14.95 | 2773.3333
2017-05-27 16:00 | 5 | 16 | 16.1 | 2773.3333
2017-05-27 17:00 | 5 | 17 | 16.1 | 2773.3333
2017-05-27 18:00 | 5 | 18 | 10.35 | 873.3333
2017-05-27 19:00 | 5 | 19 | 10.35 | 873.3333
2017-05-27 20:00 | 5 | 20 | 10.35 | 873.3333
2017-05-27 21:00 | 5 | 21 | 8.05 | 286.6667
2017-05-27 22:00 | 5 | 22 | 8.625 | 286.6667
2017-05-27 23:00 | 5 | 23 | 9.2 | 286.6667
2017-05-28 | 5 | 0 | 9.2 | 286.6667
2017-05-28 01:00 | 5 | 1 | 10.35 | 873.3333
2017-05-28 02:00 | 5 | 2 | 10.35 | 873.3333
2017-05-28 03:00 | 5 | 3 | 8.05 | 286.6667
2017-05-28 04:00 | 5 | 4 | 4.025 | 0
2017-05-28 05:00 | 5 | 5 | 5.75 | 0
2017-05-28 06:00 | 5 | 6 | 6.9 | 0
2017-05-28 07:00 | 5 | 7 | 6.9 | 0
2017-05-28 08:00 | 5 | 8 | 9.2 | 286.6667
2017-05-28 09:00 | 5 | 9 | 9.2 | 286.6667
2017-05-28 10:00 | 5 | 10 | 10.925 | 873.3333
2017-05-28 11:00 | 5 | 11 | 17.25 | 4266.6667
2017-05-28 12:00 | 5 | 12 | 17.25 | 4266.6667
2017-05-28 13:00 | 5 | 13 | 14.95 | 2773.3333
2017-05-28 14:00 | 5 | 14 | 6.9 | 0
2017-05-28 15:00 | 5 | 15 | 5.75 | 0
2017-05-28 16:00 | 5 | 16 | 4.6 | 0
2017-05-28 17:00 | 5 | 17 | 5.75 | 0
2017-05-28 18:00 | 5 | 18 | 10.35 | 873.3333
2017-05-28 19:00 | 5 | 19 | 10.925 | 873.3333
2017-05-28 20:00 | 5 | 20 | 10.35 | 873.3333
2017-05-28 21:00 | 5 | 21 | 10.35 | 873.3333
2017-05-28 22:00 | 5 | 22 | 10.35 | 873.3333
2017-05-28 23:00 | 5 | 23 | 9.2 | 286.6667
2017-05-29 | 5 | 0 | 10.35 | 873.3333
2017-05-29 01:00 | 5 | 1 | 9.2 | 286.6667
2017-05-29 02:00 | 5 | 2 | 6.9 | 0
2017-05-29 03:00 | 5 | 3 | 15.525 | 2773.3333
2017-05-29 04:00 | 5 | 4 | 14.1833 | 1666.6667
2017-05-29 05:00 | 5 | 5 | 11.5 | 873.3333
2017-05-29 06:00 | 5 | 6 | 13.8 | 1666.6667
2017-05-29 07:00 | 5 | 7 | 14.375 | 1666.6667
2017-05-29 08:00 | 5 | 8 | 16.675 | 2773.3333
2017-05-29 09:00 | 5 | 9 | 16.1 | 2773.3333
2017-05-29 10:00 | 5 | 10 | 16.675 | 2773.3333
2017-05-29 11:00 | 5 | 11 | 14.95 | 2773.3333
2017-05-29 12:00 | 5 | 12 | 13.225 | 1666.6667
2017-05-29 13:00 | 5 | 13 | 13.8 | 1666.6667
2017-05-29 14:00 | 5 | 14 | 11.5 | 873.3333
2017-05-29 15:00 | 5 | 15 | 8.05 | 286.6667
2017-05-29 16:00 | 5 | 16 | 9.775 | 286.6667
2017-05-29 17:00 | 5 | 17 | 12.65 | 1666.6667
2017-05-29 18:00 | 5 | 18 | 13.8 | 1666.6667
2017-05-29 19:00 | 5 | 19 | 12.2667 | 873.3333
2017-05-29 20:00 | 5 | 20 | 8.05 | 286.6667
2017-05-29 21:00 | 5 | 21 | 6.9 | 0
2017-05-29 22:00 | 5 | 22 | 7.475 | 0
2017-05-29 23:00 | 5 | 23 | 8.05 | 286.6667
2017-05-30 | 5 | 0 | 5.75 | 0
2017-05-30 01:00 | 5 | 1 | 5.75 | 0
2017-05-30 02:00 | 5 | 2 | 3.45 | 0
2017-05-30 03:00 | 5 | 3 | 0 | 0
2017-05-30 04:00 | 5 | 4 | 2.875 | 0
2017-05-30 05:00 | 5 | 5 | 3.0667 | 0
2017-05-30 06:00 | 5 | 6 | 3.45 | 0
2017-05-30 07:00 | 5 | 7 | 1.725 | 0
2017-05-30 08:00 | 5 | 8 | 8.05 | 286.6667
2017-05-30 09:00 | 5 | 9 | 8.625 | 286.6667
2017-05-30 10:00 | 5 | 10 | 9.2 | 286.6667
2017-05-30 11:00 | 5 | 11 | 12.075 | 873.3333
2017-05-30 12:00 | 5 | 12 | 9.775 | 286.6667
2017-05-30 13:00 | 5 | 13 | 9.2 | 286.6667
2017-05-30 14:00 | 5 | 14 | 9.2 | 286.6667
2017-05-30 15:00 | 5 | 15 | 14.95 | 2773.3333
2017-05-30 16:00 | 5 | 16 | 13.4167 | 1666.6667
2017-05-30 17:00 | 5 | 17 | 8.05 | 286.6667
2017-05-30 18:00 | 5 | 18 | 3.45 | 0
2017-05-30 19:00 | 5 | 19 | 6.9 | 0
2017-05-30 20:00 | 5 | 20 | 14.95 | 2773.3333
2017-05-30 21:00 | 5 | 21 | 13.225 | 1666.6667
2017-05-30 22:00 | 5 | 22 | 13.8 | 1666.6667
2017-05-30 23:00 | 5 | 23 | 10.35 | 873.3333
2017-05-31 | 5 | 0 | 9.2 | 286.6667
2017-05-31 01:00 | 5 | 1 | 10.925 | 873.3333
2017-05-31 02:00 | 5 | 2 | 9.2 | 286.6667
2017-05-31 03:00 | 5 | 3 | 10.35 | 873.3333
2017-05-31 04:00 | 5 | 4 | 9.775 | 286.6667
2017-05-31 05:00 | 5 | 5 | 10.35 | 873.3333
2017-05-31 06:00 | 5 | 6 | 6.9 | 0
2017-05-31 07:00 | 5 | 7 | 3.45 | 0
2017-05-31 08:00 | 5 | 8 | 0 | 0
2017-05-31 09:00 | 5 | 9 | 6.9 | 0
2017-05-31 10:00 | 5 | 10 | 5.4625 | 0
2017-05-31 11:00 | 5 | 11 | 8.05 | 286.6667
2017-05-31 12:00 | 5 | 12 | 9.775 | 286.6667
2017-05-31 13:00 | 5 | 13 | 9.775 | 286.6667
2017-05-31 14:00 | 5 | 14 | 10.35 | 873.3333
2017-05-31 15:00 | 5 | 15 | 12.65 | 1666.6667
2017-05-31 16:00 | 5 | 16 | 13.8 | 1666.6667
2017-05-31 17:00 | 5 | 17 | 9.775 | 286.6667
2017-05-31 18:00 | 5 | 18 | 11.5 | 873.3333
2017-05-31 19:00 | 5 | 19 | 10.7333 | 873.3333
2017-05-31 20:00 | 5 | 20 | 12.075 | 873.3333
2017-05-31 21:00 | 5 | 21 | 14.95 | 2773.3333
2017-05-31 22:00 | 5 | 22 | 10.925 | 873.3333
2017-05-31 23:00 | 5 | 23 | 6.9 | 0
2017-06-01 | 6 | 0 | 6.9 | 0
2017-06-01 01:00 | 6 | 1 | 8.05 | 286.6667
2017-06-01 02:00 | 6 | 2 | 3.45 | 0
2017-06-01 03:00 | 6 | 3 | 3.45 | 0
2017-06-01 04:00 | 6 | 4 | 5.75 | 0
2017-06-01 05:00 | 6 | 5 | 3.45 | 0
2017-06-01 06:00 | 6 | 6 | 8.05 | 286.6667
2017-06-01 07:00 | 6 | 7 | 7.475 | 0
2017-06-01 08:00 | 6 | 8 | 10.35 | 873.3333
2017-06-01 09:00 | 6 | 9 | 14.95 | 2773.3333
2017-06-01 10:00 | 6 | 10 | 13.8 | 1666.6667
2017-06-01 11:00 | 6 | 11 | 16.1 | 2773.3333
2017-06-01 12:00 | 6 | 12 | 19.55 | 6160
2017-06-01 13:00 | 6 | 13 | 18.975 | 4266.6667
2017-06-01 14:00 | 6 | 14 | 17.25 | 4266.6667
2017-06-01 15:00 | 6 | 15 | 8.05 | 286.6667
2017-06-01 16:00 | 6 | 16 | 12.075 | 873.3333
2017-06-01 17:00 | 6 | 17 | 11.5 | 873.3333
2017-06-01 18:00 | 6 | 18 | 11.5 | 873.3333
2017-06-01 19:00 | 6 | 19 | 10.925 | 873.3333
2017-06-01 20:00 | 6 | 20 | 10.35 | 873.3333
2017-06-01 21:00 | 6 | 21 | 10.35 | 873.3333
2017-06-01 22:00 | 6 | 22 | 11.5 | 873.3333
2017-06-01 23:00 | 6 | 23 | 17.25 | 4266.6667
2017-06-02 | 6 | 0 | 18.4 | 4266.6667
2017-06-02 01:00 | 6 | 1 | 17.825 | 4266.6667
2017-06-02 02:00 | 6 | 2 | 9.2 | 286.6667
2017-06-02 03:00 | 6 | 3 | 9.2 | 286.6667
2017-06-02 04:00 | 6 | 4 | 12.075 | 873.3333
2017-06-02 05:00 | 6 | 5 | 10.35 | 873.3333
2017-06-02 06:00 | 6 | 6 | 11.5 | 873.3333
2017-06-02 07:00 | 6 | 7 | 13.225 | 1666.6667
2017-06-02 08:00 | 6 | 8 | 23 | 7873.3333
2017-06-02 09:00 | 6 | 9 | 18.4 | 4266.6667
2017-06-02 10:00 | 6 | 10 | 21.275 | 7873.3333
2017-06-02 11:00 | 6 | 11 | 14.95 | 2773.3333
2017-06-02 12:00 | 6 | 12 | 19.55 | 6160
2017-06-02 13:00 | 6 | 13 | 20.125 | 6160
2017-06-02 14:00 | 6 | 14 | 19.55 | 6160
2017-06-02 15:00 | 6 | 15 | 18.4 | 4266.6667
2017-06-02 16:00 | 6 | 16 | 17.25 | 4266.6667
2017-06-02 17:00 | 6 | 17 | 17.25 | 4266.6667
2017-06-02 18:00 | 6 | 18 | 14.95 | 2773.3333
2017-06-02 19:00 | 6 | 19 | 14.375 | 1666.6667
2017-06-02 20:00 | 6 | 20 | 17.25 | 4266.6667
2017-06-02 21:00 | 6 | 21 | 11.5 | 873.3333
2017-06-02 22:00 | 6 | 22 | 9.775 | 286.6667
2017-06-02 23:00 | 6 | 23 | 9.2 | 286.6667
2017-06-03 | 6 | 0 | 9.2 | 286.6667
2017-06-03 01:00 | 6 | 1 | 8.625 | 286.6667
2017-06-03 02:00 | 6 | 2 | 9.2 | 286.6667
2017-06-03 03:00 | 6 | 3 | 9.2 | 286.6667
2017-06-03 04:00 | 6 | 4 | 9.2 | 286.6667
2017-06-03 05:00 | 6 | 5 | 8.05 | 286.6667
2017-06-03 06:00 | 6 | 6 | 10.35 | 873.3333
2017-06-03 07:00 | 6 | 7 | 11.5 | 873.3333
2017-06-03 08:00 | 6 | 8 | 16.1 | 2773.3333
2017-06-03 09:00 | 6 | 9 | 14.95 | 2773.3333
2017-06-03 10:00 | 6 | 10 | 16.675 | 2773.3333
2017-06-03 11:00 | 6 | 11 | 11.5 | 873.3333
2017-06-03 12:00 | 6 | 12 | 17.25 | 4266.6667
2017-06-03 13:00 | 6 | 13 | 16.675 | 2773.3333
2017-06-03 14:00 | 6 | 14 | 11.5 | 873.3333
2017-06-03 15:00 | 6 | 15 | 16.1 | 2773.3333
2017-06-03 16:00 | 6 | 16 | 16.675 | 2773.3333
2017-06-03 17:00 | 6 | 17 | 9.2 | 286.6667
2017-06-03 18:00 | 6 | 18 | 8.05 | 286.6667
2017-06-03 19:00 | 6 | 19 | 8.05 | 286.6667
2017-06-03 20:00 | 6 | 20 | 9.2 | 286.6667
2017-06-03 21:00 | 6 | 21 | 12.65 | 1666.6667
2017-06-03 22:00 | 6 | 22 | 12.65 | 1666.6667
2017-06-03 23:00 | 6 | 23 | 12.65 | 1666.6667
2017-06-04 | 6 | 0 | 8.05 | 286.6667
2017-06-04 01:00 | 6 | 1 | 9.775 | 286.6667
2017-06-04 02:00 | 6 | 2 | 9.2 | 286.6667
2017-06-04 03:00 | 6 | 3 | 11.5 | 873.3333
2017-06-04 04:00 | 6 | 4 | 12.075 | 873.3333
2017-06-04 05:00 | 6 | 5 | 11.5 | 873.3333
2017-06-04 06:00 | 6 | 6 | 9.2 | 286.6667
2017-06-04 07:00 | 6 | 7 | 9.2 | 286.6667
2017-06-04 08:00 | 6 | 8 | 0 | 0
2017-06-04 09:00 | 6 | 9 | 12.65 | 1666.6667
2017-06-04 10:00 | 6 | 10 | 11.5 | 873.3333
2017-06-04 11:00 | 6 | 11 | 11.5 | 873.3333
2017-06-04 12:00 | 6 | 12 | 14.95 | 2773.3333
2017-06-04 13:00 | 6 | 13 | 15.525 | 2773.3333
2017-06-04 14:00 | 6 | 14 | 11.5 | 873.3333
2017-06-04 15:00 | 6 | 15 | 16.1 | 2773.3333
2017-06-04 16:00 | 6 | 16 | 12.65 | 1666.6667
2017-06-04 17:00 | 6 | 17 | 10.35 | 873.3333
2017-06-04 18:00 | 6 | 18 | 9.2 | 286.6667
2017-06-04 19:00 | 6 | 19 | 10.925 | 873.3333
2017-06-04 20:00 | 6 | 20 | 16.1 | 2773.3333
2017-06-04 21:00 | 6 | 21 | 11.5 | 873.3333
2017-06-04 22:00 | 6 | 22 | 12.075 | 873.3333
2017-06-04 23:00 | 6 | 23 | 10.35 | 873.3333
2017-06-05 | 6 | 0 | 8.05 | 286.6667
2017-06-05 01:00 | 6 | 1 | 9.775 | 286.6667
2017-06-05 02:00 | 6 | 2 | 11.5 | 873.3333
2017-06-05 03:00 | 6 | 3 | 12.65 | 1666.6667
2017-06-05 04:00 | 6 | 4 | 10.925 | 873.3333
2017-06-05 05:00 | 6 | 5 | 15.41 | 2773.3333
2017-06-05 06:00 | 6 | 6 | 16.4833 | 2773.3333
2017-06-05 07:00 | 6 | 7 | 19.55 | 6160
2017-06-05 08:00 | 6 | 8 | 20.125 | 6160
2017-06-05 09:00 | 6 | 9 | 20.125 | 6160
2017-06-05 10:00 | 6 | 10 | 19.55 | 6160
2017-06-05 11:00 | 6 | 11 | 19.55 | 6160
2017-06-05 12:00 | 6 | 12 | 19.55 | 6160
2017-06-05 13:00 | 6 | 13 | 17.71 | 4266.6667
2017-06-05 14:00 | 6 | 14 | 17.25 | 4266.6667
2017-06-05 15:00 | 6 | 15 | 18.975 | 4266.6667
2017-06-05 16:00 | 6 | 16 | 19.55 | 6160
2017-06-05 17:00 | 6 | 17 | 19.55 | 6160
2017-06-05 18:00 | 6 | 18 | 19.55 | 6160
2017-06-05 19:00 | 6 | 19 | 21.0833 | 6160
2017-06-05 20:00 | 6 | 20 | 20.7 | 6160
2017-06-05 21:00 | 6 | 21 | 26.45 | 9573.3333
2017-06-05 22:00 | 6 | 22 | 25.3 | 9060
2017-06-05 23:00 | 6 | 23 | 24.15 | 9060
2017-06-06 | 6 | 0 | 29.9 | 9873.3333
2017-06-06 01:00 | 6 | 1 | 25.3 | 9060
2017-06-06 02:00 | 6 | 2 | 28.75 | 9873.3333
2017-06-06 03:00 | 6 | 3 | 26.45 | 9573.3333
2017-06-06 04:00 | 6 | 4 | 27.2167 | 9573.3333
2017-06-06 05:00 | 6 | 5 | 23 | 7873.3333
2017-06-06 06:00 | 6 | 6 | 27.6 | 9573.3333
2017-06-06 07:00 | 6 | 7 | 27.025 | 9573.3333
2017-06-06 08:00 | 6 | 8 | 25.3 | 9060
2017-06-06 09:00 | 6 | 9 | 20.7 | 6160
2017-06-06 10:00 | 6 | 10 | 20.7 | 6160
2017-06-06 11:00 | 6 | 11 | 17.25 | 4266.6667
2017-06-06 12:00 | 6 | 12 | 23.575 | 9060
2017-06-06 13:00 | 6 | 13 | 22.1375 | 7873.3333
2017-06-06 14:00 | 6 | 14 | 24.9167 | 9060
2017-06-06 15:00 | 6 | 15 | 23 | 7873.3333
2017-06-06 16:00 | 6 | 16 | 16.8667 | 4266.6667
2017-06-06 17:00 | 6 | 17 | 14.375 | 1666.6667
2017-06-06 18:00 | 6 | 18 | 10.35 | 873.3333
2017-06-06 19:00 | 6 | 19 | 6.5167 | 0
2017-06-06 20:00 | 6 | 20 | 8.625 | 286.6667
2017-06-06 21:00 | 6 | 21 | 6.9 | 0
2017-06-06 22:00 | 6 | 22 | 5.75 | 0
2017-06-06 23:00 | 6 | 23 | 8.05 | 286.6667
2017-06-07 | 6 | 0 | 6.9 | 0
2017-06-07 01:00 | 6 | 1 | 8.625 | 286.6667
2017-06-07 02:00 | 6 | 2 | 8.05 | 286.6667
2017-06-07 03:00 | 6 | 3 | 9.2 | 286.6667
2017-06-07 04:00 | 6 | 4 | 9.775 | 286.6667
2017-06-07 05:00 | 6 | 5 | 8.625 | 286.6667
2017-06-07 06:00 | 6 | 6 | 11.5 | 873.3333
2017-06-07 07:00 | 6 | 7 | 10.35 | 873.3333
2017-06-07 08:00 | 6 | 8 | 11.5 | 873.3333
2017-06-07 09:00 | 6 | 9 | 10.35 | 873.3333
2017-06-07 10:00 | 6 | 10 | 10.35 | 873.3333
2017-06-07 11:00 | 6 | 11 | 11.5 | 873.3333
2017-06-07 12:00 | 6 | 12 | 16.1 | 2773.3333
2017-06-07 13:00 | 6 | 13 | 13.225 | 1666.6667
2017-06-07 14:00 | 6 | 14 | 10.35 | 873.3333
2017-06-07 15:00 | 6 | 15 | 9.2 | 286.6667
2017-06-07 16:00 | 6 | 16 | 8.625 | 286.6667
2017-06-07 17:00 | 6 | 17 | 5.75 | 0
2017-06-07 18:00 | 6 | 18 | 8.05 | 286.6667
2017-06-07 19:00 | 6 | 19 | 7.475 | 0
2017-06-07 20:00 | 6 | 20 | 6.9 | 0
2017-06-07 21:00 | 6 | 21 | 6.9 | 0
2017-06-07 22:00 | 6 | 22 | 6.9 | 0
2017-06-07 23:00 | 6 | 23 | 5.75 | 0
2017-06-08 | 6 | 0 | 3.45 | 0
2017-06-08 01:00 | 6 | 1 | 3.45 | 0
2017-06-08 02:00 | 6 | 2 | 6.9 | 0
2017-06-08 03:00 | 6 | 3 | 6.9 | 0
2017-06-08 04:00 | 6 | 4 | 7.475 | 0
2017-06-08 05:00 | 6 | 5 | 3.45 | 0
2017-06-08 06:00 | 6 | 6 | 5.75 | 0
2017-06-08 07:00 | 6 | 7 | 6.325 | 0
2017-06-08 08:00 | 6 | 8 | 5.75 | 0
2017-06-08 09:00 | 6 | 9 | 6.9 | 0
2017-06-08 10:00 | 6 | 10 | 8.625 | 286.6667
2017-06-08 11:00 | 6 | 11 | 14.95 | 2773.3333
2017-06-08 12:00 | 6 | 12 | 11.5 | 873.3333
2017-06-08 13:00 | 6 | 13 | 14.95 | 2773.3333
2017-06-08 14:00 | 6 | 14 | 12.65 | 1666.6667
2017-06-08 15:00 | 6 | 15 | 12.65 | 1666.6667
2017-06-08 16:00 | 6 | 16 | 10.925 | 873.3333
2017-06-08 17:00 | 6 | 17 | 8.05 | 286.6667
2017-06-08 18:00 | 6 | 18 | 10.35 | 873.3333
2017-06-08 19:00 | 6 | 19 | 10.35 | 873.3333
2017-06-08 20:00 | 6 | 20 | 10.35 | 873.3333
2017-06-08 21:00 | 6 | 21 | 10.35 | 873.3333
2017-06-08 22:00 | 6 | 22 | 6.9 | 0
2017-06-08 23:00 | 6 | 23 | 6.9 | 0
2017-06-09 | 6 | 0 | 6.9 | 0
2017-06-09 01:00 | 6 | 1 | 6.5167 | 0
2017-06-09 02:00 | 6 | 2 | 6.9 | 0
2017-06-09 03:00 | 6 | 3 | 5.75 | 0
2017-06-09 04:00 | 6 | 4 | 6.9 | 0
2017-06-09 05:00 | 6 | 5 | 10.35 | 873.3333
2017-06-09 06:00 | 6 | 6 | 10.35 | 873.3333
2017-06-09 07:00 | 6 | 7 | 10.35 | 873.3333
2017-06-09 08:00 | 6 | 8 | 5.75 | 0
2017-06-09 09:00 | 6 | 9 | 8.05 | 286.6667
2017-06-09 10:00 | 6 | 10 | 9.2 | 286.6667
2017-06-09 11:00 | 6 | 11 | 9.2 | 286.6667
2017-06-09 12:00 | 6 | 12 | 24.15 | 9060
2017-06-09 13:00 | 6 | 13 | 24.15 | 9060
2017-06-09 14:00 | 6 | 14 | 14.95 | 2773.3333
2017-06-09 15:00 | 6 | 15 | 15.3333 | 2773.3333
2017-06-09 16:00 | 6 | 16 | 12.65 | 1666.6667
2017-06-09 17:00 | 6 | 17 | 11.5 | 873.3333
2017-06-09 18:00 | 6 | 18 | 11.5 | 873.3333
2017-06-09 19:00 | 6 | 19 | 11.5 | 873.3333
2017-06-09 20:00 | 6 | 20 | 11.5 | 873.3333
2017-06-09 21:00 | 6 | 21 | 12.65 | 1666.6667
2017-06-09 22:00 | 6 | 22 | 13.8 | 1666.6667
2017-06-09 23:00 | 6 | 23 | 12.65 | 1666.6667
2017-06-10 | 6 | 0 | 10.35 | 873.3333
2017-06-10 01:00 | 6 | 1 | 10.35 | 873.3333
2017-06-10 02:00 | 6 | 2 | 10.35 | 873.3333
2017-06-10 03:00 | 6 | 3 | 9.2 | 286.6667
2017-06-10 04:00 | 6 | 4 | 7.475 | 0
2017-06-10 05:00 | 6 | 5 | 6.9 | 0
2017-06-10 06:00 | 6 | 6 | 5.75 | 0
2017-06-10 07:00 | 6 | 7 | 5.75 | 0
2017-06-10 08:00 | 6 | 8 | 6.9 | 0
2017-06-10 09:00 | 6 | 9 | 9.2 | 286.6667
2017-06-10 10:00 | 6 | 10 | 10.35 | 873.3333
2017-06-10 11:00 | 6 | 11 | 16.1 | 2773.3333
2017-06-10 12:00 | 6 | 12 | 14.95 | 2773.3333
2017-06-10 13:00 | 6 | 13 | 16.675 | 2773.3333
2017-06-10 14:00 | 6 | 14 | 20.7 | 6160
2017-06-10 15:00 | 6 | 15 | 16.1 | 2773.3333
2017-06-10 16:00 | 6 | 16 | 16.675 | 2773.3333
2017-06-10 17:00 | 6 | 17 | 16.1 | 2773.3333
2017-06-10 18:00 | 6 | 18 | 17.25 | 4266.6667
2017-06-10 19:00 | 6 | 19 | 16.675 | 2773.3333
2017-06-10 20:00 | 6 | 20 | 17.25 | 4266.6667
2017-06-10 21:00 | 6 | 21 | 17.25 | 4266.6667
2017-06-10 22:00 | 6 | 22 | 17.825 | 4266.6667
2017-06-10 23:00 | 6 | 23 | 17.25 | 4266.6667
2017-06-11 | 6 | 0 | 16.1 | 2773.3333
2017-06-11 01:00 | 6 | 1 | 15.525 | 2773.3333
2017-06-11 02:00 | 6 | 2 | 16.1 | 2773.3333
2017-06-11 03:00 | 6 | 3 | 12.65 | 1666.6667
2017-06-11 04:00 | 6 | 4 | 10.35 | 873.3333
2017-06-11 05:00 | 6 | 5 | 11.5 | 873.3333
2017-06-11 06:00 | 6 | 6 | 12.65 | 1666.6667
2017-06-11 07:00 | 6 | 7 | 12.075 | 873.3333
2017-06-11 08:00 | 6 | 8 | 14.95 | 2773.3333
2017-06-11 09:00 | 6 | 9 | 23 | 7873.3333
2017-06-11 10:00 | 6 | 10 | 17.825 | 4266.6667
2017-06-11 11:00 | 6 | 11 | 18.4 | 4266.6667
2017-06-11 12:00 | 6 | 12 | 19.55 | 6160
2017-06-11 13:00 | 6 | 13 | 21.275 | 7873.3333
2017-06-11 14:00 | 6 | 14 | 23 | 7873.3333
2017-06-11 15:00 | 6 | 15 | 26.45 | 9573.3333
2017-06-11 16:00 | 6 | 16 | 23.575 | 9060
2017-06-11 17:00 | 6 | 17 | 19.55 | 6160
2017-06-11 18:00 | 6 | 18 | 18.4 | 4266.6667
2017-06-11 19:00 | 6 | 19 | 17.25 | 4266.6667
2017-06-11 20:00 | 6 | 20 | 16.1 | 2773.3333
2017-06-11 21:00 | 6 | 21 | 18.4 | 4266.6667
2017-06-11 22:00 | 6 | 22 | 16.675 | 2773.3333
2017-06-11 23:00 | 6 | 23 | 9.2 | 286.6667
2017-06-12 | 6 | 0 | 12.65 | 1666.6667
2017-06-12 01:00 | 6 | 1 | 12.075 | 873.3333
2017-06-12 02:00 | 6 | 2 | 8.05 | 286.6667
2017-06-12 03:00 | 6 | 3 | 8.05 | 286.6667
2017-06-12 04:00 | 6 | 4 | 7.475 | 0
2017-06-12 05:00 | 6 | 5 | 10.35 | 873.3333
2017-06-12 06:00 | 6 | 6 | 10.35 | 873.3333
2017-06-12 07:00 | 6 | 7 | 8.625 | 286.6667
2017-06-12 08:00 | 6 | 8 | 8.05 | 286.6667
2017-06-12 09:00 | 6 | 9 | 9.2 | 286.6667
2017-06-12 10:00 | 6 | 10 | 8.625 | 286.6667
2017-06-12 11:00 | 6 | 11 | 10.35 | 873.3333
2017-06-12 12:00 | 6 | 12 | 20.7 | 6160
2017-06-12 13:00 | 6 | 13 | 19.55 | 6160
2017-06-12 14:00 | 6 | 14 | 17.25 | 4266.6667
2017-06-12 15:00 | 6 | 15 | 17.25 | 4266.6667
2017-06-12 16:00 | 6 | 16 | 17.25 | 4266.6667
2017-06-12 17:00 | 6 | 17 | 16.1 | 2773.3333
2017-06-12 18:00 | 6 | 18 | 9.2 | 286.6667
2017-06-12 19:00 | 6 | 19 | 12.075 | 873.3333
2017-06-12 20:00 | 6 | 20 | 17.25 | 4266.6667
2017-06-12 21:00 | 6 | 21 | 16.1 | 2773.3333
2017-06-12 22:00 | 6 | 22 | 13.8 | 1666.6667
2017-06-12 23:00 | 6 | 23 | 12.65 | 1666.6667
2017-06-13 | 6 | 0 | 11.5 | 873.3333
2017-06-13 01:00 | 6 | 1 | 9.775 | 286.6667
2017-06-13 02:00 | 6 | 2 | 9.2 | 286.6667
2017-06-13 03:00 | 6 | 3 | 10.35 | 873.3333
2017-06-13 04:00 | 6 | 4 | 10.925 | 873.3333
2017-06-13 05:00 | 6 | 5 | 12.65 | 1666.6667
2017-06-13 06:00 | 6 | 6 | 18.4 | 4266.6667
2017-06-13 07:00 | 6 | 7 | 15.525 | 2773.3333
2017-06-13 08:00 | 6 | 8 | 16.1 | 2773.3333
2017-06-13 09:00 | 6 | 9 | 9.2 | 286.6667
2017-06-13 10:00 | 6 | 10 | 13.8 | 1666.6667
2017-06-13 11:00 | 6 | 11 | 16.1 | 2773.3333
2017-06-13 12:00 | 6 | 12 | 12.65 | 1666.6667
2017-06-13 13:00 | 6 | 13 | 10.925 | 873.3333
2017-06-13 14:00 | 6 | 14 | 16.1 | 2773.3333
2017-06-13 15:00 | 6 | 15 | 20.7 | 6160
2017-06-13 16:00 | 6 | 16 | 19.9812 | 6160
2017-06-13 17:00 | 6 | 17 | 11.5 | 873.3333
2017-06-13 18:00 | 6 | 18 | 5.75 | 0
2017-06-13 19:00 | 6 | 19 | 5.75 | 0
2017-06-13 20:00 | 6 | 20 | 12.65 | 1666.6667
2017-06-13 21:00 | 6 | 21 | 24.15 | 9060
2017-06-13 22:00 | 6 | 22 | 17.25 | 4266.6667
2017-06-13 23:00 | 6 | 23 | 5.75 | 0
2017-06-14 | 6 | 0 | 10.35 | 873.3333
2017-06-14 01:00 | 6 | 1 | 6.9 | 0
2017-06-14 02:00 | 6 | 2 | 6.9 | 0
2017-06-14 03:00 | 6 | 3 | 10.35 | 873.3333
2017-06-14 04:00 | 6 | 4 | 10.925 | 873.3333
2017-06-14 05:00 | 6 | 5 | 11.5 | 873.3333
2017-06-14 06:00 | 6 | 6 | 9.2 | 286.6667
2017-06-14 07:00 | 6 | 7 | 9.775 | 286.6667
2017-06-14 08:00 | 6 | 8 | 16.1 | 2773.3333
2017-06-14 09:00 | 6 | 9 | 14.95 | 2773.3333
2017-06-14 10:00 | 6 | 10 | 12.65 | 1666.6667
2017-06-14 11:00 | 6 | 11 | 14.95 | 2773.3333
2017-06-14 12:00 | 6 | 12 | 18.4 | 4266.6667
2017-06-14 13:00 | 6 | 13 | 17.825 | 4266.6667
2017-06-14 14:00 | 6 | 14 | 16.1 | 2773.3333
2017-06-14 15:00 | 6 | 15 | 17.25 | 4266.6667
2017-06-14 16:00 | 6 | 16 | 16.1 | 2773.3333
2017-06-14 17:00 | 6 | 17 | 12.65 | 1666.6667
2017-06-14 18:00 | 6 | 18 | 12.65 | 1666.6667
2017-06-14 19:00 | 6 | 19 | 11.5 | 873.3333
2017-06-14 20:00 | 6 | 20 | 9.2 | 286.6667
2017-06-14 21:00 | 6 | 21 | 10.35 | 873.3333
2017-06-14 22:00 | 6 | 22 | 11.5 | 873.3333
2017-06-14 23:00 | 6 | 23 | 8.05 | 286.6667
2017-06-15 | 6 | 0 | 9.2 | 286.6667
2017-06-15 01:00 | 6 | 1 | 8.625 | 286.6667
2017-06-15 02:00 | 6 | 2 | 8.05 | 286.6667
2017-06-15 03:00 | 6 | 3 | 5.75 | 0
2017-06-15 04:00 | 6 | 4 | 6.325 | 0
2017-06-15 05:00 | 6 | 5 | 6.9 | 0
2017-06-15 06:00 | 6 | 6 | 6.9 | 0
2017-06-15 07:00 | 6 | 7 | 6.325 | 0
2017-06-15 08:00 | 6 | 8 | 6.9 | 0
2017-06-15 09:00 | 6 | 9 | 16.1 | 2773.3333
2017-06-15 10:00 | 6 | 10 | 17.25 | 4266.6667
2017-06-15 11:00 | 6 | 11 | 18.4 | 4266.6667
2017-06-15 12:00 | 6 | 12 | 19.55 | 6160
2017-06-15 13:00 | 6 | 13 | 17.825 | 4266.6667
2017-06-15 14:00 | 6 | 14 | 17.25 | 4266.6667
2017-06-15 15:00 | 6 | 15 | 17.25 | 4266.6667
2017-06-15 16:00 | 6 | 16 | 18.4 | 4266.6667
2017-06-15 17:00 | 6 | 17 | 23 | 7873.3333
2017-06-15 18:00 | 6 | 18 | 18.4 | 4266.6667
2017-06-15 19:00 | 6 | 19 | 17.25 | 4266.6667
2017-06-15 20:00 | 6 | 20 | 14.95 | 2773.3333
2017-06-15 21:00 | 6 | 21 | 16.1 | 2773.3333
2017-06-15 22:00 | 6 | 22 | 15.525 | 2773.3333
2017-06-15 23:00 | 6 | 23 | 17.25 | 4266.6667
2017-06-16 | 6 | 0 | 10.35 | 873.3333
2017-06-16 01:00 | 6 | 1 | 10.925 | 873.3333
2017-06-16 02:00 | 6 | 2 | 10.35 | 873.3333
2017-06-16 03:00 | 6 | 3 | 11.5 | 873.3333
2017-06-16 04:00 | 6 | 4 | 10.35 | 873.3333
2017-06-16 05:00 | 6 | 5 | 12.65 | 1666.6667
2017-06-16 06:00 | 6 | 6 | 10.35 | 873.3333
2017-06-16 07:00 | 6 | 7 | 12.65 | 1666.6667
2017-06-16 08:00 | 6 | 8 | 14.95 | 2773.3333
2017-06-16 09:00 | 6 | 9 | 16.1 | 2773.3333
2017-06-16 10:00 | 6 | 10 | 16.675 | 2773.3333
2017-06-16 11:00 | 6 | 11 | 12.65 | 1666.6667
2017-06-16 12:00 | 6 | 12 | 10.35 | 873.3333
2017-06-16 13:00 | 6 | 13 | 13.225 | 1666.6667
2017-06-16 14:00 | 6 | 14 | 16.1 | 2773.3333
2017-06-16 15:00 | 6 | 15 | 16.675 | 2773.3333
2017-06-16 16:00 | 6 | 16 | 15.18 | 2773.3333
2017-06-16 17:00 | 6 | 17 | 11.04 | 873.3333
2017-06-16 18:00 | 6 | 18 | 11.1167 | 873.3333
2017-06-16 19:00 | 6 | 19 | 10.35 | 873.3333
2017-06-16 20:00 | 6 | 20 | 8.3375 | 286.6667
2017-06-16 21:00 | 6 | 21 | 6.325 | 0
2017-06-16 22:00 | 6 | 22 | 4.9833 | 0
2017-06-16 23:00 | 6 | 23 | 4.2167 | 0
2017-06-17 | 6 | 0 | 3.0667 | 0
2017-06-17 01:00 | 6 | 1 | 3.8333 | 0
2017-06-17 02:00 | 6 | 2 | 1.725 | 0
2017-06-17 03:00 | 6 | 3 | 4.6 | 0
2017-06-17 04:00 | 6 | 4 | 1.725 | 0
2017-06-17 05:00 | 6 | 5 | 5.75 | 0
2017-06-17 06:00 | 6 | 6 | 6.9 | 0
2017-06-17 07:00 | 6 | 7 | 7.475 | 0
2017-06-17 08:00 | 6 | 8 | 6.5167 | 0
2017-06-17 09:00 | 6 | 9 | 4.6 | 0
2017-06-17 10:00 | 6 | 10 | 3.45 | 0
2017-06-17 11:00 | 6 | 11 | 5.75 | 0
2017-06-17 12:00 | 6 | 12 | 7.475 | 0
2017-06-17 13:00 | 6 | 13 | 8.625 | 286.6667
2017-06-17 14:00 | 6 | 14 | 7.475 | 0
2017-06-17 15:00 | 6 | 15 | 9.2 | 286.6667
2017-06-17 16:00 | 6 | 16 | 8.05 | 286.6667
2017-06-17 17:00 | 6 | 17 | 8.05 | 286.6667
2017-06-17 18:00 | 6 | 18 | 8.05 | 286.6667
2017-06-17 19:00 | 6 | 19 | 7.6667 | 0
2017-06-17 20:00 | 6 | 20 | 6.9 | 0
2017-06-17 21:00 | 6 | 21 | 6.9 | 0
2017-06-17 22:00 | 6 | 22 | 6.9 | 0
2017-06-17 23:00 | 6 | 23 | 8.05 | 286.6667
2017-06-18 | 6 | 0 | 8.8167 | 286.6667
2017-06-18 01:00 | 6 | 1 | 7.475 | 0
2017-06-18 02:00 | 6 | 2 | 10.35 | 873.3333
2017-06-18 03:00 | 6 | 3 | 6.9 | 0
2017-06-18 04:00 | 6 | 4 | 9.2 | 286.6667
2017-06-18 05:00 | 6 | 5 | 10.35 | 873.3333
2017-06-18 06:00 | 6 | 6 | 11.5 | 873.3333
2017-06-18 07:00 | 6 | 7 | 12.075 | 873.3333
2017-06-18 08:00 | 6 | 8 | 14.95 | 2773.3333
2017-06-18 09:00 | 6 | 9 | 10.35 | 873.3333
2017-06-18 10:00 | 6 | 10 | 12.2667 | 873.3333
2017-06-18 11:00 | 6 | 11 | 17.25 | 4266.6667
2017-06-18 12:00 | 6 | 12 | 21.275 | 7873.3333
2017-06-18 13:00 | 6 | 13 | 23 | 7873.3333
2017-06-18 14:00 | 6 | 14 | 21.85 | 7873.3333
2017-06-18 15:00 | 6 | 15 | 25.3 | 9060
2017-06-18 16:00 | 6 | 16 | 20.9875 | 6160
2017-06-18 17:00 | 6 | 17 | 20.7 | 6160
2017-06-18 18:00 | 6 | 18 | 18.4 | 4266.6667
2017-06-18 19:00 | 6 | 19 | 18.975 | 4266.6667
2017-06-18 20:00 | 6 | 20 | 17.25 | 4266.6667
2017-06-18 21:00 | 6 | 21 | 20.7 | 6160
2017-06-18 22:00 | 6 | 22 | 18.7833 | 4266.6667
2017-06-18 23:00 | 6 | 23 | 16.1 | 2773.3333
2017-06-19 | 6 | 0 | 16.1 | 2773.3333
2017-06-19 01:00 | 6 | 1 | 16.1 | 2773.3333
2017-06-19 02:00 | 6 | 2 | 19.55 | 6160
2017-06-19 03:00 | 6 | 3 | 16.1 | 2773.3333
2017-06-19 04:00 | 6 | 4 | 15.525 | 2773.3333
2017-06-19 05:00 | 6 | 5 | 16.1 | 2773.3333
2017-06-19 06:00 | 6 | 6 | 12.65 | 1666.6667
2017-06-19 07:00 | 6 | 7 | 13.8 | 1666.6667
2017-06-19 08:00 | 6 | 8 | 14.95 | 2773.3333
2017-06-19 09:00 | 6 | 9 | 15.525 | 2773.3333
2017-06-19 10:00 | 6 | 10 | 16.675 | 2773.3333
2017-06-19 11:00 | 6 | 11 | 21.275 | 7873.3333
2017-06-19 12:00 | 6 | 12 | 18.4 | 4266.6667
2017-06-19 13:00 | 6 | 13 | 22.425 | 7873.3333
2017-06-19 14:00 | 6 | 14 | 26.45 | 9573.3333
2017-06-19 15:00 | 6 | 15 | 24.15 | 9060
2017-06-19 16:00 | 6 | 16 | 22.425 | 7873.3333
2017-06-19 17:00 | 6 | 17 | 26.45 | 9573.3333
2017-06-19 18:00 | 6 | 18 | 16.1 | 2773.3333
2017-06-19 19:00 | 6 | 19 | 18.0167 | 4266.6667
2017-06-19 20:00 | 6 | 20 | 18.4 | 4266.6667
2017-06-19 21:00 | 6 | 21 | 18.975 | 4266.6667
2017-06-19 22:00 | 6 | 22 | 17.25 | 4266.6667
2017-06-19 23:00 | 6 | 23 | 15.3333 | 2773.3333
2017-06-20 | 6 | 0 | 13.4167 | 1666.6667
2017-06-20 01:00 | 6 | 1 | 16.1 | 2773.3333
2017-06-20 02:00 | 6 | 2 | 17.25 | 4266.6667
2017-06-20 03:00 | 6 | 3 | 14.95 | 2773.3333
2017-06-20 04:00 | 6 | 4 | 10.35 | 873.3333
2017-06-20 05:00 | 6 | 5 | 9.4875 | 286.6667
2017-06-20 06:00 | 6 | 6 | 9.2 | 286.6667
2017-06-20 07:00 | 6 | 7 | 13.225 | 1666.6667
2017-06-20 08:00 | 6 | 8 | 17.25 | 4266.6667
2017-06-20 09:00 | 6 | 9 | 19.55 | 6160
2017-06-20 10:00 | 6 | 10 | 21.275 | 7873.3333
2017-06-20 11:00 | 6 | 11 | 19.55 | 6160
2017-06-20 12:00 | 6 | 12 | 24.15 | 9060
2017-06-20 13:00 | 6 | 13 | 24.725 | 9060
2017-06-20 14:00 | 6 | 14 | 25.3 | 9060
2017-06-20 15:00 | 6 | 15 | 19.55 | 6160
2017-06-20 16:00 | 6 | 16 | 21.275 | 7873.3333
2017-06-20 17:00 | 6 | 17 | 20.7 | 6160
2017-06-20 18:00 | 6 | 18 | 10.35 | 873.3333
2017-06-20 19:00 | 6 | 19 | 10.35 | 873.3333
2017-06-20 20:00 | 6 | 20 | 12.65 | 1666.6667
2017-06-20 21:00 | 6 | 21 | 8.05 | 286.6667
2017-06-20 22:00 | 6 | 22 | 9.2 | 286.6667
2017-06-20 23:00 | 6 | 23 | 10.35 | 873.3333
2017-06-21 | 6 | 0 | 10.35 | 873.3333
2017-06-21 01:00 | 6 | 1 | 10.35 | 873.3333
2017-06-21 02:00 | 6 | 2 | 12.65 | 1666.6667
2017-06-21 03:00 | 6 | 3 | 12.65 | 1666.6667
2017-06-21 04:00 | 6 | 4 | 12.075 | 873.3333
2017-06-21 05:00 | 6 | 5 | 11.5 | 873.3333
2017-06-21 06:00 | 6 | 6 | 10.35 | 873.3333
2017-06-21 07:00 | 6 | 7 | 10.925 | 873.3333
2017-06-21 08:00 | 6 | 8 | 16.1 | 2773.3333
2017-06-21 09:00 | 6 | 9 | 18.4 | 4266.6667
2017-06-21 10:00 | 6 | 10 | 19.55 | 6160
2017-06-21 11:00 | 6 | 11 | 20.7 | 6160
2017-06-21 12:00 | 6 | 12 | 16.1 | 2773.3333
2017-06-21 13:00 | 6 | 13 | 17.825 | 4266.6667
2017-06-21 14:00 | 6 | 14 | 16.1 | 2773.3333
2017-06-21 15:00 | 6 | 15 | 18.4 | 4266.6667
2017-06-21 16:00 | 6 | 16 | 11.5 | 873.3333
2017-06-21 17:00 | 6 | 17 | 19.55 | 6160
2017-06-21 18:00 | 6 | 18 | 14.95 | 2773.3333
2017-06-21 19:00 | 6 | 19 | 15.525 | 2773.3333
2017-06-21 20:00 | 6 | 20 | 11.5 | 873.3333
2017-06-21 21:00 | 6 | 21 | 11.5 | 873.3333
2017-06-21 22:00 | 6 | 22 | 12.075 | 873.3333
2017-06-21 23:00 | 6 | 23 | 10.35 | 873.3333
2017-06-22 | 6 | 0 | 11.5 | 873.3333
2017-06-22 01:00 | 6 | 1 | 12.075 | 873.3333
2017-06-22 02:00 | 6 | 2 | 10.35 | 873.3333
2017-06-22 03:00 | 6 | 3 | 9.2 | 286.6667
2017-06-22 04:00 | 6 | 4 | 9.2 | 286.6667
2017-06-22 05:00 | 6 | 5 | 5.75 | 0
2017-06-22 06:00 | 6 | 6 | 9.2 | 286.6667
2017-06-22 07:00 | 6 | 7 | 9.2 | 286.6667
2017-06-22 08:00 | 6 | 8 | 0 | 0
2017-06-22 09:00 | 6 | 9 | 9.2 | 286.6667
2017-06-22 10:00 | 6 | 10 | 9.2 | 286.6667
2017-06-22 11:00 | 6 | 11 | 10.35 | 873.3333
2017-06-22 12:00 | 6 | 12 | 14.95 | 2773.3333
2017-06-22 13:00 | 6 | 13 | 10.925 | 873.3333
2017-06-22 14:00 | 6 | 14 | 0 | 0
2017-06-22 15:00 | 6 | 15 | 11.5 | 873.3333
2017-06-22 16:00 | 6 | 16 | 11.5 | 873.3333
2017-06-22 17:00 | 6 | 17 | 11.5 | 873.3333
2017-06-22 18:00 | 6 | 18 | 10.35 | 873.3333
2017-06-22 19:00 | 6 | 19 | 9.775 | 286.6667
2017-06-22 20:00 | 6 | 20 | 11.5 | 873.3333
2017-06-22 21:00 | 6 | 21 | 8.05 | 286.6667
2017-06-22 22:00 | 6 | 22 | 9.775 | 286.6667
2017-06-22 23:00 | 6 | 23 | 11.5 | 873.3333
2017-06-23 | 6 | 0 | 14.95 | 2773.3333
2017-06-23 01:00 | 6 | 1 | 10.925 | 873.3333
2017-06-23 02:00 | 6 | 2 | 6.9 | 0
2017-06-23 03:00 | 6 | 3 | 3.45 | 0
2017-06-23 04:00 | 6 | 4 | 7.475 | 0
2017-06-23 05:00 | 6 | 5 | 10.35 | 873.3333
2017-06-23 06:00 | 6 | 6 | 9.2 | 286.6667
2017-06-23 07:00 | 6 | 7 | 8.05 | 286.6667
2017-06-23 08:00 | 6 | 8 | 8.05 | 286.6667
2017-06-23 09:00 | 6 | 9 | 11.5 | 873.3333
2017-06-23 10:00 | 6 | 10 | 11.5 | 873.3333
2017-06-23 11:00 | 6 | 11 | 19.55 | 6160
2017-06-23 12:00 | 6 | 12 | 21.275 | 7873.3333
2017-06-23 13:00 | 6 | 13 | 21.16 | 6160
2017-06-23 14:00 | 6 | 14 | 24.15 | 9060
2017-06-23 15:00 | 6 | 15 | 19.55 | 6160
2017-06-23 16:00 | 6 | 16 | 17.825 | 4266.6667
2017-06-23 17:00 | 6 | 17 | 23 | 7873.3333
2017-06-23 18:00 | 6 | 18 | 18.4 | 4266.6667
2017-06-23 19:00 | 6 | 19 | 19.9333 | 6160
2017-06-23 20:00 | 6 | 20 | 12.65 | 1666.6667
2017-06-23 21:00 | 6 | 21 | 11.5 | 873.3333
2017-06-23 22:00 | 6 | 22 | 10.925 | 873.3333
2017-06-23 23:00 | 6 | 23 | 12.65 | 1666.6667
2017-06-24 | 6 | 0 | 12.65 | 1666.6667
2017-06-24 01:00 | 6 | 1 | 14.375 | 1666.6667
2017-06-24 02:00 | 6 | 2 | 12.65 | 1666.6667
2017-06-24 03:00 | 6 | 3 | 13.4167 | 1666.6667
2017-06-24 04:00 | 6 | 4 | 15.525 | 2773.3333
2017-06-24 05:00 | 6 | 5 | 14.95 | 2773.3333
2017-06-24 06:00 | 6 | 6 | 9.2 | 286.6667
2017-06-24 07:00 | 6 | 7 | 12.075 | 873.3333
2017-06-24 08:00 | 6 | 8 | 11.5 | 873.3333
2017-06-24 09:00 | 6 | 9 | 6.9 | 0
2017-06-24 10:00 | 6 | 10 | 10.35 | 873.3333
2017-06-24 11:00 | 6 | 11 | 10.35 | 873.3333
2017-06-24 12:00 | 6 | 12 | 14.95 | 2773.3333
2017-06-24 13:00 | 6 | 13 | 14.95 | 2773.3333
2017-06-24 14:00 | 6 | 14 | 19.55 | 6160
2017-06-24 15:00 | 6 | 15 | 24.15 | 9060
2017-06-24 16:00 | 6 | 16 | 21.275 | 7873.3333
2017-06-24 17:00 | 6 | 17 | 19.55 | 6160
2017-06-24 18:00 | 6 | 18 | 17.25 | 4266.6667
2017-06-24 19:00 | 6 | 19 | 16.675 | 2773.3333
2017-06-24 20:00 | 6 | 20 | 17.25 | 4266.6667
2017-06-24 21:00 | 6 | 21 | 16.1 | 2773.3333
2017-06-24 22:00 | 6 | 22 | 16.1 | 2773.3333
2017-06-24 23:00 | 6 | 23 | 12.65 | 1666.6667
2017-06-25 | 6 | 0 | 12.65 | 1666.6667
2017-06-25 01:00 | 6 | 1 | 10.35 | 873.3333
2017-06-25 02:00 | 6 | 2 | 10.35 | 873.3333
2017-06-25 03:00 | 6 | 3 | 10.35 | 873.3333
2017-06-25 04:00 | 6 | 4 | 10.35 | 873.3333
2017-06-25 05:00 | 6 | 5 | 12.65 | 1666.6667
2017-06-25 06:00 | 6 | 6 | 10.35 | 873.3333
2017-06-25 07:00 | 6 | 7 | 10.35 | 873.3333
2017-06-25 08:00 | 6 | 8 | 12.65 | 1666.6667
2017-06-25 09:00 | 6 | 9 | 14.95 | 2773.3333
2017-06-25 10:00 | 6 | 10 | 13.225 | 1666.6667
2017-06-25 11:00 | 6 | 11 | 9.2 | 286.6667
2017-06-25 12:00 | 6 | 12 | 11.5 | 873.3333
2017-06-25 13:00 | 6 | 13 | 10.35 | 873.3333
2017-06-25 14:00 | 6 | 14 | 8.05 | 286.6667
2017-06-25 15:00 | 6 | 15 | 20.7 | 6160
2017-06-25 16:00 | 6 | 16 | 14.95 | 2773.3333
2017-06-25 17:00 | 6 | 17 | 17.25 | 4266.6667
2017-06-25 18:00 | 6 | 18 | 19.55 | 6160
2017-06-25 19:00 | 6 | 19 | 17.25 | 4266.6667
2017-06-25 20:00 | 6 | 20 | 11.5 | 873.3333
2017-06-25 21:00 | 6 | 21 | 19.55 | 6160
2017-06-25 22:00 | 6 | 22 | 10.35 | 873.3333
2017-06-25 23:00 | 6 | 23 | 9.2 | 286.6667
2017-06-26 | 6 | 0 | 10.35 | 873.3333
2017-06-26 01:00 | 6 | 1 | 10.35 | 873.3333
2017-06-26 02:00 | 6 | 2 | 11.5 | 873.3333
2017-06-26 03:00 | 6 | 3 | 11.5 | 873.3333
2017-06-26 04:00 | 6 | 4 | 11.5 | 873.3333
2017-06-26 05:00 | 6 | 5 | 11.5 | 873.3333
2017-06-26 06:00 | 6 | 6 | 9.2 | 286.6667
2017-06-26 07:00 | 6 | 7 | 12.65 | 1666.6667
2017-06-26 08:00 | 6 | 8 | 17.25 | 4266.6667
2017-06-26 09:00 | 6 | 9 | 11.5 | 873.3333
2017-06-26 10:00 | 6 | 10 | 13.225 | 1666.6667
2017-06-26 11:00 | 6 | 11 | 18.4 | 4266.6667
2017-06-26 12:00 | 6 | 12 | 17.25 | 4266.6667
2017-06-26 13:00 | 6 | 13 | 17.25 | 4266.6667
2017-06-26 14:00 | 6 | 14 | 16.1 | 2773.3333
2017-06-26 15:00 | 6 | 15 | 11.5 | 873.3333
2017-06-26 16:00 | 6 | 16 | 12.075 | 873.3333
2017-06-26 17:00 | 6 | 17 | 17.25 | 4266.6667
2017-06-26 18:00 | 6 | 18 | 12.65 | 1666.6667
2017-06-26 19:00 | 6 | 19 | 15.525 | 2773.3333
2017-06-26 20:00 | 6 | 20 | 6.9 | 0
2017-06-26 21:00 | 6 | 21 | 11.5 | 873.3333
2017-06-26 22:00 | 6 | 22 | 9.775 | 286.6667
2017-06-26 23:00 | 6 | 23 | 6.9 | 0
2017-06-27 | 6 | 0 | 3.45 | 0
2017-06-27 01:00 | 6 | 1 | 3.45 | 0
2017-06-27 02:00 | 6 | 2 | 0 | 0
2017-06-27 03:00 | 6 | 3 | 6.9 | 0
2017-06-27 04:00 | 6 | 4 | 6.9 | 0
2017-06-27 05:00 | 6 | 5 | 6.9 | 0
2017-06-27 06:00 | 6 | 6 | 6.9 | 0
2017-06-27 07:00 | 6 | 7 | 6.325 | 0
2017-06-27 08:00 | 6 | 8 | 6.9 | 0
2017-06-27 09:00 | 6 | 9 | 10.35 | 873.3333
2017-06-27 10:00 | 6 | 10 | 8.625 | 286.6667
2017-06-27 11:00 | 6 | 11 | 8.05 | 286.6667
2017-06-27 12:00 | 6 | 12 | 8.05 | 286.6667
2017-06-27 13:00 | 6 | 13 | 13.8 | 1666.6667
2017-06-27 14:00 | 6 | 14 | 28.75 | 9873.3333
2017-06-27 15:00 | 6 | 15 | 25.3 | 9060
2017-06-27 16:00 | 6 | 16 | 19.9333 | 6160
2017-06-27 17:00 | 6 | 17 | 17.25 | 4266.6667
2017-06-27 18:00 | 6 | 18 | 13.225 | 1666.6667
2017-06-27 19:00 | 6 | 19 | 17.5375 | 4266.6667
2017-06-27 20:00 | 6 | 20 | 7.475 | 0
2017-06-27 21:00 | 6 | 21 | 6.9 | 0
2017-06-27 22:00 | 6 | 22 | 5.175 | 0
2017-06-27 23:00 | 6 | 23 | 8.05 | 286.6667
2017-06-28 | 6 | 0 | 12.65 | 1666.6667
2017-06-28 01:00 | 6 | 1 | 12.075 | 873.3333
2017-06-28 02:00 | 6 | 2 | 6.9 | 0
2017-06-28 03:00 | 6 | 3 | 10.35 | 873.3333
2017-06-28 04:00 | 6 | 4 | 10.35 | 873.3333
2017-06-28 05:00 | 6 | 5 | 12.65 | 1666.6667
2017-06-28 06:00 | 6 | 6 | 16.1 | 2773.3333
2017-06-28 07:00 | 6 | 7 | 15.525 | 2773.3333
2017-06-28 08:00 | 6 | 8 | 12.65 | 1666.6667
2017-06-28 09:00 | 6 | 9 | 14.95 | 2773.3333
2017-06-28 10:00 | 6 | 10 | 15.525 | 2773.3333
2017-06-28 11:00 | 6 | 11 | 10.35 | 873.3333
2017-06-28 12:00 | 6 | 12 | 17.25 | 4266.6667
2017-06-28 13:00 | 6 | 13 | 16.675 | 2773.3333
2017-06-28 14:00 | 6 | 14 | 17.25 | 4266.6667
2017-06-28 15:00 | 6 | 15 | 11.5 | 873.3333
2017-06-28 16:00 | 6 | 16 | 14.375 | 1666.6667
2017-06-28 17:00 | 6 | 17 | 16.1 | 2773.3333
2017-06-28 18:00 | 6 | 18 | 12.65 | 1666.6667
2017-06-28 19:00 | 6 | 19 | 10.925 | 873.3333
2017-06-28 20:00 | 6 | 20 | 8.05 | 286.6667
2017-06-28 21:00 | 6 | 21 | 8.05 | 286.6667
2017-06-28 22:00 | 6 | 22 | 9.2 | 286.6667
2017-06-28 23:00 | 6 | 23 | 12.65 | 1666.6667
2017-06-29 | 6 | 0 | 12.65 | 1666.6667
2017-06-29 01:00 | 6 | 1 | 12.075 | 873.3333
2017-06-29 02:00 | 6 | 2 | 9.2 | 286.6667
2017-06-29 03:00 | 6 | 3 | 6.9 | 0
2017-06-29 04:00 | 6 | 4 | 8.625 | 286.6667
2017-06-29 05:00 | 6 | 5 | 14.95 | 2773.3333
2017-06-29 06:00 | 6 | 6 | 10.35 | 873.3333
2017-06-29 07:00 | 6 | 7 | 12.65 | 1666.6667
2017-06-29 08:00 | 6 | 8 | 12.65 | 1666.6667
2017-06-29 09:00 | 6 | 9 | 14.95 | 2773.3333
2017-06-29 10:00 | 6 | 10 | 16.1 | 2773.3333
2017-06-29 11:00 | 6 | 11 | 12.65 | 1666.6667
2017-06-29 12:00 | 6 | 12 | 14.95 | 2773.3333
2017-06-29 13:00 | 6 | 13 | 15.525 | 2773.3333
2017-06-29 14:00 | 6 | 14 | 16.1 | 2773.3333
2017-06-29 15:00 | 6 | 15 | 14.95 | 2773.3333
2017-06-29 16:00 | 6 | 16 | 14.95 | 2773.3333
2017-06-29 17:00 | 6 | 17 | 16.1 | 2773.3333
2017-06-29 18:00 | 6 | 18 | 19.55 | 6160
2017-06-29 19:00 | 6 | 19 | 18.975 | 4266.6667
2017-06-29 20:00 | 6 | 20 | 16.1 | 2773.3333
2017-06-29 21:00 | 6 | 21 | 17.25 | 4266.6667
2017-06-29 22:00 | 6 | 22 | 16.675 | 2773.3333
2017-06-29 23:00 | 6 | 23 | 16.1 | 2773.3333
2017-06-30 | 6 | 0 | 18.4 | 4266.6667
2017-06-30 01:00 | 6 | 1 | 17.25 | 4266.6667
2017-06-30 02:00 | 6 | 2 | 17.25 | 4266.6667
2017-06-30 03:00 | 6 | 3 | 14.95 | 2773.3333
2017-06-30 04:00 | 6 | 4 | 16.1 | 2773.3333
2017-06-30 05:00 | 6 | 5 | 18.4 | 4266.6667
2017-06-30 06:00 | 6 | 6 | 20.7 | 6160
2017-06-30 07:00 | 6 | 7 | 20.7 | 6160
2017-06-30 08:00 | 6 | 8 | 18.4 | 4266.6667
2017-06-30 09:00 | 6 | 9 | 12.65 | 1666.6667
2017-06-30 10:00 | 6 | 10 | 14.375 | 1666.6667
2017-06-30 11:00 | 6 | 11 | 14.95 | 2773.3333
2017-06-30 12:00 | 6 | 12 | 12.65 | 1666.6667
2017-06-30 13:00 | 6 | 13 | 12.65 | 1666.6667
2017-06-30 14:00 | 6 | 14 | 16.1 | 2773.3333
2017-06-30 15:00 | 6 | 15 | 17.25 | 4266.6667
2017-06-30 16:00 | 6 | 16 | 17.825 | 4266.6667
2017-06-30 17:00 | 6 | 17 | 12.65 | 1666.6667
2017-06-30 18:00 | 6 | 18 | 12.65 | 1666.6667
2017-06-30 19:00 | 6 | 19 | 11.5 | 873.3333
2017-06-30 20:00 | 6 | 20 | 11.5 | 873.3333
2017-06-30 21:00 | 6 | 21 | 14.95 | 2773.3333
2017-06-30 22:00 | 6 | 22 | 13.8 | 1666.6667
2017-06-30 23:00 | 6 | 23 | 10.35 | 873.3333
2017-07-01 | 7 | 0 | 16.1 | 2773.3333
2017-07-01 01:00 | 7 | 1 | 16.675 | 2773.3333
2017-07-01 02:00 | 7 | 2 | 11.5 | 873.3333
2017-07-01 03:00 | 7 | 3 | 8.05 | 286.6667
2017-07-01 04:00 | 7 | 4 | 9.2 | 286.6667
2017-07-01 05:00 | 7 | 5 | 9.2 | 286.6667
2017-07-01 06:00 | 7 | 6 | 12.65 | 1666.6667
2017-07-01 07:00 | 7 | 7 | 14.375 | 1666.6667
2017-07-01 08:00 | 7 | 8 | 11.5 | 873.3333
2017-07-01 09:00 | 7 | 9 | 12.65 | 1666.6667
2017-07-01 10:00 | 7 | 10 | 13.8 | 1666.6667
2017-07-01 11:00 | 7 | 11 | 16.1 | 2773.3333
2017-07-01 12:00 | 7 | 12 | 20.7 | 6160
2017-07-01 13:00 | 7 | 13 | 23 | 7873.3333
2017-07-01 14:00 | 7 | 14 | 20.7 | 6160
2017-07-01 15:00 | 7 | 15 | 27.025 | 9573.3333
2017-07-01 16:00 | 7 | 16 | 22.2333 | 7873.3333
2017-07-01 17:00 | 7 | 17 | 23 | 7873.3333
2017-07-01 18:00 | 7 | 18 | 18.4 | 4266.6667
2017-07-01 19:00 | 7 | 19 | 16.675 | 2773.3333
2017-07-01 20:00 | 7 | 20 | 16.1 | 2773.3333
2017-07-01 21:00 | 7 | 21 | 12.65 | 1666.6667
2017-07-01 22:00 | 7 | 22 | 13.8 | 1666.6667
2017-07-01 23:00 | 7 | 23 | 14.375 | 1666.6667
2017-07-02 | 7 | 0 | 12.65 | 1666.6667
2017-07-02 01:00 | 7 | 1 | 12.65 | 1666.6667
2017-07-02 02:00 | 7 | 2 | 10.35 | 873.3333
2017-07-02 03:00 | 7 | 3 | 10.35 | 873.3333
2017-07-02 04:00 | 7 | 4 | 9.775 | 286.6667
2017-07-02 05:00 | 7 | 5 | 9.2 | 286.6667
2017-07-02 06:00 | 7 | 6 | 12.65 | 1666.6667
2017-07-02 07:00 | 7 | 7 | 15.525 | 2773.3333
2017-07-02 08:00 | 7 | 8 | 12.65 | 1666.6667
2017-07-02 09:00 | 7 | 9 | 14.95 | 2773.3333
2017-07-02 10:00 | 7 | 10 | 16.675 | 2773.3333
2017-07-02 11:00 | 7 | 11 | 17.25 | 4266.6667
2017-07-02 12:00 | 7 | 12 | 12.65 | 1666.6667
2017-07-02 13:00 | 7 | 13 | 14.375 | 1666.6667
2017-07-02 14:00 | 7 | 14 | 12.65 | 1666.6667
2017-07-02 15:00 | 7 | 15 | 20.7 | 6160
2017-07-02 16:00 | 7 | 16 | 22.425 | 7873.3333
2017-07-02 17:00 | 7 | 17 | 14.95 | 2773.3333
2017-07-02 18:00 | 7 | 18 | 11.5 | 873.3333
2017-07-02 19:00 | 7 | 19 | 8.625 | 286.6667
2017-07-02 20:00 | 7 | 20 | 6.9 | 0
2017-07-02 21:00 | 7 | 21 | 12.65 | 1666.6667
2017-07-02 22:00 | 7 | 22 | 11.5 | 873.3333
2017-07-02 23:00 | 7 | 23 | 6.9 | 0
2017-07-03 | 7 | 0 | 14.95 | 2773.3333
2017-07-03 01:00 | 7 | 1 | 13.225 | 1666.6667
2017-07-03 02:00 | 7 | 2 | 14.95 | 2773.3333
2017-07-03 03:00 | 7 | 3 | 11.5 | 873.3333
2017-07-03 04:00 | 7 | 4 | 11.5 | 873.3333
2017-07-03 05:00 | 7 | 5 | 14.95 | 2773.3333
2017-07-03 06:00 | 7 | 6 | 16.1 | 2773.3333
2017-07-03 07:00 | 7 | 7 | 16.1 | 2773.3333
2017-07-03 08:00 | 7 | 8 | 11.5 | 873.3333
2017-07-03 09:00 | 7 | 9 | 12.65 | 1666.6667
2017-07-03 10:00 | 7 | 10 | 16.675 | 2773.3333
2017-07-03 11:00 | 7 | 11 | 16.1 | 2773.3333
2017-07-03 12:00 | 7 | 12 | 19.55 | 6160
2017-07-03 13:00 | 7 | 13 | 19.55 | 6160
2017-07-03 14:00 | 7 | 14 | 17.25 | 4266.6667
2017-07-03 15:00 | 7 | 15 | 16.1 | 2773.3333
2017-07-03 16:00 | 7 | 16 | 19.55 | 6160
2017-07-03 17:00 | 7 | 17 | 17.25 | 4266.6667
2017-07-03 18:00 | 7 | 18 | 11.5 | 873.3333
2017-07-03 19:00 | 7 | 19 | 13.8 | 1666.6667
2017-07-03 20:00 | 7 | 20 | 10.35 | 873.3333
2017-07-03 21:00 | 7 | 21 | 10.35 | 873.3333
2017-07-03 22:00 | 7 | 22 | 9.775 | 286.6667
2017-07-03 23:00 | 7 | 23 | 12.65 | 1666.6667
2017-07-04 | 7 | 0 | 10.35 | 873.3333
2017-07-04 01:00 | 7 | 1 | 9.2 | 286.6667
2017-07-04 02:00 | 7 | 2 | 5.75 | 0
2017-07-04 03:00 | 7 | 3 | 8.05 | 286.6667
2017-07-04 04:00 | 7 | 4 | 8.05 | 286.6667
2017-07-04 05:00 | 7 | 5 | 6.9 | 0
2017-07-04 06:00 | 7 | 6 | 9.2 | 286.6667
2017-07-04 07:00 | 7 | 7 | 9.775 | 286.6667
2017-07-04 08:00 | 7 | 8 | 10.35 | 873.3333
2017-07-04 09:00 | 7 | 9 | 3.45 | 0
2017-07-04 10:00 | 7 | 10 | 6.325 | 0
2017-07-04 11:00 | 7 | 11 | 11.5 | 873.3333
2017-07-04 12:00 | 7 | 12 | 6.9 | 0
2017-07-04 13:00 | 7 | 13 | 10.35 | 873.3333
2017-07-04 14:00 | 7 | 14 | 8.05 | 286.6667
2017-07-04 15:00 | 7 | 15 | 8.05 | 286.6667
2017-07-04 16:00 | 7 | 16 | 8.625 | 286.6667
2017-07-04 17:00 | 7 | 17 | 5.75 | 0
2017-07-04 18:00 | 7 | 18 | 5.75 | 0
2017-07-04 19:00 | 7 | 19 | 5.75 | 0
2017-07-04 20:00 | 7 | 20 | 6.9 | 0
2017-07-04 21:00 | 7 | 21 | 3.45 | 0
2017-07-04 22:00 | 7 | 22 | 1.725 | 0
2017-07-04 23:00 | 7 | 23 | 0 | 0
2017-07-05 | 7 | 0 | 0 | 0
2017-07-05 01:00 | 7 | 1 | 1.725 | 0
2017-07-05 02:00 | 7 | 2 | 8.05 | 286.6667
2017-07-05 03:00 | 7 | 3 | 3.45 | 0
2017-07-05 04:00 | 7 | 4 | 4.6 | 0
2017-07-05 05:00 | 7 | 5 | 5.75 | 0
2017-07-05 06:00 | 7 | 6 | 3.45 | 0
2017-07-05 07:00 | 7 | 7 | 5.175 | 0
2017-07-05 08:00 | 7 | 8 | 9.2 | 286.6667
2017-07-05 09:00 | 7 | 9 | 9.2 | 286.6667
2017-07-05 10:00 | 7 | 10 | 9.2 | 286.6667
2017-07-05 11:00 | 7 | 11 | 9.2 | 286.6667
2017-07-05 12:00 | 7 | 12 | 14.95 | 2773.3333
2017-07-05 13:00 | 7 | 13 | 16.675 | 2773.3333
2017-07-05 14:00 | 7 | 14 | 17.25 | 4266.6667
2017-07-05 15:00 | 7 | 15 | 18.4 | 4266.6667
2017-07-05 16:00 | 7 | 16 | 17.25 | 4266.6667
2017-07-05 17:00 | 7 | 17 | 12.65 | 1666.6667
2017-07-05 18:00 | 7 | 18 | 10.35 | 873.3333
2017-07-05 19:00 | 7 | 19 | 9.775 | 286.6667
2017-07-05 20:00 | 7 | 20 | 8.05 | 286.6667
2017-07-05 21:00 | 7 | 21 | 11.5 | 873.3333
2017-07-05 22:00 | 7 | 22 | 10.925 | 873.3333
2017-07-05 23:00 | 7 | 23 | 10.35 | 873.3333
2017-07-06 | 7 | 0 | 8.05 | 286.6667
2017-07-06 01:00 | 7 | 1 | 8.05 | 286.6667
2017-07-06 02:00 | 7 | 2 | 6.9 | 0
2017-07-06 03:00 | 7 | 3 | 3.45 | 0
2017-07-06 04:00 | 7 | 4 | 5.175 | 0
2017-07-06 05:00 | 7 | 5 | 9.2 | 286.6667
2017-07-06 06:00 | 7 | 6 | 8.05 | 286.6667
2017-07-06 07:00 | 7 | 7 | 8.625 | 286.6667
2017-07-06 08:00 | 7 | 8 | 10.35 | 873.3333
2017-07-06 09:00 | 7 | 9 | 9.2 | 286.6667
2017-07-06 10:00 | 7 | 10 | 10.35 | 873.3333
2017-07-06 11:00 | 7 | 11 | 8.05 | 286.6667
2017-07-06 12:00 | 7 | 12 | 16.1 | 2773.3333
2017-07-06 13:00 | 7 | 13 | 13.225 | 1666.6667
2017-07-06 14:00 | 7 | 14 | 16.1 | 2773.3333
2017-07-06 15:00 | 7 | 15 | 16.1 | 2773.3333
2017-07-06 16:00 | 7 | 16 | 15.525 | 2773.3333
2017-07-06 17:00 | 7 | 17 | 14.95 | 2773.3333
2017-07-06 18:00 | 7 | 18 | 12.65 | 1666.6667
2017-07-06 19:00 | 7 | 19 | 13.8 | 1666.6667
2017-07-06 20:00 | 7 | 20 | 14.95 | 2773.3333
2017-07-06 21:00 | 7 | 21 | 11.5 | 873.3333
2017-07-06 22:00 | 7 | 22 | 11.5 | 873.3333
2017-07-06 23:00 | 7 | 23 | 12.65 | 1666.6667
2017-07-07 | 7 | 0 | 10.35 | 873.3333
2017-07-07 01:00 | 7 | 1 | 8.625 | 286.6667
2017-07-07 02:00 | 7 | 2 | 5.75 | 0
2017-07-07 03:00 | 7 | 3 | 3.45 | 0
2017-07-07 04:00 | 7 | 4 | 5.75 | 0
2017-07-07 05:00 | 7 | 5 | 6.9 | 0
2017-07-07 06:00 | 7 | 6 | 8.05 | 286.6667
2017-07-07 07:00 | 7 | 7 | 5.75 | 0
2017-07-07 08:00 | 7 | 8 | 6.9 | 0
2017-07-07 09:00 | 7 | 9 | 5.75 | 0
2017-07-07 10:00 | 7 | 10 | 7.2833 | 0
2017-07-07 11:00 | 7 | 11 | 10.925 | 873.3333
2017-07-07 12:00 | 7 | 12 | 11.5 | 873.3333
2017-07-07 13:00 | 7 | 13 | 10.35 | 873.3333
2017-07-07 14:00 | 7 | 14 | 16.1 | 2773.3333
2017-07-07 15:00 | 7 | 15 | 18.975 | 4266.6667
2017-07-07 16:00 | 7 | 16 | 17.0857 | 4266.6667
2017-07-07 17:00 | 7 | 17 | 14.5667 | 2773.3333
2017-07-07 18:00 | 7 | 18 | 10.35 | 873.3333
2017-07-07 19:00 | 7 | 19 | 10.35 | 873.3333
2017-07-07 20:00 | 7 | 20 | 9.2 | 286.6667
2017-07-07 21:00 | 7 | 21 | 9.2 | 286.6667
2017-07-07 22:00 | 7 | 22 | 8.625 | 286.6667
2017-07-07 23:00 | 7 | 23 | 5.75 | 0
2017-07-08 | 7 | 0 | 5.75 | 0
2017-07-08 01:00 | 7 | 1 | 4.2167 | 0
2017-07-08 02:00 | 7 | 2 | 6.9 | 0
2017-07-08 03:00 | 7 | 3 | 5.75 | 0
2017-07-08 04:00 | 7 | 4 | 5.75 | 0
2017-07-08 05:00 | 7 | 5 | 8.05 | 286.6667
2017-07-08 06:00 | 7 | 6 | 15.525 | 2773.3333
2017-07-08 07:00 | 7 | 7 | 13.4167 | 1666.6667
2017-07-08 08:00 | 7 | 8 | 11.5 | 873.3333
2017-07-08 09:00 | 7 | 9 | 9.2 | 286.6667
2017-07-08 10:00 | 7 | 10 | 10.35 | 873.3333
2017-07-08 11:00 | 7 | 11 | 18.4 | 4266.6667
2017-07-08 12:00 | 7 | 12 | 14.95 | 2773.3333
2017-07-08 13:00 | 7 | 13 | 18.4 | 4266.6667
2017-07-08 14:00 | 7 | 14 | 18.0167 | 4266.6667
2017-07-08 15:00 | 7 | 15 | 9.2 | 286.6667
2017-07-08 16:00 | 7 | 16 | 8.05 | 286.6667
2017-07-08 17:00 | 7 | 17 | 9.2 | 286.6667
2017-07-08 18:00 | 7 | 18 | 9.4875 | 286.6667
2017-07-08 19:00 | 7 | 19 | 9.775 | 286.6667
2017-07-08 20:00 | 7 | 20 | 9.2 | 286.6667
2017-07-08 21:00 | 7 | 21 | 10.35 | 873.3333
2017-07-08 22:00 | 7 | 22 | 10.925 | 873.3333
2017-07-08 23:00 | 7 | 23 | 10.35 | 873.3333
2017-07-09 | 7 | 0 | 11.5 | 873.3333
2017-07-09 01:00 | 7 | 1 | 13.225 | 1666.6667
2017-07-09 02:00 | 7 | 2 | 11.5 | 873.3333
2017-07-09 03:00 | 7 | 3 | 14.95 | 2773.3333
2017-07-09 04:00 | 7 | 4 | 13.225 | 1666.6667
2017-07-09 05:00 | 7 | 5 | 14.95 | 2773.3333
2017-07-09 06:00 | 7 | 6 | 16.1 | 2773.3333
2017-07-09 07:00 | 7 | 7 | 16.675 | 2773.3333
2017-07-09 08:00 | 7 | 8 | 14.95 | 2773.3333
2017-07-09 09:00 | 7 | 9 | 14.95 | 2773.3333
2017-07-09 10:00 | 7 | 10 | 15.525 | 2773.3333
2017-07-09 11:00 | 7 | 11 | 12.65 | 1666.6667
2017-07-09 12:00 | 7 | 12 | 12.65 | 1666.6667
2017-07-09 13:00 | 7 | 13 | 11.5 | 873.3333
2017-07-09 14:00 | 7 | 14 | 18.4 | 4266.6667
2017-07-09 15:00 | 7 | 15 | 16.1 | 2773.3333
2017-07-09 16:00 | 7 | 16 | 17.25 | 4266.6667
2017-07-09 17:00 | 7 | 17 | 11.5 | 873.3333
2017-07-09 18:00 | 7 | 18 | 12.65 | 1666.6667
2017-07-09 19:00 | 7 | 19 | 10.925 | 873.3333
2017-07-09 20:00 | 7 | 20 | 10.35 | 873.3333
2017-07-09 21:00 | 7 | 21 | 10.35 | 873.3333
2017-07-09 22:00 | 7 | 22 | 11.5 | 873.3333
2017-07-09 23:00 | 7 | 23 | 12.65 | 1666.6667
2017-07-10 | 7 | 0 | 14.95 | 2773.3333
2017-07-10 01:00 | 7 | 1 | 14.95 | 2773.3333
2017-07-10 02:00 | 7 | 2 | 11.5 | 873.3333
2017-07-10 03:00 | 7 | 3 | 10.35 | 873.3333
2017-07-10 04:00 | 7 | 4 | 9.775 | 286.6667
2017-07-10 05:00 | 7 | 5 | 8.05 | 286.6667
2017-07-10 06:00 | 7 | 6 | 9.2 | 286.6667
2017-07-10 07:00 | 7 | 7 | 10.35 | 873.3333
2017-07-10 08:00 | 7 | 8 | 14.95 | 2773.3333
2017-07-10 09:00 | 7 | 9 | 18.4 | 4266.6667
2017-07-10 10:00 | 7 | 10 | 13.8 | 1666.6667
2017-07-10 11:00 | 7 | 11 | 14.95 | 2773.3333
2017-07-10 12:00 | 7 | 12 | 11.5 | 873.3333
2017-07-10 13:00 | 7 | 13 | 14.375 | 1666.6667
2017-07-10 14:00 | 7 | 14 | 24.15 | 9060
2017-07-10 15:00 | 7 | 15 | 14.95 | 2773.3333
2017-07-10 16:00 | 7 | 16 | 16.675 | 2773.3333
2017-07-10 17:00 | 7 | 17 | 11.5 | 873.3333
2017-07-10 18:00 | 7 | 18 | 23 | 7873.3333
2017-07-10 19:00 | 7 | 19 | 20.125 | 6160
2017-07-10 20:00 | 7 | 20 | 17.25 | 4266.6667
2017-07-10 21:00 | 7 | 21 | 11.5 | 873.3333
2017-07-10 22:00 | 7 | 22 | 10.925 | 873.3333
2017-07-10 23:00 | 7 | 23 | 23 | 7873.3333
2017-07-11 | 7 | 0 | 14.95 | 2773.3333
2017-07-11 01:00 | 7 | 1 | 14.95 | 2773.3333
2017-07-11 02:00 | 7 | 2 | 10.35 | 873.3333
2017-07-11 03:00 | 7 | 3 | 8.05 | 286.6667
2017-07-11 04:00 | 7 | 4 | 9.775 | 286.6667
2017-07-11 05:00 | 7 | 5 | 9.2 | 286.6667
2017-07-11 06:00 | 7 | 6 | 8.05 | 286.6667
2017-07-11 07:00 | 7 | 7 | 8.05 | 286.6667
2017-07-11 08:00 | 7 | 8 | 3.45 | 0
2017-07-11 09:00 | 7 | 9 | 4.2167 | 0
2017-07-11 10:00 | 7 | 10 | 7.1875 | 0
2017-07-11 11:00 | 7 | 11 | 8.625 | 286.6667
2017-07-11 12:00 | 7 | 12 | 9.2 | 286.6667
2017-07-11 13:00 | 7 | 13 | 8.05 | 286.6667
2017-07-11 14:00 | 7 | 14 | 3.45 | 0
2017-07-11 15:00 | 7 | 15 | 6.9 | 0
2017-07-11 16:00 | 7 | 16 | 9.2 | 286.6667
2017-07-11 17:00 | 7 | 17 | 8.05 | 286.6667
2017-07-11 18:00 | 7 | 18 | 11.5 | 873.3333
2017-07-11 19:00 | 7 | 19 | 11.5 | 873.3333
2017-07-11 20:00 | 7 | 20 | 9.2 | 286.6667
2017-07-11 21:00 | 7 | 21 | 9.2 | 286.6667
2017-07-11 22:00 | 7 | 22 | 9.775 | 286.6667
2017-07-11 23:00 | 7 | 23 | 10.35 | 873.3333
2017-07-12 | 7 | 0 | 8.05 | 286.6667
2017-07-12 01:00 | 7 | 1 | 10.35 | 873.3333
2017-07-12 02:00 | 7 | 2 | 3.45 | 0
2017-07-12 03:00 | 7 | 3 | 6.9 | 0
2017-07-12 04:00 | 7 | 4 | 7.475 | 0
2017-07-12 05:00 | 7 | 5 | 6.9 | 0
2017-07-12 06:00 | 7 | 6 | 5.75 | 0
2017-07-12 07:00 | 7 | 7 | 5.75 | 0
2017-07-12 08:00 | 7 | 8 | 5.75 | 0
2017-07-12 09:00 | 7 | 9 | 8.05 | 286.6667
2017-07-12 10:00 | 7 | 10 | 8.05 | 286.6667
2017-07-12 11:00 | 7 | 11 | 11.5 | 873.3333
2017-07-12 12:00 | 7 | 12 | 9.775 | 286.6667
2017-07-12 13:00 | 7 | 13 | 14.1833 | 1666.6667
2017-07-12 14:00 | 7 | 14 | 18.4 | 4266.6667
2017-07-12 15:00 | 7 | 15 | 11.5 | 873.3333
2017-07-12 16:00 | 7 | 16 | 8.05 | 286.6667
2017-07-12 17:00 | 7 | 17 | 8.8167 | 286.6667
2017-07-12 18:00 | 7 | 18 | 9.0083 | 286.6667
2017-07-12 19:00 | 7 | 19 | 6.9 | 0
2017-07-12 20:00 | 7 | 20 | 3.45 | 0
2017-07-12 21:00 | 7 | 21 | 10.35 | 873.3333
2017-07-12 22:00 | 7 | 22 | 8.9125 | 286.6667
2017-07-12 23:00 | 7 | 23 | 6.9 | 0
2017-07-13 | 7 | 0 | 6.325 | 0
2017-07-13 01:00 | 7 | 1 | 8.05 | 286.6667
2017-07-13 02:00 | 7 | 2 | 5.75 | 0
2017-07-13 03:00 | 7 | 3 | 6.9 | 0
2017-07-13 04:00 | 7 | 4 | 5.175 | 0
2017-07-13 05:00 | 7 | 5 | 10.35 | 873.3333
2017-07-13 06:00 | 7 | 6 | 11.5 | 873.3333
2017-07-13 07:00 | 7 | 7 | 11.8833 | 873.3333
2017-07-13 08:00 | 7 | 8 | 9.5833 | 286.6667
2017-07-13 09:00 | 7 | 9 | 13.8 | 1666.6667
2017-07-13 10:00 | 7 | 10 | 17.25 | 4266.6667
2017-07-13 11:00 | 7 | 11 | 17.825 | 4266.6667
2017-07-13 12:00 | 7 | 12 | 17.5375 | 4266.6667
2017-07-13 13:00 | 7 | 13 | 17.6333 | 4266.6667
2017-07-13 14:00 | 7 | 14 | 18.4 | 4266.6667
2017-07-13 15:00 | 7 | 15 | 12.65 | 1666.6667
2017-07-13 16:00 | 7 | 16 | 12.2667 | 873.3333
2017-07-13 17:00 | 7 | 17 | 16.675 | 2773.3333
2017-07-13 18:00 | 7 | 18 | 11.5 | 873.3333
2017-07-13 19:00 | 7 | 19 | 13.225 | 1666.6667
2017-07-13 20:00 | 7 | 20 | 12.65 | 1666.6667
2017-07-13 21:00 | 7 | 21 | 8.05 | 286.6667
2017-07-13 22:00 | 7 | 22 | 8.8167 | 286.6667
2017-07-13 23:00 | 7 | 23 | 8.05 | 286.6667
2017-07-14 | 7 | 0 | 9.2 | 286.6667
2017-07-14 01:00 | 7 | 1 | 10.35 | 873.3333
2017-07-14 02:00 | 7 | 2 | 9.2 | 286.6667
2017-07-14 03:00 | 7 | 3 | 6.9 | 0
2017-07-14 04:00 | 7 | 4 | 6.9 | 0
2017-07-14 05:00 | 7 | 5 | 8.05 | 286.6667
2017-07-14 06:00 | 7 | 6 | 8.05 | 286.6667
2017-07-14 07:00 | 7 | 7 | 8.05 | 286.6667
2017-07-14 08:00 | 7 | 8 | 8.4333 | 286.6667
2017-07-14 09:00 | 7 | 9 | 9.2 | 286.6667
2017-07-14 10:00 | 7 | 10 | 9.5833 | 286.6667
2017-07-14 11:00 | 7 | 11 | 9.9667 | 286.6667
2017-07-14 12:00 | 7 | 12 | 10.925 | 873.3333
2017-07-14 13:00 | 7 | 13 | 9.5833 | 286.6667
2017-07-14 14:00 | 7 | 14 | 8.625 | 286.6667
2017-07-14 15:00 | 7 | 15 | 9.775 | 286.6667
2017-07-14 16:00 | 7 | 16 | 9.5833 | 286.6667
2017-07-14 17:00 | 7 | 17 | 11.5 | 873.3333
2017-07-14 18:00 | 7 | 18 | 10.35 | 873.3333
2017-07-14 19:00 | 7 | 19 | 9.775 | 286.6667
2017-07-14 20:00 | 7 | 20 | 5.75 | 0
2017-07-14 21:00 | 7 | 21 | 3.45 | 0
2017-07-14 22:00 | 7 | 22 | 4.6 | 0
2017-07-14 23:00 | 7 | 23 | 4.2167 | 0
2017-07-15 | 7 | 0 | 3.45 | 0
2017-07-15 01:00 | 7 | 1 | 4.2167 | 0
2017-07-15 02:00 | 7 | 2 | 3.45 | 0
2017-07-15 03:00 | 7 | 3 | 3.45 | 0
2017-07-15 04:00 | 7 | 4 | 5.175 | 0
2017-07-15 05:00 | 7 | 5 | 6.9 | 0
2017-07-15 06:00 | 7 | 6 | 6.9 | 0
2017-07-15 07:00 | 7 | 7 | 4.6 | 0
2017-07-15 08:00 | 7 | 8 | 5.75 | 0
2017-07-15 09:00 | 7 | 9 | 5.75 | 0
2017-07-15 10:00 | 7 | 10 | 8.625 | 286.6667
2017-07-15 11:00 | 7 | 11 | 8.05 | 286.6667
2017-07-15 12:00 | 7 | 12 | 8.05 | 286.6667
2017-07-15 13:00 | 7 | 13 | 9.2 | 286.6667
2017-07-15 14:00 | 7 | 14 | 11.5 | 873.3333
2017-07-15 15:00 | 7 | 15 | 12.65 | 1666.6667
2017-07-15 16:00 | 7 | 16 | 12.075 | 873.3333
2017-07-15 17:00 | 7 | 17 | 6.9 | 0
2017-07-15 18:00 | 7 | 18 | 6.9 | 0
2017-07-15 19:00 | 7 | 19 | 6.9 | 0
2017-07-15 20:00 | 7 | 20 | 8.05 | 286.6667
2017-07-15 21:00 | 7 | 21 | 9.2 | 286.6667
2017-07-15 22:00 | 7 | 22 | 9.2 | 286.6667
2017-07-15 23:00 | 7 | 23 | 9.2 | 286.6667
2017-07-16 | 7 | 0 | 6.9 | 0
2017-07-16 01:00 | 7 | 1 | 8.625 | 286.6667
2017-07-16 02:00 | 7 | 2 | 10.35 | 873.3333
2017-07-16 03:00 | 7 | 3 | 9.2 | 286.6667
2017-07-16 04:00 | 7 | 4 | 9.2 | 286.6667
2017-07-16 05:00 | 7 | 5 | 12.65 | 1666.6667
2017-07-16 06:00 | 7 | 6 | 9.2 | 286.6667
2017-07-16 07:00 | 7 | 7 | 8.625 | 286.6667
2017-07-16 08:00 | 7 | 8 | 3.45 | 0
2017-07-16 09:00 | 7 | 9 | 10.35 | 873.3333
2017-07-16 10:00 | 7 | 10 | 10.925 | 873.3333
2017-07-16 11:00 | 7 | 11 | 14.95 | 2773.3333
2017-07-16 12:00 | 7 | 12 | 12.65 | 1666.6667
2017-07-16 13:00 | 7 | 13 | 14.95 | 2773.3333
2017-07-16 14:00 | 7 | 14 | 18.4 | 4266.6667
2017-07-16 15:00 | 7 | 15 | 16.1 | 2773.3333
2017-07-16 16:00 | 7 | 16 | 15.525 | 2773.3333
2017-07-16 17:00 | 7 | 17 | 10.35 | 873.3333
2017-07-16 18:00 | 7 | 18 | 10.35 | 873.3333
2017-07-16 19:00 | 7 | 19 | 10.925 | 873.3333
2017-07-16 20:00 | 7 | 20 | 8.05 | 286.6667
2017-07-16 21:00 | 7 | 21 | 9.2 | 286.6667
2017-07-16 22:00 | 7 | 22 | 8.625 | 286.6667
2017-07-16 23:00 | 7 | 23 | 8.05 | 286.6667
2017-07-17 | 7 | 0 | 5.75 | 0
2017-07-17 01:00 | 7 | 1 | 2.875 | 0
2017-07-17 02:00 | 7 | 2 | 6.9 | 0
2017-07-17 03:00 | 7 | 3 | 10.35 | 873.3333
2017-07-17 04:00 | 7 | 4 | 9.2 | 286.6667
2017-07-17 05:00 | 7 | 5 | 6.9 | 0
2017-07-17 06:00 | 7 | 6 | 6.9 | 0
2017-07-17 07:00 | 7 | 7 | 7.475 | 0
2017-07-17 08:00 | 7 | 8 | 8.05 | 286.6667
2017-07-17 09:00 | 7 | 9 | 9.2 | 286.6667
2017-07-17 10:00 | 7 | 10 | 10.35 | 873.3333
2017-07-17 11:00 | 7 | 11 | 14.95 | 2773.3333
2017-07-17 12:00 | 7 | 12 | 12.65 | 1666.6667
2017-07-17 13:00 | 7 | 13 | 12.075 | 873.3333
2017-07-17 14:00 | 7 | 14 | 12.65 | 1666.6667
2017-07-17 15:00 | 7 | 15 | 11.5 | 873.3333
2017-07-17 16:00 | 7 | 16 | 12.075 | 873.3333
2017-07-17 17:00 | 7 | 17 | 14.95 | 2773.3333
2017-07-17 18:00 | 7 | 18 | 14.95 | 2773.3333
2017-07-17 19:00 | 7 | 19 | 13.225 | 1666.6667
2017-07-17 20:00 | 7 | 20 | 9.2 | 286.6667
2017-07-17 21:00 | 7 | 21 | 9.2 | 286.6667
2017-07-17 22:00 | 7 | 22 | 9.775 | 286.6667
2017-07-17 23:00 | 7 | 23 | 3.45 | 0
2017-07-18 | 7 | 0 | 6.325 | 0
2017-07-18 01:00 | 7 | 1 | 6.1333 | 0
2017-07-18 02:00 | 7 | 2 | 9.2 | 286.6667
2017-07-18 03:00 | 7 | 3 | 6.9 | 0
2017-07-18 04:00 | 7 | 4 | 6.9 | 0
2017-07-18 05:00 | 7 | 5 | 10.925 | 873.3333
2017-07-18 06:00 | 7 | 6 | 8.05 | 286.6667
2017-07-18 07:00 | 7 | 7 | 10.35 | 873.3333
2017-07-18 08:00 | 7 | 8 | 9.2 | 286.6667
2017-07-18 09:00 | 7 | 9 | 7.2833 | 0
2017-07-18 10:00 | 7 | 10 | 9.2 | 286.6667
2017-07-18 11:00 | 7 | 11 | 16.1 | 2773.3333
2017-07-18 12:00 | 7 | 12 | 8.05 | 286.6667
2017-07-18 13:00 | 7 | 13 | 11.5 | 873.3333
2017-07-18 14:00 | 7 | 14 | 8.05 | 286.6667
2017-07-18 15:00 | 7 | 15 | 8.05 | 286.6667
2017-07-18 16:00 | 7 | 16 | 8.625 | 286.6667
2017-07-18 17:00 | 7 | 17 | 8.05 | 286.6667
2017-07-18 18:00 | 7 | 18 | 10.35 | 873.3333
2017-07-18 19:00 | 7 | 19 | 6.325 | 0
2017-07-18 20:00 | 7 | 20 | 10.35 | 873.3333
2017-07-18 21:00 | 7 | 21 | 9.2 | 286.6667
2017-07-18 22:00 | 7 | 22 | 9.775 | 286.6667
2017-07-18 23:00 | 7 | 23 | 10.35 | 873.3333
2017-07-19 | 7 | 0 | 10.35 | 873.3333
2017-07-19 01:00 | 7 | 1 | 6.9 | 0
2017-07-19 02:00 | 7 | 2 | 6.9 | 0
2017-07-19 03:00 | 7 | 3 | 5.75 | 0
2017-07-19 04:00 | 7 | 4 | 6.9 | 0
2017-07-19 05:00 | 7 | 5 | 8.05 | 286.6667
2017-07-19 06:00 | 7 | 6 | 9.2 | 286.6667
2017-07-19 07:00 | 7 | 7 | 8.05 | 286.6667
2017-07-19 08:00 | 7 | 8 | 9.2 | 286.6667
2017-07-19 09:00 | 7 | 9 | 10.35 | 873.3333
2017-07-19 10:00 | 7 | 10 | 11.5 | 873.3333
2017-07-19 11:00 | 7 | 11 | 6.9 | 0
2017-07-19 12:00 | 7 | 12 | 14.95 | 2773.3333
2017-07-19 13:00 | 7 | 13 | 16.675 | 2773.3333
2017-07-19 14:00 | 7 | 14 | 16.1 | 2773.3333
2017-07-19 15:00 | 7 | 15 | 10.35 | 873.3333
2017-07-19 16:00 | 7 | 16 | 11.5 | 873.3333
2017-07-19 17:00 | 7 | 17 | 18.4 | 4266.6667
2017-07-19 18:00 | 7 | 18 | 11.5 | 873.3333
2017-07-19 19:00 | 7 | 19 | 12.075 | 873.3333
2017-07-19 20:00 | 7 | 20 | 8.05 | 286.6667
2017-07-19 21:00 | 7 | 21 | 8.05 | 286.6667
2017-07-19 22:00 | 7 | 22 | 8.625 | 286.6667
2017-07-19 23:00 | 7 | 23 | 9.2 | 286.6667
2017-07-20 | 7 | 0 | 10.35 | 873.3333
2017-07-20 01:00 | 7 | 1 | 6.9 | 0
2017-07-20 02:00 | 7 | 2 | 6.9 | 0
2017-07-20 03:00 | 7 | 3 | 0 | 0
2017-07-20 04:00 | 7 | 4 | 3.45 | 0
2017-07-20 05:00 | 7 | 5 | 9.2 | 286.6667
2017-07-20 06:00 | 7 | 6 | 9.2 | 286.6667
2017-07-20 07:00 | 7 | 7 | 8.05 | 286.6667
2017-07-20 08:00 | 7 | 8 | 9.2 | 286.6667
2017-07-20 09:00 | 7 | 9 | 9.2 | 286.6667
2017-07-20 10:00 | 7 | 10 | 10.35 | 873.3333
2017-07-20 11:00 | 7 | 11 | 10.35 | 873.3333
2017-07-20 12:00 | 7 | 12 | 12.65 | 1666.6667
2017-07-20 13:00 | 7 | 13 | 10.925 | 873.3333
2017-07-20 14:00 | 7 | 14 | 12.65 | 1666.6667
2017-07-20 15:00 | 7 | 15 | 12.65 | 1666.6667
2017-07-20 16:00 | 7 | 16 | 14.375 | 1666.6667
2017-07-20 17:00 | 7 | 17 | 11.5 | 873.3333
2017-07-20 18:00 | 7 | 18 | 6.9 | 0
2017-07-20 19:00 | 7 | 19 | 10.925 | 873.3333
2017-07-20 20:00 | 7 | 20 | 5.75 | 0
2017-07-20 21:00 | 7 | 21 | 5.75 | 0
2017-07-20 22:00 | 7 | 22 | 5.75 | 0
2017-07-20 23:00 | 7 | 23 | 5.75 | 0
2017-07-21 | 7 | 0 | 3.45 | 0
2017-07-21 01:00 | 7 | 1 | 4.6 | 0
2017-07-21 02:00 | 7 | 2 | 8.05 | 286.6667
2017-07-21 03:00 | 7 | 3 | 9.2 | 286.6667
2017-07-21 04:00 | 7 | 4 | 8.625 | 286.6667
2017-07-21 05:00 | 7 | 5 | 8.05 | 286.6667
2017-07-21 06:00 | 7 | 6 | 8.05 | 286.6667
2017-07-21 07:00 | 7 | 7 | 9.775 | 286.6667
2017-07-21 08:00 | 7 | 8 | 11.5 | 873.3333
2017-07-21 09:00 | 7 | 9 | 14.95 | 2773.3333
2017-07-21 10:00 | 7 | 10 | 13.225 | 1666.6667
2017-07-21 11:00 | 7 | 11 | 12.65 | 1666.6667
2017-07-21 12:00 | 7 | 12 | 11.5 | 873.3333
2017-07-21 13:00 | 7 | 13 | 11.5 | 873.3333
2017-07-21 14:00 | 7 | 14 | 12.65 | 1666.6667
2017-07-21 15:00 | 7 | 15 | 10.35 | 873.3333
2017-07-21 16:00 | 7 | 16 | 13.225 | 1666.6667
2017-07-21 17:00 | 7 | 17 | 14.95 | 2773.3333
2017-07-21 18:00 | 7 | 18 | 16.1 | 2773.3333
2017-07-21 19:00 | 7 | 19 | 15.525 | 2773.3333
2017-07-21 20:00 | 7 | 20 | 14.95 | 2773.3333
2017-07-21 21:00 | 7 | 21 | 12.65 | 1666.6667
2017-07-21 22:00 | 7 | 22 | 14.375 | 1666.6667
2017-07-21 23:00 | 7 | 23 | 16.1 | 2773.3333
2017-07-22 | 7 | 0 | 12.65 | 1666.6667
2017-07-22 01:00 | 7 | 1 | 12.65 | 1666.6667
2017-07-22 02:00 | 7 | 2 | 11.5 | 873.3333
2017-07-22 03:00 | 7 | 3 | 11.5 | 873.3333
2017-07-22 04:00 | 7 | 4 | 11.5 | 873.3333
2017-07-22 05:00 | 7 | 5 | 11.5 | 873.3333
2017-07-22 06:00 | 7 | 6 | 9.2 | 286.6667
2017-07-22 07:00 | 7 | 7 | 9.775 | 286.6667
2017-07-22 08:00 | 7 | 8 | 3.45 | 0
2017-07-22 09:00 | 7 | 9 | 5.75 | 0
2017-07-22 10:00 | 7 | 10 | 6.325 | 0
2017-07-22 11:00 | 7 | 11 | 6.9 | 0
2017-07-22 12:00 | 7 | 12 | 9.2 | 286.6667
2017-07-22 13:00 | 7 | 13 | 10.925 | 873.3333
2017-07-22 14:00 | 7 | 14 | 10.35 | 873.3333
2017-07-22 15:00 | 7 | 15 | 8.05 | 286.6667
2017-07-22 16:00 | 7 | 16 | 6.9 | 0
2017-07-22 17:00 | 7 | 17 | 3.45 | 0
2017-07-22 18:00 | 7 | 18 | 6.9 | 0
2017-07-22 19:00 | 7 | 19 | 7.475 | 0
2017-07-22 20:00 | 7 | 20 | 6.9 | 0
2017-07-22 21:00 | 7 | 21 | 3.45 | 0
2017-07-22 22:00 | 7 | 22 | 5.75 | 0
2017-07-22 23:00 | 7 | 23 | 6.9 | 0
2017-07-23 | 7 | 0 | 3.45 | 0
2017-07-23 01:00 | 7 | 1 | 11.5 | 873.3333
2017-07-23 02:00 | 7 | 2 | 23 | 7873.3333
2017-07-23 03:00 | 7 | 3 | 26.45 | 9573.3333
2017-07-23 04:00 | 7 | 4 | 23 | 7873.3333
2017-07-23 05:00 | 7 | 5 | 17.25 | 4266.6667
2017-07-23 06:00 | 7 | 6 | 17.25 | 4266.6667
2017-07-23 07:00 | 7 | 7 | 18.975 | 4266.6667
2017-07-23 08:00 | 7 | 8 | 17.25 | 4266.6667
2017-07-23 09:00 | 7 | 9 | 16.1 | 2773.3333
2017-07-23 10:00 | 7 | 10 | 16.675 | 2773.3333
2017-07-23 11:00 | 7 | 11 | 16.1 | 2773.3333
2017-07-23 12:00 | 7 | 12 | 16.1 | 2773.3333
2017-07-23 13:00 | 7 | 13 | 15.525 | 2773.3333
2017-07-23 14:00 | 7 | 14 | 12.65 | 1666.6667
2017-07-23 15:00 | 7 | 15 | 12.65 | 1666.6667
2017-07-23 16:00 | 7 | 16 | 12.65 | 1666.6667
2017-07-23 17:00 | 7 | 17 | 11.5 | 873.3333
2017-07-23 18:00 | 7 | 18 | 10.35 | 873.3333
2017-07-23 19:00 | 7 | 19 | 9.2 | 286.6667
2017-07-23 20:00 | 7 | 20 | 6.9 | 0
2017-07-23 21:00 | 7 | 21 | 5.75 | 0
2017-07-23 22:00 | 7 | 22 | 5.75 | 0
2017-07-23 23:00 | 7 | 23 | 5.75 | 0
2017-07-24 | 7 | 0 | 0 | 0
2017-07-24 01:00 | 7 | 1 | 1.725 | 0
2017-07-24 02:00 | 7 | 2 | 6.9 | 0
2017-07-24 03:00 | 7 | 3 | 10.35 | 873.3333
2017-07-24 04:00 | 7 | 4 | 10.35 | 873.3333
2017-07-24 05:00 | 7 | 5 | 10.35 | 873.3333
2017-07-24 06:00 | 7 | 6 | 16.1 | 2773.3333
2017-07-24 07:00 | 7 | 7 | 16.675 | 2773.3333
2017-07-24 08:00 | 7 | 8 | 23 | 7873.3333
2017-07-24 09:00 | 7 | 9 | 24.15 | 9060
2017-07-24 10:00 | 7 | 10 | 25.3 | 9060
2017-07-24 11:00 | 7 | 11 | 20.3167 | 6160
2017-07-24 12:00 | 7 | 12 | 20.47 | 6160
2017-07-24 13:00 | 7 | 13 | 20.125 | 6160
2017-07-24 14:00 | 7 | 14 | 18.975 | 4266.6667
2017-07-24 15:00 | 7 | 15 | 20.125 | 6160
2017-07-24 16:00 | 7 | 16 | 21.4667 | 7873.3333
2017-07-24 17:00 | 7 | 17 | 20.7 | 6160
2017-07-24 18:00 | 7 | 18 | 19.9333 | 6160
2017-07-24 19:00 | 7 | 19 | 17.825 | 4266.6667
2017-07-24 20:00 | 7 | 20 | 13.8 | 1666.6667
2017-07-24 21:00 | 7 | 21 | 16.1 | 2773.3333
2017-07-24 22:00 | 7 | 22 | 15.525 | 2773.3333
2017-07-24 23:00 | 7 | 23 | 12.65 | 1666.6667
2017-07-25 | 7 | 0 | 14.95 | 2773.3333
2017-07-25 01:00 | 7 | 1 | 13.225 | 1666.6667
2017-07-25 02:00 | 7 | 2 | 11.1167 | 873.3333
2017-07-25 03:00 | 7 | 3 | 10.925 | 873.3333
2017-07-25 04:00 | 7 | 4 | 10.35 | 873.3333
2017-07-25 05:00 | 7 | 5 | 9.2 | 286.6667
2017-07-25 06:00 | 7 | 6 | 10.35 | 873.3333
2017-07-25 07:00 | 7 | 7 | 11.5 | 873.3333
2017-07-25 08:00 | 7 | 8 | 11.5 | 873.3333
2017-07-25 09:00 | 7 | 9 | 12.075 | 873.3333
2017-07-25 10:00 | 7 | 10 | 13.8 | 1666.6667
2017-07-25 11:00 | 7 | 11 | 6.9 | 0
2017-07-25 12:00 | 7 | 12 | 11.5 | 873.3333
2017-07-25 13:00 | 7 | 13 | 11.5 | 873.3333
2017-07-25 14:00 | 7 | 14 | 10.35 | 873.3333
2017-07-25 15:00 | 7 | 15 | 13.225 | 1666.6667
2017-07-25 16:00 | 7 | 16 | 12.65 | 1666.6667
2017-07-25 17:00 | 7 | 17 | 6.9 | 0
2017-07-25 18:00 | 7 | 18 | 3.45 | 0
2017-07-25 19:00 | 7 | 19 | 3.45 | 0
2017-07-25 20:00 | 7 | 20 | 0 | 0
2017-07-25 21:00 | 7 | 21 | 5.75 | 0
2017-07-25 22:00 | 7 | 22 | 5.75 | 0
2017-07-25 23:00 | 7 | 23 | 6.9 | 0
2017-07-26 | 7 | 0 | 3.45 | 0
2017-07-26 01:00 | 7 | 1 | 3.45 | 0
2017-07-26 02:00 | 7 | 2 | 6.9 | 0
2017-07-26 03:00 | 7 | 3 | 5.75 | 0
2017-07-26 04:00 | 7 | 4 | 7.475 | 0
2017-07-26 05:00 | 7 | 5 | 5.75 | 0
2017-07-26 06:00 | 7 | 6 | 3.45 | 0
2017-07-26 07:00 | 7 | 7 | 3.45 | 0
2017-07-26 08:00 | 7 | 8 | 6.9 | 0
2017-07-26 09:00 | 7 | 9 | 9.2 | 286.6667
2017-07-26 10:00 | 7 | 10 | 10.35 | 873.3333
2017-07-26 11:00 | 7 | 11 | 10.35 | 873.3333
2017-07-26 12:00 | 7 | 12 | 11.5 | 873.3333
2017-07-26 13:00 | 7 | 13 | 10.925 | 873.3333
2017-07-26 14:00 | 7 | 14 | 11.5 | 873.3333
2017-07-26 15:00 | 7 | 15 | 17.25 | 4266.6667
2017-07-26 16:00 | 7 | 16 | 16.675 | 2773.3333
2017-07-26 17:00 | 7 | 17 | 10.35 | 873.3333
2017-07-26 18:00 | 7 | 18 | 8.05 | 286.6667
2017-07-26 19:00 | 7 | 19 | 9.2 | 286.6667
2017-07-26 20:00 | 7 | 20 | 14.95 | 2773.3333
2017-07-26 21:00 | 7 | 21 | 12.65 | 1666.6667
2017-07-26 22:00 | 7 | 22 | 12.075 | 873.3333
2017-07-26 23:00 | 7 | 23 | 11.5 | 873.3333
2017-07-27 | 7 | 0 | 12.65 | 1666.6667
2017-07-27 01:00 | 7 | 1 | 11.5 | 873.3333
2017-07-27 02:00 | 7 | 2 | 14.95 | 2773.3333
2017-07-27 03:00 | 7 | 3 | 11.5 | 873.3333
2017-07-27 04:00 | 7 | 4 | 12.075 | 873.3333
2017-07-27 05:00 | 7 | 5 | 12.65 | 1666.6667
2017-07-27 06:00 | 7 | 6 | 12.65 | 1666.6667
2017-07-27 07:00 | 7 | 7 | 12.65 | 1666.6667
2017-07-27 08:00 | 7 | 8 | 12.65 | 1666.6667
2017-07-27 09:00 | 7 | 9 | 20.7 | 6160
2017-07-27 10:00 | 7 | 10 | 18.975 | 4266.6667
2017-07-27 11:00 | 7 | 11 | 18.4 | 4266.6667
2017-07-27 12:00 | 7 | 12 | 17.25 | 4266.6667
2017-07-27 13:00 | 7 | 13 | 16.1 | 2773.3333
2017-07-27 14:00 | 7 | 14 | 17.25 | 4266.6667
2017-07-27 15:00 | 7 | 15 | 10.35 | 873.3333
2017-07-27 16:00 | 7 | 16 | 11.5 | 873.3333
2017-07-27 17:00 | 7 | 17 | 12.075 | 873.3333
2017-07-27 18:00 | 7 | 18 | 12.65 | 1666.6667
2017-07-27 19:00 | 7 | 19 | 11.5 | 873.3333
2017-07-27 20:00 | 7 | 20 | 12.65 | 1666.6667
2017-07-27 21:00 | 7 | 21 | 14.95 | 2773.3333
2017-07-27 22:00 | 7 | 22 | 14.95 | 2773.3333
2017-07-27 23:00 | 7 | 23 | 12.65 | 1666.6667
2017-07-28 | 7 | 0 | 9.2 | 286.6667
2017-07-28 01:00 | 7 | 1 | 9.775 | 286.6667
2017-07-28 02:00 | 7 | 2 | 11.5 | 873.3333
2017-07-28 03:00 | 7 | 3 | 6.9 | 0
2017-07-28 04:00 | 7 | 4 | 8.05 | 286.6667
2017-07-28 05:00 | 7 | 5 | 9.2 | 286.6667
2017-07-28 06:00 | 7 | 6 | 9.2 | 286.6667
2017-07-28 07:00 | 7 | 7 | 10.925 | 873.3333
2017-07-28 08:00 | 7 | 8 | 11.5 | 873.3333
2017-07-28 09:00 | 7 | 9 | 10.35 | 873.3333
2017-07-28 10:00 | 7 | 10 | 9.775 | 286.6667
2017-07-28 11:00 | 7 | 11 | 0 | 0
2017-07-28 12:00 | 7 | 12 | 9.2 | 286.6667
2017-07-28 13:00 | 7 | 13 | 9.2 | 286.6667
2017-07-28 14:00 | 7 | 14 | 10.35 | 873.3333
2017-07-28 15:00 | 7 | 15 | 12.65 | 1666.6667
2017-07-28 16:00 | 7 | 16 | 11.5 | 873.3333
2017-07-28 17:00 | 7 | 17 | 8.05 | 286.6667
2017-07-28 18:00 | 7 | 18 | 10.35 | 873.3333
2017-07-28 19:00 | 7 | 19 | 5.175 | 0
2017-07-28 20:00 | 7 | 20 | 6.9 | 0
2017-07-28 21:00 | 7 | 21 | 6.9 | 0
2017-07-28 22:00 | 7 | 22 | 8.05 | 286.6667
2017-07-28 23:00 | 7 | 23 | 11.5 | 873.3333
2017-07-29 | 7 | 0 | 16.1 | 2773.3333
2017-07-29 01:00 | 7 | 1 | 18.4 | 4266.6667
2017-07-29 02:00 | 7 | 2 | 20.7 | 6160
2017-07-29 03:00 | 7 | 3 | 14.95 | 2773.3333
2017-07-29 04:00 | 7 | 4 | 16.675 | 2773.3333
2017-07-29 05:00 | 7 | 5 | 17.25 | 4266.6667
2017-07-29 06:00 | 7 | 6 | 14.95 | 2773.3333
2017-07-29 07:00 | 7 | 7 | 16.675 | 2773.3333
2017-07-29 08:00 | 7 | 8 | 18.4 | 4266.6667
2017-07-29 09:00 | 7 | 9 | 24.15 | 9060
2017-07-29 10:00 | 7 | 10 | 19.55 | 6160
2017-07-29 11:00 | 7 | 11 | 23 | 7873.3333
2017-07-29 12:00 | 7 | 12 | 20.7 | 6160
2017-07-29 13:00 | 7 | 13 | 19.55 | 6160
2017-07-29 14:00 | 7 | 14 | 11.5 | 873.3333
2017-07-29 15:00 | 7 | 15 | 11.5 | 873.3333
2017-07-29 16:00 | 7 | 16 | 14.375 | 1666.6667
2017-07-29 17:00 | 7 | 17 | 17.25 | 4266.6667
2017-07-29 18:00 | 7 | 18 | 11.5 | 873.3333
2017-07-29 19:00 | 7 | 19 | 10.925 | 873.3333
2017-07-29 20:00 | 7 | 20 | 11.5 | 873.3333
2017-07-29 21:00 | 7 | 21 | 9.2 | 286.6667
2017-07-29 22:00 | 7 | 22 | 9.2 | 286.6667
2017-07-29 23:00 | 7 | 23 | 10.35 | 873.3333
2017-07-30 | 7 | 0 | 11.5 | 873.3333
2017-07-30 01:00 | 7 | 1 | 9.775 | 286.6667
2017-07-30 02:00 | 7 | 2 | 10.35 | 873.3333
2017-07-30 03:00 | 7 | 3 | 14.95 | 2773.3333
2017-07-30 04:00 | 7 | 4 | 12.65 | 1666.6667
2017-07-30 05:00 | 7 | 5 | 12.65 | 1666.6667
2017-07-30 06:00 | 7 | 6 | 12.65 | 1666.6667
2017-07-30 07:00 | 7 | 7 | 12.075 | 873.3333
2017-07-30 08:00 | 7 | 8 | 9.2 | 286.6667
2017-07-30 09:00 | 7 | 9 | 11.5 | 873.3333
2017-07-30 10:00 | 7 | 10 | 13.8 | 1666.6667
2017-07-30 11:00 | 7 | 11 | 17.25 | 4266.6667
2017-07-30 12:00 | 7 | 12 | 14.95 | 2773.3333
2017-07-30 13:00 | 7 | 13 | 13.8 | 1666.6667
2017-07-30 14:00 | 7 | 14 | 14.95 | 2773.3333
2017-07-30 15:00 | 7 | 15 | 11.5 | 873.3333
2017-07-30 16:00 | 7 | 16 | 12.075 | 873.3333
2017-07-30 17:00 | 7 | 17 | 11.5 | 873.3333
2017-07-30 18:00 | 7 | 18 | 8.05 | 286.6667
2017-07-30 19:00 | 7 | 19 | 7.475 | 0
2017-07-30 20:00 | 7 | 20 | 9.2 | 286.6667
2017-07-30 21:00 | 7 | 21 | 8.05 | 286.6667
2017-07-30 22:00 | 7 | 22 | 9.2 | 286.6667
2017-07-30 23:00 | 7 | 23 | 8.05 | 286.6667
2017-07-31 | 7 | 0 | 6.9 | 0
2017-07-31 01:00 | 7 | 1 | 6.9 | 0
2017-07-31 02:00 | 7 | 2 | 9.2 | 286.6667
2017-07-31 03:00 | 7 | 3 | 9.2 | 286.6667
2017-07-31 04:00 | 7 | 4 | 8.625 | 286.6667
2017-07-31 05:00 | 7 | 5 | 6.9 | 0
2017-07-31 06:00 | 7 | 6 | 0 | 0
2017-07-31 07:00 | 7 | 7 | 2.875 | 0
2017-07-31 08:00 | 7 | 8 | 5.75 | 0
2017-07-31 09:00 | 7 | 9 | 6.9 | 0
2017-07-31 10:00 | 7 | 10 | 8.05 | 286.6667
2017-07-31 11:00 | 7 | 11 | 10.35 | 873.3333
2017-07-31 12:00 | 7 | 12 | 14.95 | 2773.3333
2017-07-31 13:00 | 7 | 13 | 14.95 | 2773.3333
2017-07-31 14:00 | 7 | 14 | 17.25 | 4266.6667
2017-07-31 15:00 | 7 | 15 | 16.1 | 2773.3333
2017-07-31 16:00 | 7 | 16 | 14.375 | 1666.6667
2017-07-31 17:00 | 7 | 17 | 10.35 | 873.3333
2017-07-31 18:00 | 7 | 18 | 16.1 | 2773.3333
2017-07-31 19:00 | 7 | 19 | 13.225 | 1666.6667
2017-07-31 20:00 | 7 | 20 | 12.65 | 1666.6667
2017-07-31 21:00 | 7 | 21 | 5.75 | 0
2017-07-31 22:00 | 7 | 22 | 6.9 | 0
2017-07-31 23:00 | 7 | 23 | 11.5 | 873.3333
2017-08-01 | 8 | 0 | 8.05 | 286.6667
2017-08-01 01:00 | 8 | 1 | 9.2 | 286.6667
2017-08-01 02:00 | 8 | 2 | 6.9 | 0
2017-08-01 03:00 | 8 | 3 | 8.05 | 286.6667
2017-08-01 04:00 | 8 | 4 | 6.9 | 0
2017-08-01 05:00 | 8 | 5 | 9.2 | 286.6667
2017-08-01 06:00 | 8 | 6 | 8.05 | 286.6667
2017-08-01 07:00 | 8 | 7 | 6.9 | 0
2017-08-01 08:00 | 8 | 8 | 5.75 | 0
2017-08-01 09:00 | 8 | 9 | 9.2 | 286.6667
2017-08-01 10:00 | 8 | 10 | 9.775 | 286.6667
2017-08-01 11:00 | 8 | 11 | 11.5 | 873.3333
2017-08-01 12:00 | 8 | 12 | 14.95 | 2773.3333
2017-08-01 13:00 | 8 | 13 | 14.95 | 2773.3333
2017-08-01 14:00 | 8 | 14 | 14.95 | 2773.3333
2017-08-01 15:00 | 8 | 15 | 14.95 | 2773.3333
2017-08-01 16:00 | 8 | 16 | 13.8 | 1666.6667
2017-08-01 17:00 | 8 | 17 | 6.9 | 0
2017-08-01 18:00 | 8 | 18 | 6.9 | 0
2017-08-01 19:00 | 8 | 19 | 6.325 | 0
2017-08-01 20:00 | 8 | 20 | 3.45 | 0
2017-08-01 21:00 | 8 | 21 | 0 | 0
2017-08-01 22:00 | 8 | 22 | 4.6 | 0
2017-08-01 23:00 | 8 | 23 | 9.2 | 286.6667
2017-08-02 | 8 | 0 | 9.2 | 286.6667
2017-08-02 01:00 | 8 | 1 | 8.625 | 286.6667
2017-08-02 02:00 | 8 | 2 | 5.75 | 0
2017-08-02 03:00 | 8 | 3 | 5.75 | 0
2017-08-02 04:00 | 8 | 4 | 6.325 | 0
2017-08-02 05:00 | 8 | 5 | 8.05 | 286.6667
2017-08-02 06:00 | 8 | 6 | 5.75 | 0
2017-08-02 07:00 | 8 | 7 | 6.9 | 0
2017-08-02 08:00 | 8 | 8 | 9.2 | 286.6667
2017-08-02 09:00 | 8 | 9 | 10.35 | 873.3333
2017-08-02 10:00 | 8 | 10 | 10.925 | 873.3333
2017-08-02 11:00 | 8 | 11 | 12.65 | 1666.6667
2017-08-02 12:00 | 8 | 12 | 12.65 | 1666.6667
2017-08-02 13:00 | 8 | 13 | 16.675 | 2773.3333
2017-08-02 14:00 | 8 | 14 | 7.475 | 0
2017-08-02 15:00 | 8 | 15 | 16.675 | 2773.3333
2017-08-02 16:00 | 8 | 16 | 16.9625 | 4266.6667
2017-08-02 17:00 | 8 | 17 | 18.1125 | 4266.6667
2017-08-02 18:00 | 8 | 18 | 10.35 | 873.3333
2017-08-02 19:00 | 8 | 19 | 13.4167 | 1666.6667
2017-08-02 20:00 | 8 | 20 | 8.05 | 286.6667
2017-08-02 21:00 | 8 | 21 | 5.75 | 0
2017-08-02 22:00 | 8 | 22 | 4.6 | 0
2017-08-02 23:00 | 8 | 23 | 5.75 | 0
2017-08-03 | 8 | 0 | 7.475 | 0
2017-08-03 01:00 | 8 | 1 | 6.9 | 0
2017-08-03 02:00 | 8 | 2 | 5.75 | 0
2017-08-03 03:00 | 8 | 3 | 8.05 | 286.6667
2017-08-03 04:00 | 8 | 4 | 8.05 | 286.6667
2017-08-03 05:00 | 8 | 5 | 8.05 | 286.6667
2017-08-03 06:00 | 8 | 6 | 10.35 | 873.3333
2017-08-03 07:00 | 8 | 7 | 9.5833 | 286.6667
2017-08-03 08:00 | 8 | 8 | 11.5 | 873.3333
2017-08-03 09:00 | 8 | 9 | 11.5 | 873.3333
2017-08-03 10:00 | 8 | 10 | 13.225 | 1666.6667
2017-08-03 11:00 | 8 | 11 | 14.95 | 2773.3333
2017-08-03 12:00 | 8 | 12 | 14.95 | 2773.3333
2017-08-03 13:00 | 8 | 13 | 13.225 | 1666.6667
2017-08-03 14:00 | 8 | 14 | 12.65 | 1666.6667
2017-08-03 15:00 | 8 | 15 | 14.95 | 2773.3333
2017-08-03 16:00 | 8 | 16 | 16.1 | 2773.3333
2017-08-03 17:00 | 8 | 17 | 14.95 | 2773.3333
2017-08-03 18:00 | 8 | 18 | 16.1 | 2773.3333
2017-08-03 19:00 | 8 | 19 | 16.675 | 2773.3333
2017-08-03 20:00 | 8 | 20 | 18.4 | 4266.6667
2017-08-03 21:00 | 8 | 21 | 8.05 | 286.6667
2017-08-03 22:00 | 8 | 22 | 8.625 | 286.6667
2017-08-03 23:00 | 8 | 23 | 9.2 | 286.6667
2017-08-04 | 8 | 0 | 9.2 | 286.6667
2017-08-04 01:00 | 8 | 1 | 8.05 | 286.6667
2017-08-04 02:00 | 8 | 2 | 8.05 | 286.6667
2017-08-04 03:00 | 8 | 3 | 9.2 | 286.6667
2017-08-04 04:00 | 8 | 4 | 5.3667 | 0
2017-08-04 05:00 | 8 | 5 | 10.35 | 873.3333
2017-08-04 06:00 | 8 | 6 | 8.625 | 286.6667
2017-08-04 07:00 | 8 | 7 | 8.05 | 286.6667
2017-08-04 08:00 | 8 | 8 | 10.35 | 873.3333
2017-08-04 09:00 | 8 | 9 | 10.35 | 873.3333
2017-08-04 10:00 | 8 | 10 | 10.35 | 873.3333
2017-08-04 11:00 | 8 | 11 | 8.05 | 286.6667
2017-08-04 12:00 | 8 | 12 | 14.95 | 2773.3333
2017-08-04 13:00 | 8 | 13 | 14.95 | 2773.3333
2017-08-04 14:00 | 8 | 14 | 20.7 | 6160
2017-08-04 15:00 | 8 | 15 | 19.55 | 6160
2017-08-04 16:00 | 8 | 16 | 18.4 | 4266.6667
2017-08-04 17:00 | 8 | 17 | 14.95 | 2773.3333
2017-08-04 18:00 | 8 | 18 | 14.95 | 2773.3333
2017-08-04 19:00 | 8 | 19 | 12.65 | 1666.6667
2017-08-04 20:00 | 8 | 20 | 11.5 | 873.3333
2017-08-04 21:00 | 8 | 21 | 8.05 | 286.6667
2017-08-04 22:00 | 8 | 22 | 9.775 | 286.6667
2017-08-04 23:00 | 8 | 23 | 12.65 | 1666.6667
2017-08-05 | 8 | 0 | 9.2 | 286.6667
2017-08-05 01:00 | 8 | 1 | 10.35 | 873.3333
2017-08-05 02:00 | 8 | 2 | 10.35 | 873.3333
2017-08-05 03:00 | 8 | 3 | 9.2 | 286.6667
2017-08-05 04:00 | 8 | 4 | 9.9667 | 286.6667
2017-08-05 05:00 | 8 | 5 | 5.75 | 0
2017-08-05 06:00 | 8 | 6 | 5.75 | 0
2017-08-05 07:00 | 8 | 7 | 8.05 | 286.6667
2017-08-05 08:00 | 8 | 8 | 10.35 | 873.3333
2017-08-05 09:00 | 8 | 9 | 3.45 | 0
2017-08-05 10:00 | 8 | 10 | 5.4625 | 0
2017-08-05 11:00 | 8 | 11 | 10.35 | 873.3333
2017-08-05 12:00 | 8 | 12 | 6.9 | 0
2017-08-05 13:00 | 8 | 13 | 9.9667 | 286.6667
2017-08-05 14:00 | 8 | 14 | 14.95 | 2773.3333
2017-08-05 15:00 | 8 | 15 | 11.5 | 873.3333
2017-08-05 16:00 | 8 | 16 | 16.4833 | 2773.3333
2017-08-05 17:00 | 8 | 17 | 11.5 | 873.3333
2017-08-05 18:00 | 8 | 18 | 11.5 | 873.3333
2017-08-05 19:00 | 8 | 19 | 13.225 | 1666.6667
2017-08-05 20:00 | 8 | 20 | 12.65 | 1666.6667
2017-08-05 21:00 | 8 | 21 | 12.65 | 1666.6667
2017-08-05 22:00 | 8 | 22 | 16.1 | 2773.3333
2017-08-05 23:00 | 8 | 23 | 11.5 | 873.3333
2017-08-06 | 8 | 0 | 14.95 | 2773.3333
2017-08-06 01:00 | 8 | 1 | 13.8 | 1666.6667
2017-08-06 02:00 | 8 | 2 | 14.95 | 2773.3333
2017-08-06 03:00 | 8 | 3 | 12.65 | 1666.6667
2017-08-06 04:00 | 8 | 4 | 14.375 | 1666.6667
2017-08-06 05:00 | 8 | 5 | 14.95 | 2773.3333
2017-08-06 06:00 | 8 | 6 | 16.1 | 2773.3333
2017-08-06 07:00 | 8 | 7 | 19.55 | 6160
2017-08-06 08:00 | 8 | 8 | 23 | 7873.3333
2017-08-06 09:00 | 8 | 9 | 19.55 | 6160
2017-08-06 10:00 | 8 | 10 | 23 | 7873.3333
2017-08-06 11:00 | 8 | 11 | 18.4 | 4266.6667
2017-08-06 12:00 | 8 | 12 | 14.95 | 2773.3333
2017-08-06 13:00 | 8 | 13 | 17.825 | 4266.6667
2017-08-06 14:00 | 8 | 14 | 18.4 | 4266.6667
2017-08-06 15:00 | 8 | 15 | 19.55 | 6160
2017-08-06 16:00 | 8 | 16 | 17.25 | 4266.6667
2017-08-06 17:00 | 8 | 17 | 12.65 | 1666.6667
2017-08-06 18:00 | 8 | 18 | 14.95 | 2773.3333
2017-08-06 19:00 | 8 | 19 | 12.65 | 1666.6667
2017-08-06 20:00 | 8 | 20 | 10.35 | 873.3333
2017-08-06 21:00 | 8 | 21 | 11.5 | 873.3333
2017-08-06 22:00 | 8 | 22 | 12.075 | 873.3333
2017-08-06 23:00 | 8 | 23 | 12.65 | 1666.6667
2017-08-07 | 8 | 0 | 10.35 | 873.3333
2017-08-07 01:00 | 8 | 1 | 9.2 | 286.6667
2017-08-07 02:00 | 8 | 2 | 8.05 | 286.6667
2017-08-07 03:00 | 8 | 3 | 8.05 | 286.6667
2017-08-07 04:00 | 8 | 4 | 8.05 | 286.6667
2017-08-07 05:00 | 8 | 5 | 6.9 | 0
2017-08-07 06:00 | 8 | 6 | 8.05 | 286.6667
2017-08-07 07:00 | 8 | 7 | 8.625 | 286.6667
2017-08-07 08:00 | 8 | 8 | 9.775 | 286.6667
2017-08-07 09:00 | 8 | 9 | 12.65 | 1666.6667
2017-08-07 10:00 | 8 | 10 | 15.525 | 2773.3333
2017-08-07 11:00 | 8 | 11 | 16.1 | 2773.3333
2017-08-07 12:00 | 8 | 12 | 18.4 | 4266.6667
2017-08-07 13:00 | 8 | 13 | 18.4 | 4266.6667
2017-08-07 14:00 | 8 | 14 | 14.95 | 2773.3333
2017-08-07 15:00 | 8 | 15 | 11.5 | 873.3333
2017-08-07 16:00 | 8 | 16 | 12.075 | 873.3333
2017-08-07 17:00 | 8 | 17 | 18.4 | 4266.6667
2017-08-07 18:00 | 8 | 18 | 16.1 | 2773.3333
2017-08-07 19:00 | 8 | 19 | 13.225 | 1666.6667
2017-08-07 20:00 | 8 | 20 | 8.05 | 286.6667
2017-08-07 21:00 | 8 | 21 | 9.2 | 286.6667
2017-08-07 22:00 | 8 | 22 | 8.05 | 286.6667
2017-08-07 23:00 | 8 | 23 | 0 | 0
2017-08-08 | 8 | 0 | 5.75 | 0
2017-08-08 01:00 | 8 | 1 | 7.475 | 0
2017-08-08 02:00 | 8 | 2 | 7.475 | 0
2017-08-08 03:00 | 8 | 3 | 6.9 | 0
2017-08-08 04:00 | 8 | 4 | 8.4333 | 286.6667
2017-08-08 05:00 | 8 | 5 | 7.475 | 0
2017-08-08 06:00 | 8 | 6 | 5.3667 | 0
2017-08-08 07:00 | 8 | 7 | 4.2167 | 0
2017-08-08 08:00 | 8 | 8 | 6.9 | 0
2017-08-08 09:00 | 8 | 9 | 11.5 | 873.3333
2017-08-08 10:00 | 8 | 10 | 12.075 | 873.3333
2017-08-08 11:00 | 8 | 11 | 14.95 | 2773.3333
2017-08-08 12:00 | 8 | 12 | 16.1 | 2773.3333
2017-08-08 13:00 | 8 | 13 | 14.5667 | 2773.3333
2017-08-08 14:00 | 8 | 14 | 10.35 | 873.3333
2017-08-08 15:00 | 8 | 15 | 10.35 | 873.3333
2017-08-08 16:00 | 8 | 16 | 9.775 | 286.6667
2017-08-08 17:00 | 8 | 17 | 10.35 | 873.3333
2017-08-08 18:00 | 8 | 18 | 10.35 | 873.3333
2017-08-08 19:00 | 8 | 19 | 9.2 | 286.6667
2017-08-08 20:00 | 8 | 20 | 9.2 | 286.6667
2017-08-08 21:00 | 8 | 21 | 9.2 | 286.6667
2017-08-08 22:00 | 8 | 22 | 9.2 | 286.6667
2017-08-08 23:00 | 8 | 23 | 9.2 | 286.6667
2017-08-09 | 8 | 0 | 9.2 | 286.6667
2017-08-09 01:00 | 8 | 1 | 9.2 | 286.6667
2017-08-09 02:00 | 8 | 2 | 9.2 | 286.6667
2017-08-09 03:00 | 8 | 3 | 9.2 | 286.6667
2017-08-09 04:00 | 8 | 4 | 9.2 | 286.6667
2017-08-09 05:00 | 8 | 5 | 6.9 | 0
2017-08-09 06:00 | 8 | 6 | 9.2 | 286.6667
2017-08-09 07:00 | 8 | 7 | 7.475 | 0
2017-08-09 08:00 | 8 | 8 | 3.45 | 0
2017-08-09 09:00 | 8 | 9 | 8.05 | 286.6667
2017-08-09 10:00 | 8 | 10 | 9.2 | 286.6667
2017-08-09 11:00 | 8 | 11 | 8.05 | 286.6667
2017-08-09 12:00 | 8 | 12 | 5.75 | 0
2017-08-09 13:00 | 8 | 13 | 5.75 | 0
2017-08-09 14:00 | 8 | 14 | 17.25 | 4266.6667
2017-08-09 15:00 | 8 | 15 | 8.05 | 286.6667
2017-08-09 16:00 | 8 | 16 | 11.5 | 873.3333
2017-08-09 17:00 | 8 | 17 | 14.95 | 2773.3333
2017-08-09 18:00 | 8 | 18 | 14.95 | 2773.3333
2017-08-09 19:00 | 8 | 19 | 13.8 | 1666.6667
2017-08-09 20:00 | 8 | 20 | 12.65 | 1666.6667
2017-08-09 21:00 | 8 | 21 | 10.35 | 873.3333
2017-08-09 22:00 | 8 | 22 | 9.775 | 286.6667
2017-08-09 23:00 | 8 | 23 | 8.05 | 286.6667
2017-08-10 | 8 | 0 | 8.05 | 286.6667
2017-08-10 01:00 | 8 | 1 | 6.9 | 0
2017-08-10 02:00 | 8 | 2 | 8.05 | 286.6667
2017-08-10 03:00 | 8 | 3 | 8.05 | 286.6667
2017-08-10 04:00 | 8 | 4 | 9.2 | 286.6667
2017-08-10 05:00 | 8 | 5 | 8.05 | 286.6667
2017-08-10 06:00 | 8 | 6 | 8.05 | 286.6667
2017-08-10 07:00 | 8 | 7 | 4.025 | 0
2017-08-10 08:00 | 8 | 8 | 5.75 | 0
2017-08-10 09:00 | 8 | 9 | 8.05 | 286.6667
2017-08-10 10:00 | 8 | 10 | 8.05 | 286.6667
2017-08-10 11:00 | 8 | 11 | 10.35 | 873.3333
2017-08-10 12:00 | 8 | 12 | 14.95 | 2773.3333
2017-08-10 13:00 | 8 | 13 | 17.25 | 4266.6667
2017-08-10 14:00 | 8 | 14 | 16.1 | 2773.3333
2017-08-10 15:00 | 8 | 15 | 14.95 | 2773.3333
2017-08-10 16:00 | 8 | 16 | 12.075 | 873.3333
2017-08-10 17:00 | 8 | 17 | 16.1 | 2773.3333
2017-08-10 18:00 | 8 | 18 | 10.35 | 873.3333
2017-08-10 19:00 | 8 | 19 | 10.925 | 873.3333
2017-08-10 20:00 | 8 | 20 | 9.2 | 286.6667
2017-08-10 21:00 | 8 | 21 | 9.2 | 286.6667
2017-08-10 22:00 | 8 | 22 | 9.2 | 286.6667
2017-08-10 23:00 | 8 | 23 | 8.05 | 286.6667
2017-08-11 | 8 | 0 | 8.05 | 286.6667
2017-08-11 01:00 | 8 | 1 | 8.05 | 286.6667
2017-08-11 02:00 | 8 | 2 | 10.35 | 873.3333
2017-08-11 03:00 | 8 | 3 | 6.9 | 0
2017-08-11 04:00 | 8 | 4 | 6.9 | 0
2017-08-11 05:00 | 8 | 5 | 6.9 | 0
2017-08-11 06:00 | 8 | 6 | 5.75 | 0
2017-08-11 07:00 | 8 | 7 | 5.75 | 0
2017-08-11 08:00 | 8 | 8 | 6.9 | 0
2017-08-11 09:00 | 8 | 9 | 9.2 | 286.6667
2017-08-11 10:00 | 8 | 10 | 12.075 | 873.3333
2017-08-11 11:00 | 8 | 11 | 16.1 | 2773.3333
2017-08-11 12:00 | 8 | 12 | 17.25 | 4266.6667
2017-08-11 13:00 | 8 | 13 | 18.4 | 4266.6667
2017-08-11 14:00 | 8 | 14 | 20.7 | 6160
2017-08-11 15:00 | 8 | 15 | 19.55 | 6160
2017-08-11 16:00 | 8 | 16 | 17.825 | 4266.6667
2017-08-11 17:00 | 8 | 17 | 11.5 | 873.3333
2017-08-11 18:00 | 8 | 18 | 11.5 | 873.3333
2017-08-11 19:00 | 8 | 19 | 10.925 | 873.3333
2017-08-11 20:00 | 8 | 20 | 8.05 | 286.6667
2017-08-11 21:00 | 8 | 21 | 6.9 | 0
2017-08-11 22:00 | 8 | 22 | 7.475 | 0
2017-08-11 23:00 | 8 | 23 | 8.05 | 286.6667
2017-08-12 | 8 | 0 | 11.5 | 873.3333
2017-08-12 01:00 | 8 | 1 | 9.775 | 286.6667
2017-08-12 02:00 | 8 | 2 | 9.2 | 286.6667
2017-08-12 03:00 | 8 | 3 | 11.5 | 873.3333
2017-08-12 04:00 | 8 | 4 | 9.775 | 286.6667
2017-08-12 05:00 | 8 | 5 | 3.45 | 0
2017-08-12 06:00 | 8 | 6 | 3.45 | 0
2017-08-12 07:00 | 8 | 7 | 5.75 | 0
2017-08-12 08:00 | 8 | 8 | 8.05 | 286.6667
2017-08-12 09:00 | 8 | 9 | 5.75 | 0
2017-08-12 10:00 | 8 | 10 | 6.9 | 0
2017-08-12 11:00 | 8 | 11 | 10.35 | 873.3333
2017-08-12 12:00 | 8 | 12 | 14.95 | 2773.3333
2017-08-12 13:00 | 8 | 13 | 12.075 | 873.3333
2017-08-12 14:00 | 8 | 14 | 10.925 | 873.3333
2017-08-12 15:00 | 8 | 15 | 10.35 | 873.3333
2017-08-12 16:00 | 8 | 16 | 11.5 | 873.3333
2017-08-12 17:00 | 8 | 17 | 14.95 | 2773.3333
2017-08-12 18:00 | 8 | 18 | 11.5 | 873.3333
2017-08-12 19:00 | 8 | 19 | 13.225 | 1666.6667
2017-08-12 20:00 | 8 | 20 | 11.5 | 873.3333
2017-08-12 21:00 | 8 | 21 | 10.35 | 873.3333
2017-08-12 22:00 | 8 | 22 | 10.925 | 873.3333
2017-08-12 23:00 | 8 | 23 | 17.25 | 4266.6667
2017-08-13 | 8 | 0 | 17.25 | 4266.6667
2017-08-13 01:00 | 8 | 1 | 16.1 | 2773.3333
2017-08-13 02:00 | 8 | 2 | 9.2 | 286.6667
2017-08-13 03:00 | 8 | 3 | 9.2 | 286.6667
2017-08-13 04:00 | 8 | 4 | 8.05 | 286.6667
2017-08-13 05:00 | 8 | 5 | 9.2 | 286.6667
2017-08-13 06:00 | 8 | 6 | 10.35 | 873.3333
2017-08-13 07:00 | 8 | 7 | 13.225 | 1666.6667
2017-08-13 08:00 | 8 | 8 | 10.35 | 873.3333
2017-08-13 09:00 | 8 | 9 | 16.1 | 2773.3333
2017-08-13 10:00 | 8 | 10 | 12.65 | 1666.6667
2017-08-13 11:00 | 8 | 11 | 18.4 | 4266.6667
2017-08-13 12:00 | 8 | 12 | 18.4 | 4266.6667
2017-08-13 13:00 | 8 | 13 | 18.4 | 4266.6667
2017-08-13 14:00 | 8 | 14 | 14.95 | 2773.3333
2017-08-13 15:00 | 8 | 15 | 16.1 | 2773.3333
2017-08-13 16:00 | 8 | 16 | 13.225 | 1666.6667
2017-08-13 17:00 | 8 | 17 | 14.95 | 2773.3333
2017-08-13 18:00 | 8 | 18 | 11.5 | 873.3333
2017-08-13 19:00 | 8 | 19 | 9.775 | 286.6667
2017-08-13 20:00 | 8 | 20 | 6.9 | 0
2017-08-13 21:00 | 8 | 21 | 3.45 | 0
2017-08-13 22:00 | 8 | 22 | 3.45 | 0
2017-08-13 23:00 | 8 | 23 | 0 | 0
2017-08-14 | 8 | 0 | 5.75 | 0
2017-08-14 01:00 | 8 | 1 | 2.875 | 0
2017-08-14 02:00 | 8 | 2 | 3.45 | 0
2017-08-14 03:00 | 8 | 3 | 3.45 | 0
2017-08-14 04:00 | 8 | 4 | 1.725 | 0
2017-08-14 05:00 | 8 | 5 | 0 | 0
2017-08-14 06:00 | 8 | 6 | 0 | 0
2017-08-14 07:00 | 8 | 7 | 2.875 | 0
2017-08-14 08:00 | 8 | 8 | 3.45 | 0
2017-08-14 09:00 | 8 | 9 | 6.9 | 0
2017-08-14 10:00 | 8 | 10 | 6.9 | 0
2017-08-14 11:00 | 8 | 11 | 10.35 | 873.3333
2017-08-14 12:00 | 8 | 12 | 14.95 | 2773.3333
2017-08-14 13:00 | 8 | 13 | 13.8 | 1666.6667
2017-08-14 14:00 | 8 | 14 | 12.65 | 1666.6667
2017-08-14 15:00 | 8 | 15 | 11.5 | 873.3333
2017-08-14 16:00 | 8 | 16 | 11.5 | 873.3333
2017-08-14 17:00 | 8 | 17 | 8.05 | 286.6667
2017-08-14 18:00 | 8 | 18 | 9.2 | 286.6667
2017-08-14 19:00 | 8 | 19 | 8.625 | 286.6667
2017-08-14 20:00 | 8 | 20 | 5.75 | 0
2017-08-14 21:00 | 8 | 21 | 6.9 | 0
2017-08-14 22:00 | 8 | 22 | 6.9 | 0
2017-08-14 23:00 | 8 | 23 | 6.9 | 0
2017-08-15 | 8 | 0 | 5.75 | 0
2017-08-15 01:00 | 8 | 1 | 5.75 | 0
2017-08-15 02:00 | 8 | 2 | 6.9 | 0
2017-08-15 03:00 | 8 | 3 | 3.45 | 0
2017-08-15 04:00 | 8 | 4 | 5.175 | 0
2017-08-15 05:00 | 8 | 5 | 3.45 | 0
2017-08-15 06:00 | 8 | 6 | 6.9 | 0
2017-08-15 07:00 | 8 | 7 | 7.475 | 0
2017-08-15 08:00 | 8 | 8 | 10.35 | 873.3333
2017-08-15 09:00 | 8 | 9 | 6.9 | 0
2017-08-15 10:00 | 8 | 10 | 8.4333 | 286.6667
2017-08-15 11:00 | 8 | 11 | 12.65 | 1666.6667
2017-08-15 12:00 | 8 | 12 | 11.5 | 873.3333
2017-08-15 13:00 | 8 | 13 | 16.1 | 2773.3333
2017-08-15 14:00 | 8 | 14 | 9.2 | 286.6667
2017-08-15 15:00 | 8 | 15 | 14.95 | 2773.3333
2017-08-15 16:00 | 8 | 16 | 16.1 | 2773.3333
2017-08-15 17:00 | 8 | 17 | 17.25 | 4266.6667
2017-08-15 18:00 | 8 | 18 | 17.25 | 4266.6667
2017-08-15 19:00 | 8 | 19 | 14.95 | 2773.3333
2017-08-15 20:00 | 8 | 20 | 12.65 | 1666.6667
2017-08-15 21:00 | 8 | 21 | 10.35 | 873.3333
2017-08-15 22:00 | 8 | 22 | 9.775 | 286.6667
2017-08-15 23:00 | 8 | 23 | 8.05 | 286.6667
2017-08-16 | 8 | 0 | 10.35 | 873.3333
2017-08-16 01:00 | 8 | 1 | 9.775 | 286.6667
2017-08-16 02:00 | 8 | 2 | 9.2 | 286.6667
2017-08-16 03:00 | 8 | 3 | 8.05 | 286.6667
2017-08-16 04:00 | 8 | 4 | 8.625 | 286.6667
2017-08-16 05:00 | 8 | 5 | 8.05 | 286.6667
2017-08-16 06:00 | 8 | 6 | 8.05 | 286.6667
2017-08-16 07:00 | 8 | 7 | 10.35 | 873.3333
2017-08-16 08:00 | 8 | 8 | 12.65 | 1666.6667
2017-08-16 09:00 | 8 | 9 | 14.95 | 2773.3333
2017-08-16 10:00 | 8 | 10 | 14.95 | 2773.3333
2017-08-16 11:00 | 8 | 11 | 10.35 | 873.3333
2017-08-16 12:00 | 8 | 12 | 17.825 | 4266.6667
2017-08-16 13:00 | 8 | 13 | 16.1 | 2773.3333
2017-08-16 14:00 | 8 | 14 | 12.65 | 1666.6667
2017-08-16 15:00 | 8 | 15 | 17.25 | 4266.6667
2017-08-16 16:00 | 8 | 16 | 17.25 | 4266.6667
2017-08-16 17:00 | 8 | 17 | 17.25 | 4266.6667
2017-08-16 18:00 | 8 | 18 | 10.35 | 873.3333
2017-08-16 19:00 | 8 | 19 | 9.2 | 286.6667
2017-08-16 20:00 | 8 | 20 | 6.9 | 0
2017-08-16 21:00 | 8 | 21 | 11.5 | 873.3333
2017-08-16 22:00 | 8 | 22 | 10.35 | 873.3333
2017-08-16 23:00 | 8 | 23 | 11.5 | 873.3333
2017-08-17 | 8 | 0 | 10.35 | 873.3333
2017-08-17 01:00 | 8 | 1 | 10.35 | 873.3333
2017-08-17 02:00 | 8 | 2 | 9.2 | 286.6667
2017-08-17 03:00 | 8 | 3 | 8.05 | 286.6667
2017-08-17 04:00 | 8 | 4 | 6.9 | 0
2017-08-17 05:00 | 8 | 5 | 6.9 | 0
2017-08-17 06:00 | 8 | 6 | 8.05 | 286.6667
2017-08-17 07:00 | 8 | 7 | 8.625 | 286.6667
2017-08-17 08:00 | 8 | 8 | 3.45 | 0
2017-08-17 09:00 | 8 | 9 | 0 | 0
2017-08-17 10:00 | 8 | 10 | 3.45 | 0
2017-08-17 11:00 | 8 | 11 | 9.2 | 286.6667
2017-08-17 12:00 | 8 | 12 | 9.2 | 286.6667
2017-08-17 13:00 | 8 | 13 | 10.925 | 873.3333
2017-08-17 14:00 | 8 | 14 | 11.5 | 873.3333
2017-08-17 15:00 | 8 | 15 | 11.5 | 873.3333
2017-08-17 16:00 | 8 | 16 | 11.5 | 873.3333
2017-08-17 17:00 | 8 | 17 | 8.05 | 286.6667
2017-08-17 18:00 | 8 | 18 | 10.35 | 873.3333
2017-08-17 19:00 | 8 | 19 | 10.35 | 873.3333
2017-08-17 20:00 | 8 | 20 | 10.35 | 873.3333
2017-08-17 21:00 | 8 | 21 | 9.2 | 286.6667
2017-08-17 22:00 | 8 | 22 | 9.775 | 286.6667
2017-08-17 23:00 | 8 | 23 | 5.75 | 0
2017-08-18 | 8 | 0 | 8.05 | 286.6667
2017-08-18 01:00 | 8 | 1 | 8.05 | 286.6667
2017-08-18 02:00 | 8 | 2 | 8.05 | 286.6667
2017-08-18 03:00 | 8 | 3 | 3.45 | 0
2017-08-18 04:00 | 8 | 4 | 6.325 | 0
2017-08-18 05:00 | 8 | 5 | 6.9 | 0
2017-08-18 06:00 | 8 | 6 | 9.2 | 286.6667
2017-08-18 07:00 | 8 | 7 | 9.775 | 286.6667
2017-08-18 08:00 | 8 | 8 | 9.2 | 286.6667
2017-08-18 09:00 | 8 | 9 | 12.65 | 1666.6667
2017-08-18 10:00 | 8 | 10 | 14.5667 | 2773.3333
2017-08-18 11:00 | 8 | 11 | 18.4 | 4266.6667
2017-08-18 12:00 | 8 | 12 | 23 | 7873.3333
2017-08-18 13:00 | 8 | 13 | 23.575 | 9060
2017-08-18 14:00 | 8 | 14 | 19.55 | 6160
2017-08-18 15:00 | 8 | 15 | 17.25 | 4266.6667
2017-08-18 16:00 | 8 | 16 | 16.8667 | 4266.6667
2017-08-18 17:00 | 8 | 17 | 16.675 | 2773.3333
2017-08-18 18:00 | 8 | 18 | 15.525 | 2773.3333
2017-08-18 19:00 | 8 | 19 | 14.375 | 1666.6667
2017-08-18 20:00 | 8 | 20 | 11.5 | 873.3333
2017-08-18 21:00 | 8 | 21 | 9.2 | 286.6667
2017-08-18 22:00 | 8 | 22 | 9.2 | 286.6667
2017-08-18 23:00 | 8 | 23 | 8.05 | 286.6667
2017-08-19 | 8 | 0 | 7.0917 | 0
2017-08-19 01:00 | 8 | 1 | 6.5167 | 0
2017-08-19 02:00 | 8 | 2 | 3.8333 | 0
2017-08-19 03:00 | 8 | 3 | 11.5 | 873.3333
2017-08-19 04:00 | 8 | 4 | 9.775 | 286.6667
2017-08-19 05:00 | 8 | 5 | 8.05 | 286.6667
2017-08-19 06:00 | 8 | 6 | 6.9 | 0
2017-08-19 07:00 | 8 | 7 | 4.6 | 0
2017-08-19 08:00 | 8 | 8 | 6.9 | 0
2017-08-19 09:00 | 8 | 9 | 8.05 | 286.6667
2017-08-19 10:00 | 8 | 10 | 8.4333 | 286.6667
2017-08-19 11:00 | 8 | 11 | 10.35 | 873.3333
2017-08-19 12:00 | 8 | 12 | 16.675 | 2773.3333
2017-08-19 13:00 | 8 | 13 | 14.49 | 1666.6667
2017-08-19 14:00 | 8 | 14 | 9.2 | 286.6667
2017-08-19 15:00 | 8 | 15 | 10.35 | 873.3333
2017-08-19 16:00 | 8 | 16 | 8.4333 | 286.6667
2017-08-19 17:00 | 8 | 17 | 6.325 | 0
2017-08-19 18:00 | 8 | 18 | 0 | 0
2017-08-19 19:00 | 8 | 19 | 1.15 | 0
2017-08-19 20:00 | 8 | 20 | 0 | 0
2017-08-19 21:00 | 8 | 21 | 5.75 | 0
2017-08-19 22:00 | 8 | 22 | 6.9 | 0
2017-08-19 23:00 | 8 | 23 | 9.2 | 286.6667
2017-08-20 | 8 | 0 | 9.2 | 286.6667
2017-08-20 01:00 | 8 | 1 | 9.775 | 286.6667
2017-08-20 02:00 | 8 | 2 | 10.35 | 873.3333
2017-08-20 03:00 | 8 | 3 | 9.2 | 286.6667
2017-08-20 04:00 | 8 | 4 | 10.35 | 873.3333
2017-08-20 05:00 | 8 | 5 | 11.5 | 873.3333
2017-08-20 06:00 | 8 | 6 | 17.25 | 4266.6667
2017-08-20 07:00 | 8 | 7 | 16.675 | 2773.3333
2017-08-20 08:00 | 8 | 8 | 19.55 | 6160
2017-08-20 09:00 | 8 | 9 | 16.1 | 2773.3333
2017-08-20 10:00 | 8 | 10 | 13.8 | 1666.6667
2017-08-20 11:00 | 8 | 11 | 14.95 | 2773.3333
2017-08-20 12:00 | 8 | 12 | 14.95 | 2773.3333
2017-08-20 13:00 | 8 | 13 | 14.95 | 2773.3333
2017-08-20 14:00 | 8 | 14 | 16.1 | 2773.3333
2017-08-20 15:00 | 8 | 15 | 17.25 | 4266.6667
2017-08-20 16:00 | 8 | 16 | 17.25 | 4266.6667
2017-08-20 17:00 | 8 | 17 | 14.95 | 2773.3333
2017-08-20 18:00 | 8 | 18 | 9.2 | 286.6667
2017-08-20 19:00 | 8 | 19 | 8.05 | 286.6667
2017-08-20 20:00 | 8 | 20 | 9.2 | 286.6667
2017-08-20 21:00 | 8 | 21 | 5.75 | 0
2017-08-20 22:00 | 8 | 22 | 6.9 | 0
2017-08-20 23:00 | 8 | 23 | 5.75 | 0
2017-08-21 | 8 | 0 | 9.2 | 286.6667
2017-08-21 01:00 | 8 | 1 | 9.775 | 286.6667
2017-08-21 02:00 | 8 | 2 | 10.35 | 873.3333
2017-08-21 03:00 | 8 | 3 | 9.2 | 286.6667
2017-08-21 04:00 | 8 | 4 | 9.775 | 286.6667
2017-08-21 05:00 | 8 | 5 | 8.05 | 286.6667
2017-08-21 06:00 | 8 | 6 | 8.05 | 286.6667
2017-08-21 07:00 | 8 | 7 | 7.475 | 0
2017-08-21 08:00 | 8 | 8 | 8.05 | 286.6667
2017-08-21 09:00 | 8 | 9 | 5.75 | 0
2017-08-21 10:00 | 8 | 10 | 7.475 | 0
2017-08-21 11:00 | 8 | 11 | 8.05 | 286.6667
2017-08-21 12:00 | 8 | 12 | 12.65 | 1666.6667
2017-08-21 13:00 | 8 | 13 | 12.65 | 1666.6667
2017-08-21 14:00 | 8 | 14 | 14.95 | 2773.3333
2017-08-21 15:00 | 8 | 15 | 11.5 | 873.3333
2017-08-21 16:00 | 8 | 16 | 12.075 | 873.3333
2017-08-21 17:00 | 8 | 17 | 12.65 | 1666.6667
2017-08-21 18:00 | 8 | 18 | 11.5 | 873.3333
2017-08-21 19:00 | 8 | 19 | 12.075 | 873.3333
2017-08-21 20:00 | 8 | 20 | 14.95 | 2773.3333
2017-08-21 21:00 | 8 | 21 | 17.25 | 4266.6667
2017-08-21 22:00 | 8 | 22 | 14.375 | 1666.6667
2017-08-21 23:00 | 8 | 23 | 12.65 | 1666.6667
2017-08-22 | 8 | 0 | 11.5 | 873.3333
2017-08-22 01:00 | 8 | 1 | 10.35 | 873.3333
2017-08-22 02:00 | 8 | 2 | 3.45 | 0
2017-08-22 03:00 | 8 | 3 | 8.05 | 286.6667
2017-08-22 04:00 | 8 | 4 | 8.05 | 286.6667
2017-08-22 05:00 | 8 | 5 | 3.45 | 0
2017-08-22 06:00 | 8 | 6 | 0 | 0
2017-08-22 07:00 | 8 | 7 | 8.05 | 286.6667
2017-08-22 08:00 | 8 | 8 | 16.1 | 2773.3333
2017-08-22 09:00 | 8 | 9 | 14.95 | 2773.3333
2017-08-22 10:00 | 8 | 10 | 14.375 | 1666.6667
2017-08-22 11:00 | 8 | 11 | 14.95 | 2773.3333
2017-08-22 12:00 | 8 | 12 | 18.4 | 4266.6667
2017-08-22 13:00 | 8 | 13 | 18.975 | 4266.6667
2017-08-22 14:00 | 8 | 14 | 23 | 7873.3333
2017-08-22 15:00 | 8 | 15 | 18.4 | 4266.6667
2017-08-22 16:00 | 8 | 16 | 21.275 | 7873.3333
2017-08-22 17:00 | 8 | 17 | 20.7 | 6160
2017-08-22 18:00 | 8 | 18 | 20.7 | 6160
2017-08-22 19:00 | 8 | 19 | 18.4 | 4266.6667
2017-08-22 20:00 | 8 | 20 | 18.4 | 4266.6667
2017-08-22 21:00 | 8 | 21 | 16.1 | 2773.3333
2017-08-22 22:00 | 8 | 22 | 17.825 | 4266.6667
2017-08-22 23:00 | 8 | 23 | 16.1 | 2773.3333
2017-08-23 | 8 | 0 | 11.5 | 873.3333
2017-08-23 01:00 | 8 | 1 | 14.95 | 2773.3333
2017-08-23 02:00 | 8 | 2 | 12.075 | 873.3333
2017-08-23 03:00 | 8 | 3 | 14.95 | 2773.3333
2017-08-23 04:00 | 8 | 4 | 13.8 | 1666.6667
2017-08-23 05:00 | 8 | 5 | 12.65 | 1666.6667
2017-08-23 06:00 | 8 | 6 | 12.65 | 1666.6667
2017-08-23 07:00 | 8 | 7 | 12.075 | 873.3333
2017-08-23 08:00 | 8 | 8 | 16.1 | 2773.3333
2017-08-23 09:00 | 8 | 9 | 16.1 | 2773.3333
2017-08-23 10:00 | 8 | 10 | 16.1 | 2773.3333
2017-08-23 11:00 | 8 | 11 | 17.25 | 4266.6667
2017-08-23 12:00 | 8 | 12 | 12.65 | 1666.6667
2017-08-23 13:00 | 8 | 13 | 14.95 | 2773.3333
2017-08-23 14:00 | 8 | 14 | 16.1 | 2773.3333
2017-08-23 15:00 | 8 | 15 | 17.25 | 4266.6667
2017-08-23 16:00 | 8 | 16 | 14.95 | 2773.3333
2017-08-23 17:00 | 8 | 17 | 14.95 | 2773.3333
2017-08-23 18:00 | 8 | 18 | 11.5 | 873.3333
2017-08-23 19:00 | 8 | 19 | 11.5 | 873.3333
2017-08-23 20:00 | 8 | 20 | 9.2 | 286.6667
2017-08-23 21:00 | 8 | 21 | 10.35 | 873.3333
2017-08-23 22:00 | 8 | 22 | 10.35 | 873.3333
2017-08-23 23:00 | 8 | 23 | 10.35 | 873.3333
2017-08-24 | 8 | 0 | 10.35 | 873.3333
2017-08-24 01:00 | 8 | 1 | 9.775 | 286.6667
2017-08-24 02:00 | 8 | 2 | 8.05 | 286.6667
2017-08-24 03:00 | 8 | 3 | 10.35 | 873.3333
2017-08-24 04:00 | 8 | 4 | 8.05 | 286.6667
2017-08-24 05:00 | 8 | 5 | 3.45 | 0
2017-08-24 06:00 | 8 | 6 | 6.9 | 0
2017-08-24 07:00 | 8 | 7 | 8.05 | 286.6667
2017-08-24 08:00 | 8 | 8 | 10.35 | 873.3333
2017-08-24 09:00 | 8 | 9 | 10.35 | 873.3333
2017-08-24 10:00 | 8 | 10 | 13.225 | 1666.6667
2017-08-24 11:00 | 8 | 11 | 16.1 | 2773.3333
2017-08-24 12:00 | 8 | 12 | 14.95 | 2773.3333
2017-08-24 13:00 | 8 | 13 | 14.95 | 2773.3333
2017-08-24 14:00 | 8 | 14 | 12.65 | 1666.6667
2017-08-24 15:00 | 8 | 15 | 3.45 | 0
2017-08-24 16:00 | 8 | 16 | 6.9 | 0
2017-08-24 17:00 | 8 | 17 | 11.5 | 873.3333
2017-08-24 18:00 | 8 | 18 | 5.75 | 0
2017-08-24 19:00 | 8 | 19 | 5.75 | 0
2017-08-24 20:00 | 8 | 20 | 3.45 | 0
2017-08-24 21:00 | 8 | 21 | 0 | 0
2017-08-24 22:00 | 8 | 22 | 2.875 | 0
2017-08-24 23:00 | 8 | 23 | 10.35 | 873.3333
2017-08-25 | 8 | 0 | 9.2 | 286.6667
2017-08-25 01:00 | 8 | 1 | 9.775 | 286.6667
2017-08-25 02:00 | 8 | 2 | 9.2 | 286.6667
2017-08-25 03:00 | 8 | 3 | 8.05 | 286.6667
2017-08-25 04:00 | 8 | 4 | 8.05 | 286.6667
2017-08-25 05:00 | 8 | 5 | 11.5 | 873.3333
2017-08-25 06:00 | 8 | 6 | 8.05 | 286.6667
2017-08-25 07:00 | 8 | 7 | 12.075 | 873.3333
2017-08-25 08:00 | 8 | 8 | 9.2 | 286.6667
2017-08-25 09:00 | 8 | 9 | 11.5 | 873.3333
2017-08-25 10:00 | 8 | 10 | 10.35 | 873.3333
2017-08-25 11:00 | 8 | 11 | 8.05 | 286.6667
2017-08-25 12:00 | 8 | 12 | 10.35 | 873.3333
2017-08-25 13:00 | 8 | 13 | 8.05 | 286.6667
2017-08-25 14:00 | 8 | 14 | 9.2 | 286.6667
2017-08-25 15:00 | 8 | 15 | 8.05 | 286.6667
2017-08-25 16:00 | 8 | 16 | 7.475 | 0
2017-08-25 17:00 | 8 | 17 | 6.9 | 0
2017-08-25 18:00 | 8 | 18 | 10.35 | 873.3333
2017-08-25 19:00 | 8 | 19 | 9.2 | 286.6667
2017-08-25 20:00 | 8 | 20 | 8.05 | 286.6667
2017-08-25 21:00 | 8 | 21 | 8.05 | 286.6667
2017-08-25 22:00 | 8 | 22 | 8.05 | 286.6667
2017-08-25 23:00 | 8 | 23 | 9.2 | 286.6667
2017-08-26 | 8 | 0 | 8.05 | 286.6667
2017-08-26 01:00 | 8 | 1 | 8.05 | 286.6667
2017-08-26 02:00 | 8 | 2 | 8.05 | 286.6667
2017-08-26 03:00 | 8 | 3 | 9.2 | 286.6667
2017-08-26 04:00 | 8 | 4 | 8.625 | 286.6667
2017-08-26 05:00 | 8 | 5 | 9.2 | 286.6667
2017-08-26 06:00 | 8 | 6 | 10.35 | 873.3333
2017-08-26 07:00 | 8 | 7 | 11.5 | 873.3333
2017-08-26 08:00 | 8 | 8 | 9.2 | 286.6667
2017-08-26 09:00 | 8 | 9 | 11.5 | 873.3333
2017-08-26 10:00 | 8 | 10 | 11.5 | 873.3333
2017-08-26 11:00 | 8 | 11 | 8.05 | 286.6667
2017-08-26 12:00 | 8 | 12 | 10.35 | 873.3333
2017-08-26 13:00 | 8 | 13 | 9.775 | 286.6667
2017-08-26 14:00 | 8 | 14 | 10.35 | 873.3333
2017-08-26 15:00 | 8 | 15 | 11.5 | 873.3333
2017-08-26 16:00 | 8 | 16 | 14.375 | 1666.6667
2017-08-26 17:00 | 8 | 17 | 10.35 | 873.3333
2017-08-26 18:00 | 8 | 18 | 8.05 | 286.6667
2017-08-26 19:00 | 8 | 19 | 4.025 | 0
2017-08-26 20:00 | 8 | 20 | 3.45 | 0
2017-08-26 21:00 | 8 | 21 | 5.75 | 0
2017-08-26 22:00 | 8 | 22 | 6.325 | 0
2017-08-26 23:00 | 8 | 23 | 0 | 0
2017-08-27 | 8 | 0 | 6.9 | 0
2017-08-27 01:00 | 8 | 1 | 6.325 | 0
2017-08-27 02:00 | 8 | 2 | 9.2 | 286.6667
2017-08-27 03:00 | 8 | 3 | 10.35 | 873.3333
2017-08-27 04:00 | 8 | 4 | 9.775 | 286.6667
2017-08-27 05:00 | 8 | 5 | 8.05 | 286.6667
2017-08-27 06:00 | 8 | 6 | 8.05 | 286.6667
2017-08-27 07:00 | 8 | 7 | 7.475 | 0
2017-08-27 08:00 | 8 | 8 | 6.9 | 0
2017-08-27 09:00 | 8 | 9 | 9.2 | 286.6667
2017-08-27 10:00 | 8 | 10 | 9.775 | 286.6667
2017-08-27 11:00 | 8 | 11 | 11.5 | 873.3333
2017-08-27 12:00 | 8 | 12 | 14.95 | 2773.3333
2017-08-27 13:00 | 8 | 13 | 14.95 | 2773.3333
2017-08-27 14:00 | 8 | 14 | 17.25 | 4266.6667
2017-08-27 15:00 | 8 | 15 | 16.1 | 2773.3333
2017-08-27 16:00 | 8 | 16 | 13.8 | 1666.6667
2017-08-27 17:00 | 8 | 17 | 9.2 | 286.6667
2017-08-27 18:00 | 8 | 18 | 5.75 | 0
2017-08-27 19:00 | 8 | 19 | 4.6 | 0
2017-08-27 20:00 | 8 | 20 | 3.45 | 0
2017-08-27 21:00 | 8 | 21 | 0 | 0
2017-08-27 22:00 | 8 | 22 | 1.725 | 0
2017-08-27 23:00 | 8 | 23 | 3.45 | 0
2017-08-28 | 8 | 0 | 5.75 | 0
2017-08-28 01:00 | 8 | 1 | 5.75 | 0
2017-08-28 02:00 | 8 | 2 | 5.75 | 0
2017-08-28 03:00 | 8 | 3 | 5.75 | 0
2017-08-28 04:00 | 8 | 4 | 2.875 | 0
2017-08-28 05:00 | 8 | 5 | 3.45 | 0
2017-08-28 06:00 | 8 | 6 | 3.45 | 0
2017-08-28 07:00 | 8 | 7 | 5.75 | 0
2017-08-28 08:00 | 8 | 8 | 8.05 | 286.6667
2017-08-28 09:00 | 8 | 9 | 8.05 | 286.6667
2017-08-28 10:00 | 8 | 10 | 10.35 | 873.3333
2017-08-28 11:00 | 8 | 11 | 14.95 | 2773.3333
2017-08-28 12:00 | 8 | 12 | 16.1 | 2773.3333
2017-08-28 13:00 | 8 | 13 | 16.1 | 2773.3333
2017-08-28 14:00 | 8 | 14 | 12.65 | 1666.6667
2017-08-28 15:00 | 8 | 15 | 11.5 | 873.3333
2017-08-28 16:00 | 8 | 16 | 10.925 | 873.3333
2017-08-28 17:00 | 8 | 17 | 6.9 | 0
2017-08-28 18:00 | 8 | 18 | 6.9 | 0
2017-08-28 19:00 | 8 | 19 | 6.325 | 0
2017-08-28 20:00 | 8 | 20 | 6.9 | 0
2017-08-28 21:00 | 8 | 21 | 3.45 | 0
2017-08-28 22:00 | 8 | 22 | 3.45 | 0
2017-08-28 23:00 | 8 | 23 | 3.45 | 0
2017-08-29 | 8 | 0 | 0 | 0
2017-08-29 01:00 | 8 | 1 | 2.875 | 0
2017-08-29 02:00 | 8 | 2 | 0 | 0
2017-08-29 03:00 | 8 | 3 | 3.45 | 0
2017-08-29 04:00 | 8 | 4 | 3.45 | 0
2017-08-29 05:00 | 8 | 5 | 5.75 | 0
2017-08-29 06:00 | 8 | 6 | 8.05 | 286.6667
2017-08-29 07:00 | 8 | 7 | 6.9 | 0
2017-08-29 08:00 | 8 | 8 | 9.2 | 286.6667
2017-08-29 09:00 | 8 | 9 | 12.65 | 1666.6667
2017-08-29 10:00 | 8 | 10 | 13.8 | 1666.6667
2017-08-29 11:00 | 8 | 11 | 14.95 | 2773.3333
2017-08-29 12:00 | 8 | 12 | 10.35 | 873.3333
2017-08-29 13:00 | 8 | 13 | 12.65 | 1666.6667
2017-08-29 14:00 | 8 | 14 | 10.35 | 873.3333
2017-08-29 15:00 | 8 | 15 | 10.35 | 873.3333
2017-08-29 16:00 | 8 | 16 | 10.35 | 873.3333
2017-08-29 17:00 | 8 | 17 | 10.35 | 873.3333
2017-08-29 18:00 | 8 | 18 | 9.2 | 286.6667
2017-08-29 19:00 | 8 | 19 | 9.2 | 286.6667
2017-08-29 20:00 | 8 | 20 | 11.5 | 873.3333
2017-08-29 21:00 | 8 | 21 | 9.2 | 286.6667
2017-08-29 22:00 | 8 | 22 | 8.625 | 286.6667
2017-08-29 23:00 | 8 | 23 | 6.9 | 0
2017-08-30 | 8 | 0 | 6.9 | 0
2017-08-30 01:00 | 8 | 1 | 8.8167 | 286.6667
2017-08-30 02:00 | 8 | 2 | 8.05 | 286.6667
2017-08-30 03:00 | 8 | 3 | 9.2 | 286.6667
2017-08-30 04:00 | 8 | 4 | 12.075 | 873.3333
2017-08-30 05:00 | 8 | 5 | 11.5 | 873.3333
2017-08-30 06:00 | 8 | 6 | 13.8 | 1666.6667
2017-08-30 07:00 | 8 | 7 | 13.8 | 1666.6667
2017-08-30 08:00 | 8 | 8 | 18.4 | 4266.6667
2017-08-30 09:00 | 8 | 9 | 11.5 | 873.3333
2017-08-30 10:00 | 8 | 10 | 14.375 | 1666.6667
2017-08-30 11:00 | 8 | 11 | 14.95 | 2773.3333
2017-08-30 12:00 | 8 | 12 | 10.35 | 873.3333
2017-08-30 13:00 | 8 | 13 | 11.5 | 873.3333
2017-08-30 14:00 | 8 | 14 | 14.95 | 2773.3333
2017-08-30 15:00 | 8 | 15 | 14.95 | 2773.3333
2017-08-30 16:00 | 8 | 16 | 12.075 | 873.3333
2017-08-30 17:00 | 8 | 17 | 3.45 | 0
2017-08-30 18:00 | 8 | 18 | 5.75 | 0
2017-08-30 19:00 | 8 | 19 | 5.75 | 0
2017-08-30 20:00 | 8 | 20 | 9.2 | 286.6667
2017-08-30 21:00 | 8 | 21 | 6.9 | 0
2017-08-30 22:00 | 8 | 22 | 8.05 | 286.6667
2017-08-30 23:00 | 8 | 23 | 6.9 | 0
2017-08-31 | 8 | 0 | 9.2 | 286.6667
2017-08-31 01:00 | 8 | 1 | 9.775 | 286.6667
2017-08-31 02:00 | 8 | 2 | 11.5 | 873.3333
2017-08-31 03:00 | 8 | 3 | 11.5 | 873.3333
2017-08-31 04:00 | 8 | 4 | 11.5 | 873.3333
2017-08-31 05:00 | 8 | 5 | 10.35 | 873.3333
2017-08-31 06:00 | 8 | 6 | 10.35 | 873.3333
2017-08-31 07:00 | 8 | 7 | 11.5 | 873.3333
2017-08-31 08:00 | 8 | 8 | 12.65 | 1666.6667
2017-08-31 09:00 | 8 | 9 | 10.35 | 873.3333
2017-08-31 10:00 | 8 | 10 | 13.225 | 1666.6667
2017-08-31 11:00 | 8 | 11 | 18.4 | 4266.6667
2017-08-31 12:00 | 8 | 12 | 18.4 | 4266.6667
2017-08-31 13:00 | 8 | 13 | 15.525 | 2773.3333
2017-08-31 14:00 | 8 | 14 | 16.1 | 2773.3333
2017-08-31 15:00 | 8 | 15 | 16.1 | 2773.3333
2017-08-31 16:00 | 8 | 16 | 15.525 | 2773.3333
2017-08-31 17:00 | 8 | 17 | 17.25 | 4266.6667
2017-08-31 18:00 | 8 | 18 | 11.5 | 873.3333
2017-08-31 19:00 | 8 | 19 | 12.075 | 873.3333
2017-08-31 20:00 | 8 | 20 | 11.5 | 873.3333
2017-08-31 21:00 | 8 | 21 | 10.35 | 873.3333
2017-08-31 22:00 | 8 | 22 | 14.95 | 2773.3333
2017-08-31 23:00 | 8 | 23 | 20.7 | 6160
2017-09-01 | 9 | 0 | 17.25 | 4266.6667
2017-09-01 01:00 | 9 | 1 | 18.4 | 4266.6667
2017-09-01 02:00 | 9 | 2 | 17.25 | 4266.6667
2017-09-01 03:00 | 9 | 3 | 18.4 | 4266.6667
2017-09-01 04:00 | 9 | 4 | 18.4 | 4266.6667
2017-09-01 05:00 | 9 | 5 | 18.4 | 4266.6667
2017-09-01 06:00 | 9 | 6 | 17.25 | 4266.6667
2017-09-01 07:00 | 9 | 7 | 16.675 | 2773.3333
2017-09-01 08:00 | 9 | 8 | 18.4 | 4266.6667
2017-09-01 09:00 | 9 | 9 | 24.15 | 9060
2017-09-01 10:00 | 9 | 10 | 21.85 | 7873.3333
2017-09-01 11:00 | 9 | 11 | 23 | 7873.3333
2017-09-01 12:00 | 9 | 12 | 19.55 | 6160
2017-09-01 13:00 | 9 | 13 | 19.55 | 6160
2017-09-01 14:00 | 9 | 14 | 20.7 | 6160
2017-09-01 15:00 | 9 | 15 | 19.55 | 6160
2017-09-01 16:00 | 9 | 16 | 20.125 | 6160
2017-09-01 17:00 | 9 | 17 | 14.95 | 2773.3333
2017-09-01 18:00 | 9 | 18 | 11.5 | 873.3333
2017-09-01 19:00 | 9 | 19 | 12.075 | 873.3333
2017-09-01 20:00 | 9 | 20 | 6.9 | 0
2017-09-01 21:00 | 9 | 21 | 10.35 | 873.3333
2017-09-01 22:00 | 9 | 22 | 10.35 | 873.3333
2017-09-01 23:00 | 9 | 23 | 10.35 | 873.3333
2017-09-02 | 9 | 0 | 10.35 | 873.3333
2017-09-02 01:00 | 9 | 1 | 10.925 | 873.3333
2017-09-02 02:00 | 9 | 2 | 11.5 | 873.3333
2017-09-02 03:00 | 9 | 3 | 16.1 | 2773.3333
2017-09-02 04:00 | 9 | 4 | 14.375 | 1666.6667
2017-09-02 05:00 | 9 | 5 | 16.1 | 2773.3333
2017-09-02 06:00 | 9 | 6 | 14.95 | 2773.3333
2017-09-02 07:00 | 9 | 7 | 13.225 | 1666.6667
2017-09-02 08:00 | 9 | 8 | 10.35 | 873.3333
2017-09-02 09:00 | 9 | 9 | 11.5 | 873.3333
2017-09-02 10:00 | 9 | 10 | 8.625 | 286.6667
2017-09-02 11:00 | 9 | 11 | 12.65 | 1666.6667
2017-09-02 12:00 | 9 | 12 | 11.5 | 873.3333
2017-09-02 13:00 | 9 | 13 | 12.075 | 873.3333
2017-09-02 14:00 | 9 | 14 | 11.5 | 873.3333
2017-09-02 15:00 | 9 | 15 | 11.5 | 873.3333
2017-09-02 16:00 | 9 | 16 | 10.925 | 873.3333
2017-09-02 17:00 | 9 | 17 | 9.2 | 286.6667
2017-09-02 18:00 | 9 | 18 | 11.5 | 873.3333
2017-09-02 19:00 | 9 | 19 | 12.075 | 873.3333
2017-09-02 20:00 | 9 | 20 | 10.35 | 873.3333
2017-09-02 21:00 | 9 | 21 | 9.2 | 286.6667
2017-09-02 22:00 | 9 | 22 | 7.475 | 0
2017-09-02 23:00 | 9 | 23 | 3.45 | 0
2017-09-03 | 9 | 0 | 5.75 | 0
2017-09-03 01:00 | 9 | 1 | 6.9 | 0
2017-09-03 02:00 | 9 | 2 | 10.35 | 873.3333
2017-09-03 03:00 | 9 | 3 | 14.95 | 2773.3333
2017-09-03 04:00 | 9 | 4 | 14.95 | 2773.3333
2017-09-03 05:00 | 9 | 5 | 9.2 | 286.6667
2017-09-03 06:00 | 9 | 6 | 12.65 | 1666.6667
2017-09-03 07:00 | 9 | 7 | 14.375 | 1666.6667
2017-09-03 08:00 | 9 | 8 | 21.85 | 7873.3333
2017-09-03 09:00 | 9 | 9 | 26.45 | 9573.3333
2017-09-03 10:00 | 9 | 10 | 24.15 | 9060
2017-09-03 11:00 | 9 | 11 | 21.85 | 7873.3333
2017-09-03 12:00 | 9 | 12 | 14.95 | 2773.3333
2017-09-03 13:00 | 9 | 13 | 9.9667 | 286.6667
2017-09-03 14:00 | 9 | 14 | 10.6375 | 873.3333
2017-09-03 15:00 | 9 | 15 | 10.35 | 873.3333
2017-09-03 16:00 | 9 | 16 | 8.05 | 286.6667
2017-09-03 17:00 | 9 | 17 | 18.4 | 4266.6667
2017-09-03 18:00 | 9 | 18 | 16.4833 | 2773.3333
2017-09-03 19:00 | 9 | 19 | 18.4 | 4266.6667
2017-09-03 20:00 | 9 | 20 | 17.25 | 4266.6667
2017-09-03 21:00 | 9 | 21 | 18.4 | 4266.6667
2017-09-03 22:00 | 9 | 22 | 18.975 | 4266.6667
2017-09-03 23:00 | 9 | 23 | 19.55 | 6160
2017-09-04 | 9 | 0 | 16.1 | 2773.3333
2017-09-04 01:00 | 9 | 1 | 17.825 | 4266.6667
2017-09-04 02:00 | 9 | 2 | 14.95 | 2773.3333
2017-09-04 03:00 | 9 | 3 | 14.95 | 2773.3333
2017-09-04 04:00 | 9 | 4 | 12.65 | 1666.6667
2017-09-04 05:00 | 9 | 5 | 17.25 | 4266.6667
2017-09-04 06:00 | 9 | 6 | 18.4 | 4266.6667
2017-09-04 07:00 | 9 | 7 | 17.25 | 4266.6667
2017-09-04 08:00 | 9 | 8 | 12.65 | 1666.6667
2017-09-04 09:00 | 9 | 9 | 14.95 | 2773.3333
2017-09-04 10:00 | 9 | 10 | 13.225 | 1666.6667
2017-09-04 11:00 | 9 | 11 | 17.25 | 4266.6667
2017-09-04 12:00 | 9 | 12 | 14.95 | 2773.3333
2017-09-04 13:00 | 9 | 13 | 14.95 | 2773.3333
2017-09-04 14:00 | 9 | 14 | 19.55 | 6160
2017-09-04 15:00 | 9 | 15 | 23 | 7873.3333
2017-09-04 16:00 | 9 | 16 | 20.125 | 6160
2017-09-04 17:00 | 9 | 17 | 18.4 | 4266.6667
2017-09-04 18:00 | 9 | 18 | 18.4 | 4266.6667
2017-09-04 19:00 | 9 | 19 | 17.825 | 4266.6667
2017-09-04 20:00 | 9 | 20 | 12.65 | 1666.6667
2017-09-04 21:00 | 9 | 21 | 12.65 | 1666.6667
2017-09-04 22:00 | 9 | 22 | 14.95 | 2773.3333
2017-09-04 23:00 | 9 | 23 | 14.95 | 2773.3333
2017-09-05 | 9 | 0 | 14.95 | 2773.3333
2017-09-05 01:00 | 9 | 1 | 16.675 | 2773.3333
2017-09-05 02:00 | 9 | 2 | 16.1 | 2773.3333
2017-09-05 03:00 | 9 | 3 | 18.4 | 4266.6667
2017-09-05 04:00 | 9 | 4 | 17.825 | 4266.6667
2017-09-05 05:00 | 9 | 5 | 18.4 | 4266.6667
2017-09-05 06:00 | 9 | 6 | 20.7 | 6160
2017-09-05 07:00 | 9 | 7 | 20.7 | 6160
2017-09-05 08:00 | 9 | 8 | 23 | 7873.3333
2017-09-05 09:00 | 9 | 9 | 14.95 | 2773.3333
2017-09-05 10:00 | 9 | 10 | 16.675 | 2773.3333
2017-09-05 11:00 | 9 | 11 | 25.3 | 9060
2017-09-05 12:00 | 9 | 12 | 19.55 | 6160
2017-09-05 13:00 | 9 | 13 | 21.85 | 7873.3333
2017-09-05 14:00 | 9 | 14 | 23 | 7873.3333
2017-09-05 15:00 | 9 | 15 | 23 | 7873.3333
2017-09-05 16:00 | 9 | 16 | 21.275 | 7873.3333
2017-09-05 17:00 | 9 | 17 | 24.15 | 9060
2017-09-05 18:00 | 9 | 18 | 25.3 | 9060
2017-09-05 19:00 | 9 | 19 | 24.725 | 9060
2017-09-05 20:00 | 9 | 20 | 18.4 | 4266.6667
2017-09-05 21:00 | 9 | 21 | 14.95 | 2773.3333
2017-09-05 22:00 | 9 | 22 | 16.1 | 2773.3333
2017-09-05 23:00 | 9 | 23 | 12.65 | 1666.6667
2017-09-06 | 9 | 0 | 13.225 | 1666.6667
2017-09-06 01:00 | 9 | 1 | 13.225 | 1666.6667
2017-09-06 02:00 | 9 | 2 | 7.475 | 0
2017-09-06 03:00 | 9 | 3 | 10.35 | 873.3333
2017-09-06 04:00 | 9 | 4 | 8.625 | 286.6667
2017-09-06 05:00 | 9 | 5 | 8.8167 | 286.6667
2017-09-06 06:00 | 9 | 6 | 6.9 | 0
2017-09-06 07:00 | 9 | 7 | 5.3667 | 0
2017-09-06 08:00 | 9 | 8 | 9.2 | 286.6667
2017-09-06 09:00 | 9 | 9 | 13.225 | 1666.6667
2017-09-06 10:00 | 9 | 10 | 14.03 | 1666.6667
2017-09-06 11:00 | 9 | 11 | 15.525 | 2773.3333
2017-09-06 12:00 | 9 | 12 | 12.075 | 873.3333
2017-09-06 13:00 | 9 | 13 | 11.1167 | 873.3333
2017-09-06 14:00 | 9 | 14 | 6.9 | 0
2017-09-06 15:00 | 9 | 15 | 5.75 | 0
2017-09-06 16:00 | 9 | 16 | 6.6125 | 0
2017-09-06 17:00 | 9 | 17 | 6.9 | 0
2017-09-06 18:00 | 9 | 18 | 6.5167 | 0
2017-09-06 19:00 | 9 | 19 | 8.05 | 286.6667
2017-09-06 20:00 | 9 | 20 | 10.7333 | 873.3333
2017-09-06 21:00 | 9 | 21 | 9.2 | 286.6667
2017-09-06 22:00 | 9 | 22 | 7.475 | 0
2017-09-06 23:00 | 9 | 23 | 8.05 | 286.6667
2017-09-07 | 9 | 0 | 8.05 | 286.6667
2017-09-07 01:00 | 9 | 1 | 10.6375 | 873.3333
2017-09-07 02:00 | 9 | 2 | 8.625 | 286.6667
2017-09-07 03:00 | 9 | 3 | 16.675 | 2773.3333
2017-09-07 04:00 | 9 | 4 | 13.4167 | 1666.6667
2017-09-07 05:00 | 9 | 5 | 3.45 | 0
2017-09-07 06:00 | 9 | 6 | 13.8 | 1666.6667
2017-09-07 07:00 | 9 | 7 | 11.5 | 873.3333
2017-09-07 08:00 | 9 | 8 | 12.2667 | 873.3333
2017-09-07 09:00 | 9 | 9 | 11.5 | 873.3333
2017-09-07 10:00 | 9 | 10 | 14.5667 | 2773.3333
2017-09-07 11:00 | 9 | 11 | 14.95 | 2773.3333
2017-09-07 12:00 | 9 | 12 | 18.4 | 4266.6667
2017-09-07 13:00 | 9 | 13 | 18.4 | 4266.6667
2017-09-07 14:00 | 9 | 14 | 12.65 | 1666.6667
2017-09-07 15:00 | 9 | 15 | 12.65 | 1666.6667
2017-09-07 16:00 | 9 | 16 | 14.95 | 2773.3333
2017-09-07 17:00 | 9 | 17 | 10.35 | 873.3333
2017-09-07 18:00 | 9 | 18 | 16.1 | 2773.3333
2017-09-07 19:00 | 9 | 19 | 16.8667 | 4266.6667
2017-09-07 20:00 | 9 | 20 | 6.9 | 0
2017-09-07 21:00 | 9 | 21 | 8.05 | 286.6667
2017-09-07 22:00 | 9 | 22 | 8.625 | 286.6667
2017-09-07 23:00 | 9 | 23 | 11.5 | 873.3333
2017-09-08 | 9 | 0 | 11.5 | 873.3333
2017-09-08 01:00 | 9 | 1 | 10.35 | 873.3333
2017-09-08 02:00 | 9 | 2 | 12.65 | 1666.6667
2017-09-08 03:00 | 9 | 3 | 9.2 | 286.6667
2017-09-08 04:00 | 9 | 4 | 9.2 | 286.6667
2017-09-08 05:00 | 9 | 5 | 10.35 | 873.3333
2017-09-08 06:00 | 9 | 6 | 10.35 | 873.3333
2017-09-08 07:00 | 9 | 7 | 11.5 | 873.3333
2017-09-08 08:00 | 9 | 8 | 14.95 | 2773.3333
2017-09-08 09:00 | 9 | 9 | 11.5 | 873.3333
2017-09-08 10:00 | 9 | 10 | 11.5 | 873.3333
2017-09-08 11:00 | 9 | 11 | 12.65 | 1666.6667
2017-09-08 12:00 | 9 | 12 | 17.25 | 4266.6667
2017-09-08 13:00 | 9 | 13 | 14.375 | 1666.6667
2017-09-08 14:00 | 9 | 14 | 12.65 | 1666.6667
2017-09-08 15:00 | 9 | 15 | 10.35 | 873.3333
2017-09-08 16:00 | 9 | 16 | 10.35 | 873.3333
2017-09-08 17:00 | 9 | 17 | 12.65 | 1666.6667
2017-09-08 18:00 | 9 | 18 | 12.65 | 1666.6667
2017-09-08 19:00 | 9 | 19 | 12.65 | 1666.6667
2017-09-08 20:00 | 9 | 20 | 11.5 | 873.3333
2017-09-08 21:00 | 9 | 21 | 8.05 | 286.6667
2017-09-08 22:00 | 9 | 22 | 9.2 | 286.6667
2017-09-08 23:00 | 9 | 23 | 9.2 | 286.6667
2017-09-09 | 9 | 0 | 12.65 | 1666.6667
2017-09-09 01:00 | 9 | 1 | 11.5 | 873.3333
2017-09-09 02:00 | 9 | 2 | 10.35 | 873.3333
2017-09-09 03:00 | 9 | 3 | 10.35 | 873.3333
2017-09-09 04:00 | 9 | 4 | 9.775 | 286.6667
2017-09-09 05:00 | 9 | 5 | 11.5 | 873.3333
2017-09-09 06:00 | 9 | 6 | 11.5 | 873.3333
2017-09-09 07:00 | 9 | 7 | 10.35 | 873.3333
2017-09-09 08:00 | 9 | 8 | 8.05 | 286.6667
2017-09-09 09:00 | 9 | 9 | 10.35 | 873.3333
2017-09-09 10:00 | 9 | 10 | 10.925 | 873.3333
2017-09-09 11:00 | 9 | 11 | 12.65 | 1666.6667
2017-09-09 12:00 | 9 | 12 | 11.5 | 873.3333
2017-09-09 13:00 | 9 | 13 | 10.925 | 873.3333
2017-09-09 14:00 | 9 | 14 | 10.35 | 873.3333
2017-09-09 15:00 | 9 | 15 | 8.05 | 286.6667
2017-09-09 16:00 | 9 | 16 | 5.75 | 0
2017-09-09 17:00 | 9 | 17 | 5.75 | 0
2017-09-09 18:00 | 9 | 18 | 0 | 0
2017-09-09 19:00 | 9 | 19 | 4.025 | 0
2017-09-09 20:00 | 9 | 20 | 9.2 | 286.6667
2017-09-09 21:00 | 9 | 21 | 11.5 | 873.3333
2017-09-09 22:00 | 9 | 22 | 9.2 | 286.6667
2017-09-09 23:00 | 9 | 23 | 10.35 | 873.3333
2017-09-10 | 9 | 0 | 9.2 | 286.6667
2017-09-10 01:00 | 9 | 1 | 10.35 | 873.3333
2017-09-10 02:00 | 9 | 2 | 9.2 | 286.6667
2017-09-10 03:00 | 9 | 3 | 10.35 | 873.3333
2017-09-10 04:00 | 9 | 4 | 11.5 | 873.3333
2017-09-10 05:00 | 9 | 5 | 9.2 | 286.6667
2017-09-10 06:00 | 9 | 6 | 10.35 | 873.3333
2017-09-10 07:00 | 9 | 7 | 10.925 | 873.3333
2017-09-10 08:00 | 9 | 8 | 12.65 | 1666.6667
2017-09-10 09:00 | 9 | 9 | 12.65 | 1666.6667
2017-09-10 10:00 | 9 | 10 | 11.5 | 873.3333
2017-09-10 11:00 | 9 | 11 | 14.95 | 2773.3333
2017-09-10 12:00 | 9 | 12 | 12.65 | 1666.6667
2017-09-10 13:00 | 9 | 13 | 10.35 | 873.3333
2017-09-10 14:00 | 9 | 14 | 6.9 | 0
2017-09-10 15:00 | 9 | 15 | 8.05 | 286.6667
2017-09-10 16:00 | 9 | 16 | 4.025 | 0
2017-09-10 17:00 | 9 | 17 | 3.45 | 0
2017-09-10 18:00 | 9 | 18 | 3.45 | 0
2017-09-10 19:00 | 9 | 19 | 5.175 | 0
2017-09-10 20:00 | 9 | 20 | 9.2 | 286.6667
2017-09-10 21:00 | 9 | 21 | 11.5 | 873.3333
2017-09-10 22:00 | 9 | 22 | 12.075 | 873.3333
2017-09-10 23:00 | 9 | 23 | 14.95 | 2773.3333
2017-09-11 | 9 | 0 | 12.65 | 1666.6667
2017-09-11 01:00 | 9 | 1 | 12.65 | 1666.6667
2017-09-11 02:00 | 9 | 2 | 12.65 | 1666.6667
2017-09-11 03:00 | 9 | 3 | 16.1 | 2773.3333
2017-09-11 04:00 | 9 | 4 | 13.8 | 1666.6667
2017-09-11 05:00 | 9 | 5 | 11.5 | 873.3333
2017-09-11 06:00 | 9 | 6 | 14.95 | 2773.3333
2017-09-11 07:00 | 9 | 7 | 15.525 | 2773.3333
2017-09-11 08:00 | 9 | 8 | 12.65 | 1666.6667
2017-09-11 09:00 | 9 | 9 | 12.65 | 1666.6667
2017-09-11 10:00 | 9 | 10 | 12.075 | 873.3333
2017-09-11 11:00 | 9 | 11 | 9.2 | 286.6667
2017-09-11 12:00 | 9 | 12 | 5.75 | 0
2017-09-11 13:00 | 9 | 13 | 6.9 | 0
2017-09-11 14:00 | 9 | 14 | 9.2 | 286.6667
2017-09-11 15:00 | 9 | 15 | 10.35 | 873.3333
2017-09-11 16:00 | 9 | 16 | 10.35 | 873.3333
2017-09-11 17:00 | 9 | 17 | 11.5 | 873.3333
2017-09-11 18:00 | 9 | 18 | 11.5 | 873.3333
2017-09-11 19:00 | 9 | 19 | 10.35 | 873.3333
2017-09-11 20:00 | 9 | 20 | 9.2 | 286.6667
2017-09-11 21:00 | 9 | 21 | 9.2 | 286.6667
2017-09-11 22:00 | 9 | 22 | 9.2 | 286.6667
2017-09-11 23:00 | 9 | 23 | 8.05 | 286.6667
2017-09-12 | 9 | 0 | 6.9 | 0
2017-09-12 01:00 | 9 | 1 | 6.9 | 0
2017-09-12 02:00 | 9 | 2 | 5.75 | 0
2017-09-12 03:00 | 9 | 3 | 9.2 | 286.6667
2017-09-12 04:00 | 9 | 4 | 8.05 | 286.6667
2017-09-12 05:00 | 9 | 5 | 8.05 | 286.6667
2017-09-12 06:00 | 9 | 6 | 5.75 | 0
2017-09-12 07:00 | 9 | 7 | 6.9 | 0
2017-09-12 08:00 | 9 | 8 | 8.05 | 286.6667
2017-09-12 09:00 | 9 | 9 | 3.45 | 0
2017-09-12 10:00 | 9 | 10 | 5.75 | 0
2017-09-12 11:00 | 9 | 11 | 9.2 | 286.6667
2017-09-12 12:00 | 9 | 12 | 10.35 | 873.3333
2017-09-12 13:00 | 9 | 13 | 10.925 | 873.3333
2017-09-12 14:00 | 9 | 14 | 14.95 | 2773.3333
2017-09-12 15:00 | 9 | 15 | 16.1 | 2773.3333
2017-09-12 16:00 | 9 | 16 | 17.825 | 4266.6667
2017-09-12 17:00 | 9 | 17 | 10.35 | 873.3333
2017-09-12 18:00 | 9 | 18 | 10.35 | 873.3333
2017-09-12 19:00 | 9 | 19 | 10.925 | 873.3333
2017-09-12 20:00 | 9 | 20 | 12.65 | 1666.6667
2017-09-12 21:00 | 9 | 21 | 9.2 | 286.6667
2017-09-12 22:00 | 9 | 22 | 9.775 | 286.6667
2017-09-12 23:00 | 9 | 23 | 10.35 | 873.3333
2017-09-13 | 9 | 0 | 9.2 | 286.6667
2017-09-13 01:00 | 9 | 1 | 10.35 | 873.3333
2017-09-13 02:00 | 9 | 2 | 10.35 | 873.3333
2017-09-13 03:00 | 9 | 3 | 10.35 | 873.3333
2017-09-13 04:00 | 9 | 4 | 11.5 | 873.3333
2017-09-13 05:00 | 9 | 5 | 10.35 | 873.3333
2017-09-13 06:00 | 9 | 6 | 6.9 | 0
2017-09-13 07:00 | 9 | 7 | 6.9 | 0
2017-09-13 08:00 | 9 | 8 | 5.75 | 0
2017-09-13 09:00 | 9 | 9 | 8.05 | 286.6667
2017-09-13 10:00 | 9 | 10 | 8.625 | 286.6667
2017-09-13 11:00 | 9 | 11 | 10.35 | 873.3333
2017-09-13 12:00 | 9 | 12 | 10.35 | 873.3333
2017-09-13 13:00 | 9 | 13 | 11.5 | 873.3333
2017-09-13 14:00 | 9 | 14 | 12.65 | 1666.6667
2017-09-13 15:00 | 9 | 15 | 10.35 | 873.3333
2017-09-13 16:00 | 9 | 16 | 8.05 | 286.6667
2017-09-13 17:00 | 9 | 17 | 5.75 | 0
2017-09-13 18:00 | 9 | 18 | 6.9 | 0
2017-09-13 19:00 | 9 | 19 | 8.05 | 286.6667
2017-09-13 20:00 | 9 | 20 | 14.95 | 2773.3333
2017-09-13 21:00 | 9 | 21 | 9.5833 | 286.6667
2017-09-13 22:00 | 9 | 22 | 10.925 | 873.3333
2017-09-13 23:00 | 9 | 23 | 10.35 | 873.3333
2017-09-14 | 9 | 0 | 18.4 | 4266.6667
2017-09-14 01:00 | 9 | 1 | 14.375 | 1666.6667
2017-09-14 02:00 | 9 | 2 | 14.95 | 2773.3333
2017-09-14 03:00 | 9 | 3 | 6.9 | 0
2017-09-14 04:00 | 9 | 4 | 7.475 | 0
2017-09-14 05:00 | 9 | 5 | 11.5 | 873.3333
2017-09-14 06:00 | 9 | 6 | 11.5 | 873.3333
2017-09-14 07:00 | 9 | 7 | 10.925 | 873.3333
2017-09-14 08:00 | 9 | 8 | 14.95 | 2773.3333
2017-09-14 09:00 | 9 | 9 | 17.25 | 4266.6667
2017-09-14 10:00 | 9 | 10 | 16.675 | 2773.3333
2017-09-14 11:00 | 9 | 11 | 19.55 | 6160
2017-09-14 12:00 | 9 | 12 | 17.25 | 4266.6667
2017-09-14 13:00 | 9 | 13 | 17.25 | 4266.6667
2017-09-14 14:00 | 9 | 14 | 12.65 | 1666.6667
2017-09-14 15:00 | 9 | 15 | 12.65 | 1666.6667
2017-09-14 16:00 | 9 | 16 | 12.65 | 1666.6667
2017-09-14 17:00 | 9 | 17 | 22.8083 | 7873.3333
2017-09-14 18:00 | 9 | 18 | 13.8 | 1666.6667
2017-09-14 19:00 | 9 | 19 | 10.35 | 873.3333
2017-09-14 20:00 | 9 | 20 | 6.9 | 0
2017-09-14 21:00 | 9 | 21 | 6.9 | 0
2017-09-14 22:00 | 9 | 22 | 8.05 | 286.6667
2017-09-14 23:00 | 9 | 23 | 8.05 | 286.6667
2017-09-15 | 9 | 0 | 6.9 | 0
2017-09-15 01:00 | 9 | 1 | 6.9 | 0
2017-09-15 02:00 | 9 | 2 | 6.325 | 0
2017-09-15 03:00 | 9 | 3 | 6.9 | 0
2017-09-15 04:00 | 9 | 4 | 7.2833 | 0
2017-09-15 05:00 | 9 | 5 | 7.2833 | 0
2017-09-15 06:00 | 9 | 6 | 8.05 | 286.6667
2017-09-15 07:00 | 9 | 7 | 9.4875 | 286.6667
2017-09-15 08:00 | 9 | 8 | 6.9 | 0
2017-09-15 09:00 | 9 | 9 | 9.2 | 286.6667
2017-09-15 10:00 | 9 | 10 | 8.05 | 286.6667
2017-09-15 11:00 | 9 | 11 | 12.65 | 1666.6667
2017-09-15 12:00 | 9 | 12 | 12.65 | 1666.6667
2017-09-15 13:00 | 9 | 13 | 14.375 | 1666.6667
2017-09-15 14:00 | 9 | 14 | 12.65 | 1666.6667
2017-09-15 15:00 | 9 | 15 | 6.9 | 0
2017-09-15 16:00 | 9 | 16 | 7.2833 | 0
2017-09-15 17:00 | 9 | 17 | 11.5 | 873.3333
2017-09-15 18:00 | 9 | 18 | 6.9 | 0
2017-09-15 19:00 | 9 | 19 | 6.9 | 0
2017-09-15 20:00 | 9 | 20 | 5.75 | 0
2017-09-15 21:00 | 9 | 21 | 4.83 | 0
2017-09-15 22:00 | 9 | 22 | 2.6833 | 0
2017-09-15 23:00 | 9 | 23 | 6.9 | 0
2017-09-16 | 9 | 0 | 1.38 | 0
2017-09-16 01:00 | 9 | 1 | 0 | 0
2017-09-16 02:00 | 9 | 2 | 4.2167 | 0
2017-09-16 03:00 | 9 | 3 | 8.4333 | 286.6667
2017-09-16 04:00 | 9 | 4 | 6.1333 | 0
2017-09-16 05:00 | 9 | 5 | 7.2833 | 0
2017-09-16 06:00 | 9 | 6 | 2.875 | 0
2017-09-16 07:00 | 9 | 7 | 2.875 | 0
2017-09-16 08:00 | 9 | 8 | 5.75 | 0
2017-09-16 09:00 | 9 | 9 | 1.725 | 0
2017-09-16 10:00 | 9 | 10 | 2.5875 | 0
2017-09-16 11:00 | 9 | 11 | 3.45 | 0
2017-09-16 12:00 | 9 | 12 | 5.75 | 0
2017-09-16 13:00 | 9 | 13 | 7.6667 | 0
2017-09-16 14:00 | 9 | 14 | 9.2 | 286.6667
2017-09-16 15:00 | 9 | 15 | 9.2 | 286.6667
2017-09-16 16:00 | 9 | 16 | 9.2 | 286.6667
2017-09-16 17:00 | 9 | 17 | 5.3667 | 0
2017-09-16 18:00 | 9 | 18 | 5.75 | 0
2017-09-16 19:00 | 9 | 19 | 5.3667 | 0
2017-09-16 20:00 | 9 | 20 | 2.3 | 0
2017-09-16 21:00 | 9 | 21 | 5.75 | 0
2017-09-16 22:00 | 9 | 22 | 4.9833 | 0
2017-09-16 23:00 | 9 | 23 | 4.6 | 0
2017-09-17 | 9 | 0 | 1.725 | 0
2017-09-17 01:00 | 9 | 1 | 1.725 | 0
2017-09-17 02:00 | 9 | 2 | 0 | 0
2017-09-17 03:00 | 9 | 3 | 0 | 0
2017-09-17 04:00 | 9 | 4 | 0 | 0
2017-09-17 05:00 | 9 | 5 | 3.45 | 0
2017-09-17 06:00 | 9 | 6 | 3.45 | 0
2017-09-17 07:00 | 9 | 7 | 1.725 | 0
2017-09-17 08:00 | 9 | 8 | 1.38 | 0
2017-09-17 09:00 | 9 | 9 | 5.3667 | 0
2017-09-17 10:00 | 9 | 10 | 7.59 | 0
2017-09-17 11:00 | 9 | 11 | 6.67 | 0
2017-09-17 12:00 | 9 | 12 | 8.05 | 286.6667
2017-09-17 13:00 | 9 | 13 | 8.625 | 286.6667
2017-09-17 14:00 | 9 | 14 | 10.35 | 873.3333
2017-09-17 15:00 | 9 | 15 | 11.5 | 873.3333
2017-09-17 16:00 | 9 | 16 | 10.5417 | 873.3333
2017-09-17 17:00 | 9 | 17 | 8.625 | 286.6667
2017-09-17 18:00 | 9 | 18 | 7.2833 | 0
2017-09-17 19:00 | 9 | 19 | 3.45 | 0
2017-09-17 20:00 | 9 | 20 | 0 | 0
2017-09-17 21:00 | 9 | 21 | 3.45 | 0
2017-09-17 22:00 | 9 | 22 | 4.6 | 0
2017-09-17 23:00 | 9 | 23 | 8.8167 | 286.6667
2017-09-18 | 9 | 0 | 5.75 | 0
2017-09-18 01:00 | 9 | 1 | 4.9833 | 0
2017-09-18 02:00 | 9 | 2 | 2.875 | 0
2017-09-18 03:00 | 9 | 3 | 0 | 0
2017-09-18 04:00 | 9 | 4 | 0.69 | 0
2017-09-18 05:00 | 9 | 5 | 4.6 | 0
2017-09-18 06:00 | 9 | 6 | 6.0375 | 0
2017-09-18 07:00 | 9 | 7 | 4.6 | 0
2017-09-18 08:00 | 9 | 8 | 8.625 | 286.6667
2017-09-18 09:00 | 9 | 9 | 9.2 | 286.6667
2017-09-18 10:00 | 9 | 10 | 9.5833 | 286.6667
2017-09-18 11:00 | 9 | 11 | 10.7333 | 873.3333
2017-09-18 12:00 | 9 | 12 | 10.6375 | 873.3333
2017-09-18 13:00 | 9 | 13 | 10.35 | 873.3333
2017-09-18 14:00 | 9 | 14 | 9.775 | 286.6667
2017-09-18 15:00 | 9 | 15 | 7.475 | 0
2017-09-18 16:00 | 9 | 16 | 7.6667 | 0
2017-09-18 17:00 | 9 | 17 | 10.35 | 873.3333
2017-09-18 18:00 | 9 | 18 | 10.35 | 873.3333
2017-09-18 19:00 | 9 | 19 | 10.35 | 873.3333
2017-09-18 20:00 | 9 | 20 | 11.5 | 873.3333
2017-09-18 21:00 | 9 | 21 | 11.5 | 873.3333
2017-09-18 22:00 | 9 | 22 | 10.925 | 873.3333
2017-09-18 23:00 | 9 | 23 | 10.35 | 873.3333
2017-09-19 | 9 | 0 | 8.05 | 286.6667
2017-09-19 01:00 | 9 | 1 | 9.2 | 286.6667
2017-09-19 02:00 | 9 | 2 | 10.35 | 873.3333
2017-09-19 03:00 | 9 | 3 | 12.65 | 1666.6667
2017-09-19 04:00 | 9 | 4 | 12.075 | 873.3333
2017-09-19 05:00 | 9 | 5 | 12.65 | 1666.6667
2017-09-19 06:00 | 9 | 6 | 13.8 | 1666.6667
2017-09-19 07:00 | 9 | 7 | 13.8 | 1666.6667
2017-09-19 08:00 | 9 | 8 | 12.65 | 1666.6667
2017-09-19 09:00 | 9 | 9 | 17.25 | 4266.6667
2017-09-19 10:00 | 9 | 10 | 18.4 | 4266.6667
2017-09-19 11:00 | 9 | 11 | 17.25 | 4266.6667
2017-09-19 12:00 | 9 | 12 | 17.25 | 4266.6667
2017-09-19 13:00 | 9 | 13 | 18.975 | 4266.6667
2017-09-19 14:00 | 9 | 14 | 17.25 | 4266.6667
2017-09-19 15:00 | 9 | 15 | 17.25 | 4266.6667
2017-09-19 16:00 | 9 | 16 | 16.8667 | 4266.6667
2017-09-19 17:00 | 9 | 17 | 17.825 | 4266.6667
2017-09-19 18:00 | 9 | 18 | 16.1 | 2773.3333
2017-09-19 19:00 | 9 | 19 | 18.4 | 4266.6667
2017-09-19 20:00 | 9 | 20 | 17.25 | 4266.6667
2017-09-19 21:00 | 9 | 21 | 17.825 | 4266.6667
2017-09-19 22:00 | 9 | 22 | 17.825 | 4266.6667
2017-09-19 23:00 | 9 | 23 | 18.4 | 4266.6667
2017-09-20 | 9 | 0 | 18.4 | 4266.6667
2017-09-20 01:00 | 9 | 1 | 18.7833 | 4266.6667
2017-09-20 02:00 | 9 | 2 | 20.125 | 6160
2017-09-20 03:00 | 9 | 3 | 21.275 | 7873.3333
2017-09-20 04:00 | 9 | 4 | 23.575 | 9060
2017-09-20 05:00 | 9 | 5 | 22.7125 | 7873.3333
2017-09-20 06:00 | 9 | 6 | 25.875 | 9573.3333
2017-09-20 07:00 | 9 | 7 | 25.875 | 9573.3333
2017-09-20 08:00 | 9 | 8 | 24.725 | 9060
2017-09-20 09:00 | 9 | 9 | 25.3 | 9060
2017-09-20 10:00 | 9 | 10 | 24.9167 | 9060
2017-09-20 11:00 | 9 | 11 | 26.45 | 9573.3333
2017-09-20 12:00 | 9 | 12 | 27.025 | 9573.3333
2017-09-20 13:00 | 9 | 13 | 26.8333 | 9573.3333
2017-09-20 14:00 | 9 | 14 | 27.6 | 9573.3333
2017-09-20 15:00 | 9 | 15 | 26.45 | 9573.3333
2017-09-20 16:00 | 9 | 16 | 24.9167 | 9060
2017-09-20 17:00 | 9 | 17 | 25.875 | 9573.3333
2017-09-20 18:00 | 9 | 18 | 18.4 | 4266.6667
2017-09-20 19:00 | 9 | 19 | 16.675 | 2773.3333
2017-09-20 20:00 | 9 | 20 | 18.4 | 4266.6667
2017-09-20 21:00 | 9 | 21 | 23 | 7873.3333
2017-09-20 22:00 | 9 | 22 | 23 | 7873.3333
2017-09-20 23:00 | 9 | 23 | 25.3 | 9060
2017-09-21 | 9 | 0 | 24.15 | 9060
2017-09-21 01:00 | 9 | 1 | 24.15 | 9060
2017-09-21 02:00 | 9 | 2 | 28.3667 | 9873.3333
2017-09-21 03:00 | 9 | 3 | 27.6 | 9573.3333
2017-09-21 04:00 | 9 | 4 | 29.9 | 9873.3333
2017-09-21 05:00 | 9 | 5 | 28.75 | 9873.3333
2017-09-21 06:00 | 9 | 6 | 27.6 | 9573.3333
2017-09-21 07:00 | 9 | 7 | 27.9833 | 9873.3333
2017-09-21 08:00 | 9 | 8 | 29.9 | 9873.3333
2017-09-21 09:00 | 9 | 9 | 29.9 | 9873.3333
2017-09-21 10:00 | 9 | 10 | 31.625 | 9960
2017-09-21 11:00 | 9 | 11 | 29.9 | 9873.3333
2017-09-21 12:00 | 9 | 12 | 32.2 | 9960
2017-09-21 13:00 | 9 | 13 | 27.6 | 9573.3333
2017-09-21 14:00 | 9 | 14 | 26.45 | 9573.3333
2017-09-21 15:00 | 9 | 15 | 24.15 | 9060
2017-09-21 16:00 | 9 | 16 | 22.425 | 7873.3333
2017-09-21 17:00 | 9 | 17 | 18.4 | 4266.6667
2017-09-21 18:00 | 9 | 18 | 14.95 | 2773.3333
2017-09-21 19:00 | 9 | 19 | 17.25 | 4266.6667
2017-09-21 20:00 | 9 | 20 | 23 | 7873.3333
2017-09-21 21:00 | 9 | 21 | 24.15 | 9060
2017-09-21 22:00 | 9 | 22 | 24.725 | 9060
2017-09-21 23:00 | 9 | 23 | 33.35 | 10000
2017-09-22 | 9 | 0 | 27.6 | 9573.3333
2017-09-22 01:00 | 9 | 1 | 27.6 | 9573.3333
2017-09-22 02:00 | 9 | 2 | 28.75 | 9873.3333
2017-09-22 03:00 | 9 | 3 | 24.15 | 9060
2017-09-22 04:00 | 9 | 4 | 25.5875 | 9060
2017-09-22 05:00 | 9 | 5 | 25.6833 | 9060
2017-09-22 06:00 | 9 | 6 | 25.3 | 9060
2017-09-22 07:00 | 9 | 7 | 27.025 | 9573.3333
2017-09-22 08:00 | 9 | 8 | 25.3 | 9060
2017-09-22 09:00 | 9 | 9 | 25.3 | 9060
2017-09-22 10:00 | 9 | 10 | 26.45 | 9573.3333
2017-09-22 11:00 | 9 | 11 | 28.75 | 9873.3333
2017-09-22 12:00 | 9 | 12 | 27.6 | 9573.3333
2017-09-22 13:00 | 9 | 13 | 26.45 | 9573.3333
2017-09-22 14:00 | 9 | 14 | 26.45 | 9573.3333
2017-09-22 15:00 | 9 | 15 | 28.75 | 9873.3333
2017-09-22 16:00 | 9 | 16 | 27.6 | 9573.3333
2017-09-22 17:00 | 9 | 17 | 25.875 | 9573.3333
2017-09-22 18:00 | 9 | 18 | 25.3 | 9060
2017-09-22 19:00 | 9 | 19 | 23.7667 | 9060
2017-09-22 20:00 | 9 | 20 | 26.45 | 9573.3333
2017-09-22 21:00 | 9 | 21 | 19.55 | 6160
2017-09-22 22:00 | 9 | 22 | 20.9875 | 6160
2017-09-22 23:00 | 9 | 23 | 22.425 | 7873.3333
2017-09-23 | 9 | 0 | 18.4 | 4266.6667
2017-09-23 01:00 | 9 | 1 | 18.4 | 4266.6667
2017-09-23 02:00 | 9 | 2 | 19.55 | 6160
2017-09-23 03:00 | 9 | 3 | 19.55 | 6160
2017-09-23 04:00 | 9 | 4 | 16.1 | 2773.3333
2017-09-23 05:00 | 9 | 5 | 11.5 | 873.3333
2017-09-23 06:00 | 9 | 6 | 14.95 | 2773.3333
2017-09-23 07:00 | 9 | 7 | 14.95 | 2773.3333
2017-09-23 08:00 | 9 | 8 | 11.5 | 873.3333
2017-09-23 09:00 | 9 | 9 | 13.8 | 1666.6667
2017-09-23 10:00 | 9 | 10 | 12.65 | 1666.6667
2017-09-23 11:00 | 9 | 11 | 10.35 | 873.3333
2017-09-23 12:00 | 9 | 12 | 14.95 | 2773.3333
2017-09-23 13:00 | 9 | 13 | 14.95 | 2773.3333
2017-09-23 14:00 | 9 | 14 | 9.2 | 286.6667
2017-09-23 15:00 | 9 | 15 | 8.05 | 286.6667
2017-09-23 16:00 | 9 | 16 | 8.05 | 286.6667
2017-09-23 17:00 | 9 | 17 | 1.725 | 0
2017-09-23 18:00 | 9 | 18 | 3.45 | 0
2017-09-23 19:00 | 9 | 19 | 2.3 | 0
2017-09-23 20:00 | 9 | 20 | 1.725 | 0
2017-09-23 21:00 | 9 | 21 | 0 | 0
2017-09-23 22:00 | 9 | 22 | 0 | 0
2017-09-23 23:00 | 9 | 23 | 0 | 0
2017-09-24 | 9 | 0 | 0 | 0
2017-09-24 01:00 | 9 | 1 | 0 | 0
2017-09-24 02:00 | 9 | 2 | 0 | 0
2017-09-24 03:00 | 9 | 3 | 0 | 0
2017-09-24 04:00 | 9 | 4 | 0 | 0
2017-09-24 05:00 | 9 | 5 | 0 | 0
2017-09-24 06:00 | 9 | 6 | 5.75 | 0
2017-09-24 07:00 | 9 | 7 | 4.6 | 0
2017-09-24 08:00 | 9 | 8 | 3.45 | 0
2017-09-24 09:00 | 9 | 9 | 5.75 | 0
2017-09-24 10:00 | 9 | 10 | 5.75 | 0
2017-09-24 11:00 | 9 | 11 | 6.9 | 0
2017-09-24 12:00 | 9 | 12 | 8.05 | 286.6667
2017-09-24 13:00 | 9 | 13 | 8.625 | 286.6667
2017-09-24 14:00 | 9 | 14 | 6.9 | 0
2017-09-24 15:00 | 9 | 15 | 6.9 | 0
2017-09-24 16:00 | 9 | 16 | 5.175 | 0
2017-09-24 17:00 | 9 | 17 | 5.75 | 0
2017-09-24 18:00 | 9 | 18 | 0 | 0
2017-09-24 19:00 | 9 | 19 | 0 | 0
2017-09-24 20:00 | 9 | 20 | 0 | 0
2017-09-24 21:00 | 9 | 21 | 5.75 | 0
2017-09-24 22:00 | 9 | 22 | 6.325 | 0
2017-09-24 23:00 | 9 | 23 | 5.75 | 0
2017-09-25 | 9 | 0 | 0 | 0
2017-09-25 01:00 | 9 | 1 | 0 | 0
2017-09-25 02:00 | 9 | 2 | 0 | 0
2017-09-25 03:00 | 9 | 3 | 0 | 0
2017-09-25 04:00 | 9 | 4 | 1.725 | 0
2017-09-25 05:00 | 9 | 5 | 0 | 0
2017-09-25 06:00 | 9 | 6 | 3.45 | 0
2017-09-25 07:00 | 9 | 7 | 3.45 | 0
2017-09-25 08:00 | 9 | 8 | 0 | 0
2017-09-25 09:00 | 9 | 9 | 5.75 | 0
2017-09-25 10:00 | 9 | 10 | 7.475 | 0
2017-09-25 11:00 | 9 | 11 | 9.2 | 286.6667
2017-09-25 12:00 | 9 | 12 | 10.35 | 873.3333
2017-09-25 13:00 | 9 | 13 | 10.925 | 873.3333
2017-09-25 14:00 | 9 | 14 | 11.5 | 873.3333
2017-09-25 15:00 | 9 | 15 | 9.2 | 286.6667
2017-09-25 16:00 | 9 | 16 | 9.775 | 286.6667
2017-09-25 17:00 | 9 | 17 | 11.5 | 873.3333
2017-09-25 18:00 | 9 | 18 | 6.9 | 0
2017-09-25 19:00 | 9 | 19 | 6.325 | 0
2017-09-25 20:00 | 9 | 20 | 5.75 | 0
2017-09-25 21:00 | 9 | 21 | 0 | 0
2017-09-25 22:00 | 9 | 22 | 3.45 | 0
2017-09-25 23:00 | 9 | 23 | 6.1333 | 0
2017-09-26 | 9 | 0 | 3.0667 | 0
2017-09-26 01:00 | 9 | 1 | 0 | 0
2017-09-26 02:00 | 9 | 2 | 0 | 0
2017-09-26 03:00 | 9 | 3 | 3.45 | 0
2017-09-26 04:00 | 9 | 4 | 4.2167 | 0
2017-09-26 05:00 | 9 | 5 | 4.9833 | 0
2017-09-26 06:00 | 9 | 6 | 6.9 | 0
2017-09-26 07:00 | 9 | 7 | 3.45 | 0
2017-09-26 08:00 | 9 | 8 | 4.3125 | 0
2017-09-26 09:00 | 9 | 9 | 8.05 | 286.6667
2017-09-26 10:00 | 9 | 10 | 8.625 | 286.6667
2017-09-26 11:00 | 9 | 11 | 10.35 | 873.3333
2017-09-26 12:00 | 9 | 12 | 9.2 | 286.6667
2017-09-26 13:00 | 9 | 13 | 9.2 | 286.6667
2017-09-26 14:00 | 9 | 14 | 9.2 | 286.6667
2017-09-26 15:00 | 9 | 15 | 8.05 | 286.6667
2017-09-26 16:00 | 9 | 16 | 8.05 | 286.6667
2017-09-26 17:00 | 9 | 17 | 0 | 0
2017-09-26 18:00 | 9 | 18 | 0 | 0
2017-09-26 19:00 | 9 | 19 | 4.6 | 0
2017-09-26 20:00 | 9 | 20 | 6.9 | 0
2017-09-26 21:00 | 9 | 21 | 8.05 | 286.6667
2017-09-26 22:00 | 9 | 22 | 8.05 | 286.6667
2017-09-26 23:00 | 9 | 23 | 9.2 | 286.6667
2017-09-27 | 9 | 0 | 9.2 | 286.6667
2017-09-27 01:00 | 9 | 1 | 4.6 | 0
2017-09-27 02:00 | 9 | 2 | 5.75 | 0
2017-09-27 03:00 | 9 | 3 | 8.05 | 286.6667
2017-09-27 04:00 | 9 | 4 | 5.75 | 0
2017-09-27 05:00 | 9 | 5 | 8.05 | 286.6667
2017-09-27 06:00 | 9 | 6 | 6.9 | 0
2017-09-27 07:00 | 9 | 7 | 8.625 | 286.6667
2017-09-27 08:00 | 9 | 8 | 6.9 | 0
2017-09-27 09:00 | 9 | 9 | 10.35 | 873.3333
2017-09-27 10:00 | 9 | 10 | 8.625 | 286.6667
2017-09-27 11:00 | 9 | 11 | 12.65 | 1666.6667
2017-09-27 12:00 | 9 | 12 | 9.2 | 286.6667
2017-09-27 13:00 | 9 | 13 | 10.925 | 873.3333
2017-09-27 14:00 | 9 | 14 | 12.65 | 1666.6667
2017-09-27 15:00 | 9 | 15 | 14.95 | 2773.3333
2017-09-27 16:00 | 9 | 16 | 14.95 | 2773.3333
2017-09-27 17:00 | 9 | 17 | 12.65 | 1666.6667
2017-09-27 18:00 | 9 | 18 | 11.5 | 873.3333
2017-09-27 19:00 | 9 | 19 | 10.925 | 873.3333
2017-09-27 20:00 | 9 | 20 | 11.5 | 873.3333
2017-09-27 21:00 | 9 | 21 | 11.5 | 873.3333
2017-09-27 22:00 | 9 | 22 | 12.075 | 873.3333
2017-09-27 23:00 | 9 | 23 | 9.2 | 286.6667
2017-09-28 | 9 | 0 | 8.05 | 286.6667
2017-09-28 01:00 | 9 | 1 | 7.7625 | 0
2017-09-28 02:00 | 9 | 2 | 9.5833 | 286.6667
2017-09-28 03:00 | 9 | 3 | 7.2833 | 0
2017-09-28 04:00 | 9 | 4 | 7.475 | 0
2017-09-28 05:00 | 9 | 5 | 10.35 | 873.3333
2017-09-28 06:00 | 9 | 6 | 11.5 | 873.3333
2017-09-28 07:00 | 9 | 7 | 16.1 | 2773.3333
2017-09-28 08:00 | 9 | 8 | 23 | 7873.3333
2017-09-28 09:00 | 9 | 9 | 18.4 | 4266.6667
2017-09-28 10:00 | 9 | 10 | 18.4 | 4266.6667
2017-09-28 11:00 | 9 | 11 | 10.35 | 873.3333
2017-09-28 12:00 | 9 | 12 | 17.25 | 4266.6667
2017-09-28 13:00 | 9 | 13 | 20.125 | 6160
2017-09-28 14:00 | 9 | 14 | 19.55 | 6160
2017-09-28 15:00 | 9 | 15 | 14.95 | 2773.3333
2017-09-28 16:00 | 9 | 16 | 17.25 | 4266.6667
2017-09-28 17:00 | 9 | 17 | 14.95 | 2773.3333
2017-09-28 18:00 | 9 | 18 | 17.25 | 4266.6667
2017-09-28 19:00 | 9 | 19 | 20.7 | 6160
2017-09-28 20:00 | 9 | 20 | 14.95 | 2773.3333
2017-09-28 21:00 | 9 | 21 | 16.1 | 2773.3333
2017-09-28 22:00 | 9 | 22 | 14.375 | 1666.6667
2017-09-28 23:00 | 9 | 23 | 16.1 | 2773.3333
2017-09-29 | 9 | 0 | 14.95 | 2773.3333
2017-09-29 01:00 | 9 | 1 | 15.525 | 2773.3333
2017-09-29 02:00 | 9 | 2 | 11.5 | 873.3333
2017-09-29 03:00 | 9 | 3 | 12.65 | 1666.6667
2017-09-29 04:00 | 9 | 4 | 12.65 | 1666.6667
2017-09-29 05:00 | 9 | 5 | 11.5 | 873.3333
2017-09-29 06:00 | 9 | 6 | 11.5 | 873.3333
2017-09-29 07:00 | 9 | 7 | 11.5 | 873.3333
2017-09-29 08:00 | 9 | 8 | 8.05 | 286.6667
2017-09-29 09:00 | 9 | 9 | 5.75 | 0
2017-09-29 10:00 | 9 | 10 | 5.75 | 0
2017-09-29 11:00 | 9 | 11 | 12.65 | 1666.6667
2017-09-29 12:00 | 9 | 12 | 10.35 | 873.3333
2017-09-29 13:00 | 9 | 13 | 10.35 | 873.3333
2017-09-29 14:00 | 9 | 14 | 8.05 | 286.6667
2017-09-29 15:00 | 9 | 15 | 16.1 | 2773.3333
2017-09-29 16:00 | 9 | 16 | 13.8 | 1666.6667
2017-09-29 17:00 | 9 | 17 | 12.65 | 1666.6667
2017-09-29 18:00 | 9 | 18 | 11.5 | 873.3333
2017-09-29 19:00 | 9 | 19 | 11.5 | 873.3333
2017-09-29 20:00 | 9 | 20 | 6.9 | 0
2017-09-29 21:00 | 9 | 21 | 5.75 | 0
2017-09-29 22:00 | 9 | 22 | 6.9 | 0
2017-09-29 23:00 | 9 | 23 | 10.35 | 873.3333
2017-09-30 | 9 | 0 | 8.05 | 286.6667
2017-09-30 01:00 | 9 | 1 | 7.475 | 0
2017-09-30 02:00 | 9 | 2 | 0 | 0
2017-09-30 03:00 | 9 | 3 | 5.75 | 0
2017-09-30 04:00 | 9 | 4 | 7.475 | 0
2017-09-30 05:00 | 9 | 5 | 10.925 | 873.3333
2017-09-30 06:00 | 9 | 6 | 19.55 | 6160
2017-09-30 07:00 | 9 | 7 | 21.275 | 7873.3333
2017-09-30 08:00 | 9 | 8 | 17.825 | 4266.6667
2017-09-30 09:00 | 9 | 9 | 14.95 | 2773.3333
2017-09-30 10:00 | 9 | 10 | 15.525 | 2773.3333
2017-09-30 11:00 | 9 | 11 | 10.35 | 873.3333
2017-09-30 12:00 | 9 | 12 | 17.25 | 4266.6667
2017-09-30 13:00 | 9 | 13 | 17.825 | 4266.6667
2017-09-30 14:00 | 9 | 14 | 20.7 | 6160
2017-09-30 15:00 | 9 | 15 | 14.95 | 2773.3333
2017-09-30 16:00 | 9 | 16 | 14.95 | 2773.3333
2017-09-30 17:00 | 9 | 17 | 11.5 | 873.3333
2017-09-30 18:00 | 9 | 18 | 10.35 | 873.3333
2017-09-30 19:00 | 9 | 19 | 9.775 | 286.6667
2017-09-30 20:00 | 9 | 20 | 9.2 | 286.6667
2017-09-30 21:00 | 9 | 21 | 10.35 | 873.3333
2017-09-30 22:00 | 9 | 22 | 9.775 | 286.6667
2017-09-30 23:00 | 9 | 23 | 10.35 | 873.3333
2017-10-01 | 10 | 0 | 8.05 | 286.6667
2017-10-01 01:00 | 10 | 1 | 8.05 | 286.6667
2017-10-01 02:00 | 10 | 2 | 11.5 | 873.3333
2017-10-01 03:00 | 10 | 3 | 10.35 | 873.3333
2017-10-01 04:00 | 10 | 4 | 10.35 | 873.3333
2017-10-01 05:00 | 10 | 5 | 10.35 | 873.3333
2017-10-01 06:00 | 10 | 6 | 10.35 | 873.3333
2017-10-01 07:00 | 10 | 7 | 10.35 | 873.3333
2017-10-01 08:00 | 10 | 8 | 9.2 | 286.6667
2017-10-01 09:00 | 10 | 9 | 9.2 | 286.6667
2017-10-01 10:00 | 10 | 10 | 10.35 | 873.3333
2017-10-01 11:00 | 10 | 11 | 6.9 | 0
2017-10-01 12:00 | 10 | 12 | 8.05 | 286.6667
2017-10-01 13:00 | 10 | 13 | 9.2 | 286.6667
2017-10-01 14:00 | 10 | 14 | 3.45 | 0
2017-10-01 15:00 | 10 | 15 | 9.2 | 286.6667
2017-10-01 16:00 | 10 | 16 | 9.2 | 286.6667
2017-10-01 17:00 | 10 | 17 | 9.2 | 286.6667
2017-10-01 18:00 | 10 | 18 | 8.05 | 286.6667
2017-10-01 19:00 | 10 | 19 | 8.05 | 286.6667
2017-10-01 20:00 | 10 | 20 | 10.35 | 873.3333
2017-10-01 21:00 | 10 | 21 | 9.2 | 286.6667
2017-10-01 22:00 | 10 | 22 | 9.2 | 286.6667
2017-10-01 23:00 | 10 | 23 | 12.65 | 1666.6667
2017-10-02 | 10 | 0 | 10.35 | 873.3333
2017-10-02 01:00 | 10 | 1 | 10.925 | 873.3333
2017-10-02 02:00 | 10 | 2 | 10.35 | 873.3333
2017-10-02 03:00 | 10 | 3 | 9.2 | 286.6667
2017-10-02 04:00 | 10 | 4 | 9.2 | 286.6667
2017-10-02 05:00 | 10 | 5 | 8.05 | 286.6667
2017-10-02 06:00 | 10 | 6 | 10.35 | 873.3333
2017-10-02 07:00 | 10 | 7 | 9.2 | 286.6667
2017-10-02 08:00 | 10 | 8 | 11.5 | 873.3333
2017-10-02 09:00 | 10 | 9 | 10.35 | 873.3333
2017-10-02 10:00 | 10 | 10 | 11.5 | 873.3333
2017-10-02 11:00 | 10 | 11 | 14.95 | 2773.3333
2017-10-02 12:00 | 10 | 12 | 14.95 | 2773.3333
2017-10-02 13:00 | 10 | 13 | 16.1 | 2773.3333
2017-10-02 14:00 | 10 | 14 | 17.25 | 4266.6667
2017-10-02 15:00 | 10 | 15 | 12.65 | 1666.6667
2017-10-02 16:00 | 10 | 16 | 11.5 | 873.3333
2017-10-02 17:00 | 10 | 17 | 8.05 | 286.6667
2017-10-02 18:00 | 10 | 18 | 6.9 | 0
2017-10-02 19:00 | 10 | 19 | 6.325 | 0
2017-10-02 20:00 | 10 | 20 | 5.75 | 0
2017-10-02 21:00 | 10 | 21 | 5.75 | 0
2017-10-02 22:00 | 10 | 22 | 4.6 | 0
2017-10-02 23:00 | 10 | 23 | 0 | 0
2017-10-03 | 10 | 0 | 0 | 0
2017-10-03 01:00 | 10 | 1 | 1.725 | 0
2017-10-03 02:00 | 10 | 2 | 0 | 0
2017-10-03 03:00 | 10 | 3 | 0 | 0
2017-10-03 04:00 | 10 | 4 | 0 | 0
2017-10-03 05:00 | 10 | 5 | 0 | 0
2017-10-03 06:00 | 10 | 6 | 0 | 0
2017-10-03 07:00 | 10 | 7 | 2.875 | 0
2017-10-03 08:00 | 10 | 8 | 6.9 | 0
2017-10-03 09:00 | 10 | 9 | 6.9 | 0
2017-10-03 10:00 | 10 | 10 | 9.2 | 286.6667
2017-10-03 11:00 | 10 | 11 | 11.5 | 873.3333
2017-10-03 12:00 | 10 | 12 | 16.1 | 2773.3333
2017-10-03 13:00 | 10 | 13 | 16.1 | 2773.3333
2017-10-03 14:00 | 10 | 14 | 19.55 | 6160
2017-10-03 15:00 | 10 | 15 | 17.25 | 4266.6667
2017-10-03 16:00 | 10 | 16 | 17.25 | 4266.6667
2017-10-03 17:00 | 10 | 17 | 16.1 | 2773.3333
2017-10-03 18:00 | 10 | 18 | 17.25 | 4266.6667
2017-10-03 19:00 | 10 | 19 | 17.25 | 4266.6667
2017-10-03 20:00 | 10 | 20 | 17.25 | 4266.6667
2017-10-03 21:00 | 10 | 21 | 19.55 | 6160
2017-10-03 22:00 | 10 | 22 | 17.25 | 4266.6667
2017-10-03 23:00 | 10 | 23 | 11.5 | 873.3333
2017-10-04 | 10 | 0 | 11.5 | 873.3333
2017-10-04 01:00 | 10 | 1 | 13.225 | 1666.6667
2017-10-04 02:00 | 10 | 2 | 12.65 | 1666.6667
2017-10-04 03:00 | 10 | 3 | 17.25 | 4266.6667
2017-10-04 04:00 | 10 | 4 | 14.375 | 1666.6667
2017-10-04 05:00 | 10 | 5 | 16.1 | 2773.3333
2017-10-04 06:00 | 10 | 6 | 12.65 | 1666.6667
2017-10-04 07:00 | 10 | 7 | 14.375 | 1666.6667
2017-10-04 08:00 | 10 | 8 | 16.1 | 2773.3333
2017-10-04 09:00 | 10 | 9 | 16.1 | 2773.3333
2017-10-04 10:00 | 10 | 10 | 16.1 | 2773.3333
2017-10-04 11:00 | 10 | 11 | 17.25 | 4266.6667
2017-10-04 12:00 | 10 | 12 | 19.55 | 6160
2017-10-04 13:00 | 10 | 13 | 18.4 | 4266.6667
2017-10-04 14:00 | 10 | 14 | 20.7 | 6160
2017-10-04 15:00 | 10 | 15 | 23 | 7873.3333
2017-10-04 16:00 | 10 | 16 | 20.125 | 6160
2017-10-04 17:00 | 10 | 17 | 19.55 | 6160
2017-10-04 18:00 | 10 | 18 | 19.55 | 6160
2017-10-04 19:00 | 10 | 19 | 19.55 | 6160
2017-10-04 20:00 | 10 | 20 | 23 | 7873.3333
2017-10-04 21:00 | 10 | 21 | 25.3 | 9060
2017-10-04 22:00 | 10 | 22 | 25.875 | 9573.3333
2017-10-04 23:00 | 10 | 23 | 25.3 | 9060
2017-10-05 | 10 | 0 | 23 | 7873.3333
2017-10-05 01:00 | 10 | 1 | 21.85 | 7873.3333
2017-10-05 02:00 | 10 | 2 | 17.25 | 4266.6667
2017-10-05 03:00 | 10 | 3 | 12.65 | 1666.6667
2017-10-05 04:00 | 10 | 4 | 12.65 | 1666.6667
2017-10-05 05:00 | 10 | 5 | 11.5 | 873.3333
2017-10-05 06:00 | 10 | 6 | 12.65 | 1666.6667
2017-10-05 07:00 | 10 | 7 | 13.8 | 1666.6667
2017-10-05 08:00 | 10 | 8 | 11.5 | 873.3333
2017-10-05 09:00 | 10 | 9 | 11.5 | 873.3333
2017-10-05 10:00 | 10 | 10 | 11.5 | 873.3333
2017-10-05 11:00 | 10 | 11 | 10.35 | 873.3333
2017-10-05 12:00 | 10 | 12 | 14.95 | 2773.3333
2017-10-05 13:00 | 10 | 13 | 16.675 | 2773.3333
2017-10-05 14:00 | 10 | 14 | 12.65 | 1666.6667
2017-10-05 15:00 | 10 | 15 | 16.1 | 2773.3333
2017-10-05 16:00 | 10 | 16 | 13.8 | 1666.6667
2017-10-05 17:00 | 10 | 17 | 10.35 | 873.3333
2017-10-05 18:00 | 10 | 18 | 8.05 | 286.6667
2017-10-05 19:00 | 10 | 19 | 5.75 | 0
2017-10-05 20:00 | 10 | 20 | 5.75 | 0
2017-10-05 21:00 | 10 | 21 | 6.9 | 0
2017-10-05 22:00 | 10 | 22 | 8.05 | 286.6667
2017-10-05 23:00 | 10 | 23 | 8.05 | 286.6667
2017-10-06 | 10 | 0 | 6.9 | 0
2017-10-06 01:00 | 10 | 1 | 7.475 | 0
2017-10-06 02:00 | 10 | 2 | 3.45 | 0
2017-10-06 03:00 | 10 | 3 | 5.75 | 0
2017-10-06 04:00 | 10 | 4 | 2.875 | 0
2017-10-06 05:00 | 10 | 5 | 8.05 | 286.6667
2017-10-06 06:00 | 10 | 6 | 8.05 | 286.6667
2017-10-06 07:00 | 10 | 7 | 8.625 | 286.6667
2017-10-06 08:00 | 10 | 8 | 5.75 | 0
2017-10-06 09:00 | 10 | 9 | 11.5 | 873.3333
2017-10-06 10:00 | 10 | 10 | 9.775 | 286.6667
2017-10-06 11:00 | 10 | 11 | 16.1 | 2773.3333
2017-10-06 12:00 | 10 | 12 | 12.65 | 1666.6667
2017-10-06 13:00 | 10 | 13 | 12.075 | 873.3333
2017-10-06 14:00 | 10 | 14 | 10.35 | 873.3333
2017-10-06 15:00 | 10 | 15 | 10.35 | 873.3333
2017-10-06 16:00 | 10 | 16 | 10.35 | 873.3333
2017-10-06 17:00 | 10 | 17 | 0 | 0
2017-10-06 18:00 | 10 | 18 | 6.9 | 0
2017-10-06 19:00 | 10 | 19 | 6.9 | 0
2017-10-06 20:00 | 10 | 20 | 6.9 | 0
2017-10-06 21:00 | 10 | 21 | 3.45 | 0
2017-10-06 22:00 | 10 | 22 | 1.725 | 0
2017-10-06 23:00 | 10 | 23 | 0 | 0
2017-10-07 | 10 | 0 | 3.45 | 0
2017-10-07 01:00 | 10 | 1 | 3.45 | 0
2017-10-07 02:00 | 10 | 2 | 3.45 | 0
2017-10-07 03:00 | 10 | 3 | 6.9 | 0
2017-10-07 04:00 | 10 | 4 | 3.45 | 0
2017-10-07 05:00 | 10 | 5 | 3.45 | 0
2017-10-07 06:00 | 10 | 6 | 0 | 0
2017-10-07 07:00 | 10 | 7 | 2.875 | 0
2017-10-07 08:00 | 10 | 8 | 8.05 | 286.6667
2017-10-07 09:00 | 10 | 9 | 3.45 | 0
2017-10-07 10:00 | 10 | 10 | 7.475 | 0
2017-10-07 11:00 | 10 | 11 | 14.95 | 2773.3333
2017-10-07 12:00 | 10 | 12 | 11.5 | 873.3333
2017-10-07 13:00 | 10 | 13 | 10.925 | 873.3333
2017-10-07 14:00 | 10 | 14 | 10.35 | 873.3333
2017-10-07 15:00 | 10 | 15 | 14.95 | 2773.3333
2017-10-07 16:00 | 10 | 16 | 16.675 | 2773.3333
2017-10-07 17:00 | 10 | 17 | 16.1 | 2773.3333
2017-10-07 18:00 | 10 | 18 | 16.1 | 2773.3333
2017-10-07 19:00 | 10 | 19 | 16.675 | 2773.3333
2017-10-07 20:00 | 10 | 20 | 17.25 | 4266.6667
2017-10-07 21:00 | 10 | 21 | 16.675 | 2773.3333
2017-10-07 22:00 | 10 | 22 | 17.25 | 4266.6667
2017-10-07 23:00 | 10 | 23 | 12.65 | 1666.6667
2017-10-08 | 10 | 0 | 18.4 | 4266.6667
2017-10-08 01:00 | 10 | 1 | 16.8667 | 4266.6667
2017-10-08 02:00 | 10 | 2 | 18.4 | 4266.6667
2017-10-08 03:00 | 10 | 3 | 18.4 | 4266.6667
2017-10-08 04:00 | 10 | 4 | 18.4 | 4266.6667
2017-10-08 05:00 | 10 | 5 | 19.55 | 6160
2017-10-08 06:00 | 10 | 6 | 17.25 | 4266.6667
2017-10-08 07:00 | 10 | 7 | 21.275 | 7873.3333
2017-10-08 08:00 | 10 | 8 | 18.4 | 4266.6667
2017-10-08 09:00 | 10 | 9 | 16.1 | 2773.3333
2017-10-08 10:00 | 10 | 10 | 18.4 | 4266.6667
2017-10-08 11:00 | 10 | 11 | 22.425 | 7873.3333
2017-10-08 12:00 | 10 | 12 | 18.4 | 4266.6667
2017-10-08 13:00 | 10 | 13 | 18.4 | 4266.6667
2017-10-08 14:00 | 10 | 14 | 17.825 | 4266.6667
2017-10-08 15:00 | 10 | 15 | 15.525 | 2773.3333
2017-10-08 16:00 | 10 | 16 | 15.7167 | 2773.3333
2017-10-08 17:00 | 10 | 17 | 14.375 | 1666.6667
2017-10-08 18:00 | 10 | 18 | 10.35 | 873.3333
2017-10-08 19:00 | 10 | 19 | 9.5833 | 286.6667
2017-10-08 20:00 | 10 | 20 | 9.775 | 286.6667
2017-10-08 21:00 | 10 | 21 | 9.2 | 286.6667
2017-10-08 22:00 | 10 | 22 | 8.625 | 286.6667
2017-10-08 23:00 | 10 | 23 | 8.05 | 286.6667
2017-10-09 | 10 | 0 | 8.05 | 286.6667
2017-10-09 01:00 | 10 | 1 | 4.025 | 0
2017-10-09 02:00 | 10 | 2 | 8.05 | 286.6667
2017-10-09 03:00 | 10 | 3 | 7.475 | 0
2017-10-09 04:00 | 10 | 4 | 3.91 | 0
2017-10-09 05:00 | 10 | 5 | 6.1333 | 0
2017-10-09 06:00 | 10 | 6 | 5.75 | 0
2017-10-09 07:00 | 10 | 7 | 5.6062 | 0
2017-10-09 08:00 | 10 | 8 | 10.35 | 873.3333
2017-10-09 09:00 | 10 | 9 | 9.2 | 286.6667
2017-10-09 10:00 | 10 | 10 | 11.5 | 873.3333
2017-10-09 11:00 | 10 | 11 | 13.4167 | 1666.6667
2017-10-09 12:00 | 10 | 12 | 15.7167 | 2773.3333
2017-10-09 13:00 | 10 | 13 | 14.95 | 2773.3333
2017-10-09 14:00 | 10 | 14 | 16.1 | 2773.3333
2017-10-09 15:00 | 10 | 15 | 24.15 | 9060
2017-10-09 16:00 | 10 | 16 | 21.4667 | 7873.3333
2017-10-09 17:00 | 10 | 17 | 26.7375 | 9573.3333
2017-10-09 18:00 | 10 | 18 | 19.55 | 6160
2017-10-09 19:00 | 10 | 19 | 19.1667 | 6160
2017-10-09 20:00 | 10 | 20 | 14.95 | 2773.3333
2017-10-09 21:00 | 10 | 21 | 17.25 | 4266.6667
2017-10-09 22:00 | 10 | 22 | 16.1 | 2773.3333
2017-10-09 23:00 | 10 | 23 | 12.075 | 873.3333
2017-10-10 | 10 | 0 | 11.5 | 873.3333
2017-10-10 01:00 | 10 | 1 | 13.225 | 1666.6667
2017-10-10 02:00 | 10 | 2 | 12.65 | 1666.6667
2017-10-10 03:00 | 10 | 3 | 16.1 | 2773.3333
2017-10-10 04:00 | 10 | 4 | 13.8 | 1666.6667
2017-10-10 05:00 | 10 | 5 | 14.95 | 2773.3333
2017-10-10 06:00 | 10 | 6 | 17.25 | 4266.6667
2017-10-10 07:00 | 10 | 7 | 14.375 | 1666.6667
2017-10-10 08:00 | 10 | 8 | 16.1 | 2773.3333
2017-10-10 09:00 | 10 | 9 | 17.25 | 4266.6667
2017-10-10 10:00 | 10 | 10 | 16.1 | 2773.3333
2017-10-10 11:00 | 10 | 11 | 12.65 | 1666.6667
2017-10-10 12:00 | 10 | 12 | 10.35 | 873.3333
2017-10-10 13:00 | 10 | 13 | 12.65 | 1666.6667
2017-10-10 14:00 | 10 | 14 | 14.95 | 2773.3333
2017-10-10 15:00 | 10 | 15 | 11.5 | 873.3333
2017-10-10 16:00 | 10 | 16 | 13.225 | 1666.6667
2017-10-10 17:00 | 10 | 17 | 10.35 | 873.3333
2017-10-10 18:00 | 10 | 18 | 6.9 | 0
2017-10-10 19:00 | 10 | 19 | 8.05 | 286.6667
2017-10-10 20:00 | 10 | 20 | 5.75 | 0
2017-10-10 21:00 | 10 | 21 | 9.2 | 286.6667
2017-10-10 22:00 | 10 | 22 | 9.2 | 286.6667
2017-10-10 23:00 | 10 | 23 | 9.2 | 286.6667
2017-10-11 | 10 | 0 | 10.35 | 873.3333
2017-10-11 01:00 | 10 | 1 | 9.775 | 286.6667
2017-10-11 02:00 | 10 | 2 | 8.05 | 286.6667
2017-10-11 03:00 | 10 | 3 | 9.2 | 286.6667
2017-10-11 04:00 | 10 | 4 | 9.2 | 286.6667
2017-10-11 05:00 | 10 | 5 | 9.2 | 286.6667
2017-10-11 06:00 | 10 | 6 | 8.05 | 286.6667
2017-10-11 07:00 | 10 | 7 | 9.775 | 286.6667
2017-10-11 08:00 | 10 | 8 | 12.65 | 1666.6667
2017-10-11 09:00 | 10 | 9 | 14.95 | 2773.3333
2017-10-11 10:00 | 10 | 10 | 13.225 | 1666.6667
2017-10-11 11:00 | 10 | 11 | 11.5 | 873.3333
2017-10-11 12:00 | 10 | 12 | 12.65 | 1666.6667
2017-10-11 13:00 | 10 | 13 | 13.8 | 1666.6667
2017-10-11 14:00 | 10 | 14 | 14.95 | 2773.3333
2017-10-11 15:00 | 10 | 15 | 12.65 | 1666.6667
2017-10-11 16:00 | 10 | 16 | 10.925 | 873.3333
2017-10-11 17:00 | 10 | 17 | 5.75 | 0
2017-10-11 18:00 | 10 | 18 | 9.2 | 286.6667
2017-10-11 19:00 | 10 | 19 | 8.625 | 286.6667
2017-10-11 20:00 | 10 | 20 | 10.35 | 873.3333
2017-10-11 21:00 | 10 | 21 | 18.4 | 4266.6667
2017-10-11 22:00 | 10 | 22 | 17.825 | 4266.6667
2017-10-11 23:00 | 10 | 23 | 20.7 | 6160
2017-10-12 | 10 | 0 | 16.1 | 2773.3333
2017-10-12 01:00 | 10 | 1 | 19.55 | 6160
2017-10-12 02:00 | 10 | 2 | 19.55 | 6160
2017-10-12 03:00 | 10 | 3 | 18.4 | 4266.6667
2017-10-12 04:00 | 10 | 4 | 19.55 | 6160
2017-10-12 05:00 | 10 | 5 | 18.4 | 4266.6667
2017-10-12 06:00 | 10 | 6 | 18.4 | 4266.6667
2017-10-12 07:00 | 10 | 7 | 18.4 | 4266.6667
2017-10-12 08:00 | 10 | 8 | 20.7 | 6160
2017-10-12 09:00 | 10 | 9 | 24.15 | 9060
2017-10-12 10:00 | 10 | 10 | 22.425 | 7873.3333
2017-10-12 11:00 | 10 | 11 | 18.4 | 4266.6667
2017-10-12 12:00 | 10 | 12 | 18.4 | 4266.6667
2017-10-12 13:00 | 10 | 13 | 17.825 | 4266.6667
2017-10-12 14:00 | 10 | 14 | 16.1 | 2773.3333
2017-10-12 15:00 | 10 | 15 | 16.1 | 2773.3333
2017-10-12 16:00 | 10 | 16 | 14.375 | 1666.6667
2017-10-12 17:00 | 10 | 17 | 11.5 | 873.3333
2017-10-12 18:00 | 10 | 18 | 10.35 | 873.3333
2017-10-12 19:00 | 10 | 19 | 10.925 | 873.3333
2017-10-12 20:00 | 10 | 20 | 5.75 | 0
2017-10-12 21:00 | 10 | 21 | 5.75 | 0
2017-10-12 22:00 | 10 | 22 | 6.325 | 0
2017-10-12 23:00 | 10 | 23 | 6.9 | 0
2017-10-13 | 10 | 0 | 8.05 | 286.6667
2017-10-13 01:00 | 10 | 1 | 6.9 | 0
2017-10-13 02:00 | 10 | 2 | 6.9 | 0
2017-10-13 03:00 | 10 | 3 | 6.9 | 0
2017-10-13 04:00 | 10 | 4 | 8.625 | 286.6667
2017-10-13 05:00 | 10 | 5 | 8.05 | 286.6667
2017-10-13 06:00 | 10 | 6 | 16.1 | 2773.3333
2017-10-13 07:00 | 10 | 7 | 16.1 | 2773.3333
2017-10-13 08:00 | 10 | 8 | 14.95 | 2773.3333
2017-10-13 09:00 | 10 | 9 | 16.1 | 2773.3333
2017-10-13 10:00 | 10 | 10 | 14.375 | 1666.6667
2017-10-13 11:00 | 10 | 11 | 17.25 | 4266.6667
2017-10-13 12:00 | 10 | 12 | 17.25 | 4266.6667
2017-10-13 13:00 | 10 | 13 | 17.825 | 4266.6667
2017-10-13 14:00 | 10 | 14 | 19.55 | 6160
2017-10-13 15:00 | 10 | 15 | 20.7 | 6160
2017-10-13 16:00 | 10 | 16 | 18.975 | 4266.6667
2017-10-13 17:00 | 10 | 17 | 12.65 | 1666.6667
2017-10-13 18:00 | 10 | 18 | 11.5 | 873.3333
2017-10-13 19:00 | 10 | 19 | 10.925 | 873.3333
2017-10-13 20:00 | 10 | 20 | 5.75 | 0
2017-10-13 21:00 | 10 | 21 | 5.75 | 0
2017-10-13 22:00 | 10 | 22 | 4.6 | 0
2017-10-13 23:00 | 10 | 23 | 5.75 | 0
2017-10-14 | 10 | 0 | 3.45 | 0
2017-10-14 01:00 | 10 | 1 | 3.45 | 0
2017-10-14 02:00 | 10 | 2 | 5.75 | 0
2017-10-14 03:00 | 10 | 3 | 0 | 0
2017-10-14 04:00 | 10 | 4 | 1.725 | 0
2017-10-14 05:00 | 10 | 5 | 3.45 | 0
2017-10-14 06:00 | 10 | 6 | 0 | 0
2017-10-14 07:00 | 10 | 7 | 1.725 | 0
2017-10-14 08:00 | 10 | 8 | 0 | 0
2017-10-14 09:00 | 10 | 9 | 0 | 0
2017-10-14 10:00 | 10 | 10 | 3.0667 | 0
2017-10-14 11:00 | 10 | 11 | 3.45 | 0
2017-10-14 12:00 | 10 | 12 | 6.1333 | 0
2017-10-14 13:00 | 10 | 13 | 5.75 | 0
2017-10-14 14:00 | 10 | 14 | 5.75 | 0
2017-10-14 15:00 | 10 | 15 | 8.05 | 286.6667
2017-10-14 16:00 | 10 | 16 | 5.75 | 0
2017-10-14 17:00 | 10 | 17 | 5.75 | 0
2017-10-14 18:00 | 10 | 18 | 5.75 | 0
2017-10-14 19:00 | 10 | 19 | 4.6 | 0
2017-10-14 20:00 | 10 | 20 | 0 | 0
2017-10-14 21:00 | 10 | 21 | 0 | 0
2017-10-14 22:00 | 10 | 22 | 2.6833 | 0
2017-10-14 23:00 | 10 | 23 | 5.75 | 0
2017-10-15 | 10 | 0 | 0 | 0
2017-10-15 01:00 | 10 | 1 | 3.45 | 0
2017-10-15 02:00 | 10 | 2 | 5.75 | 0
2017-10-15 03:00 | 10 | 3 | 6.325 | 0
2017-10-15 04:00 | 10 | 4 | 4.37 | 0
2017-10-15 05:00 | 10 | 5 | 1.15 | 0
2017-10-15 06:00 | 10 | 6 | 2.3 | 0
2017-10-15 07:00 | 10 | 7 | 5.175 | 0
2017-10-15 08:00 | 10 | 8 | 10.925 | 873.3333
2017-10-15 09:00 | 10 | 9 | 12.65 | 1666.6667
2017-10-15 10:00 | 10 | 10 | 15.525 | 2773.3333
2017-10-15 11:00 | 10 | 11 | 16.1 | 2773.3333
2017-10-15 12:00 | 10 | 12 | 20.7 | 6160
2017-10-15 13:00 | 10 | 13 | 24.15 | 9060
2017-10-15 14:00 | 10 | 14 | 25.3 | 9060
2017-10-15 15:00 | 10 | 15 | 24.15 | 9060
2017-10-15 16:00 | 10 | 16 | 21.85 | 7873.3333
2017-10-15 17:00 | 10 | 17 | 20.7 | 6160
2017-10-15 18:00 | 10 | 18 | 21.85 | 7873.3333
2017-10-15 19:00 | 10 | 19 | 23.575 | 9060
2017-10-15 20:00 | 10 | 20 | 25.875 | 9573.3333
2017-10-15 21:00 | 10 | 21 | 27.6 | 9573.3333
2017-10-15 22:00 | 10 | 22 | 27.025 | 9573.3333
2017-10-15 23:00 | 10 | 23 | 18.4 | 4266.6667
2017-10-16 | 10 | 0 | 18.4 | 4266.6667
2017-10-16 01:00 | 10 | 1 | 14.375 | 1666.6667
2017-10-16 02:00 | 10 | 2 | 13.8 | 1666.6667
2017-10-16 03:00 | 10 | 3 | 16.1 | 2773.3333
2017-10-16 04:00 | 10 | 4 | 16.1 | 2773.3333
2017-10-16 05:00 | 10 | 5 | 14.95 | 2773.3333
2017-10-16 06:00 | 10 | 6 | 16.1 | 2773.3333
2017-10-16 07:00 | 10 | 7 | 14.375 | 1666.6667
2017-10-16 08:00 | 10 | 8 | 18.4 | 4266.6667
2017-10-16 09:00 | 10 | 9 | 11.5 | 873.3333
2017-10-16 10:00 | 10 | 10 | 14.375 | 1666.6667
2017-10-16 11:00 | 10 | 11 | 16.1 | 2773.3333
2017-10-16 12:00 | 10 | 12 | 17.25 | 4266.6667
2017-10-16 13:00 | 10 | 13 | 14.95 | 2773.3333
2017-10-16 14:00 | 10 | 14 | 16.1 | 2773.3333
2017-10-16 15:00 | 10 | 15 | 14.95 | 2773.3333
2017-10-16 16:00 | 10 | 16 | 13.8 | 1666.6667
2017-10-16 17:00 | 10 | 17 | 23 | 7873.3333
2017-10-16 18:00 | 10 | 18 | 16.1 | 2773.3333
2017-10-16 19:00 | 10 | 19 | 17.825 | 4266.6667
2017-10-16 20:00 | 10 | 20 | 17.25 | 4266.6667
2017-10-16 21:00 | 10 | 21 | 17.25 | 4266.6667
2017-10-16 22:00 | 10 | 22 | 16.675 | 2773.3333
2017-10-16 23:00 | 10 | 23 | 11.5 | 873.3333
2017-10-17 | 10 | 0 | 11.5 | 873.3333
2017-10-17 01:00 | 10 | 1 | 13.225 | 1666.6667
2017-10-17 02:00 | 10 | 2 | 14.95 | 2773.3333
2017-10-17 03:00 | 10 | 3 | 16.1 | 2773.3333
2017-10-17 04:00 | 10 | 4 | 17.25 | 4266.6667
2017-10-17 05:00 | 10 | 5 | 11.5 | 873.3333
2017-10-17 06:00 | 10 | 6 | 10.35 | 873.3333
2017-10-17 07:00 | 10 | 7 | 10.925 | 873.3333
2017-10-17 08:00 | 10 | 8 | 5.75 | 0
2017-10-17 09:00 | 10 | 9 | 8.05 | 286.6667
2017-10-17 10:00 | 10 | 10 | 7.475 | 0
2017-10-17 11:00 | 10 | 11 | 5.75 | 0
2017-10-17 12:00 | 10 | 12 | 5.75 | 0
2017-10-17 13:00 | 10 | 13 | 6.325 | 0
2017-10-17 14:00 | 10 | 14 | 6.9 | 0
2017-10-17 15:00 | 10 | 15 | 11.5 | 873.3333
2017-10-17 16:00 | 10 | 16 | 11.5 | 873.3333
2017-10-17 17:00 | 10 | 17 | 10.35 | 873.3333
2017-10-17 18:00 | 10 | 18 | 16.1 | 2773.3333
2017-10-17 19:00 | 10 | 19 | 17.25 | 4266.6667
2017-10-17 20:00 | 10 | 20 | 17.25 | 4266.6667
2017-10-17 21:00 | 10 | 21 | 11.5 | 873.3333
2017-10-17 22:00 | 10 | 22 | 14.95 | 2773.3333
2017-10-17 23:00 | 10 | 23 | 14.95 | 2773.3333
2017-10-18 | 10 | 0 | 18.4 | 4266.6667
2017-10-18 01:00 | 10 | 1 | 17.825 | 4266.6667
2017-10-18 02:00 | 10 | 2 | 16.1 | 2773.3333
2017-10-18 03:00 | 10 | 3 | 16.1 | 2773.3333
2017-10-18 04:00 | 10 | 4 | 16.675 | 2773.3333
2017-10-18 05:00 | 10 | 5 | 14.95 | 2773.3333
2017-10-18 06:00 | 10 | 6 | 12.65 | 1666.6667
2017-10-18 07:00 | 10 | 7 | 11.5 | 873.3333
2017-10-18 08:00 | 10 | 8 | 10.35 | 873.3333
2017-10-18 09:00 | 10 | 9 | 14.95 | 2773.3333
2017-10-18 10:00 | 10 | 10 | 13.225 | 1666.6667
2017-10-18 11:00 | 10 | 11 | 8.05 | 286.6667
2017-10-18 12:00 | 10 | 12 | 9.2 | 286.6667
2017-10-18 13:00 | 10 | 13 | 10.35 | 873.3333
2017-10-18 14:00 | 10 | 14 | 6.9 | 0
2017-10-18 15:00 | 10 | 15 | 6.9 | 0
2017-10-18 16:00 | 10 | 16 | 8.05 | 286.6667
2017-10-18 17:00 | 10 | 17 | 6.9 | 0
2017-10-18 18:00 | 10 | 18 | 5.75 | 0
2017-10-18 19:00 | 10 | 19 | 5.75 | 0
2017-10-18 20:00 | 10 | 20 | 5.75 | 0
2017-10-18 21:00 | 10 | 21 | 5.75 | 0
2017-10-18 22:00 | 10 | 22 | 7.475 | 0
2017-10-18 23:00 | 10 | 23 | 9.2 | 286.6667
2017-10-19 | 10 | 0 | 10.35 | 873.3333
2017-10-19 01:00 | 10 | 1 | 8.625 | 286.6667
2017-10-19 02:00 | 10 | 2 | 6.9 | 0
2017-10-19 03:00 | 10 | 3 | 8.05 | 286.6667
2017-10-19 04:00 | 10 | 4 | 5.75 | 0
2017-10-19 05:00 | 10 | 5 | 9.2 | 286.6667
2017-10-19 06:00 | 10 | 6 | 6.9 | 0
2017-10-19 07:00 | 10 | 7 | 7.475 | 0
2017-10-19 08:00 | 10 | 8 | 16.1 | 2773.3333
2017-10-19 09:00 | 10 | 9 | 19.55 | 6160
2017-10-19 10:00 | 10 | 10 | 20.125 | 6160
2017-10-19 11:00 | 10 | 11 | 20.7 | 6160
2017-10-19 12:00 | 10 | 12 | 17.25 | 4266.6667
2017-10-19 13:00 | 10 | 13 | 18.4 | 4266.6667
2017-10-19 14:00 | 10 | 14 | 19.55 | 6160
2017-10-19 15:00 | 10 | 15 | 24.15 | 9060
2017-10-19 16:00 | 10 | 16 | 21.275 | 7873.3333
2017-10-19 17:00 | 10 | 17 | 14.95 | 2773.3333
2017-10-19 18:00 | 10 | 18 | 18.4 | 4266.6667
2017-10-19 19:00 | 10 | 19 | 21.275 | 7873.3333
2017-10-19 20:00 | 10 | 20 | 20.7 | 6160
2017-10-19 21:00 | 10 | 21 | 18.4 | 4266.6667
2017-10-19 22:00 | 10 | 22 | 17.825 | 4266.6667
2017-10-19 23:00 | 10 | 23 | 12.65 | 1666.6667
2017-10-20 | 10 | 0 | 16.1 | 2773.3333
2017-10-20 01:00 | 10 | 1 | 15.525 | 2773.3333
2017-10-20 02:00 | 10 | 2 | 17.25 | 4266.6667
2017-10-20 03:00 | 10 | 3 | 14.95 | 2773.3333
2017-10-20 04:00 | 10 | 4 | 17.25 | 4266.6667
2017-10-20 05:00 | 10 | 5 | 12.65 | 1666.6667
2017-10-20 06:00 | 10 | 6 | 11.5 | 873.3333
2017-10-20 07:00 | 10 | 7 | 12.075 | 873.3333
2017-10-20 08:00 | 10 | 8 | 19.55 | 6160
2017-10-20 09:00 | 10 | 9 | 16.1 | 2773.3333
2017-10-20 10:00 | 10 | 10 | 15.525 | 2773.3333
2017-10-20 11:00 | 10 | 11 | 18.4 | 4266.6667
2017-10-20 12:00 | 10 | 12 | 10.35 | 873.3333
2017-10-20 13:00 | 10 | 13 | 12.65 | 1666.6667
2017-10-20 14:00 | 10 | 14 | 16.1 | 2773.3333
2017-10-20 15:00 | 10 | 15 | 19.55 | 6160
2017-10-20 16:00 | 10 | 16 | 16.1 | 2773.3333
2017-10-20 17:00 | 10 | 17 | 10.35 | 873.3333
2017-10-20 18:00 | 10 | 18 | 11.5 | 873.3333
2017-10-20 19:00 | 10 | 19 | 13.225 | 1666.6667
2017-10-20 20:00 | 10 | 20 | 11.5 | 873.3333
2017-10-20 21:00 | 10 | 21 | 12.65 | 1666.6667
2017-10-20 22:00 | 10 | 22 | 12.075 | 873.3333
2017-10-20 23:00 | 10 | 23 | 8.05 | 286.6667
2017-10-21 | 10 | 0 | 5.75 | 0
2017-10-21 01:00 | 10 | 1 | 5.75 | 0
2017-10-21 02:00 | 10 | 2 | 6.9 | 0
2017-10-21 03:00 | 10 | 3 | 9.2 | 286.6667
2017-10-21 04:00 | 10 | 4 | 6.325 | 0
2017-10-21 05:00 | 10 | 5 | 3.45 | 0
2017-10-21 06:00 | 10 | 6 | 5.75 | 0
2017-10-21 07:00 | 10 | 7 | 5.75 | 0
2017-10-21 08:00 | 10 | 8 | 5.75 | 0
2017-10-21 09:00 | 10 | 9 | 5.75 | 0
2017-10-21 10:00 | 10 | 10 | 6.9 | 0
2017-10-21 11:00 | 10 | 11 | 9.2 | 286.6667
2017-10-21 12:00 | 10 | 12 | 5.75 | 0
2017-10-21 13:00 | 10 | 13 | 8.05 | 286.6667
2017-10-21 14:00 | 10 | 14 | 12.65 | 1666.6667
2017-10-21 15:00 | 10 | 15 | 12.65 | 1666.6667
2017-10-21 16:00 | 10 | 16 | 11.5 | 873.3333
2017-10-21 17:00 | 10 | 17 | 11.5 | 873.3333
2017-10-21 18:00 | 10 | 18 | 11.5 | 873.3333
2017-10-21 19:00 | 10 | 19 | 9.2 | 286.6667
2017-10-21 20:00 | 10 | 20 | 10.35 | 873.3333
2017-10-21 21:00 | 10 | 21 | 6.9 | 0
2017-10-21 22:00 | 10 | 22 | 6.325 | 0
2017-10-21 23:00 | 10 | 23 | 5.75 | 0
2017-10-22 | 10 | 0 | 5.75 | 0
2017-10-22 01:00 | 10 | 1 | 2.875 | 0
2017-10-22 02:00 | 10 | 2 | 0 | 0
2017-10-22 03:00 | 10 | 3 | 0 | 0
2017-10-22 04:00 | 10 | 4 | 0 | 0
2017-10-22 05:00 | 10 | 5 | 0 | 0
2017-10-22 06:00 | 10 | 6 | 5.75 | 0
2017-10-22 07:00 | 10 | 7 | 2.875 | 0
2017-10-22 08:00 | 10 | 8 | 6.9 | 0
2017-10-22 09:00 | 10 | 9 | 5.75 | 0
2017-10-22 10:00 | 10 | 10 | 6.9 | 0
2017-10-22 11:00 | 10 | 11 | 10.35 | 873.3333
2017-10-22 12:00 | 10 | 12 | 12.65 | 1666.6667
2017-10-22 13:00 | 10 | 13 | 12.65 | 1666.6667
2017-10-22 14:00 | 10 | 14 | 11.5 | 873.3333
2017-10-22 15:00 | 10 | 15 | 9.2 | 286.6667
2017-10-22 16:00 | 10 | 16 | 9.2 | 286.6667
2017-10-22 17:00 | 10 | 17 | 8.05 | 286.6667
2017-10-22 18:00 | 10 | 18 | 9.775 | 286.6667
2017-10-22 19:00 | 10 | 19 | 6.5167 | 0
2017-10-22 20:00 | 10 | 20 | 3.45 | 0
2017-10-22 21:00 | 10 | 21 | 0 | 0
2017-10-22 22:00 | 10 | 22 | 2.875 | 0
2017-10-22 23:00 | 10 | 23 | 0 | 0
2017-10-23 | 10 | 0 | 0 | 0
2017-10-23 01:00 | 10 | 1 | 1.725 | 0
2017-10-23 02:00 | 10 | 2 | 3.45 | 0
2017-10-23 03:00 | 10 | 3 | 0 | 0
2017-10-23 04:00 | 10 | 4 | 3.45 | 0
2017-10-23 05:00 | 10 | 5 | 0 | 0
2017-10-23 06:00 | 10 | 6 | 3.45 | 0
2017-10-23 07:00 | 10 | 7 | 4.7917 | 0
2017-10-23 08:00 | 10 | 8 | 3.7375 | 0
2017-10-23 09:00 | 10 | 9 | 5.75 | 0
2017-10-23 10:00 | 10 | 10 | 7.1875 | 0
2017-10-23 11:00 | 10 | 11 | 6.9 | 0
2017-10-23 12:00 | 10 | 12 | 8.4333 | 286.6667
2017-10-23 13:00 | 10 | 13 | 9.2 | 286.6667
2017-10-23 14:00 | 10 | 14 | 9.2 | 286.6667
2017-10-23 15:00 | 10 | 15 | 7.2833 | 0
2017-10-23 16:00 | 10 | 16 | 6.5167 | 0
2017-10-23 17:00 | 10 | 17 | 6.5167 | 0
2017-10-23 18:00 | 10 | 18 | 0 | 0
2017-10-23 19:00 | 10 | 19 | 0 | 0
2017-10-23 20:00 | 10 | 20 | 1.725 | 0
2017-10-23 21:00 | 10 | 21 | 6.9 | 0
2017-10-23 22:00 | 10 | 22 | 5.3667 | 0
2017-10-23 23:00 | 10 | 23 | 8.05 | 286.6667
2017-10-24 | 10 | 0 | 11.5 | 873.3333
2017-10-24 01:00 | 10 | 1 | 12.075 | 873.3333
2017-10-24 02:00 | 10 | 2 | 12.65 | 1666.6667
2017-10-24 03:00 | 10 | 3 | 12.65 | 1666.6667
2017-10-24 04:00 | 10 | 4 | 12.65 | 1666.6667
2017-10-24 05:00 | 10 | 5 | 12.075 | 873.3333
2017-10-24 06:00 | 10 | 6 | 11.5 | 873.3333
2017-10-24 07:00 | 10 | 7 | 14.375 | 1666.6667
2017-10-24 08:00 | 10 | 8 | 16.675 | 2773.3333
2017-10-24 09:00 | 10 | 9 | 23 | 7873.3333
2017-10-24 10:00 | 10 | 10 | 21.85 | 7873.3333
2017-10-24 11:00 | 10 | 11 | 24.5333 | 9060
2017-10-24 12:00 | 10 | 12 | 23.575 | 9060
2017-10-24 13:00 | 10 | 13 | 24.15 | 9060
2017-10-24 14:00 | 10 | 14 | 24.725 | 9060
2017-10-24 15:00 | 10 | 15 | 26.45 | 9573.3333
2017-10-24 16:00 | 10 | 16 | 26.45 | 9573.3333
2017-10-24 17:00 | 10 | 17 | 28.75 | 9873.3333
2017-10-24 18:00 | 10 | 18 | 32.2 | 9960
2017-10-24 19:00 | 10 | 19 | 31.05 | 9960
2017-10-24 20:00 | 10 | 20 | 26.45 | 9573.3333
2017-10-24 21:00 | 10 | 21 | 25.3 | 9060
2017-10-24 22:00 | 10 | 22 | 25.875 | 9573.3333
2017-10-24 23:00 | 10 | 23 | 27.6 | 9573.3333
2017-10-25 | 10 | 0 | 25.3 | 9060
2017-10-25 01:00 | 10 | 1 | 25.875 | 9573.3333
2017-10-25 02:00 | 10 | 2 | 25.3 | 9060
2017-10-25 03:00 | 10 | 3 | 16.1 | 2773.3333
2017-10-25 04:00 | 10 | 4 | 10.35 | 873.3333
2017-10-25 05:00 | 10 | 5 | 4.9833 | 0
2017-10-25 06:00 | 10 | 6 | 6.67 | 0
2017-10-25 07:00 | 10 | 7 | 8.9125 | 286.6667
2017-10-25 08:00 | 10 | 8 | 16.1 | 2773.3333
2017-10-25 09:00 | 10 | 9 | 14.95 | 2773.3333
2017-10-25 10:00 | 10 | 10 | 16.1 | 2773.3333
2017-10-25 11:00 | 10 | 11 | 19.55 | 6160
2017-10-25 12:00 | 10 | 12 | 12.65 | 1666.6667
2017-10-25 13:00 | 10 | 13 | 13.34 | 1666.6667
2017-10-25 14:00 | 10 | 14 | 16.1 | 2773.3333
2017-10-25 15:00 | 10 | 15 | 5.75 | 0
2017-10-25 16:00 | 10 | 16 | 10.925 | 873.3333
2017-10-25 17:00 | 10 | 17 | 16.1 | 2773.3333
2017-10-25 18:00 | 10 | 18 | 8.05 | 286.6667
2017-10-25 19:00 | 10 | 19 | 8.05 | 286.6667
2017-10-25 20:00 | 10 | 20 | 8.625 | 286.6667
2017-10-25 21:00 | 10 | 21 | 0 | 0
2017-10-25 22:00 | 10 | 22 | 3.0667 | 0
2017-10-25 23:00 | 10 | 23 | 8.4333 | 286.6667
2017-10-26 | 10 | 0 | 10.35 | 873.3333
2017-10-26 01:00 | 10 | 1 | 10.6375 | 873.3333
2017-10-26 02:00 | 10 | 2 | 11.5 | 873.3333
2017-10-26 03:00 | 10 | 3 | 6.325 | 0
2017-10-26 04:00 | 10 | 4 | 7.475 | 0
2017-10-26 05:00 | 10 | 5 | 10.35 | 873.3333
2017-10-26 06:00 | 10 | 6 | 12.65 | 1666.6667
2017-10-26 07:00 | 10 | 7 | 10.925 | 873.3333
2017-10-26 08:00 | 10 | 8 | 11.5 | 873.3333
2017-10-26 09:00 | 10 | 9 | 9.2 | 286.6667
2017-10-26 10:00 | 10 | 10 | 9.5833 | 286.6667
2017-10-26 11:00 | 10 | 11 | 12.9375 | 1666.6667
2017-10-26 12:00 | 10 | 12 | 8.8167 | 286.6667
2017-10-26 13:00 | 10 | 13 | 11.8833 | 873.3333
2017-10-26 14:00 | 10 | 14 | 18.0167 | 4266.6667
2017-10-26 15:00 | 10 | 15 | 17.25 | 4266.6667
2017-10-26 16:00 | 10 | 16 | 14.95 | 2773.3333
2017-10-26 17:00 | 10 | 17 | 17.825 | 4266.6667
2017-10-26 18:00 | 10 | 18 | 20.7 | 6160
2017-10-26 19:00 | 10 | 19 | 22.6167 | 7873.3333
2017-10-26 20:00 | 10 | 20 | 25.3 | 9060
2017-10-26 21:00 | 10 | 21 | 24.15 | 9060
2017-10-26 22:00 | 10 | 22 | 23.575 | 9060
2017-10-26 23:00 | 10 | 23 | 20.7 | 6160
2017-10-27 | 10 | 0 | 19.55 | 6160
2017-10-27 01:00 | 10 | 1 | 17.825 | 4266.6667
2017-10-27 02:00 | 10 | 2 | 18.4 | 4266.6667
2017-10-27 03:00 | 10 | 3 | 12.65 | 1666.6667
2017-10-27 04:00 | 10 | 4 | 16.1 | 2773.3333
2017-10-27 05:00 | 10 | 5 | 16.1 | 2773.3333
2017-10-27 06:00 | 10 | 6 | 11.5 | 873.3333
2017-10-27 07:00 | 10 | 7 | 11.5 | 873.3333
2017-10-27 08:00 | 10 | 8 | 11.5 | 873.3333
2017-10-27 09:00 | 10 | 9 | 12.65 | 1666.6667
2017-10-27 10:00 | 10 | 10 | 12.075 | 873.3333
2017-10-27 11:00 | 10 | 11 | 12.65 | 1666.6667
2017-10-27 12:00 | 10 | 12 | 11.5 | 873.3333
2017-10-27 13:00 | 10 | 13 | 9.775 | 286.6667
2017-10-27 14:00 | 10 | 14 | 11.5 | 873.3333
2017-10-27 15:00 | 10 | 15 | 10.35 | 873.3333
2017-10-27 16:00 | 10 | 16 | 9.775 | 286.6667
2017-10-27 17:00 | 10 | 17 | 8.05 | 286.6667
2017-10-27 18:00 | 10 | 18 | 8.05 | 286.6667
2017-10-27 19:00 | 10 | 19 | 7.475 | 0
2017-10-27 20:00 | 10 | 20 | 10.35 | 873.3333
2017-10-27 21:00 | 10 | 21 | 12.65 | 1666.6667
2017-10-27 22:00 | 10 | 22 | 11.5 | 873.3333
2017-10-27 23:00 | 10 | 23 | 14.95 | 2773.3333
2017-10-28 | 10 | 0 | 8.05 | 286.6667
2017-10-28 01:00 | 10 | 1 | 8.05 | 286.6667
2017-10-28 02:00 | 10 | 2 | 5.75 | 0
2017-10-28 03:00 | 10 | 3 | 5.75 | 0
2017-10-28 04:00 | 10 | 4 | 6.325 | 0
2017-10-28 05:00 | 10 | 5 | 5.75 | 0
2017-10-28 06:00 | 10 | 6 | 5.75 | 0
2017-10-28 07:00 | 10 | 7 | 6.325 | 0
2017-10-28 08:00 | 10 | 8 | 6.9 | 0
2017-10-28 09:00 | 10 | 9 | 11.5 | 873.3333
2017-10-28 10:00 | 10 | 10 | 12.075 | 873.3333
2017-10-28 11:00 | 10 | 11 | 14.95 | 2773.3333
2017-10-28 12:00 | 10 | 12 | 12.65 | 1666.6667
2017-10-28 13:00 | 10 | 13 | 14.95 | 2773.3333
2017-10-28 14:00 | 10 | 14 | 16.1 | 2773.3333
2017-10-28 15:00 | 10 | 15 | 17.25 | 4266.6667
2017-10-28 16:00 | 10 | 16 | 14.95 | 2773.3333
2017-10-28 17:00 | 10 | 17 | 14.95 | 2773.3333
2017-10-28 18:00 | 10 | 18 | 9.2 | 286.6667
2017-10-28 19:00 | 10 | 19 | 9.2 | 286.6667
2017-10-28 20:00 | 10 | 20 | 8.05 | 286.6667
2017-10-28 21:00 | 10 | 21 | 9.2 | 286.6667
2017-10-28 22:00 | 10 | 22 | 9.775 | 286.6667
2017-10-28 23:00 | 10 | 23 | 9.2 | 286.6667
2017-10-29 | 10 | 0 | 11.5 | 873.3333
2017-10-29 01:00 | 10 | 1 | 12.075 | 873.3333
2017-10-29 02:00 | 10 | 2 | 10.35 | 873.3333
2017-10-29 03:00 | 10 | 3 | 10.35 | 873.3333
2017-10-29 04:00 | 10 | 4 | 8.05 | 286.6667
2017-10-29 05:00 | 10 | 5 | 8.05 | 286.6667
2017-10-29 06:00 | 10 | 6 | 12.65 | 1666.6667
2017-10-29 07:00 | 10 | 7 | 11.5 | 873.3333
2017-10-29 08:00 | 10 | 8 | 14.95 | 2773.3333
2017-10-29 09:00 | 10 | 9 | 11.5 | 873.3333
2017-10-29 10:00 | 10 | 10 | 14.375 | 1666.6667
2017-10-29 11:00 | 10 | 11 | 20.7 | 6160
2017-10-29 12:00 | 10 | 12 | 20.7 | 6160
2017-10-29 13:00 | 10 | 13 | 20.7 | 6160
2017-10-29 14:00 | 10 | 14 | 18.4 | 4266.6667
2017-10-29 15:00 | 10 | 15 | 20.7 | 6160
2017-10-29 16:00 | 10 | 16 | 19.55 | 6160
2017-10-29 17:00 | 10 | 17 | 23 | 7873.3333
2017-10-29 18:00 | 10 | 18 | 24.15 | 9060
2017-10-29 19:00 | 10 | 19 | 23.3833 | 7873.3333
2017-10-29 20:00 | 10 | 20 | 24.5333 | 9060
2017-10-29 21:00 | 10 | 21 | 29.325 | 9873.3333
2017-10-29 22:00 | 10 | 22 | 36.0333 | 10000
2017-10-29 23:00 | 10 | 23 | 45.2333 | 10000
2017-10-30 | 10 | 0 | 43.125 | 10000
2017-10-30 01:00 | 10 | 1 | 44.85 | 10000
2017-10-30 02:00 | 10 | 2 | 43.7 | 10000
2017-10-30 03:00 | 10 | 3 | 17.25 | 4266.6667
2017-10-30 04:00 | 10 | 4 | 19.55 | 6160
2017-10-30 05:00 | 10 | 5 | 19.55 | 6160
2017-10-30 06:00 | 10 | 6 | 18.4 | 4266.6667
2017-10-30 07:00 | 10 | 7 | 25.3 | 9060
2017-10-30 08:00 | 10 | 8 | 31.625 | 9960
2017-10-30 09:00 | 10 | 9 | 33.35 | 10000
2017-10-30 10:00 | 10 | 10 | 34.1167 | 10000
2017-10-30 11:00 | 10 | 11 | 29.5167 | 9873.3333
2017-10-30 12:00 | 10 | 12 | 29.325 | 9873.3333
2017-10-30 13:00 | 10 | 13 | 27.025 | 9573.3333
2017-10-30 14:00 | 10 | 14 | 24.15 | 9060
2017-10-30 15:00 | 10 | 15 | 27.6 | 9573.3333
2017-10-30 16:00 | 10 | 16 | 25.3 | 9060
2017-10-30 17:00 | 10 | 17 | 14.95 | 2773.3333
2017-10-30 18:00 | 10 | 18 | 16.1 | 2773.3333
2017-10-30 19:00 | 10 | 19 | 16.675 | 2773.3333
2017-10-30 20:00 | 10 | 20 | 16.1 | 2773.3333
2017-10-30 21:00 | 10 | 21 | 20.7 | 6160
2017-10-30 22:00 | 10 | 22 | 20.7 | 6160
2017-10-30 23:00 | 10 | 23 | 16.1 | 2773.3333
2017-10-31 | 10 | 0 | 18.4 | 4266.6667
2017-10-31 01:00 | 10 | 1 | 17.825 | 4266.6667
2017-10-31 02:00 | 10 | 2 | 16.1 | 2773.3333
2017-10-31 03:00 | 10 | 3 | 16.1 | 2773.3333
2017-10-31 04:00 | 10 | 4 | 16.1 | 2773.3333
2017-10-31 05:00 | 10 | 5 | 14.95 | 2773.3333
2017-10-31 06:00 | 10 | 6 | 16.1 | 2773.3333
2017-10-31 07:00 | 10 | 7 | 15.525 | 2773.3333
2017-10-31 08:00 | 10 | 8 | 16.1 | 2773.3333
2017-10-31 09:00 | 10 | 9 | 17.25 | 4266.6667
2017-10-31 10:00 | 10 | 10 | 16.675 | 2773.3333
2017-10-31 11:00 | 10 | 11 | 18.4 | 4266.6667
2017-10-31 12:00 | 10 | 12 | 25.3 | 9060
2017-10-31 13:00 | 10 | 13 | 22.425 | 7873.3333
2017-10-31 14:00 | 10 | 14 | 19.55 | 6160
2017-10-31 15:00 | 10 | 15 | 16.1 | 2773.3333
2017-10-31 16:00 | 10 | 16 | 15.525 | 2773.3333
2017-10-31 17:00 | 10 | 17 | 10.35 | 873.3333
2017-10-31 18:00 | 10 | 18 | 11.5 | 873.3333
2017-10-31 19:00 | 10 | 19 | 14.375 | 1666.6667
2017-10-31 20:00 | 10 | 20 | 9.2 | 286.6667
2017-10-31 21:00 | 10 | 21 | 5.75 | 0
2017-10-31 22:00 | 10 | 22 | 5.75 | 0
2017-10-31 23:00 | 10 | 23 | 6.9 | 0
2017-11-01 | 11 | 0 | 3.45 | 0
2017-11-01 01:00 | 11 | 1 | 7.475 | 0
2017-11-01 02:00 | 11 | 2 | 10.35 | 873.3333
2017-11-01 03:00 | 11 | 3 | 10.35 | 873.3333
2017-11-01 04:00 | 11 | 4 | 8.05 | 286.6667
2017-11-01 05:00 | 11 | 5 | 5.75 | 0
2017-11-01 06:00 | 11 | 6 | 0 | 0
2017-11-01 07:00 | 11 | 7 | 1.725 | 0
2017-11-01 08:00 | 11 | 8 | 0 | 0
2017-11-01 09:00 | 11 | 9 | 3.45 | 0
2017-11-01 10:00 | 11 | 10 | 4.6 | 0
2017-11-01 11:00 | 11 | 11 | 6.9 | 0
2017-11-01 12:00 | 11 | 12 | 9.2 | 286.6667
2017-11-01 13:00 | 11 | 13 | 9.2 | 286.6667
2017-11-01 14:00 | 11 | 14 | 9.2 | 286.6667
2017-11-01 15:00 | 11 | 15 | 8.05 | 286.6667
2017-11-01 16:00 | 11 | 16 | 8.05 | 286.6667
2017-11-01 17:00 | 11 | 17 | 3.45 | 0
2017-11-01 18:00 | 11 | 18 | 10.35 | 873.3333
2017-11-01 19:00 | 11 | 19 | 10.35 | 873.3333
2017-11-01 20:00 | 11 | 20 | 12.65 | 1666.6667
2017-11-01 21:00 | 11 | 21 | 10.35 | 873.3333
2017-11-01 22:00 | 11 | 22 | 9.2 | 286.6667
2017-11-01 23:00 | 11 | 23 | 10.35 | 873.3333
2017-11-02 | 11 | 0 | 8.05 | 286.6667
2017-11-02 01:00 | 11 | 1 | 7.475 | 0
2017-11-02 02:00 | 11 | 2 | 8.05 | 286.6667
2017-11-02 03:00 | 11 | 3 | 8.05 | 286.6667
2017-11-02 04:00 | 11 | 4 | 9.9667 | 286.6667
2017-11-02 05:00 | 11 | 5 | 9.2 | 286.6667
2017-11-02 06:00 | 11 | 6 | 11.5 | 873.3333
2017-11-02 07:00 | 11 | 7 | 11.5 | 873.3333
2017-11-02 08:00 | 11 | 8 | 10.35 | 873.3333
2017-11-02 09:00 | 11 | 9 | 6.9 | 0
2017-11-02 10:00 | 11 | 10 | 8.05 | 286.6667
2017-11-02 11:00 | 11 | 11 | 12.65 | 1666.6667
2017-11-02 12:00 | 11 | 12 | 11.5 | 873.3333
2017-11-02 13:00 | 11 | 13 | 13.225 | 1666.6667
2017-11-02 14:00 | 11 | 14 | 10.35 | 873.3333
2017-11-02 15:00 | 11 | 15 | 16.1 | 2773.3333
2017-11-02 16:00 | 11 | 16 | 15.525 | 2773.3333
2017-11-02 17:00 | 11 | 17 | 14.95 | 2773.3333
2017-11-02 18:00 | 11 | 18 | 9.2 | 286.6667
2017-11-02 19:00 | 11 | 19 | 9.2 | 286.6667
2017-11-02 20:00 | 11 | 20 | 10.35 | 873.3333
2017-11-02 21:00 | 11 | 21 | 8.05 | 286.6667
2017-11-02 22:00 | 11 | 22 | 9.2 | 286.6667
2017-11-02 23:00 | 11 | 23 | 9.2 | 286.6667
2017-11-03 | 11 | 0 | 6.9 | 0
2017-11-03 01:00 | 11 | 1 | 8.05 | 286.6667
2017-11-03 02:00 | 11 | 2 | 6.9 | 0
2017-11-03 03:00 | 11 | 3 | 5.75 | 0
2017-11-03 04:00 | 11 | 4 | 8.05 | 286.6667
2017-11-03 05:00 | 11 | 5 | 11.5 | 873.3333
2017-11-03 06:00 | 11 | 6 | 12.65 | 1666.6667
2017-11-03 07:00 | 11 | 7 | 13.8 | 1666.6667
2017-11-03 08:00 | 11 | 8 | 14.95 | 2773.3333
2017-11-03 09:00 | 11 | 9 | 23 | 7873.3333
2017-11-03 10:00 | 11 | 10 | 21.85 | 7873.3333
2017-11-03 11:00 | 11 | 11 | 20.7 | 6160
2017-11-03 12:00 | 11 | 12 | 23 | 7873.3333
2017-11-03 13:00 | 11 | 13 | 20.7 | 6160
2017-11-03 14:00 | 11 | 14 | 18.4 | 4266.6667
2017-11-03 15:00 | 11 | 15 | 12.65 | 1666.6667
2017-11-03 16:00 | 11 | 16 | 15.525 | 2773.3333
2017-11-03 17:00 | 11 | 17 | 23 | 7873.3333
2017-11-03 18:00 | 11 | 18 | 25.3 | 9060
2017-11-03 19:00 | 11 | 19 | 22.425 | 7873.3333
2017-11-03 20:00 | 11 | 20 | 19.55 | 6160
2017-11-03 21:00 | 11 | 21 | 20.7 | 6160
2017-11-03 22:00 | 11 | 22 | 18.975 | 4266.6667
2017-11-03 23:00 | 11 | 23 | 29.9 | 9873.3333
2017-11-04 | 11 | 0 | 19.55 | 6160
2017-11-04 01:00 | 11 | 1 | 16.1 | 2773.3333
2017-11-04 02:00 | 11 | 2 | 18.4 | 4266.6667
2017-11-04 03:00 | 11 | 3 | 16.1 | 2773.3333
2017-11-04 04:00 | 11 | 4 | 13.8 | 1666.6667
2017-11-04 05:00 | 11 | 5 | 11.5 | 873.3333
2017-11-04 06:00 | 11 | 6 | 12.65 | 1666.6667
2017-11-04 07:00 | 11 | 7 | 12.075 | 873.3333
2017-11-04 08:00 | 11 | 8 | 12.65 | 1666.6667
2017-11-04 09:00 | 11 | 9 | 3.45 | 0
2017-11-04 10:00 | 11 | 10 | 4.6 | 0
2017-11-04 11:00 | 11 | 11 | 10.35 | 873.3333
2017-11-04 12:00 | 11 | 12 | 9.2 | 286.6667
2017-11-04 13:00 | 11 | 13 | 9.2 | 286.6667
2017-11-04 14:00 | 11 | 14 | 9.2 | 286.6667
2017-11-04 15:00 | 11 | 15 | 9.2 | 286.6667
2017-11-04 16:00 | 11 | 16 | 9.775 | 286.6667
2017-11-04 17:00 | 11 | 17 | 8.05 | 286.6667
2017-11-04 18:00 | 11 | 18 | 10.35 | 873.3333
2017-11-04 19:00 | 11 | 19 | 10.925 | 873.3333
2017-11-04 20:00 | 11 | 20 | 12.65 | 1666.6667
2017-11-04 21:00 | 11 | 21 | 17.25 | 4266.6667
2017-11-04 22:00 | 11 | 22 | 16.675 | 2773.3333
2017-11-04 23:00 | 11 | 23 | 16.1 | 2773.3333
2017-11-05 | 11 | 0 | 11.5 | 873.3333
2017-11-05 01:00 | 11 | 1 | 13.225 | 1666.6667
2017-11-05 02:00 | 11 | 2 | 12.65 | 1666.6667
2017-11-05 03:00 | 11 | 3 | 14.95 | 2773.3333
2017-11-05 04:00 | 11 | 4 | 15.525 | 2773.3333
2017-11-05 05:00 | 11 | 5 | 17.25 | 4266.6667
2017-11-05 06:00 | 11 | 6 | 17.25 | 4266.6667
2017-11-05 07:00 | 11 | 7 | 18.4 | 4266.6667
2017-11-05 08:00 | 11 | 8 | 18.4 | 4266.6667
2017-11-05 09:00 | 11 | 9 | 14.95 | 2773.3333
2017-11-05 10:00 | 11 | 10 | 15.7167 | 2773.3333
2017-11-05 11:00 | 11 | 11 | 14.95 | 2773.3333
2017-11-05 12:00 | 11 | 12 | 12.65 | 1666.6667
2017-11-05 13:00 | 11 | 13 | 11.5 | 873.3333
2017-11-05 14:00 | 11 | 14 | 9.2 | 286.6667
2017-11-05 15:00 | 11 | 15 | 9.2 | 286.6667
2017-11-05 16:00 | 11 | 16 | 9.2 | 286.6667
2017-11-05 17:00 | 11 | 17 | 6.9 | 0
2017-11-05 18:00 | 11 | 18 | 5.75 | 0
2017-11-05 19:00 | 11 | 19 | 6.325 | 0
2017-11-05 20:00 | 11 | 20 | 3.45 | 0
2017-11-05 21:00 | 11 | 21 | 5.75 | 0
2017-11-05 22:00 | 11 | 22 | 3.0667 | 0
2017-11-05 23:00 | 11 | 23 | 11.5 | 873.3333
2017-11-06 | 11 | 0 | 12.65 | 1666.6667
2017-11-06 01:00 | 11 | 1 | 15.7167 | 2773.3333
2017-11-06 02:00 | 11 | 2 | 16.8667 | 4266.6667
2017-11-06 03:00 | 11 | 3 | 17.825 | 4266.6667
2017-11-06 04:00 | 11 | 4 | 16.1 | 2773.3333
2017-11-06 05:00 | 11 | 5 | 14.95 | 2773.3333
2017-11-06 06:00 | 11 | 6 | 13.8 | 1666.6667
2017-11-06 07:00 | 11 | 7 | 16.675 | 2773.3333
2017-11-06 08:00 | 11 | 8 | 17.25 | 4266.6667
2017-11-06 09:00 | 11 | 9 | 17.25 | 4266.6667
2017-11-06 10:00 | 11 | 10 | 16.675 | 2773.3333
2017-11-06 11:00 | 11 | 11 | 18.7833 | 4266.6667
2017-11-06 12:00 | 11 | 12 | 10.35 | 873.3333
2017-11-06 13:00 | 11 | 13 | 11.8833 | 873.3333
2017-11-06 14:00 | 11 | 14 | 10.925 | 873.3333
2017-11-06 15:00 | 11 | 15 | 11.5 | 873.3333
2017-11-06 16:00 | 11 | 16 | 11.5 | 873.3333
2017-11-06 17:00 | 11 | 17 | 18.975 | 4266.6667
2017-11-06 18:00 | 11 | 18 | 13.8 | 1666.6667
2017-11-06 19:00 | 11 | 19 | 17.825 | 4266.6667
2017-11-06 20:00 | 11 | 20 | 17.25 | 4266.6667
2017-11-06 21:00 | 11 | 21 | 18.4 | 4266.6667
2017-11-06 22:00 | 11 | 22 | 14.95 | 2773.3333
2017-11-06 23:00 | 11 | 23 | 11.5 | 873.3333
2017-11-07 | 11 | 0 | 10.35 | 873.3333
2017-11-07 01:00 | 11 | 1 | 15.525 | 2773.3333
2017-11-07 02:00 | 11 | 2 | 17.25 | 4266.6667
2017-11-07 03:00 | 11 | 3 | 16.1 | 2773.3333
2017-11-07 04:00 | 11 | 4 | 16.675 | 2773.3333
2017-11-07 05:00 | 11 | 5 | 12.65 | 1666.6667
2017-11-07 06:00 | 11 | 6 | 18.4 | 4266.6667
2017-11-07 07:00 | 11 | 7 | 15.525 | 2773.3333
2017-11-07 08:00 | 11 | 8 | 10.35 | 873.3333
2017-11-07 09:00 | 11 | 9 | 10.35 | 873.3333
2017-11-07 10:00 | 11 | 10 | 9.2 | 286.6667
2017-11-07 11:00 | 11 | 11 | 9.2 | 286.6667
2017-11-07 12:00 | 11 | 12 | 9.2 | 286.6667
2017-11-07 13:00 | 11 | 13 | 7.475 | 0
2017-11-07 14:00 | 11 | 14 | 6.9 | 0
2017-11-07 15:00 | 11 | 15 | 11.5 | 873.3333
2017-11-07 16:00 | 11 | 16 | 10.35 | 873.3333
2017-11-07 17:00 | 11 | 17 | 8.05 | 286.6667
2017-11-07 18:00 | 11 | 18 | 9.2 | 286.6667
2017-11-07 19:00 | 11 | 19 | 8.625 | 286.6667
2017-11-07 20:00 | 11 | 20 | 11.5 | 873.3333
2017-11-07 21:00 | 11 | 21 | 14.95 | 2773.3333
2017-11-07 22:00 | 11 | 22 | 13.8 | 1666.6667
2017-11-07 23:00 | 11 | 23 | 12.075 | 873.3333
2017-11-08 | 11 | 0 | 12.075 | 873.3333
2017-11-08 01:00 | 11 | 1 | 15.7167 | 2773.3333
2017-11-08 02:00 | 11 | 2 | 18.4 | 4266.6667
2017-11-08 03:00 | 11 | 3 | 14.95 | 2773.3333
2017-11-08 04:00 | 11 | 4 | 16.1 | 2773.3333
2017-11-08 05:00 | 11 | 5 | 17.25 | 4266.6667
2017-11-08 06:00 | 11 | 6 | 17.25 | 4266.6667
2017-11-08 07:00 | 11 | 7 | 16.675 | 2773.3333
2017-11-08 08:00 | 11 | 8 | 14.95 | 2773.3333
2017-11-08 09:00 | 11 | 9 | 17.25 | 4266.6667
2017-11-08 10:00 | 11 | 10 | 18.4 | 4266.6667
2017-11-08 11:00 | 11 | 11 | 18.7833 | 4266.6667
2017-11-08 12:00 | 11 | 12 | 19.55 | 6160
2017-11-08 13:00 | 11 | 13 | 18.4 | 4266.6667
2017-11-08 14:00 | 11 | 14 | 12.65 | 1666.6667
2017-11-08 15:00 | 11 | 15 | 9.2 | 286.6667
2017-11-08 16:00 | 11 | 16 | 9.775 | 286.6667
2017-11-08 17:00 | 11 | 17 | 9.2 | 286.6667
2017-11-08 18:00 | 11 | 18 | 9.2 | 286.6667
2017-11-08 19:00 | 11 | 19 | 8.05 | 286.6667
2017-11-08 20:00 | 11 | 20 | 5.75 | 0
2017-11-08 21:00 | 11 | 21 | 3.45 | 0
2017-11-08 22:00 | 11 | 22 | 5.175 | 0
2017-11-08 23:00 | 11 | 23 | 6.9 | 0
2017-11-09 | 11 | 0 | 6.9 | 0
2017-11-09 01:00 | 11 | 1 | 8.05 | 286.6667
2017-11-09 02:00 | 11 | 2 | 8.05 | 286.6667
2017-11-09 03:00 | 11 | 3 | 9.2 | 286.6667
2017-11-09 04:00 | 11 | 4 | 8.625 | 286.6667
2017-11-09 05:00 | 11 | 5 | 9.2 | 286.6667
2017-11-09 06:00 | 11 | 6 | 8.05 | 286.6667
2017-11-09 07:00 | 11 | 7 | 6.9 | 0
2017-11-09 08:00 | 11 | 8 | 0 | 0
2017-11-09 09:00 | 11 | 9 | 0 | 0
2017-11-09 10:00 | 11 | 10 | 2.875 | 0
2017-11-09 11:00 | 11 | 11 | 8.05 | 286.6667
2017-11-09 12:00 | 11 | 12 | 6.9 | 0
2017-11-09 13:00 | 11 | 13 | 6.9 | 0
2017-11-09 14:00 | 11 | 14 | 10.35 | 873.3333
2017-11-09 15:00 | 11 | 15 | 11.5 | 873.3333
2017-11-09 16:00 | 11 | 16 | 12.075 | 873.3333
2017-11-09 17:00 | 11 | 17 | 10.35 | 873.3333
2017-11-09 18:00 | 11 | 18 | 9.2 | 286.6667
2017-11-09 19:00 | 11 | 19 | 10.925 | 873.3333
2017-11-09 20:00 | 11 | 20 | 10.35 | 873.3333
2017-11-09 21:00 | 11 | 21 | 11.5 | 873.3333
2017-11-09 22:00 | 11 | 22 | 10.925 | 873.3333
2017-11-09 23:00 | 11 | 23 | 10.35 | 873.3333
2017-11-10 | 11 | 0 | 9.2 | 286.6667
2017-11-10 01:00 | 11 | 1 | 9.2 | 286.6667
2017-11-10 02:00 | 11 | 2 | 8.05 | 286.6667
2017-11-10 03:00 | 11 | 3 | 14.95 | 2773.3333
2017-11-10 04:00 | 11 | 4 | 14.95 | 2773.3333
2017-11-10 05:00 | 11 | 5 | 29.9 | 9873.3333
2017-11-10 06:00 | 11 | 6 | 28.75 | 9873.3333
2017-11-10 07:00 | 11 | 7 | 27.6 | 9573.3333
2017-11-10 08:00 | 11 | 8 | 29.9 | 9873.3333
2017-11-10 09:00 | 11 | 9 | 28.75 | 9873.3333
2017-11-10 10:00 | 11 | 10 | 28.175 | 9873.3333
2017-11-10 11:00 | 11 | 11 | 24.15 | 9060
2017-11-10 12:00 | 11 | 12 | 23 | 7873.3333
2017-11-10 13:00 | 11 | 13 | 24.725 | 9060
2017-11-10 14:00 | 11 | 14 | 25.3 | 9060
2017-11-10 15:00 | 11 | 15 | 18.4 | 4266.6667
2017-11-10 16:00 | 11 | 16 | 19.55 | 6160
2017-11-10 17:00 | 11 | 17 | 19.55 | 6160
2017-11-10 18:00 | 11 | 18 | 17.25 | 4266.6667
2017-11-10 19:00 | 11 | 19 | 23 | 7873.3333
2017-11-10 20:00 | 11 | 20 | 23 | 7873.3333
2017-11-10 21:00 | 11 | 21 | 20.7 | 6160
2017-11-10 22:00 | 11 | 22 | 18.4 | 4266.6667
2017-11-10 23:00 | 11 | 23 | 16.1 | 2773.3333
2017-11-11 | 11 | 0 | 19.55 | 6160
2017-11-11 01:00 | 11 | 1 | 18.4 | 4266.6667
2017-11-11 02:00 | 11 | 2 | 12.65 | 1666.6667
2017-11-11 03:00 | 11 | 3 | 9.2 | 286.6667
2017-11-11 04:00 | 11 | 4 | 13.8 | 1666.6667
2017-11-11 05:00 | 11 | 5 | 17.25 | 4266.6667
2017-11-11 06:00 | 11 | 6 | 18.4 | 4266.6667
2017-11-11 07:00 | 11 | 7 | 17.25 | 4266.6667
2017-11-11 08:00 | 11 | 8 | 17.25 | 4266.6667
2017-11-11 09:00 | 11 | 9 | 16.1 | 2773.3333
2017-11-11 10:00 | 11 | 10 | 14.375 | 1666.6667
2017-11-11 11:00 | 11 | 11 | 12.65 | 1666.6667
2017-11-11 12:00 | 11 | 12 | 9.2 | 286.6667
2017-11-11 13:00 | 11 | 13 | 8.625 | 286.6667
2017-11-11 14:00 | 11 | 14 | 8.05 | 286.6667
2017-11-11 15:00 | 11 | 15 | 9.2 | 286.6667
2017-11-11 16:00 | 11 | 16 | 8.625 | 286.6667
2017-11-11 17:00 | 11 | 17 | 3.45 | 0
2017-11-11 18:00 | 11 | 18 | 6.9 | 0
2017-11-11 19:00 | 11 | 19 | 6.9 | 0
2017-11-11 20:00 | 11 | 20 | 5.75 | 0
2017-11-11 21:00 | 11 | 21 | 3.45 | 0
2017-11-11 22:00 | 11 | 22 | 4.6 | 0
2017-11-11 23:00 | 11 | 23 | 3.45 | 0
2017-11-12 | 11 | 0 | 5.75 | 0
2017-11-12 01:00 | 11 | 1 | 4.6 | 0
2017-11-12 02:00 | 11 | 2 | 5.75 | 0
2017-11-12 03:00 | 11 | 3 | 3.45 | 0
2017-11-12 04:00 | 11 | 4 | 4.6 | 0
2017-11-12 05:00 | 11 | 5 | 3.45 | 0
2017-11-12 06:00 | 11 | 6 | 6.9 | 0
2017-11-12 07:00 | 11 | 7 | 6.325 | 0
2017-11-12 08:00 | 11 | 8 | 3.45 | 0
2017-11-12 09:00 | 11 | 9 | 3.45 | 0
2017-11-12 10:00 | 11 | 10 | 3.45 | 0
2017-11-12 11:00 | 11 | 11 | 0 | 0
2017-11-12 12:00 | 11 | 12 | 3.45 | 0
2017-11-12 13:00 | 11 | 13 | 3.45 | 0
2017-11-12 14:00 | 11 | 14 | 8.05 | 286.6667
2017-11-12 15:00 | 11 | 15 | 5.75 | 0
2017-11-12 16:00 | 11 | 16 | 5.75 | 0
2017-11-12 17:00 | 11 | 17 | 3.45 | 0
2017-11-12 18:00 | 11 | 18 | 5.75 | 0
2017-11-12 19:00 | 11 | 19 | 5.75 | 0
2017-11-12 20:00 | 11 | 20 | 3.45 | 0
2017-11-12 21:00 | 11 | 21 | 0 | 0
2017-11-12 22:00 | 11 | 22 | 0 | 0
2017-11-12 23:00 | 11 | 23 | 6.9 | 0
2017-11-13 | 11 | 0 | 5.75 | 0
2017-11-13 01:00 | 11 | 1 | 5.75 | 0
2017-11-13 02:00 | 11 | 2 | 3.45 | 0
2017-11-13 03:00 | 11 | 3 | 6.325 | 0
2017-11-13 04:00 | 11 | 4 | 7.13 | 0
2017-11-13 05:00 | 11 | 5 | 6.9 | 0
2017-11-13 06:00 | 11 | 6 | 6.9 | 0
2017-11-13 07:00 | 11 | 7 | 6.5167 | 0
2017-11-13 08:00 | 11 | 8 | 10.35 | 873.3333
2017-11-13 09:00 | 11 | 9 | 8.05 | 286.6667
2017-11-13 10:00 | 11 | 10 | 9.2 | 286.6667
2017-11-13 11:00 | 11 | 11 | 10.35 | 873.3333
2017-11-13 12:00 | 11 | 12 | 9.5833 | 286.6667
2017-11-13 13:00 | 11 | 13 | 10.925 | 873.3333
2017-11-13 14:00 | 11 | 14 | 16.675 | 2773.3333
2017-11-13 15:00 | 11 | 15 | 12.65 | 1666.6667
2017-11-13 16:00 | 11 | 16 | 12.65 | 1666.6667
2017-11-13 17:00 | 11 | 17 | 11.5 | 873.3333
2017-11-13 18:00 | 11 | 18 | 14.95 | 2773.3333
2017-11-13 19:00 | 11 | 19 | 14.1833 | 1666.6667
2017-11-13 20:00 | 11 | 20 | 14.95 | 2773.3333
2017-11-13 21:00 | 11 | 21 | 16.1 | 2773.3333
2017-11-13 22:00 | 11 | 22 | 16.1 | 2773.3333
2017-11-13 23:00 | 11 | 23 | 14.95 | 2773.3333
2017-11-14 | 11 | 0 | 11.5 | 873.3333
2017-11-14 01:00 | 11 | 1 | 11.5 | 873.3333
2017-11-14 02:00 | 11 | 2 | 12.65 | 1666.6667
2017-11-14 03:00 | 11 | 3 | 13.225 | 1666.6667
2017-11-14 04:00 | 11 | 4 | 11.1167 | 873.3333
2017-11-14 05:00 | 11 | 5 | 8.05 | 286.6667
2017-11-14 06:00 | 11 | 6 | 10.35 | 873.3333
2017-11-14 07:00 | 11 | 7 | 10.35 | 873.3333
2017-11-14 08:00 | 11 | 8 | 9.2 | 286.6667
2017-11-14 09:00 | 11 | 9 | 10.35 | 873.3333
2017-11-14 10:00 | 11 | 10 | 10.35 | 873.3333
2017-11-14 11:00 | 11 | 11 | 10.35 | 873.3333
2017-11-14 12:00 | 11 | 12 | 14.95 | 2773.3333
2017-11-14 13:00 | 11 | 13 | 13.8 | 1666.6667
2017-11-14 14:00 | 11 | 14 | 11.5 | 873.3333
2017-11-14 15:00 | 11 | 15 | 11.5 | 873.3333
2017-11-14 16:00 | 11 | 16 | 10.35 | 873.3333
2017-11-14 17:00 | 11 | 17 | 9.2 | 286.6667
2017-11-14 18:00 | 11 | 18 | 9.2 | 286.6667
2017-11-14 19:00 | 11 | 19 | 12.075 | 873.3333
2017-11-14 20:00 | 11 | 20 | 10.35 | 873.3333
2017-11-14 21:00 | 11 | 21 | 11.5 | 873.3333
2017-11-14 22:00 | 11 | 22 | 10.925 | 873.3333
2017-11-14 23:00 | 11 | 23 | 11.5 | 873.3333
2017-11-15 | 11 | 0 | 11.5 | 873.3333
2017-11-15 01:00 | 11 | 1 | 10.925 | 873.3333
2017-11-15 02:00 | 11 | 2 | 10.35 | 873.3333
2017-11-15 03:00 | 11 | 3 | 10.35 | 873.3333
2017-11-15 04:00 | 11 | 4 | 9.775 | 286.6667
2017-11-15 05:00 | 11 | 5 | 9.2 | 286.6667
2017-11-15 06:00 | 11 | 6 | 10.35 | 873.3333
2017-11-15 07:00 | 11 | 7 | 10.35 | 873.3333
2017-11-15 08:00 | 11 | 8 | 9.2 | 286.6667
2017-11-15 09:00 | 11 | 9 | 11.5 | 873.3333
2017-11-15 10:00 | 11 | 10 | 9.775 | 286.6667
2017-11-15 11:00 | 11 | 11 | 11.5 | 873.3333
2017-11-15 12:00 | 11 | 12 | 11.5 | 873.3333
2017-11-15 13:00 | 11 | 13 | 8.625 | 286.6667
2017-11-15 14:00 | 11 | 14 | 9.2 | 286.6667
2017-11-15 15:00 | 11 | 15 | 9.2 | 286.6667
2017-11-15 16:00 | 11 | 16 | 8.625 | 286.6667
2017-11-15 17:00 | 11 | 17 | 8.05 | 286.6667
2017-11-15 18:00 | 11 | 18 | 9.2 | 286.6667
2017-11-15 19:00 | 11 | 19 | 9.775 | 286.6667
2017-11-15 20:00 | 11 | 20 | 6.9 | 0
2017-11-15 21:00 | 11 | 21 | 6.9 | 0
2017-11-15 22:00 | 11 | 22 | 7.475 | 0
2017-11-15 23:00 | 11 | 23 | 6.9 | 0
2017-11-16 | 11 | 0 | 5.75 | 0
2017-11-16 01:00 | 11 | 1 | 5.75 | 0
2017-11-16 02:00 | 11 | 2 | 12.65 | 1666.6667
2017-11-16 03:00 | 11 | 3 | 9.2 | 286.6667
2017-11-16 04:00 | 11 | 4 | 10.925 | 873.3333
2017-11-16 05:00 | 11 | 5 | 14.95 | 2773.3333
2017-11-16 06:00 | 11 | 6 | 10.35 | 873.3333
2017-11-16 07:00 | 11 | 7 | 11.5 | 873.3333
2017-11-16 08:00 | 11 | 8 | 12.65 | 1666.6667
2017-11-16 09:00 | 11 | 9 | 14.95 | 2773.3333
2017-11-16 10:00 | 11 | 10 | 16.1 | 2773.3333
2017-11-16 11:00 | 11 | 11 | 11.5 | 873.3333
2017-11-16 12:00 | 11 | 12 | 10.35 | 873.3333
2017-11-16 13:00 | 11 | 13 | 5.29 | 0
2017-11-16 14:00 | 11 | 14 | 3.45 | 0
2017-11-16 15:00 | 11 | 15 | 2.53 | 0
2017-11-16 16:00 | 11 | 16 | 0.8625 | 0
2017-11-16 17:00 | 11 | 17 | 11.5 | 873.3333
2017-11-16 18:00 | 11 | 18 | 15.8125 | 2773.3333
2017-11-16 19:00 | 11 | 19 | 16.675 | 2773.3333
2017-11-16 20:00 | 11 | 20 | 17.25 | 4266.6667
2017-11-16 21:00 | 11 | 21 | 19.55 | 6160
2017-11-16 22:00 | 11 | 22 | 21.275 | 7873.3333
2017-11-16 23:00 | 11 | 23 | 16.1 | 2773.3333
2017-11-17 | 11 | 0 | 19.55 | 6160
2017-11-17 01:00 | 11 | 1 | 17.25 | 4266.6667
2017-11-17 02:00 | 11 | 2 | 12.65 | 1666.6667
2017-11-17 03:00 | 11 | 3 | 16.1 | 2773.3333
2017-11-17 04:00 | 11 | 4 | 17.825 | 4266.6667
2017-11-17 05:00 | 11 | 5 | 24.15 | 9060
2017-11-17 06:00 | 11 | 6 | 20.7 | 6160
2017-11-17 07:00 | 11 | 7 | 19.55 | 6160
2017-11-17 08:00 | 11 | 8 | 27.6 | 9573.3333
2017-11-17 09:00 | 11 | 9 | 26.45 | 9573.3333
2017-11-17 10:00 | 11 | 10 | 24.725 | 9060
2017-11-17 11:00 | 11 | 11 | 24.15 | 9060
2017-11-17 12:00 | 11 | 12 | 23 | 7873.3333
2017-11-17 13:00 | 11 | 13 | 21.85 | 7873.3333
2017-11-17 14:00 | 11 | 14 | 23 | 7873.3333
2017-11-17 15:00 | 11 | 15 | 16.1 | 2773.3333
2017-11-17 16:00 | 11 | 16 | 16.1 | 2773.3333
2017-11-17 17:00 | 11 | 17 | 12.65 | 1666.6667
2017-11-17 18:00 | 11 | 18 | 16.1 | 2773.3333
2017-11-17 19:00 | 11 | 19 | 15.525 | 2773.3333
2017-11-17 20:00 | 11 | 20 | 11.5 | 873.3333
2017-11-17 21:00 | 11 | 21 | 16.1 | 2773.3333
2017-11-17 22:00 | 11 | 22 | 13.8 | 1666.6667
2017-11-17 23:00 | 11 | 23 | 14.95 | 2773.3333
2017-11-18 | 11 | 0 | 9.2 | 286.6667
2017-11-18 01:00 | 11 | 1 | 9.775 | 286.6667
2017-11-18 02:00 | 11 | 2 | 9.2 | 286.6667
2017-11-18 03:00 | 11 | 3 | 0 | 0
2017-11-18 04:00 | 11 | 4 | 1.725 | 0
2017-11-18 05:00 | 11 | 5 | 5.75 | 0
2017-11-18 06:00 | 11 | 6 | 6.9 | 0
2017-11-18 07:00 | 11 | 7 | 6.9 | 0
2017-11-18 08:00 | 11 | 8 | 5.75 | 0
2017-11-18 09:00 | 11 | 9 | 6.9 | 0
2017-11-18 10:00 | 11 | 10 | 5.175 | 0
2017-11-18 11:00 | 11 | 11 | 9.2 | 286.6667
2017-11-18 12:00 | 11 | 12 | 10.35 | 873.3333
2017-11-18 13:00 | 11 | 13 | 10.925 | 873.3333
2017-11-18 14:00 | 11 | 14 | 8.05 | 286.6667
2017-11-18 15:00 | 11 | 15 | 8.05 | 286.6667
2017-11-18 16:00 | 11 | 16 | 8.05 | 286.6667
2017-11-18 17:00 | 11 | 17 | 8.05 | 286.6667
2017-11-18 18:00 | 11 | 18 | 5.75 | 0
2017-11-18 19:00 | 11 | 19 | 6.325 | 0
2017-11-18 20:00 | 11 | 20 | 9.2 | 286.6667
2017-11-18 21:00 | 11 | 21 | 10.35 | 873.3333
2017-11-18 22:00 | 11 | 22 | 9.5833 | 286.6667
2017-11-18 23:00 | 11 | 23 | 10.925 | 873.3333
2017-11-19 | 11 | 0 | 7.475 | 0
2017-11-19 01:00 | 11 | 1 | 10.925 | 873.3333
2017-11-19 02:00 | 11 | 2 | 15.525 | 2773.3333
2017-11-19 03:00 | 11 | 3 | 12.65 | 1666.6667
2017-11-19 04:00 | 11 | 4 | 15.525 | 2773.3333
2017-11-19 05:00 | 11 | 5 | 15.525 | 2773.3333
2017-11-19 06:00 | 11 | 6 | 20.7 | 6160
2017-11-19 07:00 | 11 | 7 | 17.6333 | 4266.6667
2017-11-19 08:00 | 11 | 8 | 18.7833 | 4266.6667
2017-11-19 09:00 | 11 | 9 | 18.0167 | 4266.6667
2017-11-19 10:00 | 11 | 10 | 21.85 | 7873.3333
2017-11-19 11:00 | 11 | 11 | 32.2 | 9960
2017-11-19 12:00 | 11 | 12 | 24.15 | 9060
2017-11-19 13:00 | 11 | 13 | 27.025 | 9573.3333
2017-11-19 14:00 | 11 | 14 | 28.75 | 9873.3333
2017-11-19 15:00 | 11 | 15 | 28.75 | 9873.3333
2017-11-19 16:00 | 11 | 16 | 28.75 | 9873.3333
2017-11-19 17:00 | 11 | 17 | 25.3 | 9060
2017-11-19 18:00 | 11 | 18 | 26.45 | 9573.3333
2017-11-19 19:00 | 11 | 19 | 25.3 | 9060
2017-11-19 20:00 | 11 | 20 | 27.6 | 9573.3333
2017-11-19 21:00 | 11 | 21 | 16.1 | 2773.3333
2017-11-19 22:00 | 11 | 22 | 17.25 | 4266.6667
2017-11-19 23:00 | 11 | 23 | 19.55 | 6160
2017-11-20 | 11 | 0 | 20.7 | 6160
2017-11-20 01:00 | 11 | 1 | 17.825 | 4266.6667
2017-11-20 02:00 | 11 | 2 | 14.95 | 2773.3333
2017-11-20 03:00 | 11 | 3 | 16.1 | 2773.3333
2017-11-20 04:00 | 11 | 4 | 13.8 | 1666.6667
2017-11-20 05:00 | 11 | 5 | 18.4 | 4266.6667
2017-11-20 06:00 | 11 | 6 | 23 | 7873.3333
2017-11-20 07:00 | 11 | 7 | 23 | 7873.3333
2017-11-20 08:00 | 11 | 8 | 19.55 | 6160
2017-11-20 09:00 | 11 | 9 | 32.2 | 9960
2017-11-20 10:00 | 11 | 10 | 28.175 | 9873.3333
2017-11-20 11:00 | 11 | 11 | 28.75 | 9873.3333
2017-11-20 12:00 | 11 | 12 | 20.7 | 6160
2017-11-20 13:00 | 11 | 13 | 21.85 | 7873.3333
2017-11-20 14:00 | 11 | 14 | 23 | 7873.3333
2017-11-20 15:00 | 11 | 15 | 24.15 | 9060
2017-11-20 16:00 | 11 | 16 | 20.125 | 6160
2017-11-20 17:00 | 11 | 17 | 12.65 | 1666.6667
2017-11-20 18:00 | 11 | 18 | 12.65 | 1666.6667
2017-11-20 19:00 | 11 | 19 | 12.65 | 1666.6667
2017-11-20 20:00 | 11 | 20 | 17.25 | 4266.6667
2017-11-20 21:00 | 11 | 21 | 14.95 | 2773.3333
2017-11-20 22:00 | 11 | 22 | 13.225 | 1666.6667
2017-11-20 23:00 | 11 | 23 | 12.65 | 1666.6667
2017-11-21 | 11 | 0 | 14.95 | 2773.3333
2017-11-21 01:00 | 11 | 1 | 13.8 | 1666.6667
2017-11-21 02:00 | 11 | 2 | 9.2 | 286.6667
2017-11-21 03:00 | 11 | 3 | 9.2 | 286.6667
2017-11-21 04:00 | 11 | 4 | 9.775 | 286.6667
2017-11-21 05:00 | 11 | 5 | 6.9 | 0
2017-11-21 06:00 | 11 | 6 | 6.9 | 0
2017-11-21 07:00 | 11 | 7 | 8.625 | 286.6667
2017-11-21 08:00 | 11 | 8 | 14.95 | 2773.3333
2017-11-21 09:00 | 11 | 9 | 19.55 | 6160
2017-11-21 10:00 | 11 | 10 | 24.725 | 9060
2017-11-21 11:00 | 11 | 11 | 35.65 | 10000
2017-11-21 12:00 | 11 | 12 | 27.6 | 9573.3333
2017-11-21 13:00 | 11 | 13 | 26.45 | 9573.3333
2017-11-21 14:00 | 11 | 14 | 26.45 | 9573.3333
2017-11-21 15:00 | 11 | 15 | 18.4 | 4266.6667
2017-11-21 16:00 | 11 | 16 | 17.825 | 4266.6667
2017-11-21 17:00 | 11 | 17 | 11.5 | 873.3333
2017-11-21 18:00 | 11 | 18 | 18.4 | 4266.6667
2017-11-21 19:00 | 11 | 19 | 16.675 | 2773.3333
2017-11-21 20:00 | 11 | 20 | 18.4 | 4266.6667
2017-11-21 21:00 | 11 | 21 | 14.95 | 2773.3333
2017-11-21 22:00 | 11 | 22 | 13.8 | 1666.6667
2017-11-21 23:00 | 11 | 23 | 8.05 | 286.6667
2017-11-22 | 11 | 0 | 8.05 | 286.6667
2017-11-22 01:00 | 11 | 1 | 8.05 | 286.6667
2017-11-22 02:00 | 11 | 2 | 10.35 | 873.3333
2017-11-22 03:00 | 11 | 3 | 11.5 | 873.3333
2017-11-22 04:00 | 11 | 4 | 9.775 | 286.6667
2017-11-22 05:00 | 11 | 5 | 10.35 | 873.3333
2017-11-22 06:00 | 11 | 6 | 5.75 | 0
2017-11-22 07:00 | 11 | 7 | 2.875 | 0
2017-11-22 08:00 | 11 | 8 | 0 | 0
2017-11-22 09:00 | 11 | 9 | 3.0667 | 0
2017-11-22 10:00 | 11 | 10 | 7.82 | 0
2017-11-22 11:00 | 11 | 11 | 8.28 | 286.6667
2017-11-22 12:00 | 11 | 12 | 9.9667 | 286.6667
2017-11-22 13:00 | 11 | 13 | 11.2125 | 873.3333
2017-11-22 14:00 | 11 | 14 | 12.9375 | 1666.6667
2017-11-22 15:00 | 11 | 15 | 17.25 | 4266.6667
2017-11-22 16:00 | 11 | 16 | 16.1 | 2773.3333
2017-11-22 17:00 | 11 | 17 | 24.15 | 9060
2017-11-22 18:00 | 11 | 18 | 27.025 | 9573.3333
2017-11-22 19:00 | 11 | 19 | 24.15 | 9060
2017-11-22 20:00 | 11 | 20 | 18.4 | 4266.6667
2017-11-22 21:00 | 11 | 21 | 18.4 | 4266.6667
2017-11-22 22:00 | 11 | 22 | 19.55 | 6160
2017-11-22 23:00 | 11 | 23 | 20.7 | 6160
2017-11-23 | 11 | 0 | 23 | 7873.3333
2017-11-23 01:00 | 11 | 1 | 20.125 | 6160
2017-11-23 02:00 | 11 | 2 | 17.25 | 4266.6667
2017-11-23 03:00 | 11 | 3 | 14.95 | 2773.3333
2017-11-23 04:00 | 11 | 4 | 10.925 | 873.3333
2017-11-23 05:00 | 11 | 5 | 8.05 | 286.6667
2017-11-23 06:00 | 11 | 6 | 6.9 | 0
2017-11-23 07:00 | 11 | 7 | 10.925 | 873.3333
2017-11-23 08:00 | 11 | 8 | 14.95 | 2773.3333
2017-11-23 09:00 | 11 | 9 | 12.65 | 1666.6667
2017-11-23 10:00 | 11 | 10 | 13.8 | 1666.6667
2017-11-23 11:00 | 11 | 11 | 14.95 | 2773.3333
2017-11-23 12:00 | 11 | 12 | 8.05 | 286.6667
2017-11-23 13:00 | 11 | 13 | 8.05 | 286.6667
2017-11-23 14:00 | 11 | 14 | 8.05 | 286.6667
2017-11-23 15:00 | 11 | 15 | 8.05 | 286.6667
2017-11-23 16:00 | 11 | 16 | 8.05 | 286.6667
2017-11-23 17:00 | 11 | 17 | 8.05 | 286.6667
2017-11-23 18:00 | 11 | 18 | 8.05 | 286.6667
2017-11-23 19:00 | 11 | 19 | 5.75 | 0
2017-11-23 20:00 | 11 | 20 | 8.05 | 286.6667
2017-11-23 21:00 | 11 | 21 | 8.05 | 286.6667
2017-11-23 22:00 | 11 | 22 | 6.9 | 0
2017-11-23 23:00 | 11 | 23 | 5.75 | 0
2017-11-24 | 11 | 0 | 6.9 | 0
2017-11-24 01:00 | 11 | 1 | 6.9 | 0
2017-11-24 02:00 | 11 | 2 | 9.2 | 286.6667
2017-11-24 03:00 | 11 | 3 | 5.75 | 0
2017-11-24 04:00 | 11 | 4 | 6.9 | 0
2017-11-24 05:00 | 11 | 5 | 11.5 | 873.3333
2017-11-24 06:00 | 11 | 6 | 11.5 | 873.3333
2017-11-24 07:00 | 11 | 7 | 10.925 | 873.3333
2017-11-24 08:00 | 11 | 8 | 11.5 | 873.3333
2017-11-24 09:00 | 11 | 9 | 6.9 | 0
2017-11-24 10:00 | 11 | 10 | 6.9 | 0
2017-11-24 11:00 | 11 | 11 | 6.9 | 0
2017-11-24 12:00 | 11 | 12 | 11.5 | 873.3333
2017-11-24 13:00 | 11 | 13 | 10.925 | 873.3333
2017-11-24 14:00 | 11 | 14 | 11.5 | 873.3333
2017-11-24 15:00 | 11 | 15 | 14.95 | 2773.3333
2017-11-24 16:00 | 11 | 16 | 13.8 | 1666.6667
2017-11-24 17:00 | 11 | 17 | 14.95 | 2773.3333
2017-11-24 18:00 | 11 | 18 | 16.1 | 2773.3333
2017-11-24 19:00 | 11 | 19 | 13.8 | 1666.6667
2017-11-24 20:00 | 11 | 20 | 12.65 | 1666.6667
2017-11-24 21:00 | 11 | 21 | 8.05 | 286.6667
2017-11-24 22:00 | 11 | 22 | 10.35 | 873.3333
2017-11-24 23:00 | 11 | 23 | 11.5 | 873.3333
2017-11-25 | 11 | 0 | 9.2 | 286.6667
2017-11-25 01:00 | 11 | 1 | 8.05 | 286.6667
2017-11-25 02:00 | 11 | 2 | 8.05 | 286.6667
2017-11-25 03:00 | 11 | 3 | 9.2 | 286.6667
2017-11-25 04:00 | 11 | 4 | 9.2 | 286.6667
2017-11-25 05:00 | 11 | 5 | 12.65 | 1666.6667
2017-11-25 06:00 | 11 | 6 | 10.35 | 873.3333
2017-11-25 07:00 | 11 | 7 | 9.775 | 286.6667
2017-11-25 08:00 | 11 | 8 | 11.5 | 873.3333
2017-11-25 09:00 | 11 | 9 | 20.7 | 6160
2017-11-25 10:00 | 11 | 10 | 20.125 | 6160
2017-11-25 11:00 | 11 | 11 | 16.1 | 2773.3333
2017-11-25 12:00 | 11 | 12 | 14.95 | 2773.3333
2017-11-25 13:00 | 11 | 13 | 16.1 | 2773.3333
2017-11-25 14:00 | 11 | 14 | 16.1 | 2773.3333
2017-11-25 15:00 | 11 | 15 | 14.95 | 2773.3333
2017-11-25 16:00 | 11 | 16 | 12.075 | 873.3333
2017-11-25 17:00 | 11 | 17 | 10.35 | 873.3333
2017-11-25 18:00 | 11 | 18 | 12.65 | 1666.6667
2017-11-25 19:00 | 11 | 19 | 12.65 | 1666.6667
2017-11-25 20:00 | 11 | 20 | 11.5 | 873.3333
2017-11-25 21:00 | 11 | 21 | 11.5 | 873.3333
2017-11-25 22:00 | 11 | 22 | 10.925 | 873.3333
2017-11-25 23:00 | 11 | 23 | 8.05 | 286.6667
2017-11-26 | 11 | 0 | 10.35 | 873.3333
2017-11-26 01:00 | 11 | 1 | 11.5 | 873.3333
2017-11-26 02:00 | 11 | 2 | 11.5 | 873.3333
2017-11-26 03:00 | 11 | 3 | 17.25 | 4266.6667
2017-11-26 04:00 | 11 | 4 | 14.95 | 2773.3333
2017-11-26 05:00 | 11 | 5 | 18.4 | 4266.6667
2017-11-26 06:00 | 11 | 6 | 17.25 | 4266.6667
2017-11-26 07:00 | 11 | 7 | 17.25 | 4266.6667
2017-11-26 08:00 | 11 | 8 | 19.55 | 6160
2017-11-26 09:00 | 11 | 9 | 25.3 | 9060
2017-11-26 10:00 | 11 | 10 | 26.45 | 9573.3333
2017-11-26 11:00 | 11 | 11 | 32.2 | 9960
2017-11-26 12:00 | 11 | 12 | 23 | 7873.3333
2017-11-26 13:00 | 11 | 13 | 28.75 | 9873.3333
2017-11-26 14:00 | 11 | 14 | 20.7 | 6160
2017-11-26 15:00 | 11 | 15 | 18.4 | 4266.6667
2017-11-26 16:00 | 11 | 16 | 15.525 | 2773.3333
2017-11-26 17:00 | 11 | 17 | 12.65 | 1666.6667
2017-11-26 18:00 | 11 | 18 | 18.4 | 4266.6667
2017-11-26 19:00 | 11 | 19 | 16.675 | 2773.3333
2017-11-26 20:00 | 11 | 20 | 12.65 | 1666.6667
2017-11-26 21:00 | 11 | 21 | 11.5 | 873.3333
2017-11-26 22:00 | 11 | 22 | 12.075 | 873.3333
2017-11-26 23:00 | 11 | 23 | 12.65 | 1666.6667
2017-11-27 | 11 | 0 | 12.65 | 1666.6667
2017-11-27 01:00 | 11 | 1 | 11.5 | 873.3333
2017-11-27 02:00 | 11 | 2 | 12.65 | 1666.6667
2017-11-27 03:00 | 11 | 3 | 12.65 | 1666.6667
2017-11-27 04:00 | 11 | 4 | 14.95 | 2773.3333
2017-11-27 05:00 | 11 | 5 | 14.95 | 2773.3333
2017-11-27 06:00 | 11 | 6 | 16.1 | 2773.3333
2017-11-27 07:00 | 11 | 7 | 17.825 | 4266.6667
2017-11-27 08:00 | 11 | 8 | 14.95 | 2773.3333
2017-11-27 09:00 | 11 | 9 | 14.95 | 2773.3333
2017-11-27 10:00 | 11 | 10 | 16.675 | 2773.3333
2017-11-27 11:00 | 11 | 11 | 17.25 | 4266.6667
2017-11-27 12:00 | 11 | 12 | 16.1 | 2773.3333
2017-11-27 13:00 | 11 | 13 | 17.25 | 4266.6667
2017-11-27 14:00 | 11 | 14 | 18.4 | 4266.6667
2017-11-27 15:00 | 11 | 15 | 12.65 | 1666.6667
2017-11-27 16:00 | 11 | 16 | 14.95 | 2773.3333
2017-11-27 17:00 | 11 | 17 | 17.25 | 4266.6667
2017-11-27 18:00 | 11 | 18 | 14.95 | 2773.3333
2017-11-27 19:00 | 11 | 19 | 12.65 | 1666.6667
2017-11-27 20:00 | 11 | 20 | 11.5 | 873.3333
2017-11-27 21:00 | 11 | 21 | 14.95 | 2773.3333
2017-11-27 22:00 | 11 | 22 | 13.225 | 1666.6667
2017-11-27 23:00 | 11 | 23 | 12.65 | 1666.6667
2017-11-28 | 11 | 0 | 14.95 | 2773.3333
2017-11-28 01:00 | 11 | 1 | 13.225 | 1666.6667
2017-11-28 02:00 | 11 | 2 | 9.2 | 286.6667
2017-11-28 03:00 | 11 | 3 | 11.5 | 873.3333
2017-11-28 04:00 | 11 | 4 | 10.35 | 873.3333
2017-11-28 05:00 | 11 | 5 | 5.75 | 0
2017-11-28 06:00 | 11 | 6 | 9.2 | 286.6667
2017-11-28 07:00 | 11 | 7 | 6.325 | 0
2017-11-28 08:00 | 11 | 8 | 0 | 0
2017-11-28 09:00 | 11 | 9 | 5.75 | 0
2017-11-28 10:00 | 11 | 10 | 6.325 | 0
2017-11-28 11:00 | 11 | 11 | 5.75 | 0
2017-11-28 12:00 | 11 | 12 | 10.35 | 873.3333
2017-11-28 13:00 | 11 | 13 | 10.35 | 873.3333
2017-11-28 14:00 | 11 | 14 | 12.65 | 1666.6667
2017-11-28 15:00 | 11 | 15 | 18.4 | 4266.6667
2017-11-28 16:00 | 11 | 16 | 16.675 | 2773.3333
2017-11-28 17:00 | 11 | 17 | 14.95 | 2773.3333
2017-11-28 18:00 | 11 | 18 | 9.2 | 286.6667
2017-11-28 19:00 | 11 | 19 | 9.775 | 286.6667
2017-11-28 20:00 | 11 | 20 | 12.65 | 1666.6667
2017-11-28 21:00 | 11 | 21 | 10.35 | 873.3333
2017-11-28 22:00 | 11 | 22 | 14.95 | 2773.3333
2017-11-28 23:00 | 11 | 23 | 16.1 | 2773.3333
2017-11-29 | 11 | 0 | 19.55 | 6160
2017-11-29 01:00 | 11 | 1 | 21.85 | 7873.3333
2017-11-29 02:00 | 11 | 2 | 19.55 | 6160
2017-11-29 03:00 | 11 | 3 | 23 | 7873.3333
2017-11-29 04:00 | 11 | 4 | 21.275 | 7873.3333
2017-11-29 05:00 | 11 | 5 | 17.25 | 4266.6667
2017-11-29 06:00 | 11 | 6 | 23 | 7873.3333
2017-11-29 07:00 | 11 | 7 | 18.4 | 4266.6667
2017-11-29 08:00 | 11 | 8 | 19.55 | 6160
2017-11-29 09:00 | 11 | 9 | 17.25 | 4266.6667
2017-11-29 10:00 | 11 | 10 | 13.8 | 1666.6667
2017-11-29 11:00 | 11 | 11 | 19.55 | 6160
2017-11-29 12:00 | 11 | 12 | 26.45 | 9573.3333
2017-11-29 13:00 | 11 | 13 | 28.175 | 9873.3333
2017-11-29 14:00 | 11 | 14 | 26.45 | 9573.3333
2017-11-29 15:00 | 11 | 15 | 17.25 | 4266.6667
2017-11-29 16:00 | 11 | 16 | 18.4 | 4266.6667
2017-11-29 17:00 | 11 | 17 | 17.25 | 4266.6667
2017-11-29 18:00 | 11 | 18 | 17.25 | 4266.6667
2017-11-29 19:00 | 11 | 19 | 17.825 | 4266.6667
2017-11-29 20:00 | 11 | 20 | 11.5 | 873.3333
2017-11-29 21:00 | 11 | 21 | 14.95 | 2773.3333
2017-11-29 22:00 | 11 | 22 | 14.95 | 2773.3333
2017-11-29 23:00 | 11 | 23 | 12.65 | 1666.6667
2017-11-30 | 11 | 0 | 18.4 | 4266.6667
2017-11-30 01:00 | 11 | 1 | 15.525 | 2773.3333
2017-11-30 02:00 | 11 | 2 | 9.2 | 286.6667
2017-11-30 03:00 | 11 | 3 | 6.9 | 0
2017-11-30 04:00 | 11 | 4 | 7.475 | 0
2017-11-30 05:00 | 11 | 5 | 5.75 | 0
2017-11-30 06:00 | 11 | 6 | 12.65 | 1666.6667
2017-11-30 07:00 | 11 | 7 | 10.35 | 873.3333
2017-11-30 08:00 | 11 | 8 | 9.2 | 286.6667
2017-11-30 09:00 | 11 | 9 | 0 | 0
2017-11-30 10:00 | 11 | 10 | 2.875 | 0
2017-11-30 11:00 | 11 | 11 | 6.9 | 0
2017-11-30 12:00 | 11 | 12 | 6.9 | 0
2017-11-30 13:00 | 11 | 13 | 7.475 | 0
2017-11-30 14:00 | 11 | 14 | 14.95 | 2773.3333
2017-11-30 15:00 | 11 | 15 | 9.2 | 286.6667
2017-11-30 16:00 | 11 | 16 | 8.625 | 286.6667
2017-11-30 17:00 | 11 | 17 | 10.35 | 873.3333
2017-11-30 18:00 | 11 | 18 | 6.9 | 0
2017-11-30 19:00 | 11 | 19 | 8.625 | 286.6667
2017-11-30 20:00 | 11 | 20 | 9.2 | 286.6667
2017-11-30 21:00 | 11 | 21 | 11.5 | 873.3333
2017-11-30 22:00 | 11 | 22 | 9.775 | 286.6667
2017-11-30 23:00 | 11 | 23 | 8.4333 | 286.6667
2017-12-01 | 12 | 0 | 8.05 | 286.6667
2017-12-01 01:00 | 12 | 1 | 8.05 | 286.6667
2017-12-01 02:00 | 12 | 2 | 6.9 | 0
2017-12-01 03:00 | 12 | 3 | 5.75 | 0
2017-12-01 04:00 | 12 | 4 | 5.75 | 0
2017-12-01 05:00 | 12 | 5 | 8.625 | 286.6667
2017-12-01 06:00 | 12 | 6 | 10.35 | 873.3333
2017-12-01 07:00 | 12 | 7 | 10.925 | 873.3333
2017-12-01 08:00 | 12 | 8 | 11.5 | 873.3333
2017-12-01 09:00 | 12 | 9 | 11.5 | 873.3333
2017-12-01 10:00 | 12 | 10 | 13.225 | 1666.6667
2017-12-01 11:00 | 12 | 11 | 17.25 | 4266.6667
2017-12-01 12:00 | 12 | 12 | 17.25 | 4266.6667
2017-12-01 13:00 | 12 | 13 | 14.95 | 2773.3333
2017-12-01 14:00 | 12 | 14 | 19.55 | 6160
2017-12-01 15:00 | 12 | 15 | 11.5 | 873.3333
2017-12-01 16:00 | 12 | 16 | 13.225 | 1666.6667
2017-12-01 17:00 | 12 | 17 | 12.65 | 1666.6667
2017-12-01 18:00 | 12 | 18 | 9.2 | 286.6667
2017-12-01 19:00 | 12 | 19 | 8.625 | 286.6667
2017-12-01 20:00 | 12 | 20 | 11.5 | 873.3333
2017-12-01 21:00 | 12 | 21 | 14.95 | 2773.3333
2017-12-01 22:00 | 12 | 22 | 13.8 | 1666.6667
2017-12-01 23:00 | 12 | 23 | 12.65 | 1666.6667
2017-12-02 | 12 | 0 | 14.95 | 2773.3333
2017-12-02 01:00 | 12 | 1 | 12.65 | 1666.6667
2017-12-02 02:00 | 12 | 2 | 10.35 | 873.3333
2017-12-02 03:00 | 12 | 3 | 6.9 | 0
2017-12-02 04:00 | 12 | 4 | 8.05 | 286.6667
2017-12-02 05:00 | 12 | 5 | 10.35 | 873.3333
2017-12-02 06:00 | 12 | 6 | 9.2 | 286.6667
2017-12-02 07:00 | 12 | 7 | 9.2 | 286.6667
2017-12-02 08:00 | 12 | 8 | 8.05 | 286.6667
2017-12-02 09:00 | 12 | 9 | 3.45 | 0
2017-12-02 10:00 | 12 | 10 | 1.725 | 0
2017-12-02 11:00 | 12 | 11 | 0 | 0
2017-12-02 12:00 | 12 | 12 | 5.75 | 0
2017-12-02 13:00 | 12 | 13 | 4.6 | 0
2017-12-02 14:00 | 12 | 14 | 0 | 0
2017-12-02 15:00 | 12 | 15 | 0 | 0
2017-12-02 16:00 | 12 | 16 | 1.725 | 0
2017-12-02 17:00 | 12 | 17 | 5.75 | 0
2017-12-02 18:00 | 12 | 18 | 5.75 | 0
2017-12-02 19:00 | 12 | 19 | 5.75 | 0
2017-12-02 20:00 | 12 | 20 | 3.45 | 0
2017-12-02 21:00 | 12 | 21 | 6.9 | 0
2017-12-02 22:00 | 12 | 22 | 6.325 | 0
2017-12-02 23:00 | 12 | 23 | 5.75 | 0
2017-12-03 | 12 | 0 | 0 | 0
2017-12-03 01:00 | 12 | 1 | 3.45 | 0
2017-12-03 02:00 | 12 | 2 | 5.75 | 0
2017-12-03 03:00 | 12 | 3 | 8.05 | 286.6667
2017-12-03 04:00 | 12 | 4 | 5.75 | 0
2017-12-03 05:00 | 12 | 5 | 6.9 | 0
2017-12-03 06:00 | 12 | 6 | 5.75 | 0
2017-12-03 07:00 | 12 | 7 | 4.6 | 0
2017-12-03 08:00 | 12 | 8 | 3.45 | 0
2017-12-03 09:00 | 12 | 9 | 5.75 | 0
2017-12-03 10:00 | 12 | 10 | 6.9 | 0
2017-12-03 11:00 | 12 | 11 | 5.75 | 0
2017-12-03 12:00 | 12 | 12 | 6.9 | 0
2017-12-03 13:00 | 12 | 13 | 6.9 | 0
2017-12-03 14:00 | 12 | 14 | 8.05 | 286.6667
2017-12-03 15:00 | 12 | 15 | 6.9 | 0
2017-12-03 16:00 | 12 | 16 | 6.9 | 0
2017-12-03 17:00 | 12 | 17 | 6.9 | 0
2017-12-03 18:00 | 12 | 18 | 6.9 | 0
2017-12-03 19:00 | 12 | 19 | 6.9 | 0
2017-12-03 20:00 | 12 | 20 | 3.45 | 0
2017-12-03 21:00 | 12 | 21 | 3.45 | 0
2017-12-03 22:00 | 12 | 22 | 4.6 | 0
2017-12-03 23:00 | 12 | 23 | 5.75 | 0
2017-12-04 | 12 | 0 | 5.75 | 0
2017-12-04 01:00 | 12 | 1 | 6.9 | 0
2017-12-04 02:00 | 12 | 2 | 6.9 | 0
2017-12-04 03:00 | 12 | 3 | 8.05 | 286.6667
2017-12-04 04:00 | 12 | 4 | 9.2 | 286.6667
2017-12-04 05:00 | 12 | 5 | 8.05 | 286.6667
2017-12-04 06:00 | 12 | 6 | 9.2 | 286.6667
2017-12-04 07:00 | 12 | 7 | 8.625 | 286.6667
2017-12-04 08:00 | 12 | 8 | 5.75 | 0
2017-12-04 09:00 | 12 | 9 | 5.75 | 0
2017-12-04 10:00 | 12 | 10 | 6.9 | 0
2017-12-04 11:00 | 12 | 11 | 8.05 | 286.6667
2017-12-04 12:00 | 12 | 12 | 10.35 | 873.3333
2017-12-04 13:00 | 12 | 13 | 9.775 | 286.6667
2017-12-04 14:00 | 12 | 14 | 11.5 | 873.3333
2017-12-04 15:00 | 12 | 15 | 6.9 | 0
2017-12-04 16:00 | 12 | 16 | 8.625 | 286.6667
2017-12-04 17:00 | 12 | 17 | 8.05 | 286.6667
2017-12-04 18:00 | 12 | 18 | 9.2 | 286.6667
2017-12-04 19:00 | 12 | 19 | 9.775 | 286.6667
2017-12-04 20:00 | 12 | 20 | 10.35 | 873.3333
2017-12-04 21:00 | 12 | 21 | 10.35 | 873.3333
2017-12-04 22:00 | 12 | 22 | 7.475 | 0
2017-12-04 23:00 | 12 | 23 | 6.9 | 0
2017-12-05 | 12 | 0 | 8.05 | 286.6667
2017-12-05 01:00 | 12 | 1 | 7.475 | 0
2017-12-05 02:00 | 12 | 2 | 10.35 | 873.3333
2017-12-05 03:00 | 12 | 3 | 14.95 | 2773.3333
2017-12-05 04:00 | 12 | 4 | 14.95 | 2773.3333
2017-12-05 05:00 | 12 | 5 | 12.65 | 1666.6667
2017-12-05 06:00 | 12 | 6 | 16.1 | 2773.3333
2017-12-05 07:00 | 12 | 7 | 14.375 | 1666.6667
2017-12-05 08:00 | 12 | 8 | 16.1 | 2773.3333
2017-12-05 09:00 | 12 | 9 | 17.25 | 4266.6667
2017-12-05 10:00 | 12 | 10 | 16.675 | 2773.3333
2017-12-05 11:00 | 12 | 11 | 20.7 | 6160
2017-12-05 12:00 | 12 | 12 | 16.1 | 2773.3333
2017-12-05 13:00 | 12 | 13 | 15.525 | 2773.3333
2017-12-05 14:00 | 12 | 14 | 12.65 | 1666.6667
2017-12-05 15:00 | 12 | 15 | 15.525 | 2773.3333
2017-12-05 16:00 | 12 | 16 | 12.65 | 1666.6667
2017-12-05 17:00 | 12 | 17 | 16.1 | 2773.3333
2017-12-05 18:00 | 12 | 18 | 18.4 | 4266.6667
2017-12-05 19:00 | 12 | 19 | 23.575 | 9060
2017-12-05 20:00 | 12 | 20 | 28.75 | 9873.3333
2017-12-05 21:00 | 12 | 21 | 32.775 | 10000
2017-12-05 22:00 | 12 | 22 | 36.8 | 10000
2017-12-05 23:00 | 12 | 23 | 32.2 | 9960
2017-12-06 | 12 | 0 | 26.45 | 9573.3333
2017-12-06 01:00 | 12 | 1 | 22.7125 | 7873.3333
2017-12-06 02:00 | 12 | 2 | 11.5 | 873.3333
2017-12-06 03:00 | 12 | 3 | 14.95 | 2773.3333
2017-12-06 04:00 | 12 | 4 | 15.7167 | 2773.3333
2017-12-06 05:00 | 12 | 5 | 29.325 | 9873.3333
2017-12-06 06:00 | 12 | 6 | 20.125 | 6160
2017-12-06 07:00 | 12 | 7 | 18.975 | 4266.6667
2017-12-06 08:00 | 12 | 8 | 24.15 | 9060
2017-12-06 09:00 | 12 | 9 | 23 | 7873.3333
2017-12-06 10:00 | 12 | 10 | 17.825 | 4266.6667
2017-12-06 11:00 | 12 | 11 | 14.95 | 2773.3333
2017-12-06 12:00 | 12 | 12 | 12.65 | 1666.6667
2017-12-06 13:00 | 12 | 13 | 14.375 | 1666.6667
2017-12-06 14:00 | 12 | 14 | 12.65 | 1666.6667
2017-12-06 15:00 | 12 | 15 | 14.95 | 2773.3333
2017-12-06 16:00 | 12 | 16 | 14.95 | 2773.3333
2017-12-06 17:00 | 12 | 17 | 16.1 | 2773.3333
2017-12-06 18:00 | 12 | 18 | 10.35 | 873.3333
2017-12-06 19:00 | 12 | 19 | 9.775 | 286.6667
2017-12-06 20:00 | 12 | 20 | 11.5 | 873.3333
2017-12-06 21:00 | 12 | 21 | 11.5 | 873.3333
2017-12-06 22:00 | 12 | 22 | 10.925 | 873.3333
2017-12-06 23:00 | 12 | 23 | 12.65 | 1666.6667
2017-12-07 | 12 | 0 | 14.95 | 2773.3333
2017-12-07 01:00 | 12 | 1 | 15.525 | 2773.3333
2017-12-07 02:00 | 12 | 2 | 16.1 | 2773.3333
2017-12-07 03:00 | 12 | 3 | 14.95 | 2773.3333
2017-12-07 04:00 | 12 | 4 | 14.95 | 2773.3333
2017-12-07 05:00 | 12 | 5 | 12.65 | 1666.6667
2017-12-07 06:00 | 12 | 6 | 10.35 | 873.3333
2017-12-07 07:00 | 12 | 7 | 11.5 | 873.3333
2017-12-07 08:00 | 12 | 8 | 12.65 | 1666.6667
2017-12-07 09:00 | 12 | 9 | 12.65 | 1666.6667
2017-12-07 10:00 | 12 | 10 | 12.65 | 1666.6667
2017-12-07 11:00 | 12 | 11 | 17.25 | 4266.6667
2017-12-07 12:00 | 12 | 12 | 10.35 | 873.3333
2017-12-07 13:00 | 12 | 13 | 12.65 | 1666.6667
2017-12-07 14:00 | 12 | 14 | 14.95 | 2773.3333
2017-12-07 15:00 | 12 | 15 | 9.2 | 286.6667
2017-12-07 16:00 | 12 | 16 | 9.775 | 286.6667
2017-12-07 17:00 | 12 | 17 | 8.05 | 286.6667
2017-12-07 18:00 | 12 | 18 | 6.9 | 0
2017-12-07 19:00 | 12 | 19 | 7.475 | 0
2017-12-07 20:00 | 12 | 20 | 14.95 | 2773.3333
2017-12-07 21:00 | 12 | 21 | 16.1 | 2773.3333
2017-12-07 22:00 | 12 | 22 | 17.25 | 4266.6667
2017-12-07 23:00 | 12 | 23 | 18.4 | 4266.6667
2017-12-08 | 12 | 0 | 12.65 | 1666.6667
2017-12-08 01:00 | 12 | 1 | 12.65 | 1666.6667
2017-12-08 02:00 | 12 | 2 | 11.5 | 873.3333
2017-12-08 03:00 | 12 | 3 | 12.65 | 1666.6667
2017-12-08 04:00 | 12 | 4 | 11.5 | 873.3333
2017-12-08 05:00 | 12 | 5 | 10.35 | 873.3333
2017-12-08 06:00 | 12 | 6 | 16.1 | 2773.3333
2017-12-08 07:00 | 12 | 7 | 13.225 | 1666.6667
2017-12-08 08:00 | 12 | 8 | 11.5 | 873.3333
2017-12-08 09:00 | 12 | 9 | 12.65 | 1666.6667
2017-12-08 10:00 | 12 | 10 | 10.925 | 873.3333
2017-12-08 11:00 | 12 | 11 | 9.2 | 286.6667
2017-12-08 12:00 | 12 | 12 | 11.5 | 873.3333
2017-12-08 13:00 | 12 | 13 | 13.225 | 1666.6667
2017-12-08 14:00 | 12 | 14 | 11.5 | 873.3333
2017-12-08 15:00 | 12 | 15 | 12.65 | 1666.6667
2017-12-08 16:00 | 12 | 16 | 11.5 | 873.3333
2017-12-08 17:00 | 12 | 17 | 8.05 | 286.6667
2017-12-08 18:00 | 12 | 18 | 11.5 | 873.3333
2017-12-08 19:00 | 12 | 19 | 10.35 | 873.3333
2017-12-08 20:00 | 12 | 20 | 8.05 | 286.6667
2017-12-08 21:00 | 12 | 21 | 6.9 | 0
2017-12-08 22:00 | 12 | 22 | 6.9 | 0
2017-12-08 23:00 | 12 | 23 | 6.9 | 0
2017-12-09 | 12 | 0 | 6.9 | 0
2017-12-09 01:00 | 12 | 1 | 6.9 | 0
2017-12-09 02:00 | 12 | 2 | 3.45 | 0
2017-12-09 03:00 | 12 | 3 | 6.9 | 0
2017-12-09 04:00 | 12 | 4 | 6.9 | 0
2017-12-09 05:00 | 12 | 5 | 5.75 | 0
2017-12-09 06:00 | 12 | 6 | 0 | 0
2017-12-09 07:00 | 12 | 7 | 3.45 | 0
2017-12-09 08:00 | 12 | 8 | 5.75 | 0
2017-12-09 09:00 | 12 | 9 | 8.05 | 286.6667
2017-12-09 10:00 | 12 | 10 | 6.21 | 0
2017-12-09 11:00 | 12 | 11 | 3.68 | 0
2017-12-09 12:00 | 12 | 12 | 4.6 | 0
2017-12-09 13:00 | 12 | 13 | 8.4333 | 286.6667
2017-12-09 14:00 | 12 | 14 | 10.35 | 873.3333
2017-12-09 15:00 | 12 | 15 | 8.05 | 286.6667
2017-12-09 16:00 | 12 | 16 | 12.075 | 873.3333
2017-12-09 17:00 | 12 | 17 | 13.0333 | 1666.6667
2017-12-09 18:00 | 12 | 18 | 12.65 | 1666.6667
2017-12-09 19:00 | 12 | 19 | 12.65 | 1666.6667
2017-12-09 20:00 | 12 | 20 | 11.5 | 873.3333
2017-12-09 21:00 | 12 | 21 | 14.95 | 2773.3333
2017-12-09 22:00 | 12 | 22 | 13.8 | 1666.6667
2017-12-09 23:00 | 12 | 23 | 10.925 | 873.3333
2017-12-10 | 12 | 0 | 15.525 | 2773.3333
2017-12-10 01:00 | 12 | 1 | 12.65 | 1666.6667
2017-12-10 02:00 | 12 | 2 | 14.95 | 2773.3333
2017-12-10 03:00 | 12 | 3 | 11.5 | 873.3333
2017-12-10 04:00 | 12 | 4 | 10.35 | 873.3333
2017-12-10 05:00 | 12 | 5 | 11.5 | 873.3333
2017-12-10 06:00 | 12 | 6 | 16.1 | 2773.3333
2017-12-10 07:00 | 12 | 7 | 17.25 | 4266.6667
2017-12-10 08:00 | 12 | 8 | 12.65 | 1666.6667
2017-12-10 09:00 | 12 | 9 | 17.25 | 4266.6667
2017-12-10 10:00 | 12 | 10 | 16.675 | 2773.3333
2017-12-10 11:00 | 12 | 11 | 12.65 | 1666.6667
2017-12-10 12:00 | 12 | 12 | 16.1 | 2773.3333
2017-12-10 13:00 | 12 | 13 | 19.55 | 6160
2017-12-10 14:00 | 12 | 14 | 18.4 | 4266.6667
2017-12-10 15:00 | 12 | 15 | 9.2 | 286.6667
2017-12-10 16:00 | 12 | 16 | 10.925 | 873.3333
2017-12-10 17:00 | 12 | 17 | 11.5 | 873.3333
2017-12-10 18:00 | 12 | 18 | 14.95 | 2773.3333
2017-12-10 19:00 | 12 | 19 | 13.8 | 1666.6667
2017-12-10 20:00 | 12 | 20 | 11.5 | 873.3333
2017-12-10 21:00 | 12 | 21 | 14.95 | 2773.3333
2017-12-10 22:00 | 12 | 22 | 13.8 | 1666.6667
2017-12-10 23:00 | 12 | 23 | 10.35 | 873.3333
2017-12-11 | 12 | 0 | 14.95 | 2773.3333
2017-12-11 01:00 | 12 | 1 | 13.225 | 1666.6667
2017-12-11 02:00 | 12 | 2 | 11.5 | 873.3333
2017-12-11 03:00 | 12 | 3 | 10.35 | 873.3333
2017-12-11 04:00 | 12 | 4 | 10.925 | 873.3333
2017-12-11 05:00 | 12 | 5 | 11.5 | 873.3333
2017-12-11 06:00 | 12 | 6 | 17.25 | 4266.6667
2017-12-11 07:00 | 12 | 7 | 16.675 | 2773.3333
2017-12-11 08:00 | 12 | 8 | 14.95 | 2773.3333
2017-12-11 09:00 | 12 | 9 | 14.95 | 2773.3333
2017-12-11 10:00 | 12 | 10 | 13.225 | 1666.6667
2017-12-11 11:00 | 12 | 11 | 19.55 | 6160
2017-12-11 12:00 | 12 | 12 | 17.25 | 4266.6667
2017-12-11 13:00 | 12 | 13 | 14.375 | 1666.6667
2017-12-11 14:00 | 12 | 14 | 11.5 | 873.3333
2017-12-11 15:00 | 12 | 15 | 8.05 | 286.6667
2017-12-11 16:00 | 12 | 16 | 8.05 | 286.6667
2017-12-11 17:00 | 12 | 17 | 9.2 | 286.6667
2017-12-11 18:00 | 12 | 18 | 5.75 | 0
2017-12-11 19:00 | 12 | 19 | 5.75 | 0
2017-12-11 20:00 | 12 | 20 | 0 | 0
2017-12-11 21:00 | 12 | 21 | 5.75 | 0
2017-12-11 22:00 | 12 | 22 | 6.325 | 0
2017-12-11 23:00 | 12 | 23 | 3.45 | 0
2017-12-12 | 12 | 0 | 6.9 | 0
2017-12-12 01:00 | 12 | 1 | 7.475 | 0
2017-12-12 02:00 | 12 | 2 | 0 | 0
2017-12-12 03:00 | 12 | 3 | 5.75 | 0
2017-12-12 04:00 | 12 | 4 | 8.625 | 286.6667
2017-12-12 05:00 | 12 | 5 | 9.2 | 286.6667
2017-12-12 06:00 | 12 | 6 | 17.25 | 4266.6667
2017-12-12 07:00 | 12 | 7 | 17.825 | 4266.6667
2017-12-12 08:00 | 12 | 8 | 16.1 | 2773.3333
2017-12-12 09:00 | 12 | 9 | 18.4 | 4266.6667
2017-12-12 10:00 | 12 | 10 | 17.825 | 4266.6667
2017-12-12 11:00 | 12 | 11 | 12.075 | 873.3333
2017-12-12 12:00 | 12 | 12 | 16.675 | 2773.3333
2017-12-12 13:00 | 12 | 13 | 17.825 | 4266.6667
2017-12-12 14:00 | 12 | 14 | 16.1 | 2773.3333
2017-12-12 15:00 | 12 | 15 | 13.225 | 1666.6667
2017-12-12 16:00 | 12 | 16 | 13.4167 | 1666.6667
2017-12-12 17:00 | 12 | 17 | 6.9 | 0
2017-12-12 18:00 | 12 | 18 | 12.65 | 1666.6667
2017-12-12 19:00 | 12 | 19 | 15.64 | 2773.3333
2017-12-12 20:00 | 12 | 20 | 12.65 | 1666.6667
2017-12-12 21:00 | 12 | 21 | 13.8 | 1666.6667
2017-12-12 22:00 | 12 | 22 | 13.8 | 1666.6667
2017-12-12 23:00 | 12 | 23 | 12.65 | 1666.6667
2017-12-13 | 12 | 0 | 17.25 | 4266.6667
2017-12-13 01:00 | 12 | 1 | 18.975 | 4266.6667
2017-12-13 02:00 | 12 | 2 | 19.55 | 6160
2017-12-13 03:00 | 12 | 3 | 25.3 | 9060
2017-12-13 04:00 | 12 | 4 | 24.725 | 9060
2017-12-13 05:00 | 12 | 5 | 19.55 | 6160
2017-12-13 06:00 | 12 | 6 | 26.45 | 9573.3333
2017-12-13 07:00 | 12 | 7 | 26.45 | 9573.3333
2017-12-13 08:00 | 12 | 8 | 25.3 | 9060
2017-12-13 09:00 | 12 | 9 | 20.7 | 6160
2017-12-13 10:00 | 12 | 10 | 14.95 | 2773.3333
2017-12-13 11:00 | 12 | 11 | 25.3 | 9060
2017-12-13 12:00 | 12 | 12 | 26.45 | 9573.3333
2017-12-13 13:00 | 12 | 13 | 29.325 | 9873.3333
2017-12-13 14:00 | 12 | 14 | 25.3 | 9060
2017-12-13 15:00 | 12 | 15 | 26.45 | 9573.3333
2017-12-13 16:00 | 12 | 16 | 25.875 | 9573.3333
2017-12-13 17:00 | 12 | 17 | 24.15 | 9060
2017-12-13 18:00 | 12 | 18 | 25.3 | 9060
2017-12-13 19:00 | 12 | 19 | 24.15 | 9060
2017-12-13 20:00 | 12 | 20 | 24.15 | 9060
2017-12-13 21:00 | 12 | 21 | 25.3 | 9060
2017-12-13 22:00 | 12 | 22 | 24.725 | 9060
2017-12-13 23:00 | 12 | 23 | 23 | 7873.3333
2017-12-14 | 12 | 0 | 23 | 7873.3333
2017-12-14 01:00 | 12 | 1 | 21.85 | 7873.3333
2017-12-14 02:00 | 12 | 2 | 18.4 | 4266.6667
2017-12-14 03:00 | 12 | 3 | 17.25 | 4266.6667
2017-12-14 04:00 | 12 | 4 | 16.675 | 2773.3333
2017-12-14 05:00 | 12 | 5 | 11.5 | 873.3333
2017-12-14 06:00 | 12 | 6 | 9.2 | 286.6667
2017-12-14 07:00 | 12 | 7 | 10.35 | 873.3333
2017-12-14 08:00 | 12 | 8 | 9.2 | 286.6667
2017-12-14 09:00 | 12 | 9 | 10.35 | 873.3333
2017-12-14 10:00 | 12 | 10 | 12.65 | 1666.6667
2017-12-14 11:00 | 12 | 11 | 18.4 | 4266.6667
2017-12-14 12:00 | 12 | 12 | 16.1 | 2773.3333
2017-12-14 13:00 | 12 | 13 | 20.7 | 6160
2017-12-14 14:00 | 12 | 14 | 17.25 | 4266.6667
2017-12-14 15:00 | 12 | 15 | 17.25 | 4266.6667
2017-12-14 16:00 | 12 | 16 | 17.25 | 4266.6667
2017-12-14 17:00 | 12 | 17 | 18.4 | 4266.6667
2017-12-14 18:00 | 12 | 18 | 23 | 7873.3333
2017-12-14 19:00 | 12 | 19 | 23 | 7873.3333
2017-12-14 20:00 | 12 | 20 | 17.25 | 4266.6667
2017-12-14 21:00 | 12 | 21 | 17.25 | 4266.6667
2017-12-14 22:00 | 12 | 22 | 17.25 | 4266.6667
2017-12-14 23:00 | 12 | 23 | 19.55 | 6160
2017-12-15 | 12 | 0 | 16.1 | 2773.3333
2017-12-15 01:00 | 12 | 1 | 13.8 | 1666.6667
2017-12-15 02:00 | 12 | 2 | 9.2 | 286.6667
2017-12-15 03:00 | 12 | 3 | 12.65 | 1666.6667
2017-12-15 04:00 | 12 | 4 | 10.35 | 873.3333
2017-12-15 05:00 | 12 | 5 | 10.35 | 873.3333
2017-12-15 06:00 | 12 | 6 | 8.05 | 286.6667
2017-12-15 07:00 | 12 | 7 | 9.2 | 286.6667
2017-12-15 08:00 | 12 | 8 | 6.9 | 0
2017-12-15 09:00 | 12 | 9 | 5.75 | 0
2017-12-15 10:00 | 12 | 10 | 5.75 | 0
2017-12-15 11:00 | 12 | 11 | 6.9 | 0
2017-12-15 12:00 | 12 | 12 | 6.9 | 0
2017-12-15 13:00 | 12 | 13 | 5.175 | 0
2017-12-15 14:00 | 12 | 14 | 9.2 | 286.6667
2017-12-15 15:00 | 12 | 15 | 6.9 | 0
2017-12-15 16:00 | 12 | 16 | 6.325 | 0
2017-12-15 17:00 | 12 | 17 | 0 | 0
2017-12-15 18:00 | 12 | 18 | 6.9 | 0
2017-12-15 19:00 | 12 | 19 | 8.05 | 286.6667
2017-12-15 20:00 | 12 | 20 | 10.35 | 873.3333
2017-12-15 21:00 | 12 | 21 | 12.65 | 1666.6667
2017-12-15 22:00 | 12 | 22 | 9.775 | 286.6667
2017-12-15 23:00 | 12 | 23 | 14.95 | 2773.3333
2017-12-16 | 12 | 0 | 12.65 | 1666.6667
2017-12-16 01:00 | 12 | 1 | 12.65 | 1666.6667
2017-12-16 02:00 | 12 | 2 | 14.95 | 2773.3333
2017-12-16 03:00 | 12 | 3 | 14.95 | 2773.3333
2017-12-16 04:00 | 12 | 4 | 14.95 | 2773.3333
2017-12-16 05:00 | 12 | 5 | 16.1 | 2773.3333
2017-12-16 06:00 | 12 | 6 | 10.35 | 873.3333
2017-12-16 07:00 | 12 | 7 | 10.925 | 873.3333
2017-12-16 08:00 | 12 | 8 | 17.25 | 4266.6667
2017-12-16 09:00 | 12 | 9 | 16.1 | 2773.3333
2017-12-16 10:00 | 12 | 10 | 20.7 | 6160
2017-12-16 11:00 | 12 | 11 | 19.55 | 6160
2017-12-16 12:00 | 12 | 12 | 18.4 | 4266.6667
2017-12-16 13:00 | 12 | 13 | 18.4 | 4266.6667
2017-12-16 14:00 | 12 | 14 | 17.25 | 4266.6667
2017-12-16 15:00 | 12 | 15 | 12.65 | 1666.6667
2017-12-16 16:00 | 12 | 16 | 16.675 | 2773.3333
2017-12-16 17:00 | 12 | 17 | 18.4 | 4266.6667
2017-12-16 18:00 | 12 | 18 | 19.55 | 6160
2017-12-16 19:00 | 12 | 19 | 17.825 | 4266.6667
2017-12-16 20:00 | 12 | 20 | 9.2 | 286.6667
2017-12-16 21:00 | 12 | 21 | 12.65 | 1666.6667
2017-12-16 22:00 | 12 | 22 | 12.075 | 873.3333
2017-12-16 23:00 | 12 | 23 | 12.65 | 1666.6667
2017-12-17 | 12 | 0 | 10.35 | 873.3333
2017-12-17 01:00 | 12 | 1 | 10.925 | 873.3333
2017-12-17 02:00 | 12 | 2 | 14.95 | 2773.3333
2017-12-17 03:00 | 12 | 3 | 12.65 | 1666.6667
2017-12-17 04:00 | 12 | 4 | 14.375 | 1666.6667
2017-12-17 05:00 | 12 | 5 | 14.95 | 2773.3333
2017-12-17 06:00 | 12 | 6 | 16.1 | 2773.3333
2017-12-17 07:00 | 12 | 7 | 12.65 | 1666.6667
2017-12-17 08:00 | 12 | 8 | 12.65 | 1666.6667
2017-12-17 09:00 | 12 | 9 | 14.95 | 2773.3333
2017-12-17 10:00 | 12 | 10 | 15.525 | 2773.3333
2017-12-17 11:00 | 12 | 11 | 12.65 | 1666.6667
2017-12-17 12:00 | 12 | 12 | 10.35 | 873.3333
2017-12-17 13:00 | 12 | 13 | 10.35 | 873.3333
2017-12-17 14:00 | 12 | 14 | 9.2 | 286.6667
2017-12-17 15:00 | 12 | 15 | 10.35 | 873.3333
2017-12-17 16:00 | 12 | 16 | 10.35 | 873.3333
2017-12-17 17:00 | 12 | 17 | 9.2 | 286.6667
2017-12-17 18:00 | 12 | 18 | 6.9 | 0
2017-12-17 19:00 | 12 | 19 | 7.475 | 0
2017-12-17 20:00 | 12 | 20 | 6.9 | 0
2017-12-17 21:00 | 12 | 21 | 9.2 | 286.6667
2017-12-17 22:00 | 12 | 22 | 8.05 | 286.6667
2017-12-17 23:00 | 12 | 23 | 3.45 | 0
2017-12-18 | 12 | 0 | 5.75 | 0
2017-12-18 01:00 | 12 | 1 | 6.9 | 0
2017-12-18 02:00 | 12 | 2 | 5.75 | 0
2017-12-18 03:00 | 12 | 3 | 5.75 | 0
2017-12-18 04:00 | 12 | 4 | 4.6 | 0
2017-12-18 05:00 | 12 | 5 | 3.45 | 0
2017-12-18 06:00 | 12 | 6 | 3.45 | 0
2017-12-18 07:00 | 12 | 7 | 1.725 | 0
2017-12-18 08:00 | 12 | 8 | 5.75 | 0
2017-12-18 09:00 | 12 | 9 | 0 | 0
2017-12-18 10:00 | 12 | 10 | 2.875 | 0
2017-12-18 11:00 | 12 | 11 | 0 | 0
2017-12-18 12:00 | 12 | 12 | 0 | 0
2017-12-18 13:00 | 12 | 13 | 1.725 | 0
2017-12-18 14:00 | 12 | 14 | 0 | 0
2017-12-18 15:00 | 12 | 15 | 6.9 | 0
2017-12-18 16:00 | 12 | 16 | 4.6 | 0
2017-12-18 17:00 | 12 | 17 | 4.6 | 0
2017-12-18 18:00 | 12 | 18 | 5.75 | 0
2017-12-18 19:00 | 12 | 19 | 3.0667 | 0
2017-12-18 20:00 | 12 | 20 | 9.2 | 286.6667
2017-12-18 21:00 | 12 | 21 | 6.325 | 0
2017-12-18 22:00 | 12 | 22 | 5.75 | 0
2017-12-18 23:00 | 12 | 23 | 9.2 | 286.6667
2017-12-19 | 12 | 0 | 8.05 | 286.6667
2017-12-19 01:00 | 12 | 1 | 7.475 | 0
2017-12-19 02:00 | 12 | 2 | 6.9 | 0
2017-12-19 03:00 | 12 | 3 | 10.35 | 873.3333
2017-12-19 04:00 | 12 | 4 | 10.35 | 873.3333
2017-12-19 05:00 | 12 | 5 | 8.05 | 286.6667
2017-12-19 06:00 | 12 | 6 | 5.75 | 0
2017-12-19 07:00 | 12 | 7 | 2.875 | 0
2017-12-19 08:00 | 12 | 8 | 10.35 | 873.3333
2017-12-19 09:00 | 12 | 9 | 19.55 | 6160
2017-12-19 10:00 | 12 | 10 | 17.825 | 4266.6667
2017-12-19 11:00 | 12 | 11 | 17.25 | 4266.6667
2017-12-19 12:00 | 12 | 12 | 16.1 | 2773.3333
2017-12-19 13:00 | 12 | 13 | 15.525 | 2773.3333
2017-12-19 14:00 | 12 | 14 | 11.5 | 873.3333
2017-12-19 15:00 | 12 | 15 | 18.4 | 4266.6667
2017-12-19 16:00 | 12 | 16 | 15.525 | 2773.3333
2017-12-19 17:00 | 12 | 17 | 10.35 | 873.3333
2017-12-19 18:00 | 12 | 18 | 18.4 | 4266.6667
2017-12-19 19:00 | 12 | 19 | 21.275 | 7873.3333
2017-12-19 20:00 | 12 | 20 | 20.7 | 6160
2017-12-19 21:00 | 12 | 21 | 19.55 | 6160
2017-12-19 22:00 | 12 | 22 | 17.25 | 4266.6667
2017-12-19 23:00 | 12 | 23 | 17.25 | 4266.6667
2017-12-20 | 12 | 0 | 14.95 | 2773.3333
2017-12-20 01:00 | 12 | 1 | 20.125 | 6160
2017-12-20 02:00 | 12 | 2 | 18.4 | 4266.6667
2017-12-20 03:00 | 12 | 3 | 19.55 | 6160
2017-12-20 04:00 | 12 | 4 | 18.4 | 4266.6667
2017-12-20 05:00 | 12 | 5 | 12.65 | 1666.6667
2017-12-20 06:00 | 12 | 6 | 14.95 | 2773.3333
2017-12-20 07:00 | 12 | 7 | 16.1 | 2773.3333
2017-12-20 08:00 | 12 | 8 | 23 | 7873.3333
2017-12-20 09:00 | 12 | 9 | 28.75 | 9873.3333
2017-12-20 10:00 | 12 | 10 | 27.025 | 9573.3333
2017-12-20 11:00 | 12 | 11 | 27.6 | 9573.3333
2017-12-20 12:00 | 12 | 12 | 17.25 | 4266.6667
2017-12-20 13:00 | 12 | 13 | 20.125 | 6160
2017-12-20 14:00 | 12 | 14 | 12.65 | 1666.6667
2017-12-20 15:00 | 12 | 15 | 19.55 | 6160
2017-12-20 16:00 | 12 | 16 | 17.825 | 4266.6667
2017-12-20 17:00 | 12 | 17 | 16.1 | 2773.3333
2017-12-20 18:00 | 12 | 18 | 10.35 | 873.3333
2017-12-20 19:00 | 12 | 19 | 10.35 | 873.3333
2017-12-20 20:00 | 12 | 20 | 12.65 | 1666.6667
2017-12-20 21:00 | 12 | 21 | 11.5 | 873.3333
2017-12-20 22:00 | 12 | 22 | 12.075 | 873.3333
2017-12-20 23:00 | 12 | 23 | 14.95 | 2773.3333
2017-12-21 | 12 | 0 | 11.5 | 873.3333
2017-12-21 01:00 | 12 | 1 | 12.075 | 873.3333
2017-12-21 02:00 | 12 | 2 | 12.65 | 1666.6667
2017-12-21 03:00 | 12 | 3 | 10.35 | 873.3333
2017-12-21 04:00 | 12 | 4 | 13.225 | 1666.6667
2017-12-21 05:00 | 12 | 5 | 10.35 | 873.3333
2017-12-21 06:00 | 12 | 6 | 20.7 | 6160
2017-12-21 07:00 | 12 | 7 | 20.125 | 6160
2017-12-21 08:00 | 12 | 8 | 16.1 | 2773.3333
2017-12-21 09:00 | 12 | 9 | 16.1 | 2773.3333
2017-12-21 10:00 | 12 | 10 | 15.525 | 2773.3333
2017-12-21 11:00 | 12 | 11 | 11.5 | 873.3333
2017-12-21 12:00 | 12 | 12 | 14.95 | 2773.3333
2017-12-21 13:00 | 12 | 13 | 12.075 | 873.3333
2017-12-21 14:00 | 12 | 14 | 9.2 | 286.6667
2017-12-21 15:00 | 12 | 15 | 9.2 | 286.6667
2017-12-21 16:00 | 12 | 16 | 9.2 | 286.6667
2017-12-21 17:00 | 12 | 17 | 6.9 | 0
2017-12-21 18:00 | 12 | 18 | 6.9 | 0
2017-12-21 19:00 | 12 | 19 | 6.9 | 0
2017-12-21 20:00 | 12 | 20 | 9.2 | 286.6667
2017-12-21 21:00 | 12 | 21 | 9.2 | 286.6667
2017-12-21 22:00 | 12 | 22 | 9.2 | 286.6667
2017-12-21 23:00 | 12 | 23 | 5.75 | 0
2017-12-22 | 12 | 0 | 9.2 | 286.6667
2017-12-22 01:00 | 12 | 1 | 8.625 | 286.6667
2017-12-22 02:00 | 12 | 2 | 9.2 | 286.6667
2017-12-22 03:00 | 12 | 3 | 9.2 | 286.6667
2017-12-22 04:00 | 12 | 4 | 8.625 | 286.6667
2017-12-22 05:00 | 12 | 5 | 8.05 | 286.6667
2017-12-22 06:00 | 12 | 6 | 8.05 | 286.6667
2017-12-22 07:00 | 12 | 7 | 8.05 | 286.6667
2017-12-22 08:00 | 12 | 8 | 6.9 | 0
2017-12-22 09:00 | 12 | 9 | 5.75 | 0
2017-12-22 10:00 | 12 | 10 | 5.75 | 0
2017-12-22 11:00 | 12 | 11 | 8.625 | 286.6667
2017-12-22 12:00 | 12 | 12 | 10.35 | 873.3333
2017-12-22 13:00 | 12 | 13 | 10.7333 | 873.3333
2017-12-22 14:00 | 12 | 14 | 14.95 | 2773.3333
2017-12-22 15:00 | 12 | 15 | 16.1 | 2773.3333
2017-12-22 16:00 | 12 | 16 | 13.8 | 1666.6667
2017-12-22 17:00 | 12 | 17 | 10.35 | 873.3333
2017-12-22 18:00 | 12 | 18 | 17.25 | 4266.6667
2017-12-22 19:00 | 12 | 19 | 14.95 | 2773.3333
2017-12-22 20:00 | 12 | 20 | 10.35 | 873.3333
2017-12-22 21:00 | 12 | 21 | 8.05 | 286.6667
2017-12-22 22:00 | 12 | 22 | 9.66 | 286.6667
2017-12-22 23:00 | 12 | 23 | 11.7875 | 873.3333
2017-12-23 | 12 | 0 | 12.65 | 1666.6667
2017-12-23 01:00 | 12 | 1 | 9.2 | 286.6667
2017-12-23 02:00 | 12 | 2 | 8.05 | 286.6667
2017-12-23 03:00 | 12 | 3 | 10.925 | 873.3333
2017-12-23 04:00 | 12 | 4 | 10.35 | 873.3333
2017-12-23 05:00 | 12 | 5 | 9.2 | 286.6667
2017-12-23 06:00 | 12 | 6 | 8.4333 | 286.6667
2017-12-23 07:00 | 12 | 7 | 8.05 | 286.6667
2017-12-23 08:00 | 12 | 8 | 5.175 | 0
2017-12-23 09:00 | 12 | 9 | 6.5167 | 0
2017-12-23 10:00 | 12 | 10 | 5.75 | 0
2017-12-23 11:00 | 12 | 11 | 5.75 | 0
2017-12-23 12:00 | 12 | 12 | 6.9 | 0
2017-12-23 13:00 | 12 | 13 | 5.75 | 0
2017-12-23 14:00 | 12 | 14 | 9.2 | 286.6667
2017-12-23 15:00 | 12 | 15 | 9.2 | 286.6667
2017-12-23 16:00 | 12 | 16 | 8.05 | 286.6667
2017-12-23 17:00 | 12 | 17 | 9.2 | 286.6667
2017-12-23 18:00 | 12 | 18 | 12.65 | 1666.6667
2017-12-23 19:00 | 12 | 19 | 8.05 | 286.6667
2017-12-23 20:00 | 12 | 20 | 17.25 | 4266.6667
2017-12-23 21:00 | 12 | 21 | 14.95 | 2773.3333
2017-12-23 22:00 | 12 | 22 | 14.95 | 2773.3333
2017-12-23 23:00 | 12 | 23 | 14.95 | 2773.3333
2017-12-24 | 12 | 0 | 11.5 | 873.3333
2017-12-24 01:00 | 12 | 1 | 13.8 | 1666.6667
2017-12-24 02:00 | 12 | 2 | 12.65 | 1666.6667
2017-12-24 03:00 | 12 | 3 | 10.35 | 873.3333
2017-12-24 04:00 | 12 | 4 | 9.775 | 286.6667
2017-12-24 05:00 | 12 | 5 | 12.65 | 1666.6667
2017-12-24 06:00 | 12 | 6 | 8.05 | 286.6667
2017-12-24 07:00 | 12 | 7 | 8.05 | 286.6667
2017-12-24 08:00 | 12 | 8 | 8.05 | 286.6667
2017-12-24 09:00 | 12 | 9 | 10.7333 | 873.3333
2017-12-24 10:00 | 12 | 10 | 10.925 | 873.3333
2017-12-24 11:00 | 12 | 11 | 9.2 | 286.6667
2017-12-24 12:00 | 12 | 12 | 11.5 | 873.3333
2017-12-24 13:00 | 12 | 13 | 10.925 | 873.3333
2017-12-24 14:00 | 12 | 14 | 11.5 | 873.3333
2017-12-24 15:00 | 12 | 15 | 8.05 | 286.6667
2017-12-24 16:00 | 12 | 16 | 8.05 | 286.6667
2017-12-24 17:00 | 12 | 17 | 9.2 | 286.6667
2017-12-24 18:00 | 12 | 18 | 9.2 | 286.6667
2017-12-24 19:00 | 12 | 19 | 14.375 | 1666.6667
2017-12-24 20:00 | 12 | 20 | 19.55 | 6160
2017-12-24 21:00 | 12 | 21 | 21.275 | 7873.3333
2017-12-24 22:00 | 12 | 22 | 21.5625 | 7873.3333
2017-12-24 23:00 | 12 | 23 | 23 | 7873.3333
2017-12-25 | 12 | 0 | 26.45 | 9573.3333
2017-12-25 01:00 | 12 | 1 | 25.3 | 9060
2017-12-25 02:00 | 12 | 2 | 24.15 | 9060
2017-12-25 03:00 | 12 | 3 | 25.3 | 9060
2017-12-25 04:00 | 12 | 4 | 25.5875 | 9060
2017-12-25 05:00 | 12 | 5 | 27.2167 | 9573.3333
2017-12-25 06:00 | 12 | 6 | 20.7 | 6160
2017-12-25 07:00 | 12 | 7 | 17.02 | 4266.6667
2017-12-25 08:00 | 12 | 8 | 19.9333 | 6160
2017-12-25 09:00 | 12 | 9 | 28.75 | 9873.3333
2017-12-25 10:00 | 12 | 10 | 25.07 | 9060
2017-12-25 11:00 | 12 | 11 | 20.4125 | 6160
2017-12-25 12:00 | 12 | 12 | 12.65 | 1666.6667
2017-12-25 13:00 | 12 | 13 | 13.225 | 1666.6667
2017-12-25 14:00 | 12 | 14 | 28.75 | 9873.3333
2017-12-25 15:00 | 12 | 15 | 23 | 7873.3333
2017-12-25 16:00 | 12 | 16 | 21.275 | 7873.3333
2017-12-25 17:00 | 12 | 17 | 18.4 | 4266.6667
2017-12-25 18:00 | 12 | 18 | 24.15 | 9060
2017-12-25 19:00 | 12 | 19 | 22.425 | 7873.3333
2017-12-25 20:00 | 12 | 20 | 20.7 | 6160
2017-12-25 21:00 | 12 | 21 | 26.45 | 9573.3333
2017-12-25 22:00 | 12 | 22 | 23.575 | 9060
2017-12-25 23:00 | 12 | 23 | 17.25 | 4266.6667
2017-12-26 | 12 | 0 | 18.4 | 4266.6667
2017-12-26 01:00 | 12 | 1 | 17.25 | 4266.6667
2017-12-26 02:00 | 12 | 2 | 18.4 | 4266.6667
2017-12-26 03:00 | 12 | 3 | 17.25 | 4266.6667
2017-12-26 04:00 | 12 | 4 | 17.825 | 4266.6667
2017-12-26 05:00 | 12 | 5 | 14.95 | 2773.3333
2017-12-26 06:00 | 12 | 6 | 10.35 | 873.3333
2017-12-26 07:00 | 12 | 7 | 10.35 | 873.3333
2017-12-26 08:00 | 12 | 8 | 17.25 | 4266.6667
2017-12-26 09:00 | 12 | 9 | 19.55 | 6160
2017-12-26 10:00 | 12 | 10 | 19.55 | 6160
2017-12-26 11:00 | 12 | 11 | 29.9 | 9873.3333
2017-12-26 12:00 | 12 | 12 | 23 | 7873.3333
2017-12-26 13:00 | 12 | 13 | 21.275 | 7873.3333
2017-12-26 14:00 | 12 | 14 | 18.4 | 4266.6667
2017-12-26 15:00 | 12 | 15 | 14.95 | 2773.3333
2017-12-26 16:00 | 12 | 16 | 15.525 | 2773.3333
2017-12-26 17:00 | 12 | 17 | 12.65 | 1666.6667
2017-12-26 18:00 | 12 | 18 | 20.7 | 6160
2017-12-26 19:00 | 12 | 19 | 17.25 | 4266.6667
2017-12-26 20:00 | 12 | 20 | 17.25 | 4266.6667
2017-12-26 21:00 | 12 | 21 | 19.55 | 6160
2017-12-26 22:00 | 12 | 22 | 15.525 | 2773.3333
2017-12-26 23:00 | 12 | 23 | 19.55 | 6160
2017-12-27 | 12 | 0 | 14.95 | 2773.3333
2017-12-27 01:00 | 12 | 1 | 14.95 | 2773.3333
2017-12-27 02:00 | 12 | 2 | 11.5 | 873.3333
2017-12-27 03:00 | 12 | 3 | 16.1 | 2773.3333
2017-12-27 04:00 | 12 | 4 | 17.25 | 4266.6667
2017-12-27 05:00 | 12 | 5 | 17.25 | 4266.6667
2017-12-27 06:00 | 12 | 6 | 16.1 | 2773.3333
2017-12-27 07:00 | 12 | 7 | 16.675 | 2773.3333
2017-12-27 08:00 | 12 | 8 | 14.95 | 2773.3333
2017-12-27 09:00 | 12 | 9 | 12.65 | 1666.6667
2017-12-27 10:00 | 12 | 10 | 12.65 | 1666.6667
2017-12-27 11:00 | 12 | 11 | 14.95 | 2773.3333
2017-12-27 12:00 | 12 | 12 | 16.1 | 2773.3333
2017-12-27 13:00 | 12 | 13 | 14.375 | 1666.6667
2017-12-27 14:00 | 12 | 14 | 16.1 | 2773.3333
2017-12-27 15:00 | 12 | 15 | 16.1 | 2773.3333
2017-12-27 16:00 | 12 | 16 | 15.525 | 2773.3333
2017-12-27 17:00 | 12 | 17 | 12.65 | 1666.6667
2017-12-27 18:00 | 12 | 18 | 17.25 | 4266.6667
2017-12-27 19:00 | 12 | 19 | 17.25 | 4266.6667
2017-12-27 20:00 | 12 | 20 | 16.1 | 2773.3333
2017-12-27 21:00 | 12 | 21 | 12.65 | 1666.6667
2017-12-27 22:00 | 12 | 22 | 14.375 | 1666.6667
2017-12-27 23:00 | 12 | 23 | 17.25 | 4266.6667
2017-12-28 | 12 | 0 | 17.25 | 4266.6667
2017-12-28 01:00 | 12 | 1 | 17.825 | 4266.6667
2017-12-28 02:00 | 12 | 2 | 14.95 | 2773.3333
2017-12-28 03:00 | 12 | 3 | 12.65 | 1666.6667
2017-12-28 04:00 | 12 | 4 | 13.8 | 1666.6667
2017-12-28 05:00 | 12 | 5 | 20.7 | 6160
2017-12-28 06:00 | 12 | 6 | 17.25 | 4266.6667
2017-12-28 07:00 | 12 | 7 | 17.825 | 4266.6667
2017-12-28 08:00 | 12 | 8 | 20.7 | 6160
2017-12-28 09:00 | 12 | 9 | 24.15 | 9060
2017-12-28 10:00 | 12 | 10 | 28.175 | 9873.3333
2017-12-28 11:00 | 12 | 11 | 29.9 | 9873.3333
2017-12-28 12:00 | 12 | 12 | 25.3 | 9060
2017-12-28 13:00 | 12 | 13 | 27.025 | 9573.3333
2017-12-28 14:00 | 12 | 14 | 24.725 | 9060
2017-12-28 15:00 | 12 | 15 | 19.55 | 6160
2017-12-28 16:00 | 12 | 16 | 20.125 | 6160
2017-12-28 17:00 | 12 | 17 | 19.55 | 6160
2017-12-28 18:00 | 12 | 18 | 17.25 | 4266.6667
2017-12-28 19:00 | 12 | 19 | 17.25 | 4266.6667
2017-12-28 20:00 | 12 | 20 | 18.4 | 4266.6667
2017-12-28 21:00 | 12 | 21 | 16.1 | 2773.3333
2017-12-28 22:00 | 12 | 22 | 13.8 | 1666.6667
2017-12-28 23:00 | 12 | 23 | 17.25 | 4266.6667
2017-12-29 | 12 | 0 | 12.65 | 1666.6667
2017-12-29 01:00 | 12 | 1 | 11.5 | 873.3333
2017-12-29 02:00 | 12 | 2 | 12.65 | 1666.6667
2017-12-29 03:00 | 12 | 3 | 16.1 | 2773.3333
2017-12-29 04:00 | 12 | 4 | 13.8 | 1666.6667
2017-12-29 05:00 | 12 | 5 | 6.9 | 0
2017-12-29 06:00 | 12 | 6 | 10.35 | 873.3333
2017-12-29 07:00 | 12 | 7 | 10.35 | 873.3333
2017-12-29 08:00 | 12 | 8 | 9.2 | 286.6667
2017-12-29 09:00 | 12 | 9 | 9.2 | 286.6667
2017-12-29 10:00 | 12 | 10 | 9.775 | 286.6667
2017-12-29 11:00 | 12 | 11 | 11.5 | 873.3333
2017-12-29 12:00 | 12 | 12 | 11.5 | 873.3333
2017-12-29 13:00 | 12 | 13 | 11.5 | 873.3333
2017-12-29 14:00 | 12 | 14 | 10.35 | 873.3333
2017-12-29 15:00 | 12 | 15 | 19.55 | 6160
2017-12-29 16:00 | 12 | 16 | 17.25 | 4266.6667
2017-12-29 17:00 | 12 | 17 | 19.55 | 6160
2017-12-29 18:00 | 12 | 18 | 20.7 | 6160
2017-12-29 19:00 | 12 | 19 | 18.975 | 4266.6667
2017-12-29 20:00 | 12 | 20 | 16.1 | 2773.3333
2017-12-29 21:00 | 12 | 21 | 14.95 | 2773.3333
2017-12-29 22:00 | 12 | 22 | 14.95 | 2773.3333
2017-12-29 23:00 | 12 | 23 | 18.4 | 4266.6667
2017-12-30 | 12 | 0 | 19.55 | 6160
2017-12-30 01:00 | 12 | 1 | 18.975 | 4266.6667
2017-12-30 02:00 | 12 | 2 | 10.35 | 873.3333
2017-12-30 03:00 | 12 | 3 | 11.5 | 873.3333
2017-12-30 04:00 | 12 | 4 | 13.225 | 1666.6667
2017-12-30 05:00 | 12 | 5 | 10.35 | 873.3333
2017-12-30 06:00 | 12 | 6 | 11.5 | 873.3333
2017-12-30 07:00 | 12 | 7 | 11.5 | 873.3333
2017-12-30 08:00 | 12 | 8 | 9.2 | 286.6667
2017-12-30 09:00 | 12 | 9 | 14.95 | 2773.3333
2017-12-30 10:00 | 12 | 10 | 10.925 | 873.3333
2017-12-30 11:00 | 12 | 11 | 6.9 | 0
2017-12-30 12:00 | 12 | 12 | 5.75 | 0
2017-12-30 13:00 | 12 | 13 | 6.1333 | 0
2017-12-30 14:00 | 12 | 14 | 8.05 | 286.6667
2017-12-30 15:00 | 12 | 15 | 7.475 | 0
2017-12-30 16:00 | 12 | 16 | 6.0375 | 0
2017-12-30 17:00 | 12 | 17 | 4.6 | 0
2017-12-30 18:00 | 12 | 18 | 8.05 | 286.6667
2017-12-30 19:00 | 12 | 19 | 8.05 | 286.6667
2017-12-30 20:00 | 12 | 20 | 8.05 | 286.6667
2017-12-30 21:00 | 12 | 21 | 10.35 | 873.3333
2017-12-30 22:00 | 12 | 22 | 10.35 | 873.3333
2017-12-30 23:00 | 12 | 23 | 11.5 | 873.3333
2017-12-31 | 12 | 0 | 11.5 | 873.3333
2017-12-31 01:00 | 12 | 1 | 11.5 | 873.3333
2017-12-31 02:00 | 12 | 2 | 14.95 | 2773.3333
2017-12-31 03:00 | 12 | 3 | 14.95 | 2773.3333
2017-12-31 04:00 | 12 | 4 | 15.525 | 2773.3333
2017-12-31 05:00 | 12 | 5 | 17.25 | 4266.6667
2017-12-31 06:00 | 12 | 6 | 17.25 | 4266.6667
2017-12-31 07:00 | 12 | 7 | 16.675 | 2773.3333
2017-12-31 08:00 | 12 | 8 | 19.55 | 6160
2017-12-31 09:00 | 12 | 9 | 24.15 | 9060
2017-12-31 10:00 | 12 | 10 | 22.425 | 7873.3333
2017-12-31 11:00 | 12 | 11 | 19.55 | 6160
2017-12-31 12:00 | 12 | 12 | 23 | 7873.3333
2017-12-31 13:00 | 12 | 13 | 21.275 | 7873.3333
2017-12-31 14:00 | 12 | 14 | 19.55 | 6160
2017-12-31 15:00 | 12 | 15 | 20.7 | 6160
2017-12-31 16:00 | 12 | 16 | 18.975 | 4266.6667
2017-12-31 17:00 | 12 | 17 | 16.1 | 2773.3333
2017-12-31 18:00 | 12 | 18 | 18.4 | 4266.6667
2017-12-31 19:00 | 12 | 19 | 17.25 | 4266.6667
2017-12-31 20:00 | 12 | 20 | 14.95 | 2773.3333
2017-12-31 21:00 | 12 | 21 | 20.7 | 6160
2017-12-31 22:00 | 12 | 22 | 12.65 | 1666.6667
2017-12-31 23:00 | 12 | 23 | 19.55 | 6160
Formulas:
From: = [From:, row above]+1/24

## Solar Output
|  |  | Capacity Factor: | 15.77%
DC System Size | 10 |  | 9217.0626 | 14989898.1391
Date-time | month | hour | AC System Output (W) | Size Adjusted Output
2017-01-01 | 1 | 0 | 0 | 0 | Source: | https://pvwatts.nrel.gov/pvwatts.php
2017-01-01 01:00 | 1 | 1 | 0 | 0 | PVWatts: Hourly PV Performance Data
2017-01-01 02:00 | 1 | 2 | 0 | 0 | Requested Location: | boston, MA
2017-01-01 03:00 | 1 | 3 | 0 | 0 | Location: | Lat, Lon: 42.37, -71.06
2017-01-01 04:00 | 1 | 4 | 0 | 0 | Lat (deg N): | 42.37
2017-01-01 05:00 | 1 | 5 | 0 | 0 | Long (deg W): | 71.06
2017-01-01 06:00 | 1 | 6 | 0 | 0 | Elev (m): | 15.48
2017-01-01 07:00 | 1 | 7 | 0 | 0 | DC System Size (kW): | 10
2017-01-01 08:00 | 1 | 8 | 708.2896 | 708.2896 | Module Type: | Standard
2017-01-01 09:00 | 1 | 9 | 1129.5231 | 1129.5231 | Array Type: | Fixed (open rack)
2017-01-01 10:00 | 1 | 10 | 1224.4694 | 1224.4694 | Array Tilt (deg): | 20
2017-01-01 11:00 | 1 | 11 | 1659.0774 | 1659.0774 | Array Azimuth (deg): | 180
2017-01-01 12:00 | 1 | 12 | 2055.2789 | 2055.2789 | System Losses: | 14.08
2017-01-01 13:00 | 1 | 13 | 1889.7156 | 1889.7156 | Invert Efficiency: | 96
2017-01-01 14:00 | 1 | 14 | 628.8913 | 628.8913 | DC to AC Size Ratio: | 1.2
2017-01-01 15:00 | 1 | 15 | 394.1476 | 394.1476 | Average Cost of Electricity Purchased from Utility ($/kWh): | 0.149
2017-01-01 16:00 | 1 | 16 | 0 | 0 | Capacity Factor (%) | 14.9
2017-01-01 17:00 | 1 | 17 | 0 | 0
2017-01-01 18:00 | 1 | 18 | 0 | 0
2017-01-01 19:00 | 1 | 19 | 0 | 0
2017-01-01 20:00 | 1 | 20 | 0 | 0
2017-01-01 21:00 | 1 | 21 | 0 | 0
2017-01-01 22:00 | 1 | 22 | 0 | 0
2017-01-01 23:00 | 1 | 23 | 0 | 0
2017-01-02 | 1 | 0 | 0 | 0
2017-01-02 01:00 | 1 | 1 | 0 | 0
2017-01-02 02:00 | 1 | 2 | 0 | 0
2017-01-02 03:00 | 1 | 3 | 0 | 0
2017-01-02 04:00 | 1 | 4 | 0 | 0
2017-01-02 05:00 | 1 | 5 | 0 | 0
2017-01-02 06:00 | 1 | 6 | 0 | 0
2017-01-02 07:00 | 1 | 7 | 0 | 0
2017-01-02 08:00 | 1 | 8 | 56.3028 | 56.3028
2017-01-02 09:00 | 1 | 9 | 576.1557 | 576.1557
2017-01-02 10:00 | 1 | 10 | 1431.367 | 1431.367
2017-01-02 11:00 | 1 | 11 | 1858.0987 | 1858.0987
2017-01-02 12:00 | 1 | 12 | 1415.5718 | 1415.5718
2017-01-02 13:00 | 1 | 13 | 1486.8292 | 1486.8292
2017-01-02 14:00 | 1 | 14 | 781.2559 | 781.2559
2017-01-02 15:00 | 1 | 15 | 233.3545 | 233.3545
2017-01-02 16:00 | 1 | 16 | 0 | 0
2017-01-02 17:00 | 1 | 17 | 0 | 0
2017-01-02 18:00 | 1 | 18 | 0 | 0
2017-01-02 19:00 | 1 | 19 | 0 | 0
2017-01-02 20:00 | 1 | 20 | 0 | 0
2017-01-02 21:00 | 1 | 21 | 0 | 0
2017-01-02 22:00 | 1 | 22 | 0 | 0
2017-01-02 23:00 | 1 | 23 | 0 | 0
2017-01-03 | 1 | 0 | 0 | 0
2017-01-03 01:00 | 1 | 1 | 0 | 0
2017-01-03 02:00 | 1 | 2 | 0 | 0
2017-01-03 03:00 | 1 | 3 | 0 | 0
2017-01-03 04:00 | 1 | 4 | 0 | 0
2017-01-03 05:00 | 1 | 5 | 0 | 0
2017-01-03 06:00 | 1 | 6 | 0 | 0
2017-01-03 07:00 | 1 | 7 | 0 | 0
2017-01-03 08:00 | 1 | 8 | 2298.1554 | 2298.1554
2017-01-03 09:00 | 1 | 9 | 355.7939 | 355.7939
2017-01-03 10:00 | 1 | 10 | 794.3579 | 794.3579
2017-01-03 11:00 | 1 | 11 | 1494.9402 | 1494.9402
2017-01-03 12:00 | 1 | 12 | 2408.8038 | 2408.8038
2017-01-03 13:00 | 1 | 13 | 1058.008 | 1058.008
2017-01-03 14:00 | 1 | 14 | 140.9877 | 140.9877
2017-01-03 15:00 | 1 | 15 | 591.491 | 591.491
2017-01-03 16:00 | 1 | 16 | 0 | 0
2017-01-03 17:00 | 1 | 17 | 0 | 0
2017-01-03 18:00 | 1 | 18 | 0 | 0
2017-01-03 19:00 | 1 | 19 | 0 | 0
2017-01-03 20:00 | 1 | 20 | 0 | 0
2017-01-03 21:00 | 1 | 21 | 0 | 0
2017-01-03 22:00 | 1 | 22 | 0 | 0
2017-01-03 23:00 | 1 | 23 | 0 | 0
2017-01-04 | 1 | 0 | 0 | 0
2017-01-04 01:00 | 1 | 1 | 0 | 0
2017-01-04 02:00 | 1 | 2 | 0 | 0
2017-01-04 03:00 | 1 | 3 | 0 | 0
2017-01-04 04:00 | 1 | 4 | 0 | 0
2017-01-04 05:00 | 1 | 5 | 0 | 0
2017-01-04 06:00 | 1 | 6 | 0 | 0
2017-01-04 07:00 | 1 | 7 | 733.6448 | 733.6448
2017-01-04 08:00 | 1 | 8 | 3144.2943 | 3144.2943
2017-01-04 09:00 | 1 | 9 | 5160.0902 | 5160.0902
2017-01-04 10:00 | 1 | 10 | 3703.1104 | 3703.1104
2017-01-04 11:00 | 1 | 11 | 3526.8016 | 3526.8016
2017-01-04 12:00 | 1 | 12 | 3210.4377 | 3210.4377
2017-01-04 13:00 | 1 | 13 | 3272.2894 | 3272.2894
2017-01-04 14:00 | 1 | 14 | 4464.185 | 4464.185
2017-01-04 15:00 | 1 | 15 | 2245.505 | 2245.505
2017-01-04 16:00 | 1 | 16 | 0 | 0
2017-01-04 17:00 | 1 | 17 | 0 | 0
2017-01-04 18:00 | 1 | 18 | 0 | 0
2017-01-04 19:00 | 1 | 19 | 0 | 0
2017-01-04 20:00 | 1 | 20 | 0 | 0
2017-01-04 21:00 | 1 | 21 | 0 | 0
2017-01-04 22:00 | 1 | 22 | 0 | 0
2017-01-04 23:00 | 1 | 23 | 0 | 0
2017-01-05 | 1 | 0 | 0 | 0
2017-01-05 01:00 | 1 | 1 | 0 | 0
2017-01-05 02:00 | 1 | 2 | 0 | 0
2017-01-05 03:00 | 1 | 3 | 0 | 0
2017-01-05 04:00 | 1 | 4 | 0 | 0
2017-01-05 05:00 | 1 | 5 | 0 | 0
2017-01-05 06:00 | 1 | 6 | 0 | 0
2017-01-05 07:00 | 1 | 7 | 707.3707 | 707.3707
2017-01-05 08:00 | 1 | 8 | 3028.0374 | 3028.0374
2017-01-05 09:00 | 1 | 9 | 655.6265 | 655.6265
2017-01-05 10:00 | 1 | 10 | 1927.0918 | 1927.0918
2017-01-05 11:00 | 1 | 11 | 3099.8158 | 3099.8158
2017-01-05 12:00 | 1 | 12 | 2959.3812 | 2959.3812
2017-01-05 13:00 | 1 | 13 | 2077.6314 | 2077.6314
2017-01-05 14:00 | 1 | 14 | 2572.4649 | 2572.4649
2017-01-05 15:00 | 1 | 15 | 2092.4733 | 2092.4733
2017-01-05 16:00 | 1 | 16 | 0 | 0
2017-01-05 17:00 | 1 | 17 | 0 | 0
2017-01-05 18:00 | 1 | 18 | 0 | 0
2017-01-05 19:00 | 1 | 19 | 0 | 0
2017-01-05 20:00 | 1 | 20 | 0 | 0
2017-01-05 21:00 | 1 | 21 | 0 | 0
2017-01-05 22:00 | 1 | 22 | 0 | 0
2017-01-05 23:00 | 1 | 23 | 0 | 0
2017-01-06 | 1 | 0 | 0 | 0
2017-01-06 01:00 | 1 | 1 | 0 | 0
2017-01-06 02:00 | 1 | 2 | 0 | 0
2017-01-06 03:00 | 1 | 3 | 0 | 0
2017-01-06 04:00 | 1 | 4 | 0 | 0
2017-01-06 05:00 | 1 | 5 | 0 | 0
2017-01-06 06:00 | 1 | 6 | 0 | 0
2017-01-06 07:00 | 1 | 7 | 726.1974 | 726.1974
2017-01-06 08:00 | 1 | 8 | 3066.0667 | 3066.0667
2017-01-06 09:00 | 1 | 9 | 5005.4969 | 5005.4969
2017-01-06 10:00 | 1 | 10 | 6386.134 | 6386.134
2017-01-06 11:00 | 1 | 11 | 6955.9417 | 6955.9417
2017-01-06 12:00 | 1 | 12 | 6795.2833 | 6795.2833
2017-01-06 13:00 | 1 | 13 | 5947.2825 | 5947.2825
2017-01-06 14:00 | 1 | 14 | 2867.7998 | 2867.7998
2017-01-06 15:00 | 1 | 15 | 1499.5413 | 1499.5413
2017-01-06 16:00 | 1 | 16 | 0 | 0
2017-01-06 17:00 | 1 | 17 | 0 | 0
2017-01-06 18:00 | 1 | 18 | 0 | 0
2017-01-06 19:00 | 1 | 19 | 0 | 0
2017-01-06 20:00 | 1 | 20 | 0 | 0
2017-01-06 21:00 | 1 | 21 | 0 | 0
2017-01-06 22:00 | 1 | 22 | 0 | 0
2017-01-06 23:00 | 1 | 23 | 0 | 0
2017-01-07 | 1 | 0 | 0 | 0
2017-01-07 01:00 | 1 | 1 | 0 | 0
2017-01-07 02:00 | 1 | 2 | 0 | 0
2017-01-07 03:00 | 1 | 3 | 0 | 0
2017-01-07 04:00 | 1 | 4 | 0 | 0
2017-01-07 05:00 | 1 | 5 | 0 | 0
2017-01-07 06:00 | 1 | 6 | 0 | 0
2017-01-07 07:00 | 1 | 7 | 173.4545 | 173.4545
2017-01-07 08:00 | 1 | 8 | 3075.5278 | 3075.5278
2017-01-07 09:00 | 1 | 9 | 5064.7897 | 5064.7897
2017-01-07 10:00 | 1 | 10 | 6355.6268 | 6355.6268
2017-01-07 11:00 | 1 | 11 | 6946.4221 | 6946.422
2017-01-07 12:00 | 1 | 12 | 6827.9594 | 6827.9594
2017-01-07 13:00 | 1 | 13 | 5979.8079 | 5979.8079
2017-01-07 14:00 | 1 | 14 | 4377.5842 | 4377.5842
2017-01-07 15:00 | 1 | 15 | 2281.1331 | 2281.1331
2017-01-07 16:00 | 1 | 16 | 0 | 0
2017-01-07 17:00 | 1 | 17 | 0 | 0
2017-01-07 18:00 | 1 | 18 | 0 | 0
2017-01-07 19:00 | 1 | 19 | 0 | 0
2017-01-07 20:00 | 1 | 20 | 0 | 0
2017-01-07 21:00 | 1 | 21 | 0 | 0
2017-01-07 22:00 | 1 | 22 | 0 | 0
2017-01-07 23:00 | 1 | 23 | 0 | 0
2017-01-08 | 1 | 0 | 0 | 0
2017-01-08 01:00 | 1 | 1 | 0 | 0
2017-01-08 02:00 | 1 | 2 | 0 | 0
2017-01-08 03:00 | 1 | 3 | 0 | 0
2017-01-08 04:00 | 1 | 4 | 0 | 0
2017-01-08 05:00 | 1 | 5 | 0 | 0
2017-01-08 06:00 | 1 | 6 | 0 | 0
2017-01-08 07:00 | 1 | 7 | 26.2648 | 26.2648
2017-01-08 08:00 | 1 | 8 | 311.8742 | 311.8742
2017-01-08 09:00 | 1 | 9 | 2820.7211 | 2820.7211
2017-01-08 10:00 | 1 | 10 | 1591.439 | 1591.439
2017-01-08 11:00 | 1 | 11 | 4101.598 | 4101.598
2017-01-08 12:00 | 1 | 12 | 682.5583 | 682.5583
2017-01-08 13:00 | 1 | 13 | 932.5568 | 932.5568
2017-01-08 14:00 | 1 | 14 | 812.8832 | 812.8832
2017-01-08 15:00 | 1 | 15 | 477.2833 | 477.2833
2017-01-08 16:00 | 1 | 16 | 0 | 0
2017-01-08 17:00 | 1 | 17 | 0 | 0
2017-01-08 18:00 | 1 | 18 | 0 | 0
2017-01-08 19:00 | 1 | 19 | 0 | 0
2017-01-08 20:00 | 1 | 20 | 0 | 0
2017-01-08 21:00 | 1 | 21 | 0 | 0
2017-01-08 22:00 | 1 | 22 | 0 | 0
2017-01-08 23:00 | 1 | 23 | 0 | 0
2017-01-09 | 1 | 0 | 0 | 0
2017-01-09 01:00 | 1 | 1 | 0 | 0
2017-01-09 02:00 | 1 | 2 | 0 | 0
2017-01-09 03:00 | 1 | 3 | 0 | 0
2017-01-09 04:00 | 1 | 4 | 0 | 0
2017-01-09 05:00 | 1 | 5 | 0 | 0
2017-01-09 06:00 | 1 | 6 | 0 | 0
2017-01-09 07:00 | 1 | 7 | 760.1132 | 760.1132
2017-01-09 08:00 | 1 | 8 | 3231.9393 | 3231.9393
2017-01-09 09:00 | 1 | 9 | 5361.0067 | 5361.0067
2017-01-09 10:00 | 1 | 10 | 6734.8232 | 6734.8232
2017-01-09 11:00 | 1 | 11 | 7324.5248 | 7324.5248
2017-01-09 12:00 | 1 | 12 | 7204.1899 | 7204.1899
2017-01-09 13:00 | 1 | 13 | 6368.6068 | 6368.6068
2017-01-09 14:00 | 1 | 14 | 4803.1038 | 4803.1038
2017-01-09 15:00 | 1 | 15 | 2573.5114 | 2573.5114
2017-01-09 16:00 | 1 | 16 | 0 | 0
2017-01-09 17:00 | 1 | 17 | 0 | 0
2017-01-09 18:00 | 1 | 18 | 0 | 0
2017-01-09 19:00 | 1 | 19 | 0 | 0
2017-01-09 20:00 | 1 | 20 | 0 | 0
2017-01-09 21:00 | 1 | 21 | 0 | 0
2017-01-09 22:00 | 1 | 22 | 0 | 0
2017-01-09 23:00 | 1 | 23 | 0 | 0
2017-01-10 | 1 | 0 | 0 | 0
2017-01-10 01:00 | 1 | 1 | 0 | 0
2017-01-10 02:00 | 1 | 2 | 0 | 0
2017-01-10 03:00 | 1 | 3 | 0 | 0
2017-01-10 04:00 | 1 | 4 | 0 | 0
2017-01-10 05:00 | 1 | 5 | 0 | 0
2017-01-10 06:00 | 1 | 6 | 0 | 0
2017-01-10 07:00 | 1 | 7 | 802.1273 | 802.1273
2017-01-10 08:00 | 1 | 8 | 3259.0839 | 3259.0839
2017-01-10 09:00 | 1 | 9 | 5286.7892 | 5286.7892
2017-01-10 10:00 | 1 | 10 | 6545.0858 | 6545.0858
2017-01-10 11:00 | 1 | 11 | 7076.3352 | 7076.3352
2017-01-10 12:00 | 1 | 12 | 6975.3641 | 6975.3641
2017-01-10 13:00 | 1 | 13 | 6166.6968 | 6166.6968
2017-01-10 14:00 | 1 | 14 | 4671.0654 | 4671.0654
2017-01-10 15:00 | 1 | 15 | 2523.353 | 2523.353
2017-01-10 16:00 | 1 | 16 | 0 | 0
2017-01-10 17:00 | 1 | 17 | 0 | 0
2017-01-10 18:00 | 1 | 18 | 0 | 0
2017-01-10 19:00 | 1 | 19 | 0 | 0
2017-01-10 20:00 | 1 | 20 | 0 | 0
2017-01-10 21:00 | 1 | 21 | 0 | 0
2017-01-10 22:00 | 1 | 22 | 0 | 0
2017-01-10 23:00 | 1 | 23 | 0 | 0
2017-01-11 | 1 | 0 | 0 | 0
2017-01-11 01:00 | 1 | 1 | 0 | 0
2017-01-11 02:00 | 1 | 2 | 0 | 0
2017-01-11 03:00 | 1 | 3 | 0 | 0
2017-01-11 04:00 | 1 | 4 | 0 | 0
2017-01-11 05:00 | 1 | 5 | 0 | 0
2017-01-11 06:00 | 1 | 6 | 0 | 0
2017-01-11 07:00 | 1 | 7 | 593.6886 | 593.6886
2017-01-11 08:00 | 1 | 8 | 2954.4558 | 2954.4558
2017-01-11 09:00 | 1 | 9 | 4912.0341 | 4912.0341
2017-01-11 10:00 | 1 | 10 | 6182.2735 | 6182.2735
2017-01-11 11:00 | 1 | 11 | 6740.089 | 6740.089
2017-01-11 12:00 | 1 | 12 | 6638.7464 | 6638.7465
2017-01-11 13:00 | 1 | 13 | 5848.8195 | 5848.8195
2017-01-11 14:00 | 1 | 14 | 4354.4842 | 4354.4842
2017-01-11 15:00 | 1 | 15 | 2237.9138 | 2237.9138
2017-01-11 16:00 | 1 | 16 | 0 | 0
2017-01-11 17:00 | 1 | 17 | 0 | 0
2017-01-11 18:00 | 1 | 18 | 0 | 0
2017-01-11 19:00 | 1 | 19 | 0 | 0
2017-01-11 20:00 | 1 | 20 | 0 | 0
2017-01-11 21:00 | 1 | 21 | 0 | 0
2017-01-11 22:00 | 1 | 22 | 0 | 0
2017-01-11 23:00 | 1 | 23 | 0 | 0
2017-01-12 | 1 | 0 | 0 | 0
2017-01-12 01:00 | 1 | 1 | 0 | 0
2017-01-12 02:00 | 1 | 2 | 0 | 0
2017-01-12 03:00 | 1 | 3 | 0 | 0
2017-01-12 04:00 | 1 | 4 | 0 | 0
2017-01-12 05:00 | 1 | 5 | 0 | 0
2017-01-12 06:00 | 1 | 6 | 0 | 0
2017-01-12 07:00 | 1 | 7 | 89.4378 | 89.4378
2017-01-12 08:00 | 1 | 8 | 835.4554 | 835.4554
2017-01-12 09:00 | 1 | 9 | 1429.2396 | 1429.2396
2017-01-12 10:00 | 1 | 10 | 2151.3993 | 2151.3993
2017-01-12 11:00 | 1 | 11 | 3307.2298 | 3307.2298
2017-01-12 12:00 | 1 | 12 | 6902.875 | 6902.875
2017-01-12 13:00 | 1 | 13 | 6076.6908 | 6076.6908
2017-01-12 14:00 | 1 | 14 | 4640.8687 | 4640.8687
2017-01-12 15:00 | 1 | 15 | 2528.9535 | 2528.9535
2017-01-12 16:00 | 1 | 16 | 0 | 0
2017-01-12 17:00 | 1 | 17 | 0 | 0
2017-01-12 18:00 | 1 | 18 | 0 | 0
2017-01-12 19:00 | 1 | 19 | 0 | 0
2017-01-12 20:00 | 1 | 20 | 0 | 0
2017-01-12 21:00 | 1 | 21 | 0 | 0
2017-01-12 22:00 | 1 | 22 | 0 | 0
2017-01-12 23:00 | 1 | 23 | 0 | 0
2017-01-13 | 1 | 0 | 0 | 0
2017-01-13 01:00 | 1 | 1 | 0 | 0
2017-01-13 02:00 | 1 | 2 | 0 | 0
2017-01-13 03:00 | 1 | 3 | 0 | 0
2017-01-13 04:00 | 1 | 4 | 0 | 0
2017-01-13 05:00 | 1 | 5 | 0 | 0
2017-01-13 06:00 | 1 | 6 | 0 | 0
2017-01-13 07:00 | 1 | 7 | 804.2042 | 804.2042
2017-01-13 08:00 | 1 | 8 | 3287.3773 | 3287.3773
2017-01-13 09:00 | 1 | 9 | 5366.8706 | 5366.8706
2017-01-13 10:00 | 1 | 10 | 6655.226 | 6655.226
2017-01-13 11:00 | 1 | 11 | 7193.7479 | 7193.7479
2017-01-13 12:00 | 1 | 12 | 7020.7305 | 7020.7305
2017-01-13 13:00 | 1 | 13 | 4976.0281 | 4976.0281
2017-01-13 14:00 | 1 | 14 | 4538.1093 | 4538.1093
2017-01-13 15:00 | 1 | 15 | 2385.6451 | 2385.6451
2017-01-13 16:00 | 1 | 16 | 0 | 0
2017-01-13 17:00 | 1 | 17 | 0 | 0
2017-01-13 18:00 | 1 | 18 | 0 | 0
2017-01-13 19:00 | 1 | 19 | 0 | 0
2017-01-13 20:00 | 1 | 20 | 0 | 0
2017-01-13 21:00 | 1 | 21 | 0 | 0
2017-01-13 22:00 | 1 | 22 | 0 | 0
2017-01-13 23:00 | 1 | 23 | 0 | 0
2017-01-14 | 1 | 0 | 0 | 0
2017-01-14 01:00 | 1 | 1 | 0 | 0
2017-01-14 02:00 | 1 | 2 | 0 | 0
2017-01-14 03:00 | 1 | 3 | 0 | 0
2017-01-14 04:00 | 1 | 4 | 0 | 0
2017-01-14 05:00 | 1 | 5 | 0 | 0
2017-01-14 06:00 | 1 | 6 | 0 | 0
2017-01-14 07:00 | 1 | 7 | 230.8119 | 230.8119
2017-01-14 08:00 | 1 | 8 | 3152.6767 | 3152.6767
2017-01-14 09:00 | 1 | 9 | 5061.9217 | 5061.9217
2017-01-14 10:00 | 1 | 10 | 6320.2068 | 6320.2068
2017-01-14 11:00 | 1 | 11 | 6892.8803 | 6892.8803
2017-01-14 12:00 | 1 | 12 | 6756.442 | 6756.442
2017-01-14 13:00 | 1 | 13 | 5998.4207 | 5998.4207
2017-01-14 14:00 | 1 | 14 | 4589.4729 | 4589.4729
2017-01-14 15:00 | 1 | 15 | 2468.3232 | 2468.3232
2017-01-14 16:00 | 1 | 16 | 0 | 0
2017-01-14 17:00 | 1 | 17 | 0 | 0
2017-01-14 18:00 | 1 | 18 | 0 | 0
2017-01-14 19:00 | 1 | 19 | 0 | 0
2017-01-14 20:00 | 1 | 20 | 0 | 0
2017-01-14 21:00 | 1 | 21 | 0 | 0
2017-01-14 22:00 | 1 | 22 | 0 | 0
2017-01-14 23:00 | 1 | 23 | 0 | 0
2017-01-15 | 1 | 0 | 0 | 0
2017-01-15 01:00 | 1 | 1 | 0 | 0
2017-01-15 02:00 | 1 | 2 | 0 | 0
2017-01-15 03:00 | 1 | 3 | 0 | 0
2017-01-15 04:00 | 1 | 4 | 0 | 0
2017-01-15 05:00 | 1 | 5 | 0 | 0
2017-01-15 06:00 | 1 | 6 | 0 | 0
2017-01-15 07:00 | 1 | 7 | 35.3176 | 35.3176
2017-01-15 08:00 | 1 | 8 | 1489.6697 | 1489.6697
2017-01-15 09:00 | 1 | 9 | 1712.2867 | 1712.2867
2017-01-15 10:00 | 1 | 10 | 3710.9407 | 3710.9408
2017-01-15 11:00 | 1 | 11 | 4715.7532 | 4715.7532
2017-01-15 12:00 | 1 | 12 | 5274.2082 | 5274.2082
2017-01-15 13:00 | 1 | 13 | 4127.0257 | 4127.0257
2017-01-15 14:00 | 1 | 14 | 2187.7772 | 2187.7772
2017-01-15 15:00 | 1 | 15 | 2224.0678 | 2224.0678
2017-01-15 16:00 | 1 | 16 | 0 | 0
2017-01-15 17:00 | 1 | 17 | 0 | 0
2017-01-15 18:00 | 1 | 18 | 0 | 0
2017-01-15 19:00 | 1 | 19 | 0 | 0
2017-01-15 20:00 | 1 | 20 | 0 | 0
2017-01-15 21:00 | 1 | 21 | 0 | 0
2017-01-15 22:00 | 1 | 22 | 0 | 0
2017-01-15 23:00 | 1 | 23 | 0 | 0
2017-01-16 | 1 | 0 | 0 | 0
2017-01-16 01:00 | 1 | 1 | 0 | 0
2017-01-16 02:00 | 1 | 2 | 0 | 0
2017-01-16 03:00 | 1 | 3 | 0 | 0
2017-01-16 04:00 | 1 | 4 | 0 | 0
2017-01-16 05:00 | 1 | 5 | 0 | 0
2017-01-16 06:00 | 1 | 6 | 0 | 0
2017-01-16 07:00 | 1 | 7 | 236.4802 | 236.4802
2017-01-16 08:00 | 1 | 8 | 3024.5242 | 3024.5242
2017-01-16 09:00 | 1 | 9 | 4974.9287 | 4974.9287
2017-01-16 10:00 | 1 | 10 | 6205.1355 | 6205.1355
2017-01-16 11:00 | 1 | 11 | 6758.2429 | 6758.2429
2017-01-16 12:00 | 1 | 12 | 6647.0057 | 6647.0057
2017-01-16 13:00 | 1 | 13 | 5910.1869 | 5910.1869
2017-01-16 14:00 | 1 | 14 | 4532.0821 | 4532.0821
2017-01-16 15:00 | 1 | 15 | 2472.8392 | 2472.8392
2017-01-16 16:00 | 1 | 16 | 0 | 0
2017-01-16 17:00 | 1 | 17 | 0 | 0
2017-01-16 18:00 | 1 | 18 | 0 | 0
2017-01-16 19:00 | 1 | 19 | 0 | 0
2017-01-16 20:00 | 1 | 20 | 0 | 0
2017-01-16 21:00 | 1 | 21 | 0 | 0
2017-01-16 22:00 | 1 | 22 | 0 | 0
2017-01-16 23:00 | 1 | 23 | 0 | 0
2017-01-17 | 1 | 0 | 0 | 0
2017-01-17 01:00 | 1 | 1 | 0 | 0
2017-01-17 02:00 | 1 | 2 | 0 | 0
2017-01-17 03:00 | 1 | 3 | 0 | 0
2017-01-17 04:00 | 1 | 4 | 0 | 0
2017-01-17 05:00 | 1 | 5 | 0 | 0
2017-01-17 06:00 | 1 | 6 | 0 | 0
2017-01-17 07:00 | 1 | 7 | 66.6448 | 66.6448
2017-01-17 08:00 | 1 | 8 | 2464.2292 | 2464.2292
2017-01-17 09:00 | 1 | 9 | 3486.4044 | 3486.4044
2017-01-17 10:00 | 1 | 10 | 5145.6865 | 5145.6865
2017-01-17 11:00 | 1 | 11 | 4836.3319 | 4836.3319
2017-01-17 12:00 | 1 | 12 | 3121.3311 | 3121.3311
2017-01-17 13:00 | 1 | 13 | 1053.8749 | 1053.8749
2017-01-17 14:00 | 1 | 14 | 461.3927 | 461.3926
2017-01-17 15:00 | 1 | 15 | 229.7217 | 229.7217
2017-01-17 16:00 | 1 | 16 | 0 | 0
2017-01-17 17:00 | 1 | 17 | 0 | 0
2017-01-17 18:00 | 1 | 18 | 0 | 0
2017-01-17 19:00 | 1 | 19 | 0 | 0
2017-01-17 20:00 | 1 | 20 | 0 | 0
2017-01-17 21:00 | 1 | 21 | 0 | 0
2017-01-17 22:00 | 1 | 22 | 0 | 0
2017-01-17 23:00 | 1 | 23 | 0 | 0
2017-01-18 | 1 | 0 | 0 | 0
2017-01-18 01:00 | 1 | 1 | 0 | 0
2017-01-18 02:00 | 1 | 2 | 0 | 0
2017-01-18 03:00 | 1 | 3 | 0 | 0
2017-01-18 04:00 | 1 | 4 | 0 | 0
2017-01-18 05:00 | 1 | 5 | 0 | 0
2017-01-18 06:00 | 1 | 6 | 0 | 0
2017-01-18 07:00 | 1 | 7 | 0 | 0
2017-01-18 08:00 | 1 | 8 | 107.1271 | 107.1271
2017-01-18 09:00 | 1 | 9 | 416.6415 | 416.6415
2017-01-18 10:00 | 1 | 10 | 1209.662 | 1209.662
2017-01-18 11:00 | 1 | 11 | 302.5949 | 302.5949
2017-01-18 12:00 | 1 | 12 | 560.2156 | 560.2156
2017-01-18 13:00 | 1 | 13 | 1246.5574 | 1246.5574
2017-01-18 14:00 | 1 | 14 | 4347.6015 | 4347.6015
2017-01-18 15:00 | 1 | 15 | 2268.6314 | 2268.6314
2017-01-18 16:00 | 1 | 16 | 0 | 0
2017-01-18 17:00 | 1 | 17 | 0 | 0
2017-01-18 18:00 | 1 | 18 | 0 | 0
2017-01-18 19:00 | 1 | 19 | 0 | 0
2017-01-18 20:00 | 1 | 20 | 0 | 0
2017-01-18 21:00 | 1 | 21 | 0 | 0
2017-01-18 22:00 | 1 | 22 | 0 | 0
2017-01-18 23:00 | 1 | 23 | 0 | 0
2017-01-19 | 1 | 0 | 0 | 0
2017-01-19 01:00 | 1 | 1 | 0 | 0
2017-01-19 02:00 | 1 | 2 | 0 | 0
2017-01-19 03:00 | 1 | 3 | 0 | 0
2017-01-19 04:00 | 1 | 4 | 0 | 0
2017-01-19 05:00 | 1 | 5 | 0 | 0
2017-01-19 06:00 | 1 | 6 | 0 | 0
2017-01-19 07:00 | 1 | 7 | 334.5614 | 334.5614
2017-01-19 08:00 | 1 | 8 | 128.6677 | 128.6677
2017-01-19 09:00 | 1 | 9 | 243.1767 | 243.1767
2017-01-19 10:00 | 1 | 10 | 1029.8595 | 1029.8595
2017-01-19 11:00 | 1 | 11 | 1583.2476 | 1583.2476
2017-01-19 12:00 | 1 | 12 | 902.359 | 902.359
2017-01-19 13:00 | 1 | 13 | 219.8765 | 219.8766
2017-01-19 14:00 | 1 | 14 | 139.227 | 139.227
2017-01-19 15:00 | 1 | 15 | 35.1969 | 35.1969
2017-01-19 16:00 | 1 | 16 | 0 | 0
2017-01-19 17:00 | 1 | 17 | 0 | 0
2017-01-19 18:00 | 1 | 18 | 0 | 0
2017-01-19 19:00 | 1 | 19 | 0 | 0
2017-01-19 20:00 | 1 | 20 | 0 | 0
2017-01-19 21:00 | 1 | 21 | 0 | 0
2017-01-19 22:00 | 1 | 22 | 0 | 0
2017-01-19 23:00 | 1 | 23 | 0 | 0
2017-01-20 | 1 | 0 | 0 | 0
2017-01-20 01:00 | 1 | 1 | 0 | 0
2017-01-20 02:00 | 1 | 2 | 0 | 0
2017-01-20 03:00 | 1 | 3 | 0 | 0
2017-01-20 04:00 | 1 | 4 | 0 | 0
2017-01-20 05:00 | 1 | 5 | 0 | 0
2017-01-20 06:00 | 1 | 6 | 0 | 0
2017-01-20 07:00 | 1 | 7 | 402.8461 | 402.8461
2017-01-20 08:00 | 1 | 8 | 2649.8461 | 2649.8461
2017-01-20 09:00 | 1 | 9 | 1690.1699 | 1690.1699
2017-01-20 10:00 | 1 | 10 | 1520.5093 | 1520.5093
2017-01-20 11:00 | 1 | 11 | 1411.3904 | 1411.3904
2017-01-20 12:00 | 1 | 12 | 892.2125 | 892.2125
2017-01-20 13:00 | 1 | 13 | 1113.6807 | 1113.6807
2017-01-20 14:00 | 1 | 14 | 2763.335 | 2763.335
2017-01-20 15:00 | 1 | 15 | 2127.7484 | 2127.7484
2017-01-20 16:00 | 1 | 16 | 64.3529 | 64.3529
2017-01-20 17:00 | 1 | 17 | 0 | 0
2017-01-20 18:00 | 1 | 18 | 0 | 0
2017-01-20 19:00 | 1 | 19 | 0 | 0
2017-01-20 20:00 | 1 | 20 | 0 | 0
2017-01-20 21:00 | 1 | 21 | 0 | 0
2017-01-20 22:00 | 1 | 22 | 0 | 0
2017-01-20 23:00 | 1 | 23 | 0 | 0
2017-01-21 | 1 | 0 | 0 | 0
2017-01-21 01:00 | 1 | 1 | 0 | 0
2017-01-21 02:00 | 1 | 2 | 0 | 0
2017-01-21 03:00 | 1 | 3 | 0 | 0
2017-01-21 04:00 | 1 | 4 | 0 | 0
2017-01-21 05:00 | 1 | 5 | 0 | 0
2017-01-21 06:00 | 1 | 6 | 0 | 0
2017-01-21 07:00 | 1 | 7 | 858.3657 | 858.3657
2017-01-21 08:00 | 1 | 8 | 3273.9281 | 3273.9281
2017-01-21 09:00 | 1 | 9 | 5249.3164 | 5249.3164
2017-01-21 10:00 | 1 | 10 | 6543.0319 | 6543.0319
2017-01-21 11:00 | 1 | 11 | 7153.3841 | 7153.3841
2017-01-21 12:00 | 1 | 12 | 7044.5446 | 7044.5446
2017-01-21 13:00 | 1 | 13 | 6292.8483 | 6292.8483
2017-01-21 14:00 | 1 | 14 | 4892.5013 | 4892.5013
2017-01-21 15:00 | 1 | 15 | 2843.8902 | 2843.8902
2017-01-21 16:00 | 1 | 16 | 531.3448 | 531.3448
2017-01-21 17:00 | 1 | 17 | 0 | 0
2017-01-21 18:00 | 1 | 18 | 0 | 0
2017-01-21 19:00 | 1 | 19 | 0 | 0
2017-01-21 20:00 | 1 | 20 | 0 | 0
2017-01-21 21:00 | 1 | 21 | 0 | 0
2017-01-21 22:00 | 1 | 22 | 0 | 0
2017-01-21 23:00 | 1 | 23 | 0 | 0
2017-01-22 | 1 | 0 | 0 | 0
2017-01-22 01:00 | 1 | 1 | 0 | 0
2017-01-22 02:00 | 1 | 2 | 0 | 0
2017-01-22 03:00 | 1 | 3 | 0 | 0
2017-01-22 04:00 | 1 | 4 | 0 | 0
2017-01-22 05:00 | 1 | 5 | 0 | 0
2017-01-22 06:00 | 1 | 6 | 0 | 0
2017-01-22 07:00 | 1 | 7 | 294.0929 | 294.0929
2017-01-22 08:00 | 1 | 8 | 2479.5725 | 2479.5725
2017-01-22 09:00 | 1 | 9 | 4543.3487 | 4543.3487
2017-01-22 10:00 | 1 | 10 | 5775.4943 | 5775.4943
2017-01-22 11:00 | 1 | 11 | 6403.4909 | 6403.4909
2017-01-22 12:00 | 1 | 12 | 6203.5255 | 6203.5255
2017-01-22 13:00 | 1 | 13 | 4838.0638 | 4838.0638
2017-01-22 14:00 | 1 | 14 | 4069.367 | 4069.367
2017-01-22 15:00 | 1 | 15 | 1541.5934 | 1541.5934
2017-01-22 16:00 | 1 | 16 | 65.3085 | 65.3085
2017-01-22 17:00 | 1 | 17 | 0 | 0
2017-01-22 18:00 | 1 | 18 | 0 | 0
2017-01-22 19:00 | 1 | 19 | 0 | 0
2017-01-22 20:00 | 1 | 20 | 0 | 0
2017-01-22 21:00 | 1 | 21 | 0 | 0
2017-01-22 22:00 | 1 | 22 | 0 | 0
2017-01-22 23:00 | 1 | 23 | 0 | 0
2017-01-23 | 1 | 0 | 0 | 0
2017-01-23 01:00 | 1 | 1 | 0 | 0
2017-01-23 02:00 | 1 | 2 | 0 | 0
2017-01-23 03:00 | 1 | 3 | 0 | 0
2017-01-23 04:00 | 1 | 4 | 0 | 0
2017-01-23 05:00 | 1 | 5 | 0 | 0
2017-01-23 06:00 | 1 | 6 | 0 | 0
2017-01-23 07:00 | 1 | 7 | 1018.317 | 1018.317
2017-01-23 08:00 | 1 | 8 | 3490.756 | 3490.756
2017-01-23 09:00 | 1 | 9 | 5510.2664 | 5510.2664
2017-01-23 10:00 | 1 | 10 | 6800.824 | 6800.824
2017-01-23 11:00 | 1 | 11 | 7384.6778 | 7384.6778
2017-01-23 12:00 | 1 | 12 | 7294.9146 | 7294.9146
2017-01-23 13:00 | 1 | 13 | 6558.2844 | 6558.2844
2017-01-23 14:00 | 1 | 14 | 5172.5505 | 5172.5505
2017-01-23 15:00 | 1 | 15 | 3076.7847 | 3076.7847
2017-01-23 16:00 | 1 | 16 | 699.783 | 699.783
2017-01-23 17:00 | 1 | 17 | 0 | 0
2017-01-23 18:00 | 1 | 18 | 0 | 0
2017-01-23 19:00 | 1 | 19 | 0 | 0
2017-01-23 20:00 | 1 | 20 | 0 | 0
2017-01-23 21:00 | 1 | 21 | 0 | 0
2017-01-23 22:00 | 1 | 22 | 0 | 0
2017-01-23 23:00 | 1 | 23 | 0 | 0
2017-01-24 | 1 | 0 | 0 | 0
2017-01-24 01:00 | 1 | 1 | 0 | 0
2017-01-24 02:00 | 1 | 2 | 0 | 0
2017-01-24 03:00 | 1 | 3 | 0 | 0
2017-01-24 04:00 | 1 | 4 | 0 | 0
2017-01-24 05:00 | 1 | 5 | 0 | 0
2017-01-24 06:00 | 1 | 6 | 0 | 0
2017-01-24 07:00 | 1 | 7 | 690.828 | 690.828
2017-01-24 08:00 | 1 | 8 | 2444.5193 | 2444.5193
2017-01-24 09:00 | 1 | 9 | 3842.7963 | 3842.7963
2017-01-24 10:00 | 1 | 10 | 3880.9407 | 3880.9406
2017-01-24 11:00 | 1 | 11 | 4343.6662 | 4343.6662
2017-01-24 12:00 | 1 | 12 | 4142.8244 | 4142.8244
2017-01-24 13:00 | 1 | 13 | 3139.9094 | 3139.9094
2017-01-24 14:00 | 1 | 14 | 1342.8285 | 1342.8285
2017-01-24 15:00 | 1 | 15 | 85.407 | 85.407
2017-01-24 16:00 | 1 | 16 | 0 | 0
2017-01-24 17:00 | 1 | 17 | 0 | 0
2017-01-24 18:00 | 1 | 18 | 0 | 0
2017-01-24 19:00 | 1 | 19 | 0 | 0
2017-01-24 20:00 | 1 | 20 | 0 | 0
2017-01-24 21:00 | 1 | 21 | 0 | 0
2017-01-24 22:00 | 1 | 22 | 0 | 0
2017-01-24 23:00 | 1 | 23 | 0 | 0
2017-01-25 | 1 | 0 | 0 | 0
2017-01-25 01:00 | 1 | 1 | 0 | 0
2017-01-25 02:00 | 1 | 2 | 0 | 0
2017-01-25 03:00 | 1 | 3 | 0 | 0
2017-01-25 04:00 | 1 | 4 | 0 | 0
2017-01-25 05:00 | 1 | 5 | 0 | 0
2017-01-25 06:00 | 1 | 6 | 0 | 0
2017-01-25 07:00 | 1 | 7 | 0 | 0
2017-01-25 08:00 | 1 | 8 | 32.6565 | 32.6565
2017-01-25 09:00 | 1 | 9 | 233.9077 | 233.9077
2017-01-25 10:00 | 1 | 10 | 660.9774 | 660.9774
2017-01-25 11:00 | 1 | 11 | 499.1299 | 499.1299
2017-01-25 12:00 | 1 | 12 | 368.2196 | 368.2196
2017-01-25 13:00 | 1 | 13 | 10.7341 | 10.7341
2017-01-25 14:00 | 1 | 14 | 0 | 0
2017-01-25 15:00 | 1 | 15 | 0.50025 | 0.50025
2017-01-25 16:00 | 1 | 16 | 0 | 0
2017-01-25 17:00 | 1 | 17 | 0 | 0
2017-01-25 18:00 | 1 | 18 | 0 | 0
2017-01-25 19:00 | 1 | 19 | 0 | 0
2017-01-25 20:00 | 1 | 20 | 0 | 0
2017-01-25 21:00 | 1 | 21 | 0 | 0
2017-01-25 22:00 | 1 | 22 | 0 | 0
2017-01-25 23:00 | 1 | 23 | 0 | 0
2017-01-26 | 1 | 0 | 0 | 0
2017-01-26 01:00 | 1 | 1 | 0 | 0
2017-01-26 02:00 | 1 | 2 | 0 | 0
2017-01-26 03:00 | 1 | 3 | 0 | 0
2017-01-26 04:00 | 1 | 4 | 0 | 0
2017-01-26 05:00 | 1 | 5 | 0 | 0
2017-01-26 06:00 | 1 | 6 | 0 | 0
2017-01-26 07:00 | 1 | 7 | 76.9649 | 76.9649
2017-01-26 08:00 | 1 | 8 | 596.4693 | 596.4693
2017-01-26 09:00 | 1 | 9 | 3859.5679 | 3859.5679
2017-01-26 10:00 | 1 | 10 | 6363.6136 | 6363.6136
2017-01-26 11:00 | 1 | 11 | 6914.9028 | 6914.9029
2017-01-26 12:00 | 1 | 12 | 4356.8704 | 4356.8704
2017-01-26 13:00 | 1 | 13 | 1267.392 | 1267.392
2017-01-26 14:00 | 1 | 14 | 2863.6346 | 2863.6346
2017-01-26 15:00 | 1 | 15 | 2828.3249 | 2828.3249
2017-01-26 16:00 | 1 | 16 | 225.109 | 225.109
2017-01-26 17:00 | 1 | 17 | 0 | 0
2017-01-26 18:00 | 1 | 18 | 0 | 0
2017-01-26 19:00 | 1 | 19 | 0 | 0
2017-01-26 20:00 | 1 | 20 | 0 | 0
2017-01-26 21:00 | 1 | 21 | 0 | 0
2017-01-26 22:00 | 1 | 22 | 0 | 0
2017-01-26 23:00 | 1 | 23 | 0 | 0
2017-01-27 | 1 | 0 | 0 | 0
2017-01-27 01:00 | 1 | 1 | 0 | 0
2017-01-27 02:00 | 1 | 2 | 0 | 0
2017-01-27 03:00 | 1 | 3 | 0 | 0
2017-01-27 04:00 | 1 | 4 | 0 | 0
2017-01-27 05:00 | 1 | 5 | 0 | 0
2017-01-27 06:00 | 1 | 6 | 0 | 0
2017-01-27 07:00 | 1 | 7 | 897.0713 | 897.0713
2017-01-27 08:00 | 1 | 8 | 3200.427 | 3200.427
2017-01-27 09:00 | 1 | 9 | 5195.6436 | 5195.6436
2017-01-27 10:00 | 1 | 10 | 6542.4294 | 6542.4294
2017-01-27 11:00 | 1 | 11 | 7134.0917 | 7134.0917
2017-01-27 12:00 | 1 | 12 | 7038.3185 | 7038.3185
2017-01-27 13:00 | 1 | 13 | 6154.1249 | 6154.1249
2017-01-27 14:00 | 1 | 14 | 2365.2395 | 2365.2395
2017-01-27 15:00 | 1 | 15 | 1770.5814 | 1770.5814
2017-01-27 16:00 | 1 | 16 | 281.0761 | 281.0761
2017-01-27 17:00 | 1 | 17 | 0 | 0
2017-01-27 18:00 | 1 | 18 | 0 | 0
2017-01-27 19:00 | 1 | 19 | 0 | 0
2017-01-27 20:00 | 1 | 20 | 0 | 0
2017-01-27 21:00 | 1 | 21 | 0 | 0
2017-01-27 22:00 | 1 | 22 | 0 | 0
2017-01-27 23:00 | 1 | 23 | 0 | 0
2017-01-28 | 1 | 0 | 0 | 0
2017-01-28 01:00 | 1 | 1 | 0 | 0
2017-01-28 02:00 | 1 | 2 | 0 | 0
2017-01-28 03:00 | 1 | 3 | 0 | 0
2017-01-28 04:00 | 1 | 4 | 0 | 0
2017-01-28 05:00 | 1 | 5 | 0 | 0
2017-01-28 06:00 | 1 | 6 | 0 | 0
2017-01-28 07:00 | 1 | 7 | 756.0733 | 756.0733
2017-01-28 08:00 | 1 | 8 | 1108.0664 | 1108.0664
2017-01-28 09:00 | 1 | 9 | 1857.8825 | 1857.8825
2017-01-28 10:00 | 1 | 10 | 6569.4911 | 6569.4911
2017-01-28 11:00 | 1 | 11 | 4771.3592 | 4771.3592
2017-01-28 12:00 | 1 | 12 | 6987.5863 | 6987.5863
2017-01-28 13:00 | 1 | 13 | 646.6691 | 646.6691
2017-01-28 14:00 | 1 | 14 | 2356.7479 | 2356.7479
2017-01-28 15:00 | 1 | 15 | 54.0109 | 54.0109
2017-01-28 16:00 | 1 | 16 | 426.2751 | 426.2751
2017-01-28 17:00 | 1 | 17 | 0 | 0
2017-01-28 18:00 | 1 | 18 | 0 | 0
2017-01-28 19:00 | 1 | 19 | 0 | 0
2017-01-28 20:00 | 1 | 20 | 0 | 0
2017-01-28 21:00 | 1 | 21 | 0 | 0
2017-01-28 22:00 | 1 | 22 | 0 | 0
2017-01-28 23:00 | 1 | 23 | 0 | 0
2017-01-29 | 1 | 0 | 0 | 0
2017-01-29 01:00 | 1 | 1 | 0 | 0
2017-01-29 02:00 | 1 | 2 | 0 | 0
2017-01-29 03:00 | 1 | 3 | 0 | 0
2017-01-29 04:00 | 1 | 4 | 0 | 0
2017-01-29 05:00 | 1 | 5 | 0 | 0
2017-01-29 06:00 | 1 | 6 | 0 | 0
2017-01-29 07:00 | 1 | 7 | 1170.9116 | 1170.9116
2017-01-29 08:00 | 1 | 8 | 3887.3496 | 3887.3496
2017-01-29 09:00 | 1 | 9 | 6161.0571 | 6161.0571
2017-01-29 10:00 | 1 | 10 | 7622.9509 | 7622.951
2017-01-29 11:00 | 1 | 11 | 8309.9011 | 8309.9011
2017-01-29 12:00 | 1 | 12 | 8255.3233 | 8255.3233
2017-01-29 13:00 | 1 | 13 | 7376.5255 | 7376.5255
2017-01-29 14:00 | 1 | 14 | 5818.8459 | 5818.8459
2017-01-29 15:00 | 1 | 15 | 3563.2025 | 3563.2025
2017-01-29 16:00 | 1 | 16 | 965.8355 | 965.8356
2017-01-29 17:00 | 1 | 17 | 0 | 0
2017-01-29 18:00 | 1 | 18 | 0 | 0
2017-01-29 19:00 | 1 | 19 | 0 | 0
2017-01-29 20:00 | 1 | 20 | 0 | 0
2017-01-29 21:00 | 1 | 21 | 0 | 0
2017-01-29 22:00 | 1 | 22 | 0 | 0
2017-01-29 23:00 | 1 | 23 | 0 | 0
2017-01-30 | 1 | 0 | 0 | 0
2017-01-30 01:00 | 1 | 1 | 0 | 0
2017-01-30 02:00 | 1 | 2 | 0 | 0
2017-01-30 03:00 | 1 | 3 | 0 | 0
2017-01-30 04:00 | 1 | 4 | 0 | 0
2017-01-30 05:00 | 1 | 5 | 0 | 0
2017-01-30 06:00 | 1 | 6 | 0 | 0
2017-01-30 07:00 | 1 | 7 | 1176.7524 | 1176.7524
2017-01-30 08:00 | 1 | 8 | 3822.5459 | 3822.5459
2017-01-30 09:00 | 1 | 9 | 5959.3598 | 5959.3598
2017-01-30 10:00 | 1 | 10 | 7151.8155 | 7151.8155
2017-01-30 11:00 | 1 | 11 | 6743.6506 | 6743.6506
2017-01-30 12:00 | 1 | 12 | 7665.4342 | 7665.4343
2017-01-30 13:00 | 1 | 13 | 5993.3158 | 5993.3158
2017-01-30 14:00 | 1 | 14 | 3890.8537 | 3890.8537
2017-01-30 15:00 | 1 | 15 | 1044.9716 | 1044.9716
2017-01-30 16:00 | 1 | 16 | 132.626 | 132.626
2017-01-30 17:00 | 1 | 17 | 0 | 0
2017-01-30 18:00 | 1 | 18 | 0 | 0
2017-01-30 19:00 | 1 | 19 | 0 | 0
2017-01-30 20:00 | 1 | 20 | 0 | 0
2017-01-30 21:00 | 1 | 21 | 0 | 0
2017-01-30 22:00 | 1 | 22 | 0 | 0
2017-01-30 23:00 | 1 | 23 | 0 | 0
2017-01-31 | 1 | 0 | 0 | 0
2017-01-31 01:00 | 1 | 1 | 0 | 0
2017-01-31 02:00 | 1 | 2 | 0 | 0
2017-01-31 03:00 | 1 | 3 | 0 | 0
2017-01-31 04:00 | 1 | 4 | 0 | 0
2017-01-31 05:00 | 1 | 5 | 0 | 0
2017-01-31 06:00 | 1 | 6 | 0 | 0
2017-01-31 07:00 | 1 | 7 | 1141.8787 | 1141.8787
2017-01-31 08:00 | 1 | 8 | 3663.8011 | 3663.8011
2017-01-31 09:00 | 1 | 9 | 5592.2936 | 5592.2936
2017-01-31 10:00 | 1 | 10 | 6874.9794 | 6874.9795
2017-01-31 11:00 | 1 | 11 | 7646.5915 | 7646.5915
2017-01-31 12:00 | 1 | 12 | 7576.8854 | 7576.8854
2017-01-31 13:00 | 1 | 13 | 6796.101 | 6796.101
2017-01-31 14:00 | 1 | 14 | 5360.0994 | 5360.0994
2017-01-31 15:00 | 1 | 15 | 3227.2875 | 3227.2875
2017-01-31 16:00 | 1 | 16 | 908.0768 | 908.0768
2017-01-31 17:00 | 1 | 17 | 0 | 0
2017-01-31 18:00 | 1 | 18 | 0 | 0
2017-01-31 19:00 | 1 | 19 | 0 | 0
2017-01-31 20:00 | 1 | 20 | 0 | 0
2017-01-31 21:00 | 1 | 21 | 0 | 0
2017-01-31 22:00 | 1 | 22 | 0 | 0
2017-01-31 23:00 | 1 | 23 | 0 | 0
2017-02-01 | 2 | 0 | 0 | 0
2017-02-01 01:00 | 2 | 1 | 0 | 0
2017-02-01 02:00 | 2 | 2 | 0 | 0
2017-02-01 03:00 | 2 | 3 | 0 | 0
2017-02-01 04:00 | 2 | 4 | 0 | 0
2017-02-01 05:00 | 2 | 5 | 0 | 0
2017-02-01 06:00 | 2 | 6 | 0 | 0
2017-02-01 07:00 | 2 | 7 | 683.7796 | 683.7796
2017-02-01 08:00 | 2 | 8 | 1928.8191 | 1928.8191
2017-02-01 09:00 | 2 | 9 | 4471.8831 | 4471.8831
2017-02-01 10:00 | 2 | 10 | 6489.8076 | 6489.8076
2017-02-01 11:00 | 2 | 11 | 7016.817 | 7016.817
2017-02-01 12:00 | 2 | 12 | 5863.7603 | 5863.7603
2017-02-01 13:00 | 2 | 13 | 5115.4587 | 5115.4587
2017-02-01 14:00 | 2 | 14 | 3984.0864 | 3984.0864
2017-02-01 15:00 | 2 | 15 | 1033.5441 | 1033.5441
2017-02-01 16:00 | 2 | 16 | 137.4215 | 137.4215
2017-02-01 17:00 | 2 | 17 | 0 | 0
2017-02-01 18:00 | 2 | 18 | 0 | 0
2017-02-01 19:00 | 2 | 19 | 0 | 0
2017-02-01 20:00 | 2 | 20 | 0 | 0
2017-02-01 21:00 | 2 | 21 | 0 | 0
2017-02-01 22:00 | 2 | 22 | 0 | 0
2017-02-01 23:00 | 2 | 23 | 0 | 0
2017-02-02 | 2 | 0 | 0 | 0
2017-02-02 01:00 | 2 | 1 | 0 | 0
2017-02-02 02:00 | 2 | 2 | 0 | 0
2017-02-02 03:00 | 2 | 3 | 0 | 0
2017-02-02 04:00 | 2 | 4 | 0 | 0
2017-02-02 05:00 | 2 | 5 | 0 | 0
2017-02-02 06:00 | 2 | 6 | 0 | 0
2017-02-02 07:00 | 2 | 7 | 181.2664 | 181.2664
2017-02-02 08:00 | 2 | 8 | 1490.4816 | 1490.4816
2017-02-02 09:00 | 2 | 9 | 2766.3652 | 2766.3652
2017-02-02 10:00 | 2 | 10 | 4332.5249 | 4332.5249
2017-02-02 11:00 | 2 | 11 | 2714.1644 | 2714.1644
2017-02-02 12:00 | 2 | 12 | 3682.2402 | 3682.2402
2017-02-02 13:00 | 2 | 13 | 414.836 | 414.8361
2017-02-02 14:00 | 2 | 14 | 215.8205 | 215.8205
2017-02-02 15:00 | 2 | 15 | 831.6374 | 831.6374
2017-02-02 16:00 | 2 | 16 | 126.6817 | 126.6817
2017-02-02 17:00 | 2 | 17 | 0 | 0
2017-02-02 18:00 | 2 | 18 | 0 | 0
2017-02-02 19:00 | 2 | 19 | 0 | 0
2017-02-02 20:00 | 2 | 20 | 0 | 0
2017-02-02 21:00 | 2 | 21 | 0 | 0
2017-02-02 22:00 | 2 | 22 | 0 | 0
2017-02-02 23:00 | 2 | 23 | 0 | 0
2017-02-03 | 2 | 0 | 0 | 0
2017-02-03 01:00 | 2 | 1 | 0 | 0
2017-02-03 02:00 | 2 | 2 | 0 | 0
2017-02-03 03:00 | 2 | 3 | 0 | 0
2017-02-03 04:00 | 2 | 4 | 0 | 0
2017-02-03 05:00 | 2 | 5 | 0 | 0
2017-02-03 06:00 | 2 | 6 | 0 | 0
2017-02-03 07:00 | 2 | 7 | 66.478 | 66.478
2017-02-03 08:00 | 2 | 8 | 367.5319 | 367.5319
2017-02-03 09:00 | 2 | 9 | 387.3568 | 387.3568
2017-02-03 10:00 | 2 | 10 | 765.8563 | 765.8563
2017-02-03 11:00 | 2 | 11 | 1215.42 | 1215.42
2017-02-03 12:00 | 2 | 12 | 978.1083 | 978.1084
2017-02-03 13:00 | 2 | 13 | 1292.5275 | 1292.5275
2017-02-03 14:00 | 2 | 14 | 292.0965 | 292.0965
2017-02-03 15:00 | 2 | 15 | 0 | 0
2017-02-03 16:00 | 2 | 16 | 0 | 0
2017-02-03 17:00 | 2 | 17 | 0 | 0
2017-02-03 18:00 | 2 | 18 | 0 | 0
2017-02-03 19:00 | 2 | 19 | 0 | 0
2017-02-03 20:00 | 2 | 20 | 0 | 0
2017-02-03 21:00 | 2 | 21 | 0 | 0
2017-02-03 22:00 | 2 | 22 | 0 | 0
2017-02-03 23:00 | 2 | 23 | 0 | 0
2017-02-04 | 2 | 0 | 0 | 0
2017-02-04 01:00 | 2 | 1 | 0 | 0
2017-02-04 02:00 | 2 | 2 | 0 | 0
2017-02-04 03:00 | 2 | 3 | 0 | 0
2017-02-04 04:00 | 2 | 4 | 0 | 0
2017-02-04 05:00 | 2 | 5 | 0 | 0
2017-02-04 06:00 | 2 | 6 | 0 | 0
2017-02-04 07:00 | 2 | 7 | 368.3277 | 368.3277
2017-02-04 08:00 | 2 | 8 | 1894.771 | 1894.771
2017-02-04 09:00 | 2 | 9 | 5674.8751 | 5674.8751
2017-02-04 10:00 | 2 | 10 | 6919.7938 | 6919.7938
2017-02-04 11:00 | 2 | 11 | 7515.672 | 7515.672
2017-02-04 12:00 | 2 | 12 | 7464.4073 | 7464.4073
2017-02-04 13:00 | 2 | 13 | 6712.2648 | 6712.2648
2017-02-04 14:00 | 2 | 14 | 4875.6354 | 4875.6354
2017-02-04 15:00 | 2 | 15 | 1964.944 | 1964.944
2017-02-04 16:00 | 2 | 16 | 429.9332 | 429.9332
2017-02-04 17:00 | 2 | 17 | 0 | 0
2017-02-04 18:00 | 2 | 18 | 0 | 0
2017-02-04 19:00 | 2 | 19 | 0 | 0
2017-02-04 20:00 | 2 | 20 | 0 | 0
2017-02-04 21:00 | 2 | 21 | 0 | 0
2017-02-04 22:00 | 2 | 22 | 0 | 0
2017-02-04 23:00 | 2 | 23 | 0 | 0
2017-02-05 | 2 | 0 | 0 | 0
2017-02-05 01:00 | 2 | 1 | 0 | 0
2017-02-05 02:00 | 2 | 2 | 0 | 0
2017-02-05 03:00 | 2 | 3 | 0 | 0
2017-02-05 04:00 | 2 | 4 | 0 | 0
2017-02-05 05:00 | 2 | 5 | 0 | 0
2017-02-05 06:00 | 2 | 6 | 0 | 0
2017-02-05 07:00 | 2 | 7 | 14.7131 | 14.7131
2017-02-05 08:00 | 2 | 8 | 160.272 | 160.272
2017-02-05 09:00 | 2 | 9 | 529.5911 | 529.5911
2017-02-05 10:00 | 2 | 10 | 837.2126 | 837.2126
2017-02-05 11:00 | 2 | 11 | 2845.0448 | 2845.0448
2017-02-05 12:00 | 2 | 12 | 1255.8725 | 1255.8725
2017-02-05 13:00 | 2 | 13 | 1093.3464 | 1093.3464
2017-02-05 14:00 | 2 | 14 | 487.286 | 487.286
2017-02-05 15:00 | 2 | 15 | 168.9246 | 168.9246
2017-02-05 16:00 | 2 | 16 | 864.5746 | 864.5746
2017-02-05 17:00 | 2 | 17 | 0 | 0
2017-02-05 18:00 | 2 | 18 | 0 | 0
2017-02-05 19:00 | 2 | 19 | 0 | 0
2017-02-05 20:00 | 2 | 20 | 0 | 0
2017-02-05 21:00 | 2 | 21 | 0 | 0
2017-02-05 22:00 | 2 | 22 | 0 | 0
2017-02-05 23:00 | 2 | 23 | 0 | 0
2017-02-06 | 2 | 0 | 0 | 0
2017-02-06 01:00 | 2 | 1 | 0 | 0
2017-02-06 02:00 | 2 | 2 | 0 | 0
2017-02-06 03:00 | 2 | 3 | 0 | 0
2017-02-06 04:00 | 2 | 4 | 0 | 0
2017-02-06 05:00 | 2 | 5 | 0 | 0
2017-02-06 06:00 | 2 | 6 | 0 | 0
2017-02-06 07:00 | 2 | 7 | 1227.5445 | 1227.5445
2017-02-06 08:00 | 2 | 8 | 3817.5227 | 3817.5227
2017-02-06 09:00 | 2 | 9 | 4303.461 | 4303.461
2017-02-06 10:00 | 2 | 10 | 5638.6064 | 5638.6064
2017-02-06 11:00 | 2 | 11 | 3654.0215 | 3654.0215
2017-02-06 12:00 | 2 | 12 | 7878.42 | 7878.42
2017-02-06 13:00 | 2 | 13 | 7065.3608 | 7065.3608
2017-02-06 14:00 | 2 | 14 | 5666.9298 | 5666.9298
2017-02-06 15:00 | 2 | 15 | 3587.8447 | 3587.8447
2017-02-06 16:00 | 2 | 16 | 1120.8245 | 1120.8245
2017-02-06 17:00 | 2 | 17 | 0 | 0
2017-02-06 18:00 | 2 | 18 | 0 | 0
2017-02-06 19:00 | 2 | 19 | 0 | 0
2017-02-06 20:00 | 2 | 20 | 0 | 0
2017-02-06 21:00 | 2 | 21 | 0 | 0
2017-02-06 22:00 | 2 | 22 | 0 | 0
2017-02-06 23:00 | 2 | 23 | 0 | 0
2017-02-07 | 2 | 0 | 0 | 0
2017-02-07 01:00 | 2 | 1 | 0 | 0
2017-02-07 02:00 | 2 | 2 | 0 | 0
2017-02-07 03:00 | 2 | 3 | 0 | 0
2017-02-07 04:00 | 2 | 4 | 0 | 0
2017-02-07 05:00 | 2 | 5 | 0 | 0
2017-02-07 06:00 | 2 | 6 | 0 | 0
2017-02-07 07:00 | 2 | 7 | 1382.6128 | 1382.6128
2017-02-07 08:00 | 2 | 8 | 3951.1849 | 3951.1849
2017-02-07 09:00 | 2 | 9 | 5989.7738 | 5989.7738
2017-02-07 10:00 | 2 | 10 | 7549.3107 | 7549.3107
2017-02-07 11:00 | 2 | 11 | 8211.4312 | 8211.4312
2017-02-07 12:00 | 2 | 12 | 8138.3154 | 8138.3154
2017-02-07 13:00 | 2 | 13 | 7372.7201 | 7372.7201
2017-02-07 14:00 | 2 | 14 | 5902.5705 | 5902.5705
2017-02-07 15:00 | 2 | 15 | 3652.3425 | 3652.3425
2017-02-07 16:00 | 2 | 16 | 1218.0386 | 1218.0386
2017-02-07 17:00 | 2 | 17 | 0 | 0
2017-02-07 18:00 | 2 | 18 | 0 | 0
2017-02-07 19:00 | 2 | 19 | 0 | 0
2017-02-07 20:00 | 2 | 20 | 0 | 0
2017-02-07 21:00 | 2 | 21 | 0 | 0
2017-02-07 22:00 | 2 | 22 | 0 | 0
2017-02-07 23:00 | 2 | 23 | 0 | 0
2017-02-08 | 2 | 0 | 0 | 0
2017-02-08 01:00 | 2 | 1 | 0 | 0
2017-02-08 02:00 | 2 | 2 | 0 | 0
2017-02-08 03:00 | 2 | 3 | 0 | 0
2017-02-08 04:00 | 2 | 4 | 0 | 0
2017-02-08 05:00 | 2 | 5 | 0 | 0
2017-02-08 06:00 | 2 | 6 | 0 | 0
2017-02-08 07:00 | 2 | 7 | 1505.9951 | 1505.9951
2017-02-08 08:00 | 2 | 8 | 4139.0386 | 4139.0386
2017-02-08 09:00 | 2 | 9 | 6174.8238 | 6174.8238
2017-02-08 10:00 | 2 | 10 | 7489.0196 | 7489.0196
2017-02-08 11:00 | 2 | 11 | 8056.2583 | 8056.2583
2017-02-08 12:00 | 2 | 12 | 7913.9032 | 7913.9033
2017-02-08 13:00 | 2 | 13 | 5111.6672 | 5111.6672
2017-02-08 14:00 | 2 | 14 | 4044.4258 | 4044.4258
2017-02-08 15:00 | 2 | 15 | 1764.8647 | 1764.8647
2017-02-08 16:00 | 2 | 16 | 1131.3734 | 1131.3734
2017-02-08 17:00 | 2 | 17 | 0 | 0
2017-02-08 18:00 | 2 | 18 | 0 | 0
2017-02-08 19:00 | 2 | 19 | 0 | 0
2017-02-08 20:00 | 2 | 20 | 0 | 0
2017-02-08 21:00 | 2 | 21 | 0 | 0
2017-02-08 22:00 | 2 | 22 | 0 | 0
2017-02-08 23:00 | 2 | 23 | 0 | 0
2017-02-09 | 2 | 0 | 0 | 0
2017-02-09 01:00 | 2 | 1 | 0 | 0
2017-02-09 02:00 | 2 | 2 | 0 | 0
2017-02-09 03:00 | 2 | 3 | 0 | 0
2017-02-09 04:00 | 2 | 4 | 0 | 0
2017-02-09 05:00 | 2 | 5 | 0 | 0
2017-02-09 06:00 | 2 | 6 | 0 | 0
2017-02-09 07:00 | 2 | 7 | 1337.8927 | 1337.8927
2017-02-09 08:00 | 2 | 8 | 1264.3525 | 1264.3525
2017-02-09 09:00 | 2 | 9 | 4088.9883 | 4088.9883
2017-02-09 10:00 | 2 | 10 | 4865.8305 | 4865.8305
2017-02-09 11:00 | 2 | 11 | 6401.4302 | 6401.4302
2017-02-09 12:00 | 2 | 12 | 5233.5293 | 5233.5293
2017-02-09 13:00 | 2 | 13 | 5126.8196 | 5126.8196
2017-02-09 14:00 | 2 | 14 | 3453.2223 | 3453.2223
2017-02-09 15:00 | 2 | 15 | 1960.4406 | 1960.4406
2017-02-09 16:00 | 2 | 16 | 455.8048 | 455.8048
2017-02-09 17:00 | 2 | 17 | 0 | 0
2017-02-09 18:00 | 2 | 18 | 0 | 0
2017-02-09 19:00 | 2 | 19 | 0 | 0
2017-02-09 20:00 | 2 | 20 | 0 | 0
2017-02-09 21:00 | 2 | 21 | 0 | 0
2017-02-09 22:00 | 2 | 22 | 0 | 0
2017-02-09 23:00 | 2 | 23 | 0 | 0
2017-02-10 | 2 | 0 | 0 | 0
2017-02-10 01:00 | 2 | 1 | 0 | 0
2017-02-10 02:00 | 2 | 2 | 0 | 0
2017-02-10 03:00 | 2 | 3 | 0 | 0
2017-02-10 04:00 | 2 | 4 | 0 | 0
2017-02-10 05:00 | 2 | 5 | 0 | 0
2017-02-10 06:00 | 2 | 6 | 0 | 0
2017-02-10 07:00 | 2 | 7 | 1338.0641 | 1338.0641
2017-02-10 08:00 | 2 | 8 | 3945.5936 | 3945.5936
2017-02-10 09:00 | 2 | 9 | 6089.227 | 6089.227
2017-02-10 10:00 | 2 | 10 | 7449.7724 | 7449.7724
2017-02-10 11:00 | 2 | 11 | 8137.8899 | 8137.8899
2017-02-10 12:00 | 2 | 12 | 8108.8788 | 8108.8788
2017-02-10 13:00 | 2 | 13 | 7416.7962 | 7416.7962
2017-02-10 14:00 | 2 | 14 | 5967.3569 | 5967.3569
2017-02-10 15:00 | 2 | 15 | 3836.4115 | 3836.4115
2017-02-10 16:00 | 2 | 16 | 1298.4742 | 1298.4742
2017-02-10 17:00 | 2 | 17 | 0 | 0
2017-02-10 18:00 | 2 | 18 | 0 | 0
2017-02-10 19:00 | 2 | 19 | 0 | 0
2017-02-10 20:00 | 2 | 20 | 0 | 0
2017-02-10 21:00 | 2 | 21 | 0 | 0
2017-02-10 22:00 | 2 | 22 | 0 | 0
2017-02-10 23:00 | 2 | 23 | 0 | 0
2017-02-11 | 2 | 0 | 0 | 0
2017-02-11 01:00 | 2 | 1 | 0 | 0
2017-02-11 02:00 | 2 | 2 | 0 | 0
2017-02-11 03:00 | 2 | 3 | 0 | 0
2017-02-11 04:00 | 2 | 4 | 0 | 0
2017-02-11 05:00 | 2 | 5 | 0 | 0
2017-02-11 06:00 | 2 | 6 | 0 | 0
2017-02-11 07:00 | 2 | 7 | 1536.4368 | 1536.4368
2017-02-11 08:00 | 2 | 8 | 4213.3723 | 4213.3723
2017-02-11 09:00 | 2 | 9 | 6338.1364 | 6338.1364
2017-02-11 10:00 | 2 | 10 | 7713.3306 | 7713.3306
2017-02-11 11:00 | 2 | 11 | 8369.984 | 8369.984
2017-02-11 12:00 | 2 | 12 | 8333.3312 | 8333.3312
2017-02-11 13:00 | 2 | 13 | 7638.6507 | 7638.6507
2017-02-11 14:00 | 2 | 14 | 6185.1508 | 6185.1508
2017-02-11 15:00 | 2 | 15 | 4056.5169 | 4056.5169
2017-02-11 16:00 | 2 | 16 | 1457.6917 | 1457.6917
2017-02-11 17:00 | 2 | 17 | 0 | 0
2017-02-11 18:00 | 2 | 18 | 0 | 0
2017-02-11 19:00 | 2 | 19 | 0 | 0
2017-02-11 20:00 | 2 | 20 | 0 | 0
2017-02-11 21:00 | 2 | 21 | 0 | 0
2017-02-11 22:00 | 2 | 22 | 0 | 0
2017-02-11 23:00 | 2 | 23 | 0 | 0
2017-02-12 | 2 | 0 | 0 | 0
2017-02-12 01:00 | 2 | 1 | 0 | 0
2017-02-12 02:00 | 2 | 2 | 0 | 0
2017-02-12 03:00 | 2 | 3 | 0 | 0
2017-02-12 04:00 | 2 | 4 | 0 | 0
2017-02-12 05:00 | 2 | 5 | 0 | 0
2017-02-12 06:00 | 2 | 6 | 0 | 0
2017-02-12 07:00 | 2 | 7 | 1729.5839 | 1729.5839
2017-02-12 08:00 | 2 | 8 | 4375.7949 | 4375.7949
2017-02-12 09:00 | 2 | 9 | 6419.1344 | 6419.1344
2017-02-12 10:00 | 2 | 10 | 7745.4328 | 7745.4328
2017-02-12 11:00 | 2 | 11 | 8313.1246 | 8313.1246
2017-02-12 12:00 | 2 | 12 | 8267.4109 | 8267.4109
2017-02-12 13:00 | 2 | 13 | 6410.6428 | 6410.6428
2017-02-12 14:00 | 2 | 14 | 4886.4247 | 4886.4247
2017-02-12 15:00 | 2 | 15 | 2876.7319 | 2876.7319
2017-02-12 16:00 | 2 | 16 | 807.7082 | 807.7082
2017-02-12 17:00 | 2 | 17 | 0 | 0
2017-02-12 18:00 | 2 | 18 | 0 | 0
2017-02-12 19:00 | 2 | 19 | 0 | 0
2017-02-12 20:00 | 2 | 20 | 0 | 0
2017-02-12 21:00 | 2 | 21 | 0 | 0
2017-02-12 22:00 | 2 | 22 | 0 | 0
2017-02-12 23:00 | 2 | 23 | 0 | 0
2017-02-13 | 2 | 0 | 0 | 0
2017-02-13 01:00 | 2 | 1 | 0 | 0
2017-02-13 02:00 | 2 | 2 | 0 | 0
2017-02-13 03:00 | 2 | 3 | 0 | 0
2017-02-13 04:00 | 2 | 4 | 0 | 0
2017-02-13 05:00 | 2 | 5 | 0 | 0
2017-02-13 06:00 | 2 | 6 | 0 | 0
2017-02-13 07:00 | 2 | 7 | 192.7193 | 192.7193
2017-02-13 08:00 | 2 | 8 | 385.6973 | 385.6973
2017-02-13 09:00 | 2 | 9 | 937.8215 | 937.8215
2017-02-13 10:00 | 2 | 10 | 898.2201 | 898.2201
2017-02-13 11:00 | 2 | 11 | 970.6241 | 970.6241
2017-02-13 12:00 | 2 | 12 | 917.7839 | 917.7839
2017-02-13 13:00 | 2 | 13 | 743.3795 | 743.3795
2017-02-13 14:00 | 2 | 14 | 733.3734 | 733.3734
2017-02-13 15:00 | 2 | 15 | 230.3737 | 230.3737
2017-02-13 16:00 | 2 | 16 | 34.37 | 34.37
2017-02-13 17:00 | 2 | 17 | 0 | 0
2017-02-13 18:00 | 2 | 18 | 0 | 0
2017-02-13 19:00 | 2 | 19 | 0 | 0
2017-02-13 20:00 | 2 | 20 | 0 | 0
2017-02-13 21:00 | 2 | 21 | 0 | 0
2017-02-13 22:00 | 2 | 22 | 0 | 0
2017-02-13 23:00 | 2 | 23 | 0 | 0
2017-02-14 | 2 | 0 | 0 | 0
2017-02-14 01:00 | 2 | 1 | 0 | 0
2017-02-14 02:00 | 2 | 2 | 0 | 0
2017-02-14 03:00 | 2 | 3 | 0 | 0
2017-02-14 04:00 | 2 | 4 | 0 | 0
2017-02-14 05:00 | 2 | 5 | 0 | 0
2017-02-14 06:00 | 2 | 6 | 0 | 0
2017-02-14 07:00 | 2 | 7 | 506.8728 | 506.8728
2017-02-14 08:00 | 2 | 8 | 1516.4912 | 1516.4912
2017-02-14 09:00 | 2 | 9 | 3626.5422 | 3626.5422
2017-02-14 10:00 | 2 | 10 | 4074.7283 | 4074.7283
2017-02-14 11:00 | 2 | 11 | 5097.0116 | 5097.0116
2017-02-14 12:00 | 2 | 12 | 6011.5192 | 6011.5192
2017-02-14 13:00 | 2 | 13 | 3544.2931 | 3544.2931
2017-02-14 14:00 | 2 | 14 | 4133.0597 | 4133.0597
2017-02-14 15:00 | 2 | 15 | 3917.4807 | 3917.4807
2017-02-14 16:00 | 2 | 16 | 1395.6791 | 1395.6791
2017-02-14 17:00 | 2 | 17 | 0 | 0
2017-02-14 18:00 | 2 | 18 | 0 | 0
2017-02-14 19:00 | 2 | 19 | 0 | 0
2017-02-14 20:00 | 2 | 20 | 0 | 0
2017-02-14 21:00 | 2 | 21 | 0 | 0
2017-02-14 22:00 | 2 | 22 | 0 | 0
2017-02-14 23:00 | 2 | 23 | 0 | 0
2017-02-15 | 2 | 0 | 0 | 0
2017-02-15 01:00 | 2 | 1 | 0 | 0
2017-02-15 02:00 | 2 | 2 | 0 | 0
2017-02-15 03:00 | 2 | 3 | 0 | 0
2017-02-15 04:00 | 2 | 4 | 0 | 0
2017-02-15 05:00 | 2 | 5 | 0 | 0
2017-02-15 06:00 | 2 | 6 | 0 | 0
2017-02-15 07:00 | 2 | 7 | 205.3394 | 205.3394
2017-02-15 08:00 | 2 | 8 | 778.4902 | 778.4902
2017-02-15 09:00 | 2 | 9 | 4129.8075 | 4129.8075
2017-02-15 10:00 | 2 | 10 | 4498.0858 | 4498.0858
2017-02-15 11:00 | 2 | 11 | 4168.5487 | 4168.5487
2017-02-15 12:00 | 2 | 12 | 1814.4217 | 1814.4217
2017-02-15 13:00 | 2 | 13 | 1910.5939 | 1910.5939
2017-02-15 14:00 | 2 | 14 | 1084.6317 | 1084.6317
2017-02-15 15:00 | 2 | 15 | 436.042 | 436.042
2017-02-15 16:00 | 2 | 16 | 106.9672 | 106.9672
2017-02-15 17:00 | 2 | 17 | 0 | 0
2017-02-15 18:00 | 2 | 18 | 0 | 0
2017-02-15 19:00 | 2 | 19 | 0 | 0
2017-02-15 20:00 | 2 | 20 | 0 | 0
2017-02-15 21:00 | 2 | 21 | 0 | 0
2017-02-15 22:00 | 2 | 22 | 0 | 0
2017-02-15 23:00 | 2 | 23 | 0 | 0
2017-02-16 | 2 | 0 | 0 | 0
2017-02-16 01:00 | 2 | 1 | 0 | 0
2017-02-16 02:00 | 2 | 2 | 0 | 0
2017-02-16 03:00 | 2 | 3 | 0 | 0
2017-02-16 04:00 | 2 | 4 | 0 | 0
2017-02-16 05:00 | 2 | 5 | 0 | 0
2017-02-16 06:00 | 2 | 6 | 0 | 0
2017-02-16 07:00 | 2 | 7 | 1836.4108 | 1836.4108
2017-02-16 08:00 | 2 | 8 | 4529.2083 | 4529.2083
2017-02-16 09:00 | 2 | 9 | 6675.6419 | 6675.6419
2017-02-16 10:00 | 2 | 10 | 5799.5109 | 5799.5109
2017-02-16 11:00 | 2 | 11 | 6467.5528 | 6467.5528
2017-02-16 12:00 | 2 | 12 | 8603.7721 | 8603.7721
2017-02-16 13:00 | 2 | 13 | 6427.0809 | 6427.0809
2017-02-16 14:00 | 2 | 14 | 4707.6043 | 4707.6043
2017-02-16 15:00 | 2 | 15 | 4110.8417 | 4110.8417
2017-02-16 16:00 | 2 | 16 | 1609.3548 | 1609.3548
2017-02-16 17:00 | 2 | 17 | 0 | 0
2017-02-16 18:00 | 2 | 18 | 0 | 0
2017-02-16 19:00 | 2 | 19 | 0 | 0
2017-02-16 20:00 | 2 | 20 | 0 | 0
2017-02-16 21:00 | 2 | 21 | 0 | 0
2017-02-16 22:00 | 2 | 22 | 0 | 0
2017-02-16 23:00 | 2 | 23 | 0 | 0
2017-02-17 | 2 | 0 | 0 | 0
2017-02-17 01:00 | 2 | 1 | 0 | 0
2017-02-17 02:00 | 2 | 2 | 0 | 0
2017-02-17 03:00 | 2 | 3 | 0 | 0
2017-02-17 04:00 | 2 | 4 | 0 | 0
2017-02-17 05:00 | 2 | 5 | 0 | 0
2017-02-17 06:00 | 2 | 6 | 0 | 0
2017-02-17 07:00 | 2 | 7 | 1985.1472 | 1985.1472
2017-02-17 08:00 | 2 | 8 | 4765.9473 | 4765.9473
2017-02-17 09:00 | 2 | 9 | 6929.1686 | 6929.1686
2017-02-17 10:00 | 2 | 10 | 8272.8711 | 8272.8711
2017-02-17 11:00 | 2 | 11 | 8848.2242 | 8848.2242
2017-02-17 12:00 | 2 | 12 | 8761.5901 | 8761.5901
2017-02-17 13:00 | 2 | 13 | 8071.306 | 8071.306
2017-02-17 14:00 | 2 | 14 | 6620.4614 | 6620.4614
2017-02-17 15:00 | 2 | 15 | 4462.5531 | 4462.5531
2017-02-17 16:00 | 2 | 16 | 1790.5304 | 1790.5304
2017-02-17 17:00 | 2 | 17 | 0 | 0
2017-02-17 18:00 | 2 | 18 | 0 | 0
2017-02-17 19:00 | 2 | 19 | 0 | 0
2017-02-17 20:00 | 2 | 20 | 0 | 0
2017-02-17 21:00 | 2 | 21 | 0 | 0
2017-02-17 22:00 | 2 | 22 | 0 | 0
2017-02-17 23:00 | 2 | 23 | 0 | 0
2017-02-18 | 2 | 0 | 0 | 0
2017-02-18 01:00 | 2 | 1 | 0 | 0
2017-02-18 02:00 | 2 | 2 | 0 | 0
2017-02-18 03:00 | 2 | 3 | 0 | 0
2017-02-18 04:00 | 2 | 4 | 0 | 0
2017-02-18 05:00 | 2 | 5 | 0 | 0
2017-02-18 06:00 | 2 | 6 | 0 | 0
2017-02-18 07:00 | 2 | 7 | 47.6043 | 47.6043
2017-02-18 08:00 | 2 | 8 | 813.947 | 813.947
2017-02-18 09:00 | 2 | 9 | 701.784 | 701.784
2017-02-18 10:00 | 2 | 10 | 2648.6685 | 2648.6685
2017-02-18 11:00 | 2 | 11 | 1880.6559 | 1880.6559
2017-02-18 12:00 | 2 | 12 | 2476.4158 | 2476.4158
2017-02-18 13:00 | 2 | 13 | 1542.6514 | 1542.6514
2017-02-18 14:00 | 2 | 14 | 650.1019 | 650.1019
2017-02-18 15:00 | 2 | 15 | 656.7639 | 656.7639
2017-02-18 16:00 | 2 | 16 | 3.7237 | 3.7237
2017-02-18 17:00 | 2 | 17 | 0 | 0
2017-02-18 18:00 | 2 | 18 | 0 | 0
2017-02-18 19:00 | 2 | 19 | 0 | 0
2017-02-18 20:00 | 2 | 20 | 0 | 0
2017-02-18 21:00 | 2 | 21 | 0 | 0
2017-02-18 22:00 | 2 | 22 | 0 | 0
2017-02-18 23:00 | 2 | 23 | 0 | 0
2017-02-19 | 2 | 0 | 0 | 0
2017-02-19 01:00 | 2 | 1 | 0 | 0
2017-02-19 02:00 | 2 | 2 | 0 | 0
2017-02-19 03:00 | 2 | 3 | 0 | 0
2017-02-19 04:00 | 2 | 4 | 0 | 0
2017-02-19 05:00 | 2 | 5 | 0 | 0
2017-02-19 06:00 | 2 | 6 | 0 | 0
2017-02-19 07:00 | 2 | 7 | 1655.3353 | 1655.3353
2017-02-19 08:00 | 2 | 8 | 4120.9974 | 4120.9974
2017-02-19 09:00 | 2 | 9 | 3989.2407 | 3989.2407
2017-02-19 10:00 | 2 | 10 | 4712.9484 | 4712.9484
2017-02-19 11:00 | 2 | 11 | 3501.9834 | 3501.9834
2017-02-19 12:00 | 2 | 12 | 3450.023 | 3450.023
2017-02-19 13:00 | 2 | 13 | 1589.9888 | 1589.9888
2017-02-19 14:00 | 2 | 14 | 636.3525 | 636.3525
2017-02-19 15:00 | 2 | 15 | 819.5291 | 819.5291
2017-02-19 16:00 | 2 | 16 | 516.0464 | 516.0464
2017-02-19 17:00 | 2 | 17 | 0 | 0
2017-02-19 18:00 | 2 | 18 | 0 | 0
2017-02-19 19:00 | 2 | 19 | 0 | 0
2017-02-19 20:00 | 2 | 20 | 0 | 0
2017-02-19 21:00 | 2 | 21 | 0 | 0
2017-02-19 22:00 | 2 | 22 | 0 | 0
2017-02-19 23:00 | 2 | 23 | 0 | 0
2017-02-20 | 2 | 0 | 0 | 0
2017-02-20 01:00 | 2 | 1 | 0 | 0
2017-02-20 02:00 | 2 | 2 | 0 | 0
2017-02-20 03:00 | 2 | 3 | 0 | 0
2017-02-20 04:00 | 2 | 4 | 0 | 0
2017-02-20 05:00 | 2 | 5 | 0 | 0
2017-02-20 06:00 | 2 | 6 | 0 | 0
2017-02-20 07:00 | 2 | 7 | 1898.2084 | 1898.2084
2017-02-20 08:00 | 2 | 8 | 4380.2488 | 4380.2488
2017-02-20 09:00 | 2 | 9 | 6300.6085 | 6300.6085
2017-02-20 10:00 | 2 | 10 | 7505.8499 | 7505.8499
2017-02-20 11:00 | 2 | 11 | 8078.1761 | 8078.1761
2017-02-20 12:00 | 2 | 12 | 8064.0357 | 8064.0357
2017-02-20 13:00 | 2 | 13 | 5798.2862 | 5798.2862
2017-02-20 14:00 | 2 | 14 | 4973.0715 | 4973.0715
2017-02-20 15:00 | 2 | 15 | 1216.079 | 1216.079
2017-02-20 16:00 | 2 | 16 | 177.9659 | 177.9659
2017-02-20 17:00 | 2 | 17 | 0 | 0
2017-02-20 18:00 | 2 | 18 | 0 | 0
2017-02-20 19:00 | 2 | 19 | 0 | 0
2017-02-20 20:00 | 2 | 20 | 0 | 0
2017-02-20 21:00 | 2 | 21 | 0 | 0
2017-02-20 22:00 | 2 | 22 | 0 | 0
2017-02-20 23:00 | 2 | 23 | 0 | 0
2017-02-21 | 2 | 0 | 0 | 0
2017-02-21 01:00 | 2 | 1 | 0 | 0
2017-02-21 02:00 | 2 | 2 | 0 | 0
2017-02-21 03:00 | 2 | 3 | 0 | 0
2017-02-21 04:00 | 2 | 4 | 0 | 0
2017-02-21 05:00 | 2 | 5 | 0 | 0
2017-02-21 06:00 | 2 | 6 | 0 | 0
2017-02-21 07:00 | 2 | 7 | 0 | 0
2017-02-21 08:00 | 2 | 8 | 137.3997 | 137.3997
2017-02-21 09:00 | 2 | 9 | 1176.2603 | 1176.2603
2017-02-21 10:00 | 2 | 10 | 736.9039 | 736.9039
2017-02-21 11:00 | 2 | 11 | 443.9057 | 443.9058
2017-02-21 12:00 | 2 | 12 | 1343.7301 | 1343.7301
2017-02-21 13:00 | 2 | 13 | 1256.4428 | 1256.4428
2017-02-21 14:00 | 2 | 14 | 1470.735 | 1470.735
2017-02-21 15:00 | 2 | 15 | 518.1889 | 518.1889
2017-02-21 16:00 | 2 | 16 | 84.379 | 84.379
2017-02-21 17:00 | 2 | 17 | 0 | 0
2017-02-21 18:00 | 2 | 18 | 0 | 0
2017-02-21 19:00 | 2 | 19 | 0 | 0
2017-02-21 20:00 | 2 | 20 | 0 | 0
2017-02-21 21:00 | 2 | 21 | 0 | 0
2017-02-21 22:00 | 2 | 22 | 0 | 0
2017-02-21 23:00 | 2 | 23 | 0 | 0
2017-02-22 | 2 | 0 | 0 | 0
2017-02-22 01:00 | 2 | 1 | 0 | 0
2017-02-22 02:00 | 2 | 2 | 0 | 0
2017-02-22 03:00 | 2 | 3 | 0 | 0
2017-02-22 04:00 | 2 | 4 | 0 | 0
2017-02-22 05:00 | 2 | 5 | 0 | 0
2017-02-22 06:00 | 2 | 6 | 0 | 0
2017-02-22 07:00 | 2 | 7 | 580.4694 | 580.4694
2017-02-22 08:00 | 2 | 8 | 4397.6149 | 4397.6149
2017-02-22 09:00 | 2 | 9 | 6235.507 | 6235.507
2017-02-22 10:00 | 2 | 10 | 7514.8532 | 7514.8532
2017-02-22 11:00 | 2 | 11 | 8050.422 | 8050.422
2017-02-22 12:00 | 2 | 12 | 8164.1835 | 8164.1835
2017-02-22 13:00 | 2 | 13 | 7607.5548 | 7607.5548
2017-02-22 14:00 | 2 | 14 | 6239.8954 | 6239.8954
2017-02-22 15:00 | 2 | 15 | 4182.9341 | 4182.9341
2017-02-22 16:00 | 2 | 16 | 1722.7092 | 1722.7092
2017-02-22 17:00 | 2 | 17 | 0 | 0
2017-02-22 18:00 | 2 | 18 | 0 | 0
2017-02-22 19:00 | 2 | 19 | 0 | 0
2017-02-22 20:00 | 2 | 20 | 0 | 0
2017-02-22 21:00 | 2 | 21 | 0 | 0
2017-02-22 22:00 | 2 | 22 | 0 | 0
2017-02-22 23:00 | 2 | 23 | 0 | 0
2017-02-23 | 2 | 0 | 0 | 0
2017-02-23 01:00 | 2 | 1 | 0 | 0
2017-02-23 02:00 | 2 | 2 | 0 | 0
2017-02-23 03:00 | 2 | 3 | 0 | 0
2017-02-23 04:00 | 2 | 4 | 0 | 0
2017-02-23 05:00 | 2 | 5 | 0 | 0
2017-02-23 06:00 | 2 | 6 | 0 | 0
2017-02-23 07:00 | 2 | 7 | 356.6196 | 356.6196
2017-02-23 08:00 | 2 | 8 | 3267.0396 | 3267.0396
2017-02-23 09:00 | 2 | 9 | 4879.9778 | 4879.9778
2017-02-23 10:00 | 2 | 10 | 6243.7536 | 6243.7536
2017-02-23 11:00 | 2 | 11 | 6188.9239 | 6188.9239
2017-02-23 12:00 | 2 | 12 | 4780.9283 | 4780.9283
2017-02-23 13:00 | 2 | 13 | 3158.805 | 3158.805
2017-02-23 14:00 | 2 | 14 | 3139.3769 | 3139.3769
2017-02-23 15:00 | 2 | 15 | 1877.7372 | 1877.7372
2017-02-23 16:00 | 2 | 16 | 743.1691 | 743.1691
2017-02-23 17:00 | 2 | 17 | 0 | 0
2017-02-23 18:00 | 2 | 18 | 0 | 0
2017-02-23 19:00 | 2 | 19 | 0 | 0
2017-02-23 20:00 | 2 | 20 | 0 | 0
2017-02-23 21:00 | 2 | 21 | 0 | 0
2017-02-23 22:00 | 2 | 22 | 0 | 0
2017-02-23 23:00 | 2 | 23 | 0 | 0
2017-02-24 | 2 | 0 | 0 | 0
2017-02-24 01:00 | 2 | 1 | 0 | 0
2017-02-24 02:00 | 2 | 2 | 0 | 0
2017-02-24 03:00 | 2 | 3 | 0 | 0
2017-02-24 04:00 | 2 | 4 | 0 | 0
2017-02-24 05:00 | 2 | 5 | 0 | 0
2017-02-24 06:00 | 2 | 6 | 0 | 0
2017-02-24 07:00 | 2 | 7 | 2138.0478 | 2138.0478
2017-02-24 08:00 | 2 | 8 | 4777.2253 | 4777.2253
2017-02-24 09:00 | 2 | 9 | 6819.9715 | 6819.9715
2017-02-24 10:00 | 2 | 10 | 7019.2205 | 7019.2205
2017-02-24 11:00 | 2 | 11 | 7068.2381 | 7068.2381
2017-02-24 12:00 | 2 | 12 | 7460.809 | 7460.809
2017-02-24 13:00 | 2 | 13 | 6554.011 | 6554.011
2017-02-24 14:00 | 2 | 14 | 5774.7399 | 5774.7399
2017-02-24 15:00 | 2 | 15 | 3527.5985 | 3527.5985
2017-02-24 16:00 | 2 | 16 | 1818.3742 | 1818.3743
2017-02-24 17:00 | 2 | 17 | 0 | 0
2017-02-24 18:00 | 2 | 18 | 0 | 0
2017-02-24 19:00 | 2 | 19 | 0 | 0
2017-02-24 20:00 | 2 | 20 | 0 | 0
2017-02-24 21:00 | 2 | 21 | 0 | 0
2017-02-24 22:00 | 2 | 22 | 0 | 0
2017-02-24 23:00 | 2 | 23 | 0 | 0
2017-02-25 | 2 | 0 | 0 | 0
2017-02-25 01:00 | 2 | 1 | 0 | 0
2017-02-25 02:00 | 2 | 2 | 0 | 0
2017-02-25 03:00 | 2 | 3 | 0 | 0
2017-02-25 04:00 | 2 | 4 | 0 | 0
2017-02-25 05:00 | 2 | 5 | 0 | 0
2017-02-25 06:00 | 2 | 6 | 0 | 0
2017-02-25 07:00 | 2 | 7 | 2249.6541 | 2249.6541
2017-02-25 08:00 | 2 | 8 | 4253.3187 | 4253.3187
2017-02-25 09:00 | 2 | 9 | 4305.1204 | 4305.1204
2017-02-25 10:00 | 2 | 10 | 6849.7323 | 6849.7324
2017-02-25 11:00 | 2 | 11 | 7512.7717 | 7512.7717
2017-02-25 12:00 | 2 | 12 | 6701.3662 | 6701.3662
2017-02-25 13:00 | 2 | 13 | 7079.6932 | 7079.6932
2017-02-25 14:00 | 2 | 14 | 5773.0103 | 5773.0103
2017-02-25 15:00 | 2 | 15 | 3468.776 | 3468.776
2017-02-25 16:00 | 2 | 16 | 1927.1021 | 1927.1021
2017-02-25 17:00 | 2 | 17 | 0 | 0
2017-02-25 18:00 | 2 | 18 | 0 | 0
2017-02-25 19:00 | 2 | 19 | 0 | 0
2017-02-25 20:00 | 2 | 20 | 0 | 0
2017-02-25 21:00 | 2 | 21 | 0 | 0
2017-02-25 22:00 | 2 | 22 | 0 | 0
2017-02-25 23:00 | 2 | 23 | 0 | 0
2017-02-26 | 2 | 0 | 0 | 0
2017-02-26 01:00 | 2 | 1 | 0 | 0
2017-02-26 02:00 | 2 | 2 | 0 | 0
2017-02-26 03:00 | 2 | 3 | 0 | 0
2017-02-26 04:00 | 2 | 4 | 0 | 0
2017-02-26 05:00 | 2 | 5 | 0 | 0
2017-02-26 06:00 | 2 | 6 | 0 | 0
2017-02-26 07:00 | 2 | 7 | 1082.2477 | 1082.2477
2017-02-26 08:00 | 2 | 8 | 1846.4457 | 1846.4457
2017-02-26 09:00 | 2 | 9 | 3375.3684 | 3375.3685
2017-02-26 10:00 | 2 | 10 | 5421.6646 | 5421.6646
2017-02-26 11:00 | 2 | 11 | 8848.9142 | 8848.9142
2017-02-26 12:00 | 2 | 12 | 7218.9559 | 7218.956
2017-02-26 13:00 | 2 | 13 | 1321.1441 | 1321.1441
2017-02-26 14:00 | 2 | 14 | 5306.2713 | 5306.2713
2017-02-26 15:00 | 2 | 15 | 3479.3929 | 3479.3929
2017-02-26 16:00 | 2 | 16 | 1932.0138 | 1932.0138
2017-02-26 17:00 | 2 | 17 | 0 | 0
2017-02-26 18:00 | 2 | 18 | 0 | 0
2017-02-26 19:00 | 2 | 19 | 0 | 0
2017-02-26 20:00 | 2 | 20 | 0 | 0
2017-02-26 21:00 | 2 | 21 | 0 | 0
2017-02-26 22:00 | 2 | 22 | 0 | 0
2017-02-26 23:00 | 2 | 23 | 0 | 0
2017-02-27 | 2 | 0 | 0 | 0
2017-02-27 01:00 | 2 | 1 | 0 | 0
2017-02-27 02:00 | 2 | 2 | 0 | 0
2017-02-27 03:00 | 2 | 3 | 0 | 0
2017-02-27 04:00 | 2 | 4 | 0 | 0
2017-02-27 05:00 | 2 | 5 | 0 | 0
2017-02-27 06:00 | 2 | 6 | 0 | 0
2017-02-27 07:00 | 2 | 7 | 2420.3003 | 2420.3003
2017-02-27 08:00 | 2 | 8 | 5014.3024 | 5014.3024
2017-02-27 09:00 | 2 | 9 | 5670.604 | 5670.604
2017-02-27 10:00 | 2 | 10 | 7257.8018 | 7257.8018
2017-02-27 11:00 | 2 | 11 | 8876.9535 | 8876.9535
2017-02-27 12:00 | 2 | 12 | 7767.8728 | 7767.8728
2017-02-27 13:00 | 2 | 13 | 4405.3464 | 4405.3464
2017-02-27 14:00 | 2 | 14 | 2719.7604 | 2719.7604
2017-02-27 15:00 | 2 | 15 | 1105.7606 | 1105.7606
2017-02-27 16:00 | 2 | 16 | 1287.2283 | 1287.2283
2017-02-27 17:00 | 2 | 17 | 0 | 0
2017-02-27 18:00 | 2 | 18 | 0 | 0
2017-02-27 19:00 | 2 | 19 | 0 | 0
2017-02-27 20:00 | 2 | 20 | 0 | 0
2017-02-27 21:00 | 2 | 21 | 0 | 0
2017-02-27 22:00 | 2 | 22 | 0 | 0
2017-02-27 23:00 | 2 | 23 | 0 | 0
2017-02-28 | 2 | 0 | 0 | 0
2017-02-28 01:00 | 2 | 1 | 0 | 0
2017-02-28 02:00 | 2 | 2 | 0 | 0
2017-02-28 03:00 | 2 | 3 | 0 | 0
2017-02-28 04:00 | 2 | 4 | 0 | 0
2017-02-28 05:00 | 2 | 5 | 0 | 0
2017-02-28 06:00 | 2 | 6 | 0 | 0
2017-02-28 07:00 | 2 | 7 | 2563.0475 | 2563.0475
2017-02-28 08:00 | 2 | 8 | 5312.7171 | 5312.7171
2017-02-28 09:00 | 2 | 9 | 7414.0454 | 7414.0454
2017-02-28 10:00 | 2 | 10 | 8636.1838 | 8636.1838
2017-02-28 11:00 | 2 | 11 | 9217.0626 | 9217.0626
2017-02-28 12:00 | 2 | 12 | 9142.5472 | 9142.5472
2017-02-28 13:00 | 2 | 13 | 8424.9667 | 8424.9667
2017-02-28 14:00 | 2 | 14 | 6969.9924 | 6969.9924
2017-02-28 15:00 | 2 | 15 | 4689.3113 | 4689.3113
2017-02-28 16:00 | 2 | 16 | 2110.3121 | 2110.3121
2017-02-28 17:00 | 2 | 17 | 0 | 0
2017-02-28 18:00 | 2 | 18 | 0 | 0
2017-02-28 19:00 | 2 | 19 | 0 | 0
2017-02-28 20:00 | 2 | 20 | 0 | 0
2017-02-28 21:00 | 2 | 21 | 0 | 0
2017-02-28 22:00 | 2 | 22 | 0 | 0
2017-02-28 23:00 | 2 | 23 | 0 | 0
2017-03-01 | 3 | 0 | 0 | 0
2017-03-01 01:00 | 3 | 1 | 0 | 0
2017-03-01 02:00 | 3 | 2 | 0 | 0
2017-03-01 03:00 | 3 | 3 | 0 | 0
2017-03-01 04:00 | 3 | 4 | 0 | 0
2017-03-01 05:00 | 3 | 5 | 0 | 0
2017-03-01 06:00 | 3 | 6 | 129.3485 | 129.3485
2017-03-01 07:00 | 3 | 7 | 2161.3801 | 2161.3801
2017-03-01 08:00 | 3 | 8 | 1093.3245 | 1093.3245
2017-03-01 09:00 | 3 | 9 | 1392.1808 | 1392.1808
2017-03-01 10:00 | 3 | 10 | 2523.5531 | 2523.5531
2017-03-01 11:00 | 3 | 11 | 1545.3562 | 1545.3562
2017-03-01 12:00 | 3 | 12 | 2598.6745 | 2598.6745
2017-03-01 13:00 | 3 | 13 | 1198.5288 | 1198.5288
2017-03-01 14:00 | 3 | 14 | 1000.4321 | 1000.4321
2017-03-01 15:00 | 3 | 15 | 379.3494 | 379.3494
2017-03-01 16:00 | 3 | 16 | 96.1009 | 96.1009
2017-03-01 17:00 | 3 | 17 | 0 | 0
2017-03-01 18:00 | 3 | 18 | 0 | 0
2017-03-01 19:00 | 3 | 19 | 0 | 0
2017-03-01 20:00 | 3 | 20 | 0 | 0
2017-03-01 21:00 | 3 | 21 | 0 | 0
2017-03-01 22:00 | 3 | 22 | 0 | 0
2017-03-01 23:00 | 3 | 23 | 0 | 0
2017-03-02 | 3 | 0 | 0 | 0
2017-03-02 01:00 | 3 | 1 | 0 | 0
2017-03-02 02:00 | 3 | 2 | 0 | 0
2017-03-02 03:00 | 3 | 3 | 0 | 0
2017-03-02 04:00 | 3 | 4 | 0 | 0
2017-03-02 05:00 | 3 | 5 | 0 | 0
2017-03-02 06:00 | 3 | 6 | 188.1653 | 188.1653
2017-03-02 07:00 | 3 | 7 | 2243.9156 | 2243.9156
2017-03-02 08:00 | 3 | 8 | 4630.3818 | 4630.3818
2017-03-02 09:00 | 3 | 9 | 6478.6423 | 6478.6423
2017-03-02 10:00 | 3 | 10 | 7466.8304 | 7466.8304
2017-03-02 11:00 | 3 | 11 | 3426.8746 | 3426.8746
2017-03-02 12:00 | 3 | 12 | 3464.8396 | 3464.8396
2017-03-02 13:00 | 3 | 13 | 3081.3939 | 3081.3939
2017-03-02 14:00 | 3 | 14 | 1090.484 | 1090.484
2017-03-02 15:00 | 3 | 15 | 1145.9807 | 1145.9807
2017-03-02 16:00 | 3 | 16 | 1737.8984 | 1737.8984
2017-03-02 17:00 | 3 | 17 | 0 | 0
2017-03-02 18:00 | 3 | 18 | 0 | 0
2017-03-02 19:00 | 3 | 19 | 0 | 0
2017-03-02 20:00 | 3 | 20 | 0 | 0
2017-03-02 21:00 | 3 | 21 | 0 | 0
2017-03-02 22:00 | 3 | 22 | 0 | 0
2017-03-02 23:00 | 3 | 23 | 0 | 0
2017-03-03 | 3 | 0 | 0 | 0
2017-03-03 01:00 | 3 | 1 | 0 | 0
2017-03-03 02:00 | 3 | 2 | 0 | 0
2017-03-03 03:00 | 3 | 3 | 0 | 0
2017-03-03 04:00 | 3 | 4 | 0 | 0
2017-03-03 05:00 | 3 | 5 | 0 | 0
2017-03-03 06:00 | 3 | 6 | 0 | 0
2017-03-03 07:00 | 3 | 7 | 752.1678 | 752.1678
2017-03-03 08:00 | 3 | 8 | 1976.9351 | 1976.9351
2017-03-03 09:00 | 3 | 9 | 4266.1274 | 4266.1274
2017-03-03 10:00 | 3 | 10 | 5095.0014 | 5095.0014
2017-03-03 11:00 | 3 | 11 | 5617.9121 | 5617.9121
2017-03-03 12:00 | 3 | 12 | 5387.0543 | 5387.0543
2017-03-03 13:00 | 3 | 13 | 4182.6132 | 4182.6132
2017-03-03 14:00 | 3 | 14 | 3945.3901 | 3945.3901
2017-03-03 15:00 | 3 | 15 | 1508.8368 | 1508.8368
2017-03-03 16:00 | 3 | 16 | 682.9838 | 682.9838
2017-03-03 17:00 | 3 | 17 | 0 | 0
2017-03-03 18:00 | 3 | 18 | 0 | 0
2017-03-03 19:00 | 3 | 19 | 0 | 0
2017-03-03 20:00 | 3 | 20 | 0 | 0
2017-03-03 21:00 | 3 | 21 | 0 | 0
2017-03-03 22:00 | 3 | 22 | 0 | 0
2017-03-03 23:00 | 3 | 23 | 0 | 0
2017-03-04 | 3 | 0 | 0 | 0
2017-03-04 01:00 | 3 | 1 | 0 | 0
2017-03-04 02:00 | 3 | 2 | 0 | 0
2017-03-04 03:00 | 3 | 3 | 0 | 0
2017-03-04 04:00 | 3 | 4 | 0 | 0
2017-03-04 05:00 | 3 | 5 | 0 | 0
2017-03-04 06:00 | 3 | 6 | 312.7045 | 312.7045
2017-03-04 07:00 | 3 | 7 | 2439.9676 | 2439.9676
2017-03-04 08:00 | 3 | 8 | 4898.2651 | 4898.2651
2017-03-04 09:00 | 3 | 9 | 4775.4417 | 4775.4417
2017-03-04 10:00 | 3 | 10 | 5832.1571 | 5832.1571
2017-03-04 11:00 | 3 | 11 | 5196.099 | 5196.099
2017-03-04 12:00 | 3 | 12 | 5839.915 | 5839.915
2017-03-04 13:00 | 3 | 13 | 3767.3448 | 3767.3448
2017-03-04 14:00 | 3 | 14 | 3669.1405 | 3669.1405
2017-03-04 15:00 | 3 | 15 | 2466.3659 | 2466.3659
2017-03-04 16:00 | 3 | 16 | 790.5813 | 790.5813
2017-03-04 17:00 | 3 | 17 | 0 | 0
2017-03-04 18:00 | 3 | 18 | 0 | 0
2017-03-04 19:00 | 3 | 19 | 0 | 0
2017-03-04 20:00 | 3 | 20 | 0 | 0
2017-03-04 21:00 | 3 | 21 | 0 | 0
2017-03-04 22:00 | 3 | 22 | 0 | 0
2017-03-04 23:00 | 3 | 23 | 0 | 0
2017-03-05 | 3 | 0 | 0 | 0
2017-03-05 01:00 | 3 | 1 | 0 | 0
2017-03-05 02:00 | 3 | 2 | 0 | 0
2017-03-05 03:00 | 3 | 3 | 0 | 0
2017-03-05 04:00 | 3 | 4 | 0 | 0
2017-03-05 05:00 | 3 | 5 | 0 | 0
2017-03-05 06:00 | 3 | 6 | 320.3888 | 320.3888
2017-03-05 07:00 | 3 | 7 | 961.3379 | 961.3379
2017-03-05 08:00 | 3 | 8 | 2530.0264 | 2530.0264
2017-03-05 09:00 | 3 | 9 | 3141.3089 | 3141.3089
2017-03-05 10:00 | 3 | 10 | 3798.0141 | 3798.0141
2017-03-05 11:00 | 3 | 11 | 3067.9493 | 3067.9493
2017-03-05 12:00 | 3 | 12 | 3820.1792 | 3820.1792
2017-03-05 13:00 | 3 | 13 | 1558.7054 | 1558.7054
2017-03-05 14:00 | 3 | 14 | 2943.456 | 2943.456
2017-03-05 15:00 | 3 | 15 | 323.1684 | 323.1684
2017-03-05 16:00 | 3 | 16 | 1595.901 | 1595.901
2017-03-05 17:00 | 3 | 17 | 0 | 0
2017-03-05 18:00 | 3 | 18 | 0 | 0
2017-03-05 19:00 | 3 | 19 | 0 | 0
2017-03-05 20:00 | 3 | 20 | 0 | 0
2017-03-05 21:00 | 3 | 21 | 0 | 0
2017-03-05 22:00 | 3 | 22 | 0 | 0
2017-03-05 23:00 | 3 | 23 | 0 | 0
2017-03-06 | 3 | 0 | 0 | 0
2017-03-06 01:00 | 3 | 1 | 0 | 0
2017-03-06 02:00 | 3 | 2 | 0 | 0
2017-03-06 03:00 | 3 | 3 | 0 | 0
2017-03-06 04:00 | 3 | 4 | 0 | 0
2017-03-06 05:00 | 3 | 5 | 0 | 0
2017-03-06 06:00 | 3 | 6 | 0 | 0
2017-03-06 07:00 | 3 | 7 | 146.7745 | 146.7745
2017-03-06 08:00 | 3 | 8 | 1019.4278 | 1019.4278
2017-03-06 09:00 | 3 | 9 | 978.7155 | 978.7155
2017-03-06 10:00 | 3 | 10 | 2398.0375 | 2398.0375
2017-03-06 11:00 | 3 | 11 | 3469.4936 | 3469.4936
2017-03-06 12:00 | 3 | 12 | 2697.3595 | 2697.3595
2017-03-06 13:00 | 3 | 13 | 1950.5334 | 1950.5334
2017-03-06 14:00 | 3 | 14 | 1013.4915 | 1013.4915
2017-03-06 15:00 | 3 | 15 | 812.4002 | 812.4002
2017-03-06 16:00 | 3 | 16 | 157.2406 | 157.2406
2017-03-06 17:00 | 3 | 17 | 0 | 0
2017-03-06 18:00 | 3 | 18 | 0 | 0
2017-03-06 19:00 | 3 | 19 | 0 | 0
2017-03-06 20:00 | 3 | 20 | 0 | 0
2017-03-06 21:00 | 3 | 21 | 0 | 0
2017-03-06 22:00 | 3 | 22 | 0 | 0
2017-03-06 23:00 | 3 | 23 | 0 | 0
2017-03-07 | 3 | 0 | 0 | 0
2017-03-07 01:00 | 3 | 1 | 0 | 0
2017-03-07 02:00 | 3 | 2 | 0 | 0
2017-03-07 03:00 | 3 | 3 | 0 | 0
2017-03-07 04:00 | 3 | 4 | 0 | 0
2017-03-07 05:00 | 3 | 5 | 0 | 0
2017-03-07 06:00 | 3 | 6 | 24.0821 | 24.0821
2017-03-07 07:00 | 3 | 7 | 489.0524 | 489.0524
2017-03-07 08:00 | 3 | 8 | 1613.8847 | 1613.8847
2017-03-07 09:00 | 3 | 9 | 3051.1018 | 3051.1018
2017-03-07 10:00 | 3 | 10 | 3240.7115 | 3240.7115
2017-03-07 11:00 | 3 | 11 | 5132.6892 | 5132.6892
2017-03-07 12:00 | 3 | 12 | 3730.7 | 3730.7001
2017-03-07 13:00 | 3 | 13 | 4097.1498 | 4097.1498
2017-03-07 14:00 | 3 | 14 | 2209.8595 | 2209.8595
2017-03-07 15:00 | 3 | 15 | 1789.546 | 1789.546
2017-03-07 16:00 | 3 | 16 | 599.7388 | 599.7388
2017-03-07 17:00 | 3 | 17 | 0 | 0
2017-03-07 18:00 | 3 | 18 | 0 | 0
2017-03-07 19:00 | 3 | 19 | 0 | 0
2017-03-07 20:00 | 3 | 20 | 0 | 0
2017-03-07 21:00 | 3 | 21 | 0 | 0
2017-03-07 22:00 | 3 | 22 | 0 | 0
2017-03-07 23:00 | 3 | 23 | 0 | 0
2017-03-08 | 3 | 0 | 0 | 0
2017-03-08 01:00 | 3 | 1 | 0 | 0
2017-03-08 02:00 | 3 | 2 | 0 | 0
2017-03-08 03:00 | 3 | 3 | 0 | 0
2017-03-08 04:00 | 3 | 4 | 0 | 0
2017-03-08 05:00 | 3 | 5 | 0 | 0
2017-03-08 06:00 | 3 | 6 | 0 | 0
2017-03-08 07:00 | 3 | 7 | 137.7803 | 137.7803
2017-03-08 08:00 | 3 | 8 | 1053.5656 | 1053.5656
2017-03-08 09:00 | 3 | 9 | 1667.14 | 1667.14
2017-03-08 10:00 | 3 | 10 | 1344.7076 | 1344.7076
2017-03-08 11:00 | 3 | 11 | 3453.059 | 3453.059
2017-03-08 12:00 | 3 | 12 | 2872.4711 | 2872.4711
2017-03-08 13:00 | 3 | 13 | 3280.3876 | 3280.3876
2017-03-08 14:00 | 3 | 14 | 901.9507 | 901.9507
2017-03-08 15:00 | 3 | 15 | 362.6329 | 362.6329
2017-03-08 16:00 | 3 | 16 | 65.067 | 65.067
2017-03-08 17:00 | 3 | 17 | 0 | 0
2017-03-08 18:00 | 3 | 18 | 0 | 0
2017-03-08 19:00 | 3 | 19 | 0 | 0
2017-03-08 20:00 | 3 | 20 | 0 | 0
2017-03-08 21:00 | 3 | 21 | 0 | 0
2017-03-08 22:00 | 3 | 22 | 0 | 0
2017-03-08 23:00 | 3 | 23 | 0 | 0
2017-03-09 | 3 | 0 | 0 | 0
2017-03-09 01:00 | 3 | 1 | 0 | 0
2017-03-09 02:00 | 3 | 2 | 0 | 0
2017-03-09 03:00 | 3 | 3 | 0 | 0
2017-03-09 04:00 | 3 | 4 | 0 | 0
2017-03-09 05:00 | 3 | 5 | 0 | 0
2017-03-09 06:00 | 3 | 6 | 483.6291 | 483.6291
2017-03-09 07:00 | 3 | 7 | 2859.7901 | 2859.7901
2017-03-09 08:00 | 3 | 8 | 5412.7061 | 5412.7061
2017-03-09 09:00 | 3 | 9 | 7340.9985 | 7340.9985
2017-03-09 10:00 | 3 | 10 | 8557.6503 | 8557.6503
2017-03-09 11:00 | 3 | 11 | 9093.9803 | 9093.9803
2017-03-09 12:00 | 3 | 12 | 9016.9867 | 9016.9867
2017-03-09 13:00 | 3 | 13 | 8249.5768 | 8249.5768
2017-03-09 14:00 | 3 | 14 | 6876.9827 | 6876.9827
2017-03-09 15:00 | 3 | 15 | 4737.8792 | 4737.8792
2017-03-09 16:00 | 3 | 16 | 2281.6471 | 2281.6471
2017-03-09 17:00 | 3 | 17 | 228.7143 | 228.7143
2017-03-09 18:00 | 3 | 18 | 0 | 0
2017-03-09 19:00 | 3 | 19 | 0 | 0
2017-03-09 20:00 | 3 | 20 | 0 | 0
2017-03-09 21:00 | 3 | 21 | 0 | 0
2017-03-09 22:00 | 3 | 22 | 0 | 0
2017-03-09 23:00 | 3 | 23 | 0 | 0
2017-03-10 | 3 | 0 | 0 | 0
2017-03-10 01:00 | 3 | 1 | 0 | 0
2017-03-10 02:00 | 3 | 2 | 0 | 0
2017-03-10 03:00 | 3 | 3 | 0 | 0
2017-03-10 04:00 | 3 | 4 | 0 | 0
2017-03-10 05:00 | 3 | 5 | 0 | 0
2017-03-10 06:00 | 3 | 6 | 462.9291 | 462.9291
2017-03-10 07:00 | 3 | 7 | 1107.5293 | 1107.5293
2017-03-10 08:00 | 3 | 8 | 2910.5442 | 2910.5442
2017-03-10 09:00 | 3 | 9 | 3983.0894 | 3983.0894
2017-03-10 10:00 | 3 | 10 | 5626.9051 | 5626.9051
2017-03-10 11:00 | 3 | 11 | 6781.0544 | 6781.0544
2017-03-10 12:00 | 3 | 12 | 7199.4968 | 7199.4968
2017-03-10 13:00 | 3 | 13 | 7843.9867 | 7843.9867
2017-03-10 14:00 | 3 | 14 | 6552.9288 | 6552.9288
2017-03-10 15:00 | 3 | 15 | 4627.3838 | 4627.3838
2017-03-10 16:00 | 3 | 16 | 2194.9463 | 2194.9463
2017-03-10 17:00 | 3 | 17 | 197.5654 | 197.5654
2017-03-10 18:00 | 3 | 18 | 0 | 0
2017-03-10 19:00 | 3 | 19 | 0 | 0
2017-03-10 20:00 | 3 | 20 | 0 | 0
2017-03-10 21:00 | 3 | 21 | 0 | 0
2017-03-10 22:00 | 3 | 22 | 0 | 0
2017-03-10 23:00 | 3 | 23 | 0 | 0
2017-03-11 | 3 | 0 | 0 | 0
2017-03-11 01:00 | 3 | 1 | 0 | 0
2017-03-11 02:00 | 3 | 2 | 0 | 0
2017-03-11 03:00 | 3 | 3 | 0 | 0
2017-03-11 04:00 | 3 | 4 | 0 | 0
2017-03-11 05:00 | 3 | 5 | 0 | 0
2017-03-11 06:00 | 3 | 6 | 419.8569 | 419.8569
2017-03-11 07:00 | 3 | 7 | 1400.6206 | 1400.6206
2017-03-11 08:00 | 3 | 8 | 4871.6599 | 4871.6599
2017-03-11 09:00 | 3 | 9 | 5628.0045 | 5628.0045
2017-03-11 10:00 | 3 | 10 | 7120.4216 | 7120.4216
2017-03-11 11:00 | 3 | 11 | 7267.494 | 7267.494
2017-03-11 12:00 | 3 | 12 | 5012.252 | 5012.252
2017-03-11 13:00 | 3 | 13 | 6742.0693 | 6742.0693
2017-03-11 14:00 | 3 | 14 | 5312.7608 | 5312.7608
2017-03-11 15:00 | 3 | 15 | 3790.331 | 3790.331
2017-03-11 16:00 | 3 | 16 | 1134.0495 | 1134.0495
2017-03-11 17:00 | 3 | 17 | 22.7608 | 22.7608
2017-03-11 18:00 | 3 | 18 | 0 | 0
2017-03-11 19:00 | 3 | 19 | 0 | 0
2017-03-11 20:00 | 3 | 20 | 0 | 0
2017-03-11 21:00 | 3 | 21 | 0 | 0
2017-03-11 22:00 | 3 | 22 | 0 | 0
2017-03-11 23:00 | 3 | 23 | 0 | 0
2017-03-12 | 3 | 0 | 0 | 0
2017-03-12 01:00 | 3 | 1 | 0 | 0
2017-03-12 02:00 | 3 | 2 | 0 | 0
2017-03-12 03:00 | 3 | 3 | 0 | 0
2017-03-12 04:00 | 3 | 4 | 0 | 0
2017-03-12 05:00 | 3 | 5 | 0 | 0
2017-03-12 06:00 | 3 | 6 | 33.2511 | 33.2511
2017-03-12 07:00 | 3 | 7 | 848.1284 | 848.1284
2017-03-12 08:00 | 3 | 8 | 1087.9874 | 1087.9874
2017-03-12 09:00 | 3 | 9 | 2023.1513 | 2023.1513
2017-03-12 10:00 | 3 | 10 | 3332.2377 | 3332.2377
2017-03-12 11:00 | 3 | 11 | 3283.5835 | 3283.5835
2017-03-12 12:00 | 3 | 12 | 2671.2947 | 2671.2947
2017-03-12 13:00 | 3 | 13 | 3177.128 | 3177.128
2017-03-12 14:00 | 3 | 14 | 1849.6393 | 1849.6393
2017-03-12 15:00 | 3 | 15 | 1040.9731 | 1040.9731
2017-03-12 16:00 | 3 | 16 | 280.3171 | 280.3171
2017-03-12 17:00 | 3 | 17 | 0 | 0
2017-03-12 18:00 | 3 | 18 | 0 | 0
2017-03-12 19:00 | 3 | 19 | 0 | 0
2017-03-12 20:00 | 3 | 20 | 0 | 0
2017-03-12 21:00 | 3 | 21 | 0 | 0
2017-03-12 22:00 | 3 | 22 | 0 | 0
2017-03-12 23:00 | 3 | 23 | 0 | 0
2017-03-13 | 3 | 0 | 0 | 0
2017-03-13 01:00 | 3 | 1 | 0 | 0
2017-03-13 02:00 | 3 | 2 | 0 | 0
2017-03-13 03:00 | 3 | 3 | 0 | 0
2017-03-13 04:00 | 3 | 4 | 0 | 0
2017-03-13 05:00 | 3 | 5 | 0 | 0
2017-03-13 06:00 | 3 | 6 | 511.206 | 511.206
2017-03-13 07:00 | 3 | 7 | 2820.605 | 2820.605
2017-03-13 08:00 | 3 | 8 | 4100.0593 | 4100.0593
2017-03-13 09:00 | 3 | 9 | 5503.7942 | 5503.7942
2017-03-13 10:00 | 3 | 10 | 6490.0388 | 6490.0388
2017-03-13 11:00 | 3 | 11 | 7537.5554 | 7537.5554
2017-03-13 12:00 | 3 | 12 | 8110.6441 | 8110.6441
2017-03-13 13:00 | 3 | 13 | 7468.5416 | 7468.5416
2017-03-13 14:00 | 3 | 14 | 6224.8982 | 6224.8982
2017-03-13 15:00 | 3 | 15 | 4415.6815 | 4415.6815
2017-03-13 16:00 | 3 | 16 | 2157.4931 | 2157.4931
2017-03-13 17:00 | 3 | 17 | 252.686 | 252.686
2017-03-13 18:00 | 3 | 18 | 0 | 0
2017-03-13 19:00 | 3 | 19 | 0 | 0
2017-03-13 20:00 | 3 | 20 | 0 | 0
2017-03-13 21:00 | 3 | 21 | 0 | 0
2017-03-13 22:00 | 3 | 22 | 0 | 0
2017-03-13 23:00 | 3 | 23 | 0 | 0
2017-03-14 | 3 | 0 | 0 | 0
2017-03-14 01:00 | 3 | 1 | 0 | 0
2017-03-14 02:00 | 3 | 2 | 0 | 0
2017-03-14 03:00 | 3 | 3 | 0 | 0
2017-03-14 04:00 | 3 | 4 | 0 | 0
2017-03-14 05:00 | 3 | 5 | 0 | 0
2017-03-14 06:00 | 3 | 6 | 127.7811 | 127.7811
2017-03-14 07:00 | 3 | 7 | 743.13 | 743.13
2017-03-14 08:00 | 3 | 8 | 2211.1372 | 2211.1372
2017-03-14 09:00 | 3 | 9 | 4011.2874 | 4011.2874
2017-03-14 10:00 | 3 | 10 | 7053.4192 | 7053.4192
2017-03-14 11:00 | 3 | 11 | 4105.684 | 4105.684
2017-03-14 12:00 | 3 | 12 | 6210.629 | 6210.629
2017-03-14 13:00 | 3 | 13 | 5643.1385 | 5643.1385
2017-03-14 14:00 | 3 | 14 | 5030.3081 | 5030.3081
2017-03-14 15:00 | 3 | 15 | 3604.4944 | 3604.4944
2017-03-14 16:00 | 3 | 16 | 1274.9348 | 1274.9348
2017-03-14 17:00 | 3 | 17 | 107.4261 | 107.4261
2017-03-14 18:00 | 3 | 18 | 0 | 0
2017-03-14 19:00 | 3 | 19 | 0 | 0
2017-03-14 20:00 | 3 | 20 | 0 | 0
2017-03-14 21:00 | 3 | 21 | 0 | 0
2017-03-14 22:00 | 3 | 22 | 0 | 0
2017-03-14 23:00 | 3 | 23 | 0 | 0
2017-03-15 | 3 | 0 | 0 | 0
2017-03-15 01:00 | 3 | 1 | 0 | 0
2017-03-15 02:00 | 3 | 2 | 0 | 0
2017-03-15 03:00 | 3 | 3 | 0 | 0
2017-03-15 04:00 | 3 | 4 | 0 | 0
2017-03-15 05:00 | 3 | 5 | 0 | 0
2017-03-15 06:00 | 3 | 6 | 630.9383 | 630.9383
2017-03-15 07:00 | 3 | 7 | 2519.8386 | 2519.8386
2017-03-15 08:00 | 3 | 8 | 3805.3787 | 3805.3787
2017-03-15 09:00 | 3 | 9 | 4957.7845 | 4957.7845
2017-03-15 10:00 | 3 | 10 | 5139.8951 | 5139.8951
2017-03-15 11:00 | 3 | 11 | 7271.3131 | 7271.3131
2017-03-15 12:00 | 3 | 12 | 6936.3561 | 6936.3561
2017-03-15 13:00 | 3 | 13 | 4507.6239 | 4507.6239
2017-03-15 14:00 | 3 | 14 | 6444.3803 | 6444.3803
2017-03-15 15:00 | 3 | 15 | 4480.6289 | 4480.6289
2017-03-15 16:00 | 3 | 16 | 2207.8827 | 2207.8827
2017-03-15 17:00 | 3 | 17 | 229.931 | 229.931
2017-03-15 18:00 | 3 | 18 | 0 | 0
2017-03-15 19:00 | 3 | 19 | 0 | 0
2017-03-15 20:00 | 3 | 20 | 0 | 0
2017-03-15 21:00 | 3 | 21 | 0 | 0
2017-03-15 22:00 | 3 | 22 | 0 | 0
2017-03-15 23:00 | 3 | 23 | 0 | 0
2017-03-16 | 3 | 0 | 0 | 0
2017-03-16 01:00 | 3 | 1 | 0 | 0
2017-03-16 02:00 | 3 | 2 | 0 | 0
2017-03-16 03:00 | 3 | 3 | 0 | 0
2017-03-16 04:00 | 3 | 4 | 0 | 0
2017-03-16 05:00 | 3 | 5 | 0 | 0
2017-03-16 06:00 | 3 | 6 | 671.7173 | 671.7173
2017-03-16 07:00 | 3 | 7 | 3057.965 | 3057.965
2017-03-16 08:00 | 3 | 8 | 5372.2503 | 5372.2503
2017-03-16 09:00 | 3 | 9 | 5486.0566 | 5486.0566
2017-03-16 10:00 | 3 | 10 | 5493.9076 | 5493.9076
2017-03-16 11:00 | 3 | 11 | 5876.3171 | 5876.3171
2017-03-16 12:00 | 3 | 12 | 5995.3019 | 5995.3019
2017-03-16 13:00 | 3 | 13 | 5508.3425 | 5508.3425
2017-03-16 14:00 | 3 | 14 | 4687.4563 | 4687.4563
2017-03-16 15:00 | 3 | 15 | 4670.6709 | 4670.6709
2017-03-16 16:00 | 3 | 16 | 2351.1612 | 2351.1612
2017-03-16 17:00 | 3 | 17 | 321.3203 | 321.3203
2017-03-16 18:00 | 3 | 18 | 0 | 0
2017-03-16 19:00 | 3 | 19 | 0 | 0
2017-03-16 20:00 | 3 | 20 | 0 | 0
2017-03-16 21:00 | 3 | 21 | 0 | 0
2017-03-16 22:00 | 3 | 22 | 0 | 0
2017-03-16 23:00 | 3 | 23 | 0 | 0
2017-03-17 | 3 | 0 | 0 | 0
2017-03-17 01:00 | 3 | 1 | 0 | 0
2017-03-17 02:00 | 3 | 2 | 0 | 0
2017-03-17 03:00 | 3 | 3 | 0 | 0
2017-03-17 04:00 | 3 | 4 | 0 | 0
2017-03-17 05:00 | 3 | 5 | 0 | 0
2017-03-17 06:00 | 3 | 6 | 710.0778 | 710.0778
2017-03-17 07:00 | 3 | 7 | 3167.5784 | 3167.5784
2017-03-17 08:00 | 3 | 8 | 5520.6267 | 5520.6267
2017-03-17 09:00 | 3 | 9 | 7310.3499 | 7310.3499
2017-03-17 10:00 | 3 | 10 | 8452.4344 | 8452.4344
2017-03-17 11:00 | 3 | 11 | 8991.8098 | 8991.8098
2017-03-17 12:00 | 3 | 12 | 7947.8788 | 7947.8788
2017-03-17 13:00 | 3 | 13 | 7441.6132 | 7441.6132
2017-03-17 14:00 | 3 | 14 | 6336.7024 | 6336.7024
2017-03-17 15:00 | 3 | 15 | 4995.9358 | 4995.9358
2017-03-17 16:00 | 3 | 16 | 2514.5359 | 2514.5359
2017-03-17 17:00 | 3 | 17 | 360.9493 | 360.9493
2017-03-17 18:00 | 3 | 18 | 0 | 0
2017-03-17 19:00 | 3 | 19 | 0 | 0
2017-03-17 20:00 | 3 | 20 | 0 | 0
2017-03-17 21:00 | 3 | 21 | 0 | 0
2017-03-17 22:00 | 3 | 22 | 0 | 0
2017-03-17 23:00 | 3 | 23 | 0 | 0
2017-03-18 | 3 | 0 | 0 | 0
2017-03-18 01:00 | 3 | 1 | 0 | 0
2017-03-18 02:00 | 3 | 2 | 0 | 0
2017-03-18 03:00 | 3 | 3 | 0 | 0
2017-03-18 04:00 | 3 | 4 | 0 | 0
2017-03-18 05:00 | 3 | 5 | 0 | 0
2017-03-18 06:00 | 3 | 6 | 794.3326 | 794.3326
2017-03-18 07:00 | 3 | 7 | 2403.27 | 2403.27
2017-03-18 08:00 | 3 | 8 | 4387.9779 | 4387.9779
2017-03-18 09:00 | 3 | 9 | 6276.4021 | 6276.4021
2017-03-18 10:00 | 3 | 10 | 7258.9334 | 7258.9334
2017-03-18 11:00 | 3 | 11 | 7848.7063 | 7848.7063
2017-03-18 12:00 | 3 | 12 | 7150.7816 | 7150.7816
2017-03-18 13:00 | 3 | 13 | 6860.5964 | 6860.5964
2017-03-18 14:00 | 3 | 14 | 4568.9408 | 4568.9408
2017-03-18 15:00 | 3 | 15 | 2441.3085 | 2441.3085
2017-03-18 16:00 | 3 | 16 | 932.7236 | 932.7236
2017-03-18 17:00 | 3 | 17 | 96.9565 | 96.9565
2017-03-18 18:00 | 3 | 18 | 0 | 0
2017-03-18 19:00 | 3 | 19 | 0 | 0
2017-03-18 20:00 | 3 | 20 | 0 | 0
2017-03-18 21:00 | 3 | 21 | 0 | 0
2017-03-18 22:00 | 3 | 22 | 0 | 0
2017-03-18 23:00 | 3 | 23 | 0 | 0
2017-03-19 | 3 | 0 | 0 | 0
2017-03-19 01:00 | 3 | 1 | 0 | 0
2017-03-19 02:00 | 3 | 2 | 0 | 0
2017-03-19 03:00 | 3 | 3 | 0 | 0
2017-03-19 04:00 | 3 | 4 | 0 | 0
2017-03-19 05:00 | 3 | 5 | 0 | 0
2017-03-19 06:00 | 3 | 6 | 24.2535 | 24.2535
2017-03-19 07:00 | 3 | 7 | 697.2611 | 697.2611
2017-03-19 08:00 | 3 | 8 | 1192.1314 | 1192.1314
2017-03-19 09:00 | 3 | 9 | 1591.6667 | 1591.6667
2017-03-19 10:00 | 3 | 10 | 3666.9141 | 3666.9141
2017-03-19 11:00 | 3 | 11 | 4215.126 | 4215.126
2017-03-19 12:00 | 3 | 12 | 1739.7924 | 1739.7925
2017-03-19 13:00 | 3 | 13 | 2354.6146 | 2354.6146
2017-03-19 14:00 | 3 | 14 | 1852.9985 | 1852.9984
2017-03-19 15:00 | 3 | 15 | 4735.4976 | 4735.4976
2017-03-19 16:00 | 3 | 16 | 2337.3485 | 2337.3485
2017-03-19 17:00 | 3 | 17 | 330.5169 | 330.5169
2017-03-19 18:00 | 3 | 18 | 0 | 0
2017-03-19 19:00 | 3 | 19 | 0 | 0
2017-03-19 20:00 | 3 | 20 | 0 | 0
2017-03-19 21:00 | 3 | 21 | 0 | 0
2017-03-19 22:00 | 3 | 22 | 0 | 0
2017-03-19 23:00 | 3 | 23 | 0 | 0
2017-03-20 | 3 | 0 | 0 | 0
2017-03-20 01:00 | 3 | 1 | 0 | 0
2017-03-20 02:00 | 3 | 2 | 0 | 0
2017-03-20 03:00 | 3 | 3 | 0 | 0
2017-03-20 04:00 | 3 | 4 | 0 | 0
2017-03-20 05:00 | 3 | 5 | 0 | 0
2017-03-20 06:00 | 3 | 6 | 838.2281 | 838.2281
2017-03-20 07:00 | 3 | 7 | 3342.3657 | 3342.3657
2017-03-20 08:00 | 3 | 8 | 5824.1727 | 5824.1727
2017-03-20 09:00 | 3 | 9 | 7707.7266 | 7707.7266
2017-03-20 10:00 | 3 | 10 | 6970.4961 | 6970.4962
2017-03-20 11:00 | 3 | 11 | 7338.2247 | 7338.2247
2017-03-20 12:00 | 3 | 12 | 7412.5814 | 7412.5814
2017-03-20 13:00 | 3 | 13 | 8568.1336 | 8568.1336
2017-03-20 14:00 | 3 | 14 | 7167.3577 | 7167.3577
2017-03-20 15:00 | 3 | 15 | 5103.1917 | 5103.1917
2017-03-20 16:00 | 3 | 16 | 2602.4638 | 2602.4638
2017-03-20 17:00 | 3 | 17 | 415.9665 | 415.9665
2017-03-20 18:00 | 3 | 18 | 0 | 0
2017-03-20 19:00 | 3 | 19 | 0 | 0
2017-03-20 20:00 | 3 | 20 | 0 | 0
2017-03-20 21:00 | 3 | 21 | 0 | 0
2017-03-20 22:00 | 3 | 22 | 0 | 0
2017-03-20 23:00 | 3 | 23 | 0 | 0
2017-03-21 | 3 | 0 | 0 | 0
2017-03-21 01:00 | 3 | 1 | 0 | 0
2017-03-21 02:00 | 3 | 2 | 0 | 0
2017-03-21 03:00 | 3 | 3 | 0 | 0
2017-03-21 04:00 | 3 | 4 | 0 | 0
2017-03-21 05:00 | 3 | 5 | 0 | 0
2017-03-21 06:00 | 3 | 6 | 821.5324 | 821.5324
2017-03-21 07:00 | 3 | 7 | 551.9126 | 551.9126
2017-03-21 08:00 | 3 | 8 | 3950.8848 | 3950.8848
2017-03-21 09:00 | 3 | 9 | 5298.1064 | 5298.1064
2017-03-21 10:00 | 3 | 10 | 3030.7606 | 3030.7606
2017-03-21 11:00 | 3 | 11 | 5360.4363 | 5360.4363
2017-03-21 12:00 | 3 | 12 | 3156.9662 | 3156.9662
2017-03-21 13:00 | 3 | 13 | 4702.9664 | 4702.9664
2017-03-21 14:00 | 3 | 14 | 4820.7356 | 4820.7356
2017-03-21 15:00 | 3 | 15 | 1926.005 | 1926.0051
2017-03-21 16:00 | 3 | 16 | 421.9649 | 421.9649
2017-03-21 17:00 | 3 | 17 | 35.0255 | 35.0255
2017-03-21 18:00 | 3 | 18 | 0 | 0
2017-03-21 19:00 | 3 | 19 | 0 | 0
2017-03-21 20:00 | 3 | 20 | 0 | 0
2017-03-21 21:00 | 3 | 21 | 0 | 0
2017-03-21 22:00 | 3 | 22 | 0 | 0
2017-03-21 23:00 | 3 | 23 | 0 | 0
2017-03-22 | 3 | 0 | 0 | 0
2017-03-22 01:00 | 3 | 1 | 0 | 0
2017-03-22 02:00 | 3 | 2 | 0 | 0
2017-03-22 03:00 | 3 | 3 | 0 | 0
2017-03-22 04:00 | 3 | 4 | 0 | 0
2017-03-22 05:00 | 3 | 5 | 0 | 0
2017-03-22 06:00 | 3 | 6 | 923.3798 | 923.3798
2017-03-22 07:00 | 3 | 7 | 3421.8767 | 3421.8768
2017-03-22 08:00 | 3 | 8 | 5811.5756 | 5811.5756
2017-03-22 09:00 | 3 | 9 | 7592.8198 | 7592.8198
2017-03-22 10:00 | 3 | 10 | 8679.5054 | 8679.5054
2017-03-22 11:00 | 3 | 11 | 8198.5593 | 8198.5593
2017-03-22 12:00 | 3 | 12 | 6709.6071 | 6709.6071
2017-03-22 13:00 | 3 | 13 | 7264.2855 | 7264.2855
2017-03-22 14:00 | 3 | 14 | 7186.9606 | 7186.9606
2017-03-22 15:00 | 3 | 15 | 4160.2434 | 4160.2434
2017-03-22 16:00 | 3 | 16 | 952.6519 | 952.6519
2017-03-22 17:00 | 3 | 17 | 432.0711 | 432.0711
2017-03-22 18:00 | 3 | 18 | 0 | 0
2017-03-22 19:00 | 3 | 19 | 0 | 0
2017-03-22 20:00 | 3 | 20 | 0 | 0
2017-03-22 21:00 | 3 | 21 | 0 | 0
2017-03-22 22:00 | 3 | 22 | 0 | 0
2017-03-22 23:00 | 3 | 23 | 0 | 0
2017-03-23 | 3 | 0 | 0 | 0
2017-03-23 01:00 | 3 | 1 | 0 | 0
2017-03-23 02:00 | 3 | 2 | 0 | 0
2017-03-23 03:00 | 3 | 3 | 0 | 0
2017-03-23 04:00 | 3 | 4 | 0 | 0
2017-03-23 05:00 | 3 | 5 | 0 | 0
2017-03-23 06:00 | 3 | 6 | 984.6978 | 984.6978
2017-03-23 07:00 | 3 | 7 | 3581.6014 | 3581.6014
2017-03-23 08:00 | 3 | 8 | 6021.7208 | 6021.7208
2017-03-23 09:00 | 3 | 9 | 6921.229 | 6921.229
2017-03-23 10:00 | 3 | 10 | 7828.9148 | 7828.9148
2017-03-23 11:00 | 3 | 11 | 8448.92 | 8448.92
2017-03-23 12:00 | 3 | 12 | 8252.3609 | 8252.3609
2017-03-23 13:00 | 3 | 13 | 7409.0463 | 7409.0463
2017-03-23 14:00 | 3 | 14 | 7226.3033 | 7226.3033
2017-03-23 15:00 | 3 | 15 | 5203.3877 | 5203.3877
2017-03-23 16:00 | 3 | 16 | 2694.8605 | 2694.8605
2017-03-23 17:00 | 3 | 17 | 444.4911 | 444.4911
2017-03-23 18:00 | 3 | 18 | 0 | 0
2017-03-23 19:00 | 3 | 19 | 0 | 0
2017-03-23 20:00 | 3 | 20 | 0 | 0
2017-03-23 21:00 | 3 | 21 | 0 | 0
2017-03-23 22:00 | 3 | 22 | 0 | 0
2017-03-23 23:00 | 3 | 23 | 0 | 0
2017-03-24 | 3 | 0 | 0 | 0
2017-03-24 01:00 | 3 | 1 | 0 | 0
2017-03-24 02:00 | 3 | 2 | 0 | 0
2017-03-24 03:00 | 3 | 3 | 0 | 0
2017-03-24 04:00 | 3 | 4 | 0 | 0
2017-03-24 05:00 | 3 | 5 | 0 | 0
2017-03-24 06:00 | 3 | 6 | 1023.2033 | 1023.2033
2017-03-24 07:00 | 3 | 7 | 3566.0131 | 3566.0131
2017-03-24 08:00 | 3 | 8 | 5978.3601 | 5978.3601
2017-03-24 09:00 | 3 | 9 | 7759.5974 | 7759.5974
2017-03-24 10:00 | 3 | 10 | 8553.915 | 8553.915
2017-03-24 11:00 | 3 | 11 | 9029.9127 | 9029.9127
2017-03-24 12:00 | 3 | 12 | 8876.6211 | 8876.6211
2017-03-24 13:00 | 3 | 13 | 8189.2581 | 8189.2581
2017-03-24 14:00 | 3 | 14 | 6870.882 | 6870.882
2017-03-24 15:00 | 3 | 15 | 4997.7712 | 4997.7712
2017-03-24 16:00 | 3 | 16 | 2659.6326 | 2659.6326
2017-03-24 17:00 | 3 | 17 | 458.053 | 458.053
2017-03-24 18:00 | 3 | 18 | 0 | 0
2017-03-24 19:00 | 3 | 19 | 0 | 0
2017-03-24 20:00 | 3 | 20 | 0 | 0
2017-03-24 21:00 | 3 | 21 | 0 | 0
2017-03-24 22:00 | 3 | 22 | 0 | 0
2017-03-24 23:00 | 3 | 23 | 0 | 0
2017-03-25 | 3 | 0 | 0 | 0
2017-03-25 01:00 | 3 | 1 | 0 | 0
2017-03-25 02:00 | 3 | 2 | 0 | 0
2017-03-25 03:00 | 3 | 3 | 0 | 0
2017-03-25 04:00 | 3 | 4 | 0 | 0
2017-03-25 05:00 | 3 | 5 | 0 | 0
2017-03-25 06:00 | 3 | 6 | 896.6332 | 896.6332
2017-03-25 07:00 | 3 | 7 | 3013.4358 | 3013.4358
2017-03-25 08:00 | 3 | 8 | 5042.6695 | 5042.6695
2017-03-25 09:00 | 3 | 9 | 5989.8198 | 5989.8198
2017-03-25 10:00 | 3 | 10 | 7735.598 | 7735.598
2017-03-25 11:00 | 3 | 11 | 8322.4212 | 8322.4212
2017-03-25 12:00 | 3 | 12 | 8554.8155 | 8554.8155
2017-03-25 13:00 | 3 | 13 | 7701.9134 | 7701.9134
2017-03-25 14:00 | 3 | 14 | 5777.7621 | 5777.7621
2017-03-25 15:00 | 3 | 15 | 3550.8308 | 3550.8308
2017-03-25 16:00 | 3 | 16 | 1233.4153 | 1233.4153
2017-03-25 17:00 | 3 | 17 | 240.3097 | 240.3097
2017-03-25 18:00 | 3 | 18 | 0 | 0
2017-03-25 19:00 | 3 | 19 | 0 | 0
2017-03-25 20:00 | 3 | 20 | 0 | 0
2017-03-25 21:00 | 3 | 21 | 0 | 0
2017-03-25 22:00 | 3 | 22 | 0 | 0
2017-03-25 23:00 | 3 | 23 | 0 | 0
2017-03-26 | 3 | 0 | 0 | 0
2017-03-26 01:00 | 3 | 1 | 0 | 0
2017-03-26 02:00 | 3 | 2 | 0 | 0
2017-03-26 03:00 | 3 | 3 | 0 | 0
2017-03-26 04:00 | 3 | 4 | 0 | 0
2017-03-26 05:00 | 3 | 5 | 0 | 0
2017-03-26 06:00 | 3 | 6 | 169.74 | 169.74
2017-03-26 07:00 | 3 | 7 | 2445.9948 | 2445.9948
2017-03-26 08:00 | 3 | 8 | 6034.5928 | 6034.5928
2017-03-26 09:00 | 3 | 9 | 7551.6463 | 7551.6463
2017-03-26 10:00 | 3 | 10 | 8604.2517 | 8604.2517
2017-03-26 11:00 | 3 | 11 | 8962.8769 | 8962.8769
2017-03-26 12:00 | 3 | 12 | 8850.6392 | 8850.6392
2017-03-26 13:00 | 3 | 13 | 8178.2537 | 8178.2537
2017-03-26 14:00 | 3 | 14 | 6926.8376 | 6926.8375
2017-03-26 15:00 | 3 | 15 | 5021.0334 | 5021.0334
2017-03-26 16:00 | 3 | 16 | 2656.9404 | 2656.9404
2017-03-26 17:00 | 3 | 17 | 453.3116 | 453.3116
2017-03-26 18:00 | 3 | 18 | 0 | 0
2017-03-26 19:00 | 3 | 19 | 0 | 0
2017-03-26 20:00 | 3 | 20 | 0 | 0
2017-03-26 21:00 | 3 | 21 | 0 | 0
2017-03-26 22:00 | 3 | 22 | 0 | 0
2017-03-26 23:00 | 3 | 23 | 0 | 0
2017-03-27 | 3 | 0 | 0 | 0
2017-03-27 01:00 | 3 | 1 | 0 | 0
2017-03-27 02:00 | 3 | 2 | 0 | 0
2017-03-27 03:00 | 3 | 3 | 0 | 0
2017-03-27 04:00 | 3 | 4 | 0 | 0
2017-03-27 05:00 | 3 | 5 | 0 | 0
2017-03-27 06:00 | 3 | 6 | 1101.8391 | 1101.8391
2017-03-27 07:00 | 3 | 7 | 3532.3446 | 3532.3446
2017-03-27 08:00 | 3 | 8 | 5669.3482 | 5669.3482
2017-03-27 09:00 | 3 | 9 | 7234.7213 | 7234.7213
2017-03-27 10:00 | 3 | 10 | 8192.7115 | 8192.7115
2017-03-27 11:00 | 3 | 11 | 2355.4415 | 2355.4415
2017-03-27 12:00 | 3 | 12 | 3688.6238 | 3688.6238
2017-03-27 13:00 | 3 | 13 | 2765.359 | 2765.359
2017-03-27 14:00 | 3 | 14 | 1408.5326 | 1408.5326
2017-03-27 15:00 | 3 | 15 | 2400.6066 | 2400.6066
2017-03-27 16:00 | 3 | 16 | 2552.0259 | 2552.0259
2017-03-27 17:00 | 3 | 17 | 431.4202 | 431.4202
2017-03-27 18:00 | 3 | 18 | 0 | 0
2017-03-27 19:00 | 3 | 19 | 0 | 0
2017-03-27 20:00 | 3 | 20 | 0 | 0
2017-03-27 21:00 | 3 | 21 | 0 | 0
2017-03-27 22:00 | 3 | 22 | 0 | 0
2017-03-27 23:00 | 3 | 23 | 0 | 0
2017-03-28 | 3 | 0 | 0 | 0
2017-03-28 01:00 | 3 | 1 | 0 | 0
2017-03-28 02:00 | 3 | 2 | 0 | 0
2017-03-28 03:00 | 3 | 3 | 0 | 0
2017-03-28 04:00 | 3 | 4 | 0 | 0
2017-03-28 05:00 | 3 | 5 | 0 | 0
2017-03-28 06:00 | 3 | 6 | 343.8143 | 343.8143
2017-03-28 07:00 | 3 | 7 | 1198.4368 | 1198.4368
2017-03-28 08:00 | 3 | 8 | 4409.5853 | 4409.5853
2017-03-28 09:00 | 3 | 9 | 3624.0237 | 3624.0237
2017-03-28 10:00 | 3 | 10 | 3087.6867 | 3087.6867
2017-03-28 11:00 | 3 | 11 | 2194.1563 | 2194.1563
2017-03-28 12:00 | 3 | 12 | 1556.3226 | 1556.3226
2017-03-28 13:00 | 3 | 13 | 3013.9108 | 3013.9108
2017-03-28 14:00 | 3 | 14 | 1994.6474 | 1994.6474
2017-03-28 15:00 | 3 | 15 | 181.2814 | 181.2814
2017-03-28 16:00 | 3 | 16 | 702.5212 | 702.5212
2017-03-28 17:00 | 3 | 17 | 165.9507 | 165.9507
2017-03-28 18:00 | 3 | 18 | 0 | 0
2017-03-28 19:00 | 3 | 19 | 0 | 0
2017-03-28 20:00 | 3 | 20 | 0 | 0
2017-03-28 21:00 | 3 | 21 | 0 | 0
2017-03-28 22:00 | 3 | 22 | 0 | 0
2017-03-28 23:00 | 3 | 23 | 0 | 0
2017-03-29 | 3 | 0 | 0 | 0
2017-03-29 01:00 | 3 | 1 | 0 | 0
2017-03-29 02:00 | 3 | 2 | 0 | 0
2017-03-29 03:00 | 3 | 3 | 0 | 0
2017-03-29 04:00 | 3 | 4 | 0 | 0
2017-03-29 05:00 | 3 | 5 | 0 | 0
2017-03-29 06:00 | 3 | 6 | 1138.8174 | 1138.8174
2017-03-29 07:00 | 3 | 7 | 3514.3632 | 3514.3632
2017-03-29 08:00 | 3 | 8 | 4010.2949 | 4010.295
2017-03-29 09:00 | 3 | 9 | 4484.0133 | 4484.0133
2017-03-29 10:00 | 3 | 10 | 4713.3888 | 4713.3888
2017-03-29 11:00 | 3 | 11 | 5815.1785 | 5815.1785
2017-03-29 12:00 | 3 | 12 | 5463.9766 | 5463.9766
2017-03-29 13:00 | 3 | 13 | 5031.0016 | 5031.0016
2017-03-29 14:00 | 3 | 14 | 4157.7985 | 4157.7985
2017-03-29 15:00 | 3 | 15 | 1298.6226 | 1298.6226
2017-03-29 16:00 | 3 | 16 | 1378.5177 | 1378.5177
2017-03-29 17:00 | 3 | 17 | 0 | 0
2017-03-29 18:00 | 3 | 18 | 0 | 0
2017-03-29 19:00 | 3 | 19 | 0 | 0
2017-03-29 20:00 | 3 | 20 | 0 | 0
2017-03-29 21:00 | 3 | 21 | 0 | 0
2017-03-29 22:00 | 3 | 22 | 0 | 0
2017-03-29 23:00 | 3 | 23 | 0 | 0
2017-03-30 | 3 | 0 | 0 | 0
2017-03-30 01:00 | 3 | 1 | 0 | 0
2017-03-30 02:00 | 3 | 2 | 0 | 0
2017-03-30 03:00 | 3 | 3 | 0 | 0
2017-03-30 04:00 | 3 | 4 | 0 | 0
2017-03-30 05:00 | 3 | 5 | 0 | 0
2017-03-30 06:00 | 3 | 6 | 1174.0592 | 1174.0592
2017-03-30 07:00 | 3 | 7 | 3524.9788 | 3524.9789
2017-03-30 08:00 | 3 | 8 | 5653.668 | 5653.668
2017-03-30 09:00 | 3 | 9 | 7192.2253 | 7192.2253
2017-03-30 10:00 | 3 | 10 | 6051.3724 | 6051.3724
2017-03-30 11:00 | 3 | 11 | 6607.2065 | 6607.2065
2017-03-30 12:00 | 3 | 12 | 8437.9226 | 8437.9226
2017-03-30 13:00 | 3 | 13 | 7719.0564 | 7719.0564
2017-03-30 14:00 | 3 | 14 | 6513.8771 | 6513.8771
2017-03-30 15:00 | 3 | 15 | 4737.0972 | 4737.0972
2017-03-30 16:00 | 3 | 16 | 2579.0682 | 2579.0682
2017-03-30 17:00 | 3 | 17 | 493.2591 | 493.2591
2017-03-30 18:00 | 3 | 18 | 0 | 0
2017-03-30 19:00 | 3 | 19 | 0 | 0
2017-03-30 20:00 | 3 | 20 | 0 | 0
2017-03-30 21:00 | 3 | 21 | 0 | 0
2017-03-30 22:00 | 3 | 22 | 0 | 0
2017-03-30 23:00 | 3 | 23 | 0 | 0
2017-03-31 | 3 | 0 | 0 | 0
2017-03-31 01:00 | 3 | 1 | 0 | 0
2017-03-31 02:00 | 3 | 2 | 0 | 0
2017-03-31 03:00 | 3 | 3 | 0 | 0
2017-03-31 04:00 | 3 | 4 | 0 | 0
2017-03-31 05:00 | 3 | 5 | 0 | 0
2017-03-31 06:00 | 3 | 6 | 1232.7966 | 1232.7966
2017-03-31 07:00 | 3 | 7 | 2850.8937 | 2850.8937
2017-03-31 08:00 | 3 | 8 | 4548.2086 | 4548.2086
2017-03-31 09:00 | 3 | 9 | 6112.9227 | 6112.9227
2017-03-31 10:00 | 3 | 10 | 6728.8156 | 6728.8156
2017-03-31 11:00 | 3 | 11 | 6985.0931 | 6985.0931
2017-03-31 12:00 | 3 | 12 | 6556.2086 | 6556.2086
2017-03-31 13:00 | 3 | 13 | 5612.391 | 5612.391
2017-03-31 14:00 | 3 | 14 | 4394.3018 | 4394.3018
2017-03-31 15:00 | 3 | 15 | 3040.4562 | 3040.4562
2017-03-31 16:00 | 3 | 16 | 1536.745 | 1536.745
2017-03-31 17:00 | 3 | 17 | 192.0166 | 192.0166
2017-03-31 18:00 | 3 | 18 | 0 | 0
2017-03-31 19:00 | 3 | 19 | 0 | 0
2017-03-31 20:00 | 3 | 20 | 0 | 0
2017-03-31 21:00 | 3 | 21 | 0 | 0
2017-03-31 22:00 | 3 | 22 | 0 | 0
2017-03-31 23:00 | 3 | 23 | 0 | 0
2017-04-01 | 4 | 0 | 0 | 0
2017-04-01 01:00 | 4 | 1 | 0 | 0
2017-04-01 02:00 | 4 | 2 | 0 | 0
2017-04-01 03:00 | 4 | 3 | 0 | 0
2017-04-01 04:00 | 4 | 4 | 0 | 0
2017-04-01 05:00 | 4 | 5 | 0 | 0
2017-04-01 06:00 | 4 | 6 | 1217.9696 | 1217.9696
2017-04-01 07:00 | 4 | 7 | 3535.867 | 3535.867
2017-04-01 08:00 | 4 | 8 | 938.7645 | 938.7646
2017-04-01 09:00 | 4 | 9 | 2512.5154 | 2512.5154
2017-04-01 10:00 | 4 | 10 | 4026.7238 | 4026.7238
2017-04-01 11:00 | 4 | 11 | 6546.5912 | 6546.5912
2017-04-01 12:00 | 4 | 12 | 8214.2039 | 8214.2039
2017-04-01 13:00 | 4 | 13 | 7491.2587 | 7491.2587
2017-04-01 14:00 | 4 | 14 | 6317.8205 | 6317.8205
2017-04-01 15:00 | 4 | 15 | 4576.3376 | 4576.3376
2017-04-01 16:00 | 4 | 16 | 2456.5035 | 2456.5035
2017-04-01 17:00 | 4 | 17 | 484.5249 | 484.5249
2017-04-01 18:00 | 4 | 18 | 0 | 0
2017-04-01 19:00 | 4 | 19 | 0 | 0
2017-04-01 20:00 | 4 | 20 | 0 | 0
2017-04-01 21:00 | 4 | 21 | 0 | 0
2017-04-01 22:00 | 4 | 22 | 0 | 0
2017-04-01 23:00 | 4 | 23 | 0 | 0
2017-04-02 | 4 | 0 | 0 | 0
2017-04-02 01:00 | 4 | 1 | 0 | 0
2017-04-02 02:00 | 4 | 2 | 0 | 0
2017-04-02 03:00 | 4 | 3 | 0 | 0
2017-04-02 04:00 | 4 | 4 | 0 | 0
2017-04-02 05:00 | 4 | 5 | 0 | 0
2017-04-02 06:00 | 4 | 6 | 1234.4387 | 1234.4387
2017-04-02 07:00 | 4 | 7 | 3481.8032 | 3481.8032
2017-04-02 08:00 | 4 | 8 | 5506.415 | 5506.415
2017-04-02 09:00 | 4 | 9 | 6940.0648 | 6940.0648
2017-04-02 10:00 | 4 | 10 | 7852.8175 | 7852.8175
2017-04-02 11:00 | 4 | 11 | 8194.5078 | 8194.5078
2017-04-02 12:00 | 4 | 12 | 8022.1435 | 8022.1435
2017-04-02 13:00 | 4 | 13 | 7407.1879 | 7407.1879
2017-04-02 14:00 | 4 | 14 | 6307.1508 | 6307.1508
2017-04-02 15:00 | 4 | 15 | 4614.3888 | 4614.3888
2017-04-02 16:00 | 4 | 16 | 2471.3902 | 2471.3902
2017-04-02 17:00 | 4 | 17 | 502.1532 | 502.1532
2017-04-02 18:00 | 4 | 18 | 0 | 0
2017-04-02 19:00 | 4 | 19 | 0 | 0
2017-04-02 20:00 | 4 | 20 | 0 | 0
2017-04-02 21:00 | 4 | 21 | 0 | 0
2017-04-02 22:00 | 4 | 22 | 0 | 0
2017-04-02 23:00 | 4 | 23 | 0 | 0
2017-04-03 | 4 | 0 | 0 | 0
2017-04-03 01:00 | 4 | 1 | 0 | 0
2017-04-03 02:00 | 4 | 2 | 0 | 0
2017-04-03 03:00 | 4 | 3 | 0 | 0
2017-04-03 04:00 | 4 | 4 | 0 | 0
2017-04-03 05:00 | 4 | 5 | 0 | 0
2017-04-03 06:00 | 4 | 6 | 1245.3718 | 1245.3718
2017-04-03 07:00 | 4 | 7 | 3422.1907 | 3422.1907
2017-04-03 08:00 | 4 | 8 | 5444.3231 | 5444.3231
2017-04-03 09:00 | 4 | 9 | 6889.4924 | 6889.4924
2017-04-03 10:00 | 4 | 10 | 7819.3353 | 7819.3353
2017-04-03 11:00 | 4 | 11 | 8168.2533 | 8168.2533
2017-04-03 12:00 | 4 | 12 | 8037.8824 | 8037.8824
2017-04-03 13:00 | 4 | 13 | 7395.2038 | 7395.2038
2017-04-03 14:00 | 4 | 14 | 6251.2551 | 6251.2551
2017-04-03 15:00 | 4 | 15 | 4564.0705 | 4564.0705
2017-04-03 16:00 | 4 | 16 | 2467.6723 | 2467.6723
2017-04-03 17:00 | 4 | 17 | 517.8013 | 517.8013
2017-04-03 18:00 | 4 | 18 | 0 | 0
2017-04-03 19:00 | 4 | 19 | 0 | 0
2017-04-03 20:00 | 4 | 20 | 0 | 0
2017-04-03 21:00 | 4 | 21 | 0 | 0
2017-04-03 22:00 | 4 | 22 | 0 | 0
2017-04-03 23:00 | 4 | 23 | 0 | 0
2017-04-04 | 4 | 0 | 0 | 0
2017-04-04 01:00 | 4 | 1 | 0 | 0
2017-04-04 02:00 | 4 | 2 | 0 | 0
2017-04-04 03:00 | 4 | 3 | 0 | 0
2017-04-04 04:00 | 4 | 4 | 0 | 0
2017-04-04 05:00 | 4 | 5 | 0 | 0
2017-04-04 06:00 | 4 | 6 | 983.3868 | 983.3869
2017-04-04 07:00 | 4 | 7 | 2588.5338 | 2588.5338
2017-04-04 08:00 | 4 | 8 | 4980.351 | 4980.351
2017-04-04 09:00 | 4 | 9 | 6345.953 | 6345.953
2017-04-04 10:00 | 4 | 10 | 7463.2263 | 7463.2263
2017-04-04 11:00 | 4 | 11 | 6960.1243 | 6960.1243
2017-04-04 12:00 | 4 | 12 | 7784.2798 | 7784.2799
2017-04-04 13:00 | 4 | 13 | 7265.1491 | 7265.1491
2017-04-04 14:00 | 4 | 14 | 6168.025 | 6168.025
2017-04-04 15:00 | 4 | 15 | 4542.5414 | 4542.5414
2017-04-04 16:00 | 4 | 16 | 2491.4278 | 2491.4278
2017-04-04 17:00 | 4 | 17 | 536.9258 | 536.9258
2017-04-04 18:00 | 4 | 18 | 0 | 0
2017-04-04 19:00 | 4 | 19 | 0 | 0
2017-04-04 20:00 | 4 | 20 | 0 | 0
2017-04-04 21:00 | 4 | 21 | 0 | 0
2017-04-04 22:00 | 4 | 22 | 0 | 0
2017-04-04 23:00 | 4 | 23 | 0 | 0
2017-04-05 | 4 | 0 | 0 | 0
2017-04-05 01:00 | 4 | 1 | 0 | 0
2017-04-05 02:00 | 4 | 2 | 0 | 0
2017-04-05 03:00 | 4 | 3 | 0 | 0
2017-04-05 04:00 | 4 | 4 | 0 | 0
2017-04-05 05:00 | 4 | 5 | 0 | 0
2017-04-05 06:00 | 4 | 6 | 1365.5169 | 1365.5169
2017-04-05 07:00 | 4 | 7 | 3589.7675 | 3589.7675
2017-04-05 08:00 | 4 | 8 | 5553.5754 | 5553.5754
2017-04-05 09:00 | 4 | 9 | 5914.4431 | 5914.4431
2017-04-05 10:00 | 4 | 10 | 7905.7888 | 7905.7888
2017-04-05 11:00 | 4 | 11 | 6451.5506 | 6451.5506
2017-04-05 12:00 | 4 | 12 | 4294.6957 | 4294.6957
2017-04-05 13:00 | 4 | 13 | 6344.903 | 6344.903
2017-04-05 14:00 | 4 | 14 | 1018.4676 | 1018.4676
2017-04-05 15:00 | 4 | 15 | 4660.7855 | 4660.7855
2017-04-05 16:00 | 4 | 16 | 36.7609 | 36.7609
2017-04-05 17:00 | 4 | 17 | 0 | 0
2017-04-05 18:00 | 4 | 18 | 0 | 0
2017-04-05 19:00 | 4 | 19 | 0 | 0
2017-04-05 20:00 | 4 | 20 | 0 | 0
2017-04-05 21:00 | 4 | 21 | 0 | 0
2017-04-05 22:00 | 4 | 22 | 0 | 0
2017-04-05 23:00 | 4 | 23 | 0 | 0
2017-04-06 | 4 | 0 | 0 | 0
2017-04-06 01:00 | 4 | 1 | 0 | 0
2017-04-06 02:00 | 4 | 2 | 0 | 0
2017-04-06 03:00 | 4 | 3 | 0 | 0
2017-04-06 04:00 | 4 | 4 | 0 | 0
2017-04-06 05:00 | 4 | 5 | 38.8999 | 38.8999
2017-04-06 06:00 | 4 | 6 | 1328.1465 | 1328.1465
2017-04-06 07:00 | 4 | 7 | 3535.4657 | 3535.4657
2017-04-06 08:00 | 4 | 8 | 2059.4223 | 2059.4223
2017-04-06 09:00 | 4 | 9 | 453.4117 | 453.4117
2017-04-06 10:00 | 4 | 10 | 297.9144 | 297.9144
2017-04-06 11:00 | 4 | 11 | 336.8327 | 336.8327
2017-04-06 12:00 | 4 | 12 | 5089.5883 | 5089.5883
2017-04-06 13:00 | 4 | 13 | 561.5289 | 561.5289
2017-04-06 14:00 | 4 | 14 | 4510.2206 | 4510.2206
2017-04-06 15:00 | 4 | 15 | 1375.1021 | 1375.1021
2017-04-06 16:00 | 4 | 16 | 1311.0816 | 1311.0816
2017-04-06 17:00 | 4 | 17 | 332.3868 | 332.3868
2017-04-06 18:00 | 4 | 18 | 0 | 0
2017-04-06 19:00 | 4 | 19 | 0 | 0
2017-04-06 20:00 | 4 | 20 | 0 | 0
2017-04-06 21:00 | 4 | 21 | 0 | 0
2017-04-06 22:00 | 4 | 22 | 0 | 0
2017-04-06 23:00 | 4 | 23 | 0 | 0
2017-04-07 | 4 | 0 | 0 | 0
2017-04-07 01:00 | 4 | 1 | 0 | 0
2017-04-07 02:00 | 4 | 2 | 0 | 0
2017-04-07 03:00 | 4 | 3 | 0 | 0
2017-04-07 04:00 | 4 | 4 | 0 | 0
2017-04-07 05:00 | 4 | 5 | 52.2548 | 52.2548
2017-04-07 06:00 | 4 | 6 | 1061.3453 | 1061.3453
2017-04-07 07:00 | 4 | 7 | 3148.6494 | 3148.6494
2017-04-07 08:00 | 4 | 8 | 4316.295 | 4316.295
2017-04-07 09:00 | 4 | 9 | 5946.512 | 5946.512
2017-04-07 10:00 | 4 | 10 | 6105.2764 | 6105.2764
2017-04-07 11:00 | 4 | 11 | 7921.9992 | 7921.9992
2017-04-07 12:00 | 4 | 12 | 7682.7004 | 7682.7004
2017-04-07 13:00 | 4 | 13 | 7073.3591 | 7073.3591
2017-04-07 14:00 | 4 | 14 | 5992.7167 | 5992.7167
2017-04-07 15:00 | 4 | 15 | 4329.8121 | 4329.8121
2017-04-07 16:00 | 4 | 16 | 2277.2691 | 2277.2691
2017-04-07 17:00 | 4 | 17 | 494.1952 | 494.1952
2017-04-07 18:00 | 4 | 18 | 0 | 0
2017-04-07 19:00 | 4 | 19 | 0 | 0
2017-04-07 20:00 | 4 | 20 | 0 | 0
2017-04-07 21:00 | 4 | 21 | 0 | 0
2017-04-07 22:00 | 4 | 22 | 0 | 0
2017-04-07 23:00 | 4 | 23 | 0 | 0
2017-04-08 | 4 | 0 | 0 | 0
2017-04-08 01:00 | 4 | 1 | 0 | 0
2017-04-08 02:00 | 4 | 2 | 0 | 0
2017-04-08 03:00 | 4 | 3 | 0 | 0
2017-04-08 04:00 | 4 | 4 | 0 | 0
2017-04-08 05:00 | 4 | 5 | 42.5845 | 42.5845
2017-04-08 06:00 | 4 | 6 | 1350.7923 | 1350.7923
2017-04-08 07:00 | 4 | 7 | 3361.3545 | 3361.3545
2017-04-08 08:00 | 4 | 8 | 5273.9563 | 5273.9563
2017-04-08 09:00 | 4 | 9 | 5747.447 | 5747.447
2017-04-08 10:00 | 4 | 10 | 7727.3318 | 7727.3318
2017-04-08 11:00 | 4 | 11 | 8055.7638 | 8055.7638
2017-04-08 12:00 | 4 | 12 | 6943.9277 | 6943.9277
2017-04-08 13:00 | 4 | 13 | 4076.3992 | 4076.3992
2017-04-08 14:00 | 4 | 14 | 3158.9235 | 3158.9235
2017-04-08 15:00 | 4 | 15 | 1500.2026 | 1500.2026
2017-04-08 16:00 | 4 | 16 | 2494.5765 | 2494.5765
2017-04-08 17:00 | 4 | 17 | 626.3107 | 626.3107
2017-04-08 18:00 | 4 | 18 | 0 | 0
2017-04-08 19:00 | 4 | 19 | 0 | 0
2017-04-08 20:00 | 4 | 20 | 0 | 0
2017-04-08 21:00 | 4 | 21 | 0 | 0
2017-04-08 22:00 | 4 | 22 | 0 | 0
2017-04-08 23:00 | 4 | 23 | 0 | 0
2017-04-09 | 4 | 0 | 0 | 0
2017-04-09 01:00 | 4 | 1 | 0 | 0
2017-04-09 02:00 | 4 | 2 | 0 | 0
2017-04-09 03:00 | 4 | 3 | 0 | 0
2017-04-09 04:00 | 4 | 4 | 0 | 0
2017-04-09 05:00 | 4 | 5 | 0 | 0
2017-04-09 06:00 | 4 | 6 | 150.8593 | 150.8593
2017-04-09 07:00 | 4 | 7 | 189.4602 | 189.4602
2017-04-09 08:00 | 4 | 8 | 530.9182 | 530.9182
2017-04-09 09:00 | 4 | 9 | 1481.967 | 1481.967
2017-04-09 10:00 | 4 | 10 | 822.8399 | 822.8399
2017-04-09 11:00 | 4 | 11 | 947.4045 | 947.4045
2017-04-09 12:00 | 4 | 12 | 878.7656 | 878.7656
2017-04-09 13:00 | 4 | 13 | 533.4447 | 533.4447
2017-04-09 14:00 | 4 | 14 | 897.9924 | 897.9924
2017-04-09 15:00 | 4 | 15 | 798.1851 | 798.1851
2017-04-09 16:00 | 4 | 16 | 419.9604 | 419.9604
2017-04-09 17:00 | 4 | 17 | 1.932 | 1.932
2017-04-09 18:00 | 4 | 18 | 0 | 0
2017-04-09 19:00 | 4 | 19 | 0 | 0
2017-04-09 20:00 | 4 | 20 | 0 | 0
2017-04-09 21:00 | 4 | 21 | 0 | 0
2017-04-09 22:00 | 4 | 22 | 0 | 0
2017-04-09 23:00 | 4 | 23 | 0 | 0
2017-04-10 | 4 | 0 | 0 | 0
2017-04-10 01:00 | 4 | 1 | 0 | 0
2017-04-10 02:00 | 4 | 2 | 0 | 0
2017-04-10 03:00 | 4 | 3 | 0 | 0
2017-04-10 04:00 | 4 | 4 | 0 | 0
2017-04-10 05:00 | 4 | 5 | 85.3081 | 85.3081
2017-04-10 06:00 | 4 | 6 | 1626.8809 | 1626.8809
2017-04-10 07:00 | 4 | 7 | 4124.3864 | 4124.3864
2017-04-10 08:00 | 4 | 8 | 3186.075 | 3186.075
2017-04-10 09:00 | 4 | 9 | 7874.0833 | 7874.0833
2017-04-10 10:00 | 4 | 10 | 3995.6589 | 3995.6589
2017-04-10 11:00 | 4 | 11 | 8982.8616 | 8982.8616
2017-04-10 12:00 | 4 | 12 | 8664.583 | 8664.583
2017-04-10 13:00 | 4 | 13 | 7960.8531 | 7960.8531
2017-04-10 14:00 | 4 | 14 | 6694.9642 | 6694.9642
2017-04-10 15:00 | 4 | 15 | 4940.2068 | 4940.2068
2017-04-10 16:00 | 4 | 16 | 2744.1013 | 2744.1013
2017-04-10 17:00 | 4 | 17 | 631.9112 | 631.9112
2017-04-10 18:00 | 4 | 18 | 0 | 0
2017-04-10 19:00 | 4 | 19 | 0 | 0
2017-04-10 20:00 | 4 | 20 | 0 | 0
2017-04-10 21:00 | 4 | 21 | 0 | 0
2017-04-10 22:00 | 4 | 22 | 0 | 0
2017-04-10 23:00 | 4 | 23 | 0 | 0
2017-04-11 | 4 | 0 | 0 | 0
2017-04-11 01:00 | 4 | 1 | 0 | 0
2017-04-11 02:00 | 4 | 2 | 0 | 0
2017-04-11 03:00 | 4 | 3 | 0 | 0
2017-04-11 04:00 | 4 | 4 | 0 | 0
2017-04-11 05:00 | 4 | 5 | 54.9286 | 54.9286
2017-04-11 06:00 | 4 | 6 | 12.2256 | 12.2256
2017-04-11 07:00 | 4 | 7 | 933.9575 | 933.9575
2017-04-11 08:00 | 4 | 8 | 2743.1318 | 2743.1318
2017-04-11 09:00 | 4 | 9 | 4734.305 | 4734.305
2017-04-11 10:00 | 4 | 10 | 7719.9178 | 7719.9178
2017-04-11 11:00 | 4 | 11 | 8241.5532 | 8241.5532
2017-04-11 12:00 | 4 | 12 | 8293.8173 | 8293.8173
2017-04-11 13:00 | 4 | 13 | 7614.5858 | 7614.5859
2017-04-11 14:00 | 4 | 14 | 6530.4498 | 6530.4498
2017-04-11 15:00 | 4 | 15 | 4833.3097 | 4833.3097
2017-04-11 16:00 | 4 | 16 | 2697.5619 | 2697.5619
2017-04-11 17:00 | 4 | 17 | 654.4547 | 654.4547
2017-04-11 18:00 | 4 | 18 | 0 | 0
2017-04-11 19:00 | 4 | 19 | 0 | 0
2017-04-11 20:00 | 4 | 20 | 0 | 0
2017-04-11 21:00 | 4 | 21 | 0 | 0
2017-04-11 22:00 | 4 | 22 | 0 | 0
2017-04-11 23:00 | 4 | 23 | 0 | 0
2017-04-12 | 4 | 0 | 0 | 0
2017-04-12 01:00 | 4 | 1 | 0 | 0
2017-04-12 02:00 | 4 | 2 | 0 | 0
2017-04-12 03:00 | 4 | 3 | 0 | 0
2017-04-12 04:00 | 4 | 4 | 0 | 0
2017-04-12 05:00 | 4 | 5 | 138.5899 | 138.5899
2017-04-12 06:00 | 4 | 6 | 1640.567 | 1640.567
2017-04-12 07:00 | 4 | 7 | 3987.6284 | 3987.6284
2017-04-12 08:00 | 4 | 8 | 5985.3498 | 5985.3498
2017-04-12 09:00 | 4 | 9 | 7376.5991 | 7376.5991
2017-04-12 10:00 | 4 | 10 | 8296.9636 | 8296.9636
2017-04-12 11:00 | 4 | 11 | 6817.1022 | 6817.1022
2017-04-12 12:00 | 4 | 12 | 6449.3035 | 6449.3035
2017-04-12 13:00 | 4 | 13 | 6281.0309 | 6281.0309
2017-04-12 14:00 | 4 | 14 | 3736.0061 | 3736.0061
2017-04-12 15:00 | 4 | 15 | 3968.5281 | 3968.5281
2017-04-12 16:00 | 4 | 16 | 2738.9297 | 2738.9297
2017-04-12 17:00 | 4 | 17 | 108.6382 | 108.6382
2017-04-12 18:00 | 4 | 18 | 0 | 0
2017-04-12 19:00 | 4 | 19 | 0 | 0
2017-04-12 20:00 | 4 | 20 | 0 | 0
2017-04-12 21:00 | 4 | 21 | 0 | 0
2017-04-12 22:00 | 4 | 22 | 0 | 0
2017-04-12 23:00 | 4 | 23 | 0 | 0
2017-04-13 | 4 | 0 | 0 | 0
2017-04-13 01:00 | 4 | 1 | 0 | 0
2017-04-13 02:00 | 4 | 2 | 0 | 0
2017-04-13 03:00 | 4 | 3 | 0 | 0
2017-04-13 04:00 | 4 | 4 | 0 | 0
2017-04-13 05:00 | 4 | 5 | 160.1202 | 160.1202
2017-04-13 06:00 | 4 | 6 | 1704.2218 | 1704.2218
2017-04-13 07:00 | 4 | 7 | 3009.0911 | 3009.0911
2017-04-13 08:00 | 4 | 8 | 4186.2254 | 4186.2254
2017-04-13 09:00 | 4 | 9 | 5959.3517 | 5959.3517
2017-04-13 10:00 | 4 | 10 | 6905.3705 | 6905.3705
2017-04-13 11:00 | 4 | 11 | 7192.882 | 7192.882
2017-04-13 12:00 | 4 | 12 | 7596.1766 | 7596.1766
2017-04-13 13:00 | 4 | 13 | 7760.2287 | 7760.2287
2017-04-13 14:00 | 4 | 14 | 6559.8277 | 6559.8277
2017-04-13 15:00 | 4 | 15 | 4860.9407 | 4860.9407
2017-04-13 16:00 | 4 | 16 | 2750.3124 | 2750.3124
2017-04-13 17:00 | 4 | 17 | 691.8664 | 691.8664
2017-04-13 18:00 | 4 | 18 | 0 | 0
2017-04-13 19:00 | 4 | 19 | 0 | 0
2017-04-13 20:00 | 4 | 20 | 0 | 0
2017-04-13 21:00 | 4 | 21 | 0 | 0
2017-04-13 22:00 | 4 | 22 | 0 | 0
2017-04-13 23:00 | 4 | 23 | 0 | 0
2017-04-14 | 4 | 0 | 0 | 0
2017-04-14 01:00 | 4 | 1 | 0 | 0
2017-04-14 02:00 | 4 | 2 | 0 | 0
2017-04-14 03:00 | 4 | 3 | 0 | 0
2017-04-14 04:00 | 4 | 4 | 0 | 0
2017-04-14 05:00 | 4 | 5 | 176.7837 | 176.7837
2017-04-14 06:00 | 4 | 6 | 1705.1499 | 1705.1499
2017-04-14 07:00 | 4 | 7 | 4046.1899 | 4046.1899
2017-04-14 08:00 | 4 | 8 | 6001.3428 | 6001.3428
2017-04-14 09:00 | 4 | 9 | 7432.8444 | 7432.8444
2017-04-14 10:00 | 4 | 10 | 8284.1687 | 8284.1687
2017-04-14 11:00 | 4 | 11 | 8621.9467 | 8621.9467
2017-04-14 12:00 | 4 | 12 | 8422.0354 | 8422.0354
2017-04-14 13:00 | 4 | 13 | 7769.2194 | 7769.2194
2017-04-14 14:00 | 4 | 14 | 6581.3844 | 6581.3844
2017-04-14 15:00 | 4 | 15 | 4892.9441 | 4892.9441
2017-04-14 16:00 | 4 | 16 | 2737.6233 | 2737.6233
2017-04-14 17:00 | 4 | 17 | 675.1144 | 675.1144
2017-04-14 18:00 | 4 | 18 | 0 | 0
2017-04-14 19:00 | 4 | 19 | 0 | 0
2017-04-14 20:00 | 4 | 20 | 0 | 0
2017-04-14 21:00 | 4 | 21 | 0 | 0
2017-04-14 22:00 | 4 | 22 | 0 | 0
2017-04-14 23:00 | 4 | 23 | 0 | 0
2017-04-15 | 4 | 0 | 0 | 0
2017-04-15 01:00 | 4 | 1 | 0 | 0
2017-04-15 02:00 | 4 | 2 | 0 | 0
2017-04-15 03:00 | 4 | 3 | 0 | 0
2017-04-15 04:00 | 4 | 4 | 0 | 0
2017-04-15 05:00 | 4 | 5 | 178.1292 | 178.1292
2017-04-15 06:00 | 4 | 6 | 1742.5168 | 1742.5168
2017-04-15 07:00 | 4 | 7 | 4050.0021 | 4050.0021
2017-04-15 08:00 | 4 | 8 | 6036.6444 | 6036.6444
2017-04-15 09:00 | 4 | 9 | 7423.7985 | 7423.7985
2017-04-15 10:00 | 4 | 10 | 8283.9951 | 8283.9951
2017-04-15 11:00 | 4 | 11 | 8605.3695 | 8605.3695
2017-04-15 12:00 | 4 | 12 | 8411.0632 | 8411.0632
2017-04-15 13:00 | 4 | 13 | 7766.2041 | 7766.2041
2017-04-15 14:00 | 4 | 14 | 6606.9075 | 6606.9075
2017-04-15 15:00 | 4 | 15 | 4922.2288 | 4922.2288
2017-04-15 16:00 | 4 | 16 | 2803.2032 | 2803.2032
2017-04-15 17:00 | 4 | 17 | 668.6537 | 668.6537
2017-04-15 18:00 | 4 | 18 | 0 | 0
2017-04-15 19:00 | 4 | 19 | 0 | 0
2017-04-15 20:00 | 4 | 20 | 0 | 0
2017-04-15 21:00 | 4 | 21 | 0 | 0
2017-04-15 22:00 | 4 | 22 | 0 | 0
2017-04-15 23:00 | 4 | 23 | 0 | 0
2017-04-16 | 4 | 0 | 0 | 0
2017-04-16 01:00 | 4 | 1 | 0 | 0
2017-04-16 02:00 | 4 | 2 | 0 | 0
2017-04-16 03:00 | 4 | 3 | 0 | 0
2017-04-16 04:00 | 4 | 4 | 0 | 0
2017-04-16 05:00 | 4 | 5 | 0 | 0
2017-04-16 06:00 | 4 | 6 | 96.5402 | 96.5402
2017-04-16 07:00 | 4 | 7 | 188.347 | 188.347
2017-04-16 08:00 | 4 | 8 | 756.9265 | 756.9265
2017-04-16 09:00 | 4 | 9 | 2567.4302 | 2567.4302
2017-04-16 10:00 | 4 | 10 | 2837.9171 | 2837.9171
2017-04-16 11:00 | 4 | 11 | 765.831 | 765.831
2017-04-16 12:00 | 4 | 12 | 1227.2432 | 1227.2432
2017-04-16 13:00 | 4 | 13 | 602.1917 | 602.1917
2017-04-16 14:00 | 4 | 14 | 1459.2338 | 1459.2338
2017-04-16 15:00 | 4 | 15 | 1314.7341 | 1314.7341
2017-04-16 16:00 | 4 | 16 | 205.183 | 205.183
2017-04-16 17:00 | 4 | 17 | 248.0791 | 248.0791
2017-04-16 18:00 | 4 | 18 | 0 | 0
2017-04-16 19:00 | 4 | 19 | 0 | 0
2017-04-16 20:00 | 4 | 20 | 0 | 0
2017-04-16 21:00 | 4 | 21 | 0 | 0
2017-04-16 22:00 | 4 | 22 | 0 | 0
2017-04-16 23:00 | 4 | 23 | 0 | 0
2017-04-17 | 4 | 0 | 0 | 0
2017-04-17 01:00 | 4 | 1 | 0 | 0
2017-04-17 02:00 | 4 | 2 | 0 | 0
2017-04-17 03:00 | 4 | 3 | 0 | 0
2017-04-17 04:00 | 4 | 4 | 0 | 0
2017-04-17 05:00 | 4 | 5 | 237.2749 | 237.2749
2017-04-17 06:00 | 4 | 6 | 75.087 | 75.087
2017-04-17 07:00 | 4 | 7 | 1228.7129 | 1228.7129
2017-04-17 08:00 | 4 | 8 | 855.3827 | 855.3826
2017-04-17 09:00 | 4 | 9 | 1017.4912 | 1017.4912
2017-04-17 10:00 | 4 | 10 | 1112.1167 | 1112.1167
2017-04-17 11:00 | 4 | 11 | 1343.1091 | 1343.1091
2017-04-17 12:00 | 4 | 12 | 858.4428 | 858.4428
2017-04-17 13:00 | 4 | 13 | 2029.4602 | 2029.4602
2017-04-17 14:00 | 4 | 14 | 990.25 | 990.25
2017-04-17 15:00 | 4 | 15 | 1327.6014 | 1327.6014
2017-04-17 16:00 | 4 | 16 | 365.4458 | 365.4458
2017-04-17 17:00 | 4 | 17 | 156.9416 | 156.9416
2017-04-17 18:00 | 4 | 18 | 0 | 0
2017-04-17 19:00 | 4 | 19 | 0 | 0
2017-04-17 20:00 | 4 | 20 | 0 | 0
2017-04-17 21:00 | 4 | 21 | 0 | 0
2017-04-17 22:00 | 4 | 22 | 0 | 0
2017-04-17 23:00 | 4 | 23 | 0 | 0
2017-04-18 | 4 | 0 | 0 | 0
2017-04-18 01:00 | 4 | 1 | 0 | 0
2017-04-18 02:00 | 4 | 2 | 0 | 0
2017-04-18 03:00 | 4 | 3 | 0 | 0
2017-04-18 04:00 | 4 | 4 | 0 | 0
2017-04-18 05:00 | 4 | 5 | 106.8982 | 106.8982
2017-04-18 06:00 | 4 | 6 | 726.2468 | 726.2468
2017-04-18 07:00 | 4 | 7 | 2062.4342 | 2062.4342
2017-04-18 08:00 | 4 | 8 | 1804.5662 | 1804.5662
2017-04-18 09:00 | 4 | 9 | 2324.7664 | 2324.7664
2017-04-18 10:00 | 4 | 10 | 3033.3504 | 3033.3504
2017-04-18 11:00 | 4 | 11 | 5854.4809 | 5854.4809
2017-04-18 12:00 | 4 | 12 | 6284.0738 | 6284.0738
2017-04-18 13:00 | 4 | 13 | 5791.9451 | 5791.9451
2017-04-18 14:00 | 4 | 14 | 2454.7877 | 2454.7877
2017-04-18 15:00 | 4 | 15 | 4489.3516 | 4489.3516
2017-04-18 16:00 | 4 | 16 | 2813.4071 | 2813.4071
2017-04-18 17:00 | 4 | 17 | 139.7859 | 139.7859
2017-04-18 18:00 | 4 | 18 | 0 | 0
2017-04-18 19:00 | 4 | 19 | 0 | 0
2017-04-18 20:00 | 4 | 20 | 0 | 0
2017-04-18 21:00 | 4 | 21 | 0 | 0
2017-04-18 22:00 | 4 | 22 | 0 | 0
2017-04-18 23:00 | 4 | 23 | 0 | 0
2017-04-19 | 4 | 0 | 0 | 0
2017-04-19 01:00 | 4 | 1 | 0 | 0
2017-04-19 02:00 | 4 | 2 | 0 | 0
2017-04-19 03:00 | 4 | 3 | 0 | 0
2017-04-19 04:00 | 4 | 4 | 0 | 0
2017-04-19 05:00 | 4 | 5 | 225.7243 | 225.7243
2017-04-19 06:00 | 4 | 6 | 1920.7334 | 1920.7334
2017-04-19 07:00 | 4 | 7 | 4274.6581 | 4274.6581
2017-04-19 08:00 | 4 | 8 | 6212.0608 | 6212.0608
2017-04-19 09:00 | 4 | 9 | 7561.4961 | 7561.4961
2017-04-19 10:00 | 4 | 10 | 5556.3572 | 5556.3572
2017-04-19 11:00 | 4 | 11 | 4754.5818 | 4754.5818
2017-04-19 12:00 | 4 | 12 | 7190.4187 | 7190.4187
2017-04-19 13:00 | 4 | 13 | 3759.9158 | 3759.9158
2017-04-19 14:00 | 4 | 14 | 4397.0975 | 4397.0975
2017-04-19 15:00 | 4 | 15 | 4866.4343 | 4866.4343
2017-04-19 16:00 | 4 | 16 | 1376.3407 | 1376.3407
2017-04-19 17:00 | 4 | 17 | 746.1579 | 746.1579
2017-04-19 18:00 | 4 | 18 | 0 | 0
2017-04-19 19:00 | 4 | 19 | 0 | 0
2017-04-19 20:00 | 4 | 20 | 0 | 0
2017-04-19 21:00 | 4 | 21 | 0 | 0
2017-04-19 22:00 | 4 | 22 | 0 | 0
2017-04-19 23:00 | 4 | 23 | 0 | 0
2017-04-20 | 4 | 0 | 0 | 0
2017-04-20 01:00 | 4 | 1 | 0 | 0
2017-04-20 02:00 | 4 | 2 | 0 | 0
2017-04-20 03:00 | 4 | 3 | 0 | 0
2017-04-20 04:00 | 4 | 4 | 0 | 0
2017-04-20 05:00 | 4 | 5 | 243.8034 | 243.8034
2017-04-20 06:00 | 4 | 6 | 1864.1442 | 1864.1442
2017-04-20 07:00 | 4 | 7 | 4085.214 | 4085.214
2017-04-20 08:00 | 4 | 8 | 5938.2159 | 5938.2159
2017-04-20 09:00 | 4 | 9 | 6208.045 | 6208.045
2017-04-20 10:00 | 4 | 10 | 8135.3047 | 8135.3047
2017-04-20 11:00 | 4 | 11 | 6214.8012 | 6214.8012
2017-04-20 12:00 | 4 | 12 | 6070.2543 | 6070.2543
2017-04-20 13:00 | 4 | 13 | 5896.8837 | 5896.8837
2017-04-20 14:00 | 4 | 14 | 3556.475 | 3556.475
2017-04-20 15:00 | 4 | 15 | 2343.9633 | 2343.9633
2017-04-20 16:00 | 4 | 16 | 1535.3236 | 1535.3236
2017-04-20 17:00 | 4 | 17 | 611.624 | 611.624
2017-04-20 18:00 | 4 | 18 | 0 | 0
2017-04-20 19:00 | 4 | 19 | 0 | 0
2017-04-20 20:00 | 4 | 20 | 0 | 0
2017-04-20 21:00 | 4 | 21 | 0 | 0
2017-04-20 22:00 | 4 | 22 | 0 | 0
2017-04-20 23:00 | 4 | 23 | 0 | 0
2017-04-21 | 4 | 0 | 0 | 0
2017-04-21 01:00 | 4 | 1 | 0 | 0
2017-04-21 02:00 | 4 | 2 | 0 | 0
2017-04-21 03:00 | 4 | 3 | 0 | 0
2017-04-21 04:00 | 4 | 4 | 0 | 0
2017-04-21 05:00 | 4 | 5 | 256.7076 | 256.7076
2017-04-21 06:00 | 4 | 6 | 1819.6266 | 1819.6266
2017-04-21 07:00 | 4 | 7 | 2867.433 | 2867.433
2017-04-21 08:00 | 4 | 8 | 5266.2272 | 5266.2272
2017-04-21 09:00 | 4 | 9 | 6539.3474 | 6539.3474
2017-04-21 10:00 | 4 | 10 | 6832.0005 | 6832.0005
2017-04-21 11:00 | 4 | 11 | 5777.0192 | 5777.0192
2017-04-21 12:00 | 4 | 12 | 5132.1763 | 5132.1763
2017-04-21 13:00 | 4 | 13 | 5632.6149 | 5632.6149
2017-04-21 14:00 | 4 | 14 | 4995.9922 | 4995.9922
2017-04-21 15:00 | 4 | 15 | 3571.4043 | 3571.4043
2017-04-21 16:00 | 4 | 16 | 1280.0201 | 1280.0201
2017-04-21 17:00 | 4 | 17 | 625.6483 | 625.6483
2017-04-21 18:00 | 4 | 18 | 0 | 0
2017-04-21 19:00 | 4 | 19 | 0 | 0
2017-04-21 20:00 | 4 | 20 | 0 | 0
2017-04-21 21:00 | 4 | 21 | 0 | 0
2017-04-21 22:00 | 4 | 22 | 0 | 0
2017-04-21 23:00 | 4 | 23 | 0 | 0
2017-04-22 | 4 | 0 | 0 | 0
2017-04-22 01:00 | 4 | 1 | 0 | 0
2017-04-22 02:00 | 4 | 2 | 0 | 0
2017-04-22 03:00 | 4 | 3 | 0 | 0
2017-04-22 04:00 | 4 | 4 | 0 | 0
2017-04-22 05:00 | 4 | 5 | 289.4332 | 289.4332
2017-04-22 06:00 | 4 | 6 | 1769.0553 | 1769.0553
2017-04-22 07:00 | 4 | 7 | 3701.9604 | 3701.9604
2017-04-22 08:00 | 4 | 8 | 5431.7317 | 5431.7317
2017-04-22 09:00 | 4 | 9 | 6786.1293 | 6786.1293
2017-04-22 10:00 | 4 | 10 | 7837.5547 | 7837.5547
2017-04-22 11:00 | 4 | 11 | 5801.2797 | 5801.2797
2017-04-22 12:00 | 4 | 12 | 5903.4433 | 5903.4433
2017-04-22 13:00 | 4 | 13 | 267.245 | 267.245
2017-04-22 14:00 | 4 | 14 | 2320.3458 | 2320.3458
2017-04-22 15:00 | 4 | 15 | 170.4702 | 170.4702
2017-04-22 16:00 | 4 | 16 | 1874.1492 | 1874.1492
2017-04-22 17:00 | 4 | 17 | 769.4558 | 769.4558
2017-04-22 18:00 | 4 | 18 | 0 | 0
2017-04-22 19:00 | 4 | 19 | 0 | 0
2017-04-22 20:00 | 4 | 20 | 0 | 0
2017-04-22 21:00 | 4 | 21 | 0 | 0
2017-04-22 22:00 | 4 | 22 | 0 | 0
2017-04-22 23:00 | 4 | 23 | 0 | 0
2017-04-23 | 4 | 0 | 0 | 0
2017-04-23 01:00 | 4 | 1 | 0 | 0
2017-04-23 02:00 | 4 | 2 | 0 | 0
2017-04-23 03:00 | 4 | 3 | 0 | 0
2017-04-23 04:00 | 4 | 4 | 0 | 0
2017-04-23 05:00 | 4 | 5 | 93.1718 | 93.1718
2017-04-23 06:00 | 4 | 6 | 1083.584 | 1083.584
2017-04-23 07:00 | 4 | 7 | 2035.094 | 2035.094
2017-04-23 08:00 | 4 | 8 | 3884.7299 | 3884.7299
2017-04-23 09:00 | 4 | 9 | 5346.5006 | 5346.5006
2017-04-23 10:00 | 4 | 10 | 3944.0998 | 3944.0998
2017-04-23 11:00 | 4 | 11 | 5136.0334 | 5136.0334
2017-04-23 12:00 | 4 | 12 | 6337.8984 | 6337.8984
2017-04-23 13:00 | 4 | 13 | 3082.483 | 3082.483
2017-04-23 14:00 | 4 | 14 | 4110.9222 | 4110.9222
2017-04-23 15:00 | 4 | 15 | 439.4782 | 439.4782
2017-04-23 16:00 | 4 | 16 | 2873.168 | 2873.168
2017-04-23 17:00 | 4 | 17 | 798.4899 | 798.4899
2017-04-23 18:00 | 4 | 18 | 0 | 0
2017-04-23 19:00 | 4 | 19 | 0 | 0
2017-04-23 20:00 | 4 | 20 | 0 | 0
2017-04-23 21:00 | 4 | 21 | 0 | 0
2017-04-23 22:00 | 4 | 22 | 0 | 0
2017-04-23 23:00 | 4 | 23 | 0 | 0
2017-04-24 | 4 | 0 | 0 | 0
2017-04-24 01:00 | 4 | 1 | 0 | 0
2017-04-24 02:00 | 4 | 2 | 0 | 0
2017-04-24 03:00 | 4 | 3 | 0 | 0
2017-04-24 04:00 | 4 | 4 | 0 | 0
2017-04-24 05:00 | 4 | 5 | 316.8687 | 316.8687
2017-04-24 06:00 | 4 | 6 | 2045.6246 | 2045.6246
2017-04-24 07:00 | 4 | 7 | 4329.0542 | 4329.0542
2017-04-24 08:00 | 4 | 8 | 6204.2143 | 6204.2143
2017-04-24 09:00 | 4 | 9 | 7533.65 | 7533.65
2017-04-24 10:00 | 4 | 10 | 8288.3927 | 8288.3927
2017-04-24 11:00 | 4 | 11 | 8577.6211 | 8577.6211
2017-04-24 12:00 | 4 | 12 | 8355.9816 | 8355.9816
2017-04-24 13:00 | 4 | 13 | 7671.1267 | 7671.1267
2017-04-24 14:00 | 4 | 14 | 6567.3613 | 6567.3613
2017-04-24 15:00 | 4 | 15 | 4879.8019 | 4879.8019
2017-04-24 16:00 | 4 | 16 | 2580.1423 | 2580.1423
2017-04-24 17:00 | 4 | 17 | 801.4511 | 801.4511
2017-04-24 18:00 | 4 | 18 | 0 | 0
2017-04-24 19:00 | 4 | 19 | 0 | 0
2017-04-24 20:00 | 4 | 20 | 0 | 0
2017-04-24 21:00 | 4 | 21 | 0 | 0
2017-04-24 22:00 | 4 | 22 | 0 | 0
2017-04-24 23:00 | 4 | 23 | 0 | 0
2017-04-25 | 4 | 0 | 0 | 0
2017-04-25 01:00 | 4 | 1 | 0 | 0
2017-04-25 02:00 | 4 | 2 | 0 | 0
2017-04-25 03:00 | 4 | 3 | 0 | 0
2017-04-25 04:00 | 4 | 4 | 0 | 0
2017-04-25 05:00 | 4 | 5 | 193.1126 | 193.1126
2017-04-25 06:00 | 4 | 6 | 340.7611 | 340.7611
2017-04-25 07:00 | 4 | 7 | 2414.2582 | 2414.2582
2017-04-25 08:00 | 4 | 8 | 4579.8393 | 4579.8393
2017-04-25 09:00 | 4 | 9 | 5928.0832 | 5928.0832
2017-04-25 10:00 | 4 | 10 | 6965.9065 | 6965.9065
2017-04-25 11:00 | 4 | 11 | 6750.914 | 6750.914
2017-04-25 12:00 | 4 | 12 | 6121.8329 | 6121.8329
2017-04-25 13:00 | 4 | 13 | 6387.8187 | 6387.8187
2017-04-25 14:00 | 4 | 14 | 4884.0109 | 4884.0109
2017-04-25 15:00 | 4 | 15 | 2963.6604 | 2963.6604
2017-04-25 16:00 | 4 | 16 | 492.4909 | 492.4909
2017-04-25 17:00 | 4 | 17 | 604.9863 | 604.9863
2017-04-25 18:00 | 4 | 18 | 0 | 0
2017-04-25 19:00 | 4 | 19 | 0 | 0
2017-04-25 20:00 | 4 | 20 | 0 | 0
2017-04-25 21:00 | 4 | 21 | 0 | 0
2017-04-25 22:00 | 4 | 22 | 0 | 0
2017-04-25 23:00 | 4 | 23 | 0 | 0
2017-04-26 | 4 | 0 | 0 | 0
2017-04-26 01:00 | 4 | 1 | 0 | 0
2017-04-26 02:00 | 4 | 2 | 0 | 0
2017-04-26 03:00 | 4 | 3 | 0 | 0
2017-04-26 04:00 | 4 | 4 | 0 | 0
2017-04-26 05:00 | 4 | 5 | 291.6791 | 291.6791
2017-04-26 06:00 | 4 | 6 | 1113.346 | 1113.346
2017-04-26 07:00 | 4 | 7 | 703.2307 | 703.2307
2017-04-26 08:00 | 4 | 8 | 3086.6345 | 3086.6345
2017-04-26 09:00 | 4 | 9 | 4381.2366 | 4381.2366
2017-04-26 10:00 | 4 | 10 | 6871.5777 | 6871.5777
2017-04-26 11:00 | 4 | 11 | 6709.7026 | 6709.7026
2017-04-26 12:00 | 4 | 12 | 7090.3836 | 7090.3837
2017-04-26 13:00 | 4 | 13 | 3785.363 | 3785.363
2017-04-26 14:00 | 4 | 14 | 2591.8953 | 2591.8953
2017-04-26 15:00 | 4 | 15 | 819.3957 | 819.3957
2017-04-26 16:00 | 4 | 16 | 1905.2648 | 1905.2648
2017-04-26 17:00 | 4 | 17 | 562.6881 | 562.6881
2017-04-26 18:00 | 4 | 18 | 0 | 0
2017-04-26 19:00 | 4 | 19 | 0 | 0
2017-04-26 20:00 | 4 | 20 | 0 | 0
2017-04-26 21:00 | 4 | 21 | 0 | 0
2017-04-26 22:00 | 4 | 22 | 0 | 0
2017-04-26 23:00 | 4 | 23 | 0 | 0
2017-04-27 | 4 | 0 | 0 | 0
2017-04-27 01:00 | 4 | 1 | 0 | 0
2017-04-27 02:00 | 4 | 2 | 0 | 0
2017-04-27 03:00 | 4 | 3 | 0 | 0
2017-04-27 04:00 | 4 | 4 | 0 | 0
2017-04-27 05:00 | 4 | 5 | 83.0369 | 83.0369
2017-04-27 06:00 | 4 | 6 | 214.061 | 214.061
2017-04-27 07:00 | 4 | 7 | 943.8751 | 943.8751
2017-04-27 08:00 | 4 | 8 | 1060.4736 | 1060.4736
2017-04-27 09:00 | 4 | 9 | 1331.3343 | 1331.3343
2017-04-27 10:00 | 4 | 10 | 1292.3688 | 1292.3688
2017-04-27 11:00 | 4 | 11 | 935.027 | 935.027
2017-04-27 12:00 | 4 | 12 | 1228.2023 | 1228.2023
2017-04-27 13:00 | 4 | 13 | 1243.8515 | 1243.8515
2017-04-27 14:00 | 4 | 14 | 990.6709 | 990.6709
2017-04-27 15:00 | 4 | 15 | 161.713 | 161.713
2017-04-27 16:00 | 4 | 16 | 1170.4665 | 1170.4665
2017-04-27 17:00 | 4 | 17 | 62.4312 | 62.4312
2017-04-27 18:00 | 4 | 18 | 0 | 0
2017-04-27 19:00 | 4 | 19 | 0 | 0
2017-04-27 20:00 | 4 | 20 | 0 | 0
2017-04-27 21:00 | 4 | 21 | 0 | 0
2017-04-27 22:00 | 4 | 22 | 0 | 0
2017-04-27 23:00 | 4 | 23 | 0 | 0
2017-04-28 | 4 | 0 | 0 | 0
2017-04-28 01:00 | 4 | 1 | 0 | 0
2017-04-28 02:00 | 4 | 2 | 0 | 0
2017-04-28 03:00 | 4 | 3 | 0 | 0
2017-04-28 04:00 | 4 | 4 | 0 | 0
2017-04-28 05:00 | 4 | 5 | 353.97 | 353.97
2017-04-28 06:00 | 4 | 6 | 2218.174 | 2218.174
2017-04-28 07:00 | 4 | 7 | 1127.4462 | 1127.4462
2017-04-28 08:00 | 4 | 8 | 749.6976 | 749.6976
2017-04-28 09:00 | 4 | 9 | 1717.6699 | 1717.6699
2017-04-28 10:00 | 4 | 10 | 1791.7931 | 1791.7931
2017-04-28 11:00 | 4 | 11 | 6759.5206 | 6759.5206
2017-04-28 12:00 | 4 | 12 | 5673.5445 | 5673.5445
2017-04-28 13:00 | 4 | 13 | 4713.8741 | 4713.8741
2017-04-28 14:00 | 4 | 14 | 2210.4046 | 2210.4046
2017-04-28 15:00 | 4 | 15 | 3237.6847 | 3237.6847
2017-04-28 16:00 | 4 | 16 | 1728.0728 | 1728.0728
2017-04-28 17:00 | 4 | 17 | 511.3015 | 511.3015
2017-04-28 18:00 | 4 | 18 | 0 | 0
2017-04-28 19:00 | 4 | 19 | 0 | 0
2017-04-28 20:00 | 4 | 20 | 0 | 0
2017-04-28 21:00 | 4 | 21 | 0 | 0
2017-04-28 22:00 | 4 | 22 | 0 | 0
2017-04-28 23:00 | 4 | 23 | 0 | 0
2017-04-29 | 4 | 0 | 0 | 0
2017-04-29 01:00 | 4 | 1 | 0 | 0
2017-04-29 02:00 | 4 | 2 | 0 | 0
2017-04-29 03:00 | 4 | 3 | 0 | 0
2017-04-29 04:00 | 4 | 4 | 0 | 0
2017-04-29 05:00 | 4 | 5 | 394.8467 | 394.8467
2017-04-29 06:00 | 4 | 6 | 2219.6184 | 2219.6184
2017-04-29 07:00 | 4 | 7 | 4479.2695 | 4479.2695
2017-04-29 08:00 | 4 | 8 | 6349.227 | 6349.227
2017-04-29 09:00 | 4 | 9 | 7642.7608 | 7642.7609
2017-04-29 10:00 | 4 | 10 | 7658.4261 | 7658.4261
2017-04-29 11:00 | 4 | 11 | 9083.9178 | 9083.9178
2017-04-29 12:00 | 4 | 12 | 8973.5443 | 8973.5443
2017-04-29 13:00 | 4 | 13 | 8343.5547 | 8343.5547
2017-04-29 14:00 | 4 | 14 | 7131.1787 | 7131.1787
2017-04-29 15:00 | 4 | 15 | 5411.8528 | 5411.8528
2017-04-29 16:00 | 4 | 16 | 3074.6676 | 3074.6676
2017-04-29 17:00 | 4 | 17 | 901.0963 | 901.0963
2017-04-29 18:00 | 4 | 18 | 22.4756 | 22.4756
2017-04-29 19:00 | 4 | 19 | 0 | 0
2017-04-29 20:00 | 4 | 20 | 0 | 0
2017-04-29 21:00 | 4 | 21 | 0 | 0
2017-04-29 22:00 | 4 | 22 | 0 | 0
2017-04-29 23:00 | 4 | 23 | 0 | 0
2017-04-30 | 4 | 0 | 0 | 0
2017-04-30 01:00 | 4 | 1 | 0 | 0
2017-04-30 02:00 | 4 | 2 | 0 | 0
2017-04-30 03:00 | 4 | 3 | 0 | 0
2017-04-30 04:00 | 4 | 4 | 0 | 0
2017-04-30 05:00 | 4 | 5 | 402.9174 | 402.9174
2017-04-30 06:00 | 4 | 6 | 2249.2746 | 2249.2746
2017-04-30 07:00 | 4 | 7 | 4512.8219 | 4512.8219
2017-04-30 08:00 | 4 | 8 | 4870.8698 | 4870.8698
2017-04-30 09:00 | 4 | 9 | 6905.5522 | 6905.5522
2017-04-30 10:00 | 4 | 10 | 7648.4142 | 7648.4142
2017-04-30 11:00 | 4 | 11 | 7736.9378 | 7736.9378
2017-04-30 12:00 | 4 | 12 | 8393.1347 | 8393.1347
2017-04-30 13:00 | 4 | 13 | 7040.0412 | 7040.0412
2017-04-30 14:00 | 4 | 14 | 4475.2584 | 4475.2584
2017-04-30 15:00 | 4 | 15 | 4925.573 | 4925.573
2017-04-30 16:00 | 4 | 16 | 2856.6701 | 2856.6701
2017-04-30 17:00 | 4 | 17 | 871.0284 | 871.0284
2017-04-30 18:00 | 4 | 18 | 40.2925 | 40.2925
2017-04-30 19:00 | 4 | 19 | 0 | 0
2017-04-30 20:00 | 4 | 20 | 0 | 0
2017-04-30 21:00 | 4 | 21 | 0 | 0
2017-04-30 22:00 | 4 | 22 | 0 | 0
2017-04-30 23:00 | 4 | 23 | 0 | 0
2017-05-01 | 5 | 0 | 0 | 0
2017-05-01 01:00 | 5 | 1 | 0 | 0
2017-05-01 02:00 | 5 | 2 | 0 | 0
2017-05-01 03:00 | 5 | 3 | 0 | 0
2017-05-01 04:00 | 5 | 4 | 0 | 0
2017-05-01 05:00 | 5 | 5 | 464.5586 | 464.5586
2017-05-01 06:00 | 5 | 6 | 2281.9392 | 2281.9392
2017-05-01 07:00 | 5 | 7 | 4475.532 | 4475.532
2017-05-01 08:00 | 5 | 8 | 6328.2959 | 6328.2959
2017-05-01 09:00 | 5 | 9 | 7652.3357 | 7652.3358
2017-05-01 10:00 | 5 | 10 | 8451.3017 | 8451.3017
2017-05-01 11:00 | 5 | 11 | 8681.22 | 8681.22
2017-05-01 12:00 | 5 | 12 | 6210.1518 | 6210.1518
2017-05-01 13:00 | 5 | 13 | 5678.1767 | 5678.1767
2017-05-01 14:00 | 5 | 14 | 6654.5095 | 6654.5095
2017-05-01 15:00 | 5 | 15 | 4944.3848 | 4944.3848
2017-05-01 16:00 | 5 | 16 | 2920.9781 | 2920.9781
2017-05-01 17:00 | 5 | 17 | 979.4757 | 979.4757
2017-05-01 18:00 | 5 | 18 | 41.3425 | 41.3425
2017-05-01 19:00 | 5 | 19 | 0 | 0
2017-05-01 20:00 | 5 | 20 | 0 | 0
2017-05-01 21:00 | 5 | 21 | 0 | 0
2017-05-01 22:00 | 5 | 22 | 0 | 0
2017-05-01 23:00 | 5 | 23 | 0 | 0
2017-05-02 | 5 | 0 | 0 | 0
2017-05-02 01:00 | 5 | 1 | 0 | 0
2017-05-02 02:00 | 5 | 2 | 0 | 0
2017-05-02 03:00 | 5 | 3 | 0 | 0
2017-05-02 04:00 | 5 | 4 | 0 | 0
2017-05-02 05:00 | 5 | 5 | 0 | 0
2017-05-02 06:00 | 5 | 6 | 223.0977 | 223.0977
2017-05-02 07:00 | 5 | 7 | 536.0725 | 536.0725
2017-05-02 08:00 | 5 | 8 | 1129.8509 | 1129.8509
2017-05-02 09:00 | 5 | 9 | 1462.3664 | 1462.3664
2017-05-02 10:00 | 5 | 10 | 1025.2273 | 1025.2273
2017-05-02 11:00 | 5 | 11 | 1321.5512 | 1321.5512
2017-05-02 12:00 | 5 | 12 | 722.9923 | 722.9923
2017-05-02 13:00 | 5 | 13 | 951.909 | 951.909
2017-05-02 14:00 | 5 | 14 | 1652.4338 | 1652.4338
2017-05-02 15:00 | 5 | 15 | 1675.6201 | 1675.6201
2017-05-02 16:00 | 5 | 16 | 1104.4991 | 1104.4991
2017-05-02 17:00 | 5 | 17 | 1.6779 | 1.6779
2017-05-02 18:00 | 5 | 18 | 0 | 0
2017-05-02 19:00 | 5 | 19 | 0 | 0
2017-05-02 20:00 | 5 | 20 | 0 | 0
2017-05-02 21:00 | 5 | 21 | 0 | 0
2017-05-02 22:00 | 5 | 22 | 0 | 0
2017-05-02 23:00 | 5 | 23 | 0 | 0
2017-05-03 | 5 | 0 | 0 | 0
2017-05-03 01:00 | 5 | 1 | 0 | 0
2017-05-03 02:00 | 5 | 2 | 0 | 0
2017-05-03 03:00 | 5 | 3 | 0 | 0
2017-05-03 04:00 | 5 | 4 | 0 | 0
2017-05-03 05:00 | 5 | 5 | 0 | 0
2017-05-03 06:00 | 5 | 6 | 42.665 | 42.665
2017-05-03 07:00 | 5 | 7 | 594.4948 | 594.4948
2017-05-03 08:00 | 5 | 8 | 423.8544 | 423.8543
2017-05-03 09:00 | 5 | 9 | 393.0067 | 393.0067
2017-05-03 10:00 | 5 | 10 | 670.7409 | 670.7409
2017-05-03 11:00 | 5 | 11 | 472.2394 | 472.2394
2017-05-03 12:00 | 5 | 12 | 1237.6841 | 1237.6841
2017-05-03 13:00 | 5 | 13 | 827.1133 | 827.1133
2017-05-03 14:00 | 5 | 14 | 744.6078 | 744.6078
2017-05-03 15:00 | 5 | 15 | 271.8876 | 271.8876
2017-05-03 16:00 | 5 | 16 | 133.3287 | 133.3287
2017-05-03 17:00 | 5 | 17 | 153.5169 | 153.5169
2017-05-03 18:00 | 5 | 18 | 0 | 0
2017-05-03 19:00 | 5 | 19 | 0 | 0
2017-05-03 20:00 | 5 | 20 | 0 | 0
2017-05-03 21:00 | 5 | 21 | 0 | 0
2017-05-03 22:00 | 5 | 22 | 0 | 0
2017-05-03 23:00 | 5 | 23 | 0 | 0
2017-05-04 | 5 | 0 | 0 | 0
2017-05-04 01:00 | 5 | 1 | 0 | 0
2017-05-04 02:00 | 5 | 2 | 0 | 0
2017-05-04 03:00 | 5 | 3 | 0 | 0
2017-05-04 04:00 | 5 | 4 | 0 | 0
2017-05-04 05:00 | 5 | 5 | 314.5871 | 314.5871
2017-05-04 06:00 | 5 | 6 | 203.6627 | 203.6627
2017-05-04 07:00 | 5 | 7 | 374.639 | 374.639
2017-05-04 08:00 | 5 | 8 | 725.0704 | 725.0704
2017-05-04 09:00 | 5 | 9 | 1966.6449 | 1966.6449
2017-05-04 10:00 | 5 | 10 | 931.3643 | 931.3643
2017-05-04 11:00 | 5 | 11 | 1335.3881 | 1335.3881
2017-05-04 12:00 | 5 | 12 | 1624.981 | 1624.981
2017-05-04 13:00 | 5 | 13 | 1858.837 | 1858.837
2017-05-04 14:00 | 5 | 14 | 1636.0544 | 1636.0544
2017-05-04 15:00 | 5 | 15 | 1627.6088 | 1627.6088
2017-05-04 16:00 | 5 | 16 | 831.7064 | 831.7064
2017-05-04 17:00 | 5 | 17 | 884.2994 | 884.2994
2017-05-04 18:00 | 5 | 18 | 62.0896 | 62.0896
2017-05-04 19:00 | 5 | 19 | 0 | 0
2017-05-04 20:00 | 5 | 20 | 0 | 0
2017-05-04 21:00 | 5 | 21 | 0 | 0
2017-05-04 22:00 | 5 | 22 | 0 | 0
2017-05-04 23:00 | 5 | 23 | 0 | 0
2017-05-05 | 5 | 0 | 0 | 0
2017-05-05 01:00 | 5 | 1 | 0 | 0
2017-05-05 02:00 | 5 | 2 | 0 | 0
2017-05-05 03:00 | 5 | 3 | 0 | 0
2017-05-05 04:00 | 5 | 4 | 0 | 0
2017-05-05 05:00 | 5 | 5 | 469.9383 | 469.9383
2017-05-05 06:00 | 5 | 6 | 1886.4508 | 1886.4508
2017-05-05 07:00 | 5 | 7 | 4489.9162 | 4489.9162
2017-05-05 08:00 | 5 | 8 | 6217.9304 | 6217.9304
2017-05-05 09:00 | 5 | 9 | 7460.9459 | 7460.9459
2017-05-05 10:00 | 5 | 10 | 8226.4997 | 8226.4997
2017-05-05 11:00 | 5 | 11 | 8498.546 | 8498.546
2017-05-05 12:00 | 5 | 12 | 8286.5757 | 8286.5757
2017-05-05 13:00 | 5 | 13 | 7590.7049 | 7590.7049
2017-05-05 14:00 | 5 | 14 | 6493.0587 | 6493.0587
2017-05-05 15:00 | 5 | 15 | 4913.1312 | 4913.1312
2017-05-05 16:00 | 5 | 16 | 2933.5246 | 2933.5246
2017-05-05 17:00 | 5 | 17 | 968.7565 | 968.7565
2017-05-05 18:00 | 5 | 18 | 68.5814 | 68.5814
2017-05-05 19:00 | 5 | 19 | 0 | 0
2017-05-05 20:00 | 5 | 20 | 0 | 0
2017-05-05 21:00 | 5 | 21 | 0 | 0
2017-05-05 22:00 | 5 | 22 | 0 | 0
2017-05-05 23:00 | 5 | 23 | 0 | 0
2017-05-06 | 5 | 0 | 0 | 0
2017-05-06 01:00 | 5 | 1 | 0 | 0
2017-05-06 02:00 | 5 | 2 | 0 | 0
2017-05-06 03:00 | 5 | 3 | 0 | 0
2017-05-06 04:00 | 5 | 4 | 0 | 0
2017-05-06 05:00 | 5 | 5 | 552.3427 | 552.3427
2017-05-06 06:00 | 5 | 6 | 2257.8214 | 2257.8214
2017-05-06 07:00 | 5 | 7 | 4370.1495 | 4370.1495
2017-05-06 08:00 | 5 | 8 | 6113.2792 | 6113.2792
2017-05-06 09:00 | 5 | 9 | 6577.5273 | 6577.5273
2017-05-06 10:00 | 5 | 10 | 8088.2478 | 8088.2478
2017-05-06 11:00 | 5 | 11 | 8305.3173 | 8305.3173
2017-05-06 12:00 | 5 | 12 | 7221.6964 | 7221.6964
2017-05-06 13:00 | 5 | 13 | 7455.8157 | 7455.8157
2017-05-06 14:00 | 5 | 14 | 6328.0556 | 6328.0556
2017-05-06 15:00 | 5 | 15 | 4741.6179 | 4741.6179
2017-05-06 16:00 | 5 | 16 | 1324.1077 | 1324.1077
2017-05-06 17:00 | 5 | 17 | 1010.2589 | 1010.2589
2017-05-06 18:00 | 5 | 18 | 92.1989 | 92.1989
2017-05-06 19:00 | 5 | 19 | 0 | 0
2017-05-06 20:00 | 5 | 20 | 0 | 0
2017-05-06 21:00 | 5 | 21 | 0 | 0
2017-05-06 22:00 | 5 | 22 | 0 | 0
2017-05-06 23:00 | 5 | 23 | 0 | 0
2017-05-07 | 5 | 0 | 0 | 0
2017-05-07 01:00 | 5 | 1 | 0 | 0
2017-05-07 02:00 | 5 | 2 | 0 | 0
2017-05-07 03:00 | 5 | 3 | 0 | 0
2017-05-07 04:00 | 5 | 4 | 0 | 0
2017-05-07 05:00 | 5 | 5 | 507.9044 | 507.9044
2017-05-07 06:00 | 5 | 6 | 2309.0919 | 2309.0919
2017-05-07 07:00 | 5 | 7 | 4409.7325 | 4409.7325
2017-05-07 08:00 | 5 | 8 | 6181.4489 | 6181.4489
2017-05-07 09:00 | 5 | 9 | 7477.8003 | 7477.8003
2017-05-07 10:00 | 5 | 10 | 8181.1207 | 8181.1207
2017-05-07 11:00 | 5 | 11 | 8399.6092 | 8399.6092
2017-05-07 12:00 | 5 | 12 | 8223.382 | 8223.382
2017-05-07 13:00 | 5 | 13 | 7473.8143 | 7473.8143
2017-05-07 14:00 | 5 | 14 | 5450.5469 | 5450.5469
2017-05-07 15:00 | 5 | 15 | 4754.867 | 4754.867
2017-05-07 16:00 | 5 | 16 | 2872.5747 | 2872.5747
2017-05-07 17:00 | 5 | 17 | 896.7976 | 896.7976
2017-05-07 18:00 | 5 | 18 | 107.6009 | 107.6009
2017-05-07 19:00 | 5 | 19 | 0 | 0
2017-05-07 20:00 | 5 | 20 | 0 | 0
2017-05-07 21:00 | 5 | 21 | 0 | 0
2017-05-07 22:00 | 5 | 22 | 0 | 0
2017-05-07 23:00 | 5 | 23 | 0 | 0
2017-05-08 | 5 | 0 | 0 | 0
2017-05-08 01:00 | 5 | 1 | 0 | 0
2017-05-08 02:00 | 5 | 2 | 0 | 0
2017-05-08 03:00 | 5 | 3 | 0 | 0
2017-05-08 04:00 | 5 | 4 | 0 | 0
2017-05-08 05:00 | 5 | 5 | 316.4351 | 316.4351
2017-05-08 06:00 | 5 | 6 | 626.735 | 626.735
2017-05-08 07:00 | 5 | 7 | 884.7916 | 884.7916
2017-05-08 08:00 | 5 | 8 | 1245.749 | 1245.749
2017-05-08 09:00 | 5 | 9 | 3203.2088 | 3203.2088
2017-05-08 10:00 | 5 | 10 | 5840.1278 | 5840.1278
2017-05-08 11:00 | 5 | 11 | 4668.6596 | 4668.6596
2017-05-08 12:00 | 5 | 12 | 4621.7821 | 4621.7821
2017-05-08 13:00 | 5 | 13 | 6110.487 | 6110.487
2017-05-08 14:00 | 5 | 14 | 5654.5787 | 5654.5787
2017-05-08 15:00 | 5 | 15 | 4571.4156 | 4571.4156
2017-05-08 16:00 | 5 | 16 | 2081.8933 | 2081.8933
2017-05-08 17:00 | 5 | 17 | 378.9031 | 378.9031
2017-05-08 18:00 | 5 | 18 | 0.03565 | 0.03565
2017-05-08 19:00 | 5 | 19 | 0 | 0
2017-05-08 20:00 | 5 | 20 | 0 | 0
2017-05-08 21:00 | 5 | 21 | 0 | 0
2017-05-08 22:00 | 5 | 22 | 0 | 0
2017-05-08 23:00 | 5 | 23 | 0 | 0
2017-05-09 | 5 | 0 | 0 | 0
2017-05-09 01:00 | 5 | 1 | 0 | 0
2017-05-09 02:00 | 5 | 2 | 0 | 0
2017-05-09 03:00 | 5 | 3 | 0 | 0
2017-05-09 04:00 | 5 | 4 | 0 | 0
2017-05-09 05:00 | 5 | 5 | 408.5455 | 408.5455
2017-05-09 06:00 | 5 | 6 | 1432.2077 | 1432.2077
2017-05-09 07:00 | 5 | 7 | 1874.2688 | 1874.2688
2017-05-09 08:00 | 5 | 8 | 2028.3493 | 2028.3493
2017-05-09 09:00 | 5 | 9 | 2995.8293 | 2995.8293
2017-05-09 10:00 | 5 | 10 | 4185.2318 | 4185.2318
2017-05-09 11:00 | 5 | 11 | 2878.8951 | 2878.8951
2017-05-09 12:00 | 5 | 12 | 2483.6619 | 2483.6619
2017-05-09 13:00 | 5 | 13 | 2006.9409 | 2006.9409
2017-05-09 14:00 | 5 | 14 | 1235.5289 | 1235.5289
2017-05-09 15:00 | 5 | 15 | 1076.1907 | 1076.1907
2017-05-09 16:00 | 5 | 16 | 683.5462 | 683.5462
2017-05-09 17:00 | 5 | 17 | 864.3538 | 864.3538
2017-05-09 18:00 | 5 | 18 | 102.4408 | 102.4408
2017-05-09 19:00 | 5 | 19 | 0 | 0
2017-05-09 20:00 | 5 | 20 | 0 | 0
2017-05-09 21:00 | 5 | 21 | 0 | 0
2017-05-09 22:00 | 5 | 22 | 0 | 0
2017-05-09 23:00 | 5 | 23 | 0 | 0
2017-05-10 | 5 | 0 | 0 | 0
2017-05-10 01:00 | 5 | 1 | 0 | 0
2017-05-10 02:00 | 5 | 2 | 0 | 0
2017-05-10 03:00 | 5 | 3 | 0 | 0
2017-05-10 04:00 | 5 | 4 | 0 | 0
2017-05-10 05:00 | 5 | 5 | 314.9183 | 314.9183
2017-05-10 06:00 | 5 | 6 | 491.311 | 491.311
2017-05-10 07:00 | 5 | 7 | 2502.4057 | 2502.4057
2017-05-10 08:00 | 5 | 8 | 2360.6636 | 2360.6636
2017-05-10 09:00 | 5 | 9 | 4071.5796 | 4071.5796
2017-05-10 10:00 | 5 | 10 | 5441.0663 | 5441.0663
2017-05-10 11:00 | 5 | 11 | 7281.0858 | 7281.0859
2017-05-10 12:00 | 5 | 12 | 6734.009 | 6734.009
2017-05-10 13:00 | 5 | 13 | 6335.0464 | 6335.0464
2017-05-10 14:00 | 5 | 14 | 5530.0406 | 5530.0406
2017-05-10 15:00 | 5 | 15 | 3802.3715 | 3802.3715
2017-05-10 16:00 | 5 | 16 | 2537.9994 | 2537.9994
2017-05-10 17:00 | 5 | 17 | 920.077 | 920.0771
2017-05-10 18:00 | 5 | 18 | 120.7247 | 120.7247
2017-05-10 19:00 | 5 | 19 | 0 | 0
2017-05-10 20:00 | 5 | 20 | 0 | 0
2017-05-10 21:00 | 5 | 21 | 0 | 0
2017-05-10 22:00 | 5 | 22 | 0 | 0
2017-05-10 23:00 | 5 | 23 | 0 | 0
2017-05-11 | 5 | 0 | 0 | 0
2017-05-11 01:00 | 5 | 1 | 0 | 0
2017-05-11 02:00 | 5 | 2 | 0 | 0
2017-05-11 03:00 | 5 | 3 | 0 | 0
2017-05-11 04:00 | 5 | 4 | 0 | 0
2017-05-11 05:00 | 5 | 5 | 613.4157 | 613.4157
2017-05-11 06:00 | 5 | 6 | 2419.3447 | 2419.3447
2017-05-11 07:00 | 5 | 7 | 4610.718 | 4610.718
2017-05-11 08:00 | 5 | 8 | 6407.6539 | 6407.6539
2017-05-11 09:00 | 5 | 9 | 7671.6822 | 7671.6822
2017-05-11 10:00 | 5 | 10 | 8468.309 | 8468.309
2017-05-11 11:00 | 5 | 11 | 8738.5544 | 8738.5544
2017-05-11 12:00 | 5 | 12 | 8567.8128 | 8567.8128
2017-05-11 13:00 | 5 | 13 | 7939.3596 | 7939.3597
2017-05-11 14:00 | 5 | 14 | 6838.7855 | 6838.7855
2017-05-11 15:00 | 5 | 15 | 4542.8254 | 4542.8254
2017-05-11 16:00 | 5 | 16 | 2666.7246 | 2666.7246
2017-05-11 17:00 | 5 | 17 | 981.4203 | 981.4203
2017-05-11 18:00 | 5 | 18 | 157.619 | 157.619
2017-05-11 19:00 | 5 | 19 | 0 | 0
2017-05-11 20:00 | 5 | 20 | 0 | 0
2017-05-11 21:00 | 5 | 21 | 0 | 0
2017-05-11 22:00 | 5 | 22 | 0 | 0
2017-05-11 23:00 | 5 | 23 | 0 | 0
2017-05-12 | 5 | 0 | 0 | 0
2017-05-12 01:00 | 5 | 1 | 0 | 0
2017-05-12 02:00 | 5 | 2 | 0 | 0
2017-05-12 03:00 | 5 | 3 | 0 | 0
2017-05-12 04:00 | 5 | 4 | 0 | 0
2017-05-12 05:00 | 5 | 5 | 563.7691 | 563.7691
2017-05-12 06:00 | 5 | 6 | 1506.9968 | 1506.9968
2017-05-12 07:00 | 5 | 7 | 1951.9433 | 1951.9433
2017-05-12 08:00 | 5 | 8 | 2757.984 | 2757.984
2017-05-12 09:00 | 5 | 9 | 3770.9926 | 3770.9926
2017-05-12 10:00 | 5 | 10 | 4839.8509 | 4839.8509
2017-05-12 11:00 | 5 | 11 | 5221.4692 | 5221.4692
2017-05-12 12:00 | 5 | 12 | 5762.6661 | 5762.6661
2017-05-12 13:00 | 5 | 13 | 5180.7994 | 5180.7994
2017-05-12 14:00 | 5 | 14 | 5902.7476 | 5902.7476
2017-05-12 15:00 | 5 | 15 | 3161.5087 | 3161.5087
2017-05-12 16:00 | 5 | 16 | 1938.7884 | 1938.7884
2017-05-12 17:00 | 5 | 17 | 966.3358 | 966.3358
2017-05-12 18:00 | 5 | 18 | 158.9139 | 158.9139
2017-05-12 19:00 | 5 | 19 | 0 | 0
2017-05-12 20:00 | 5 | 20 | 0 | 0
2017-05-12 21:00 | 5 | 21 | 0 | 0
2017-05-12 22:00 | 5 | 22 | 0 | 0
2017-05-12 23:00 | 5 | 23 | 0 | 0
2017-05-13 | 5 | 0 | 0 | 0
2017-05-13 01:00 | 5 | 1 | 0 | 0
2017-05-13 02:00 | 5 | 2 | 0 | 0
2017-05-13 03:00 | 5 | 3 | 0 | 0
2017-05-13 04:00 | 5 | 4 | 0 | 0
2017-05-13 05:00 | 5 | 5 | 590.4675 | 590.4675
2017-05-13 06:00 | 5 | 6 | 2466.6856 | 2466.6856
2017-05-13 07:00 | 5 | 7 | 4593.6566 | 4593.6566
2017-05-13 08:00 | 5 | 8 | 5478.4884 | 5478.4884
2017-05-13 09:00 | 5 | 9 | 6710.7318 | 6710.7318
2017-05-13 10:00 | 5 | 10 | 8358.2736 | 8358.2736
2017-05-13 11:00 | 5 | 11 | 8586.5532 | 8586.5532
2017-05-13 12:00 | 5 | 12 | 7546.8014 | 7546.8014
2017-05-13 13:00 | 5 | 13 | 7662.9997 | 7662.9997
2017-05-13 14:00 | 5 | 14 | 5736.2391 | 5736.2391
2017-05-13 15:00 | 5 | 15 | 3996.0349 | 3996.0349
2017-05-13 16:00 | 5 | 16 | 3088.5044 | 3088.5044
2017-05-13 17:00 | 5 | 17 | 1096.947 | 1096.947
2017-05-13 18:00 | 5 | 18 | 143.8362 | 143.8362
2017-05-13 19:00 | 5 | 19 | 0 | 0
2017-05-13 20:00 | 5 | 20 | 0 | 0
2017-05-13 21:00 | 5 | 21 | 0 | 0
2017-05-13 22:00 | 5 | 22 | 0 | 0
2017-05-13 23:00 | 5 | 23 | 0 | 0
2017-05-14 | 5 | 0 | 0 | 0
2017-05-14 01:00 | 5 | 1 | 0 | 0
2017-05-14 02:00 | 5 | 2 | 0 | 0
2017-05-14 03:00 | 5 | 3 | 0 | 0
2017-05-14 04:00 | 5 | 4 | 0 | 0
2017-05-14 05:00 | 5 | 5 | 628.5452 | 628.5452
2017-05-14 06:00 | 5 | 6 | 2427.0819 | 2427.0819
2017-05-14 07:00 | 5 | 7 | 4535.5666 | 4535.5666
2017-05-14 08:00 | 5 | 8 | 6246.4285 | 6246.4285
2017-05-14 09:00 | 5 | 9 | 7489.2554 | 7489.2554
2017-05-14 10:00 | 5 | 10 | 8218.7211 | 8218.7211
2017-05-14 11:00 | 5 | 11 | 8528.7887 | 8528.7887
2017-05-14 12:00 | 5 | 12 | 8370.6039 | 8370.6039
2017-05-14 13:00 | 5 | 13 | 7680.1427 | 7680.1428
2017-05-14 14:00 | 5 | 14 | 6647.2415 | 6647.2415
2017-05-14 15:00 | 5 | 15 | 5093.3971 | 5093.3971
2017-05-14 16:00 | 5 | 16 | 3099.695 | 3099.695
2017-05-14 17:00 | 5 | 17 | 1004.4065 | 1004.4065
2017-05-14 18:00 | 5 | 18 | 152.0875 | 152.0875
2017-05-14 19:00 | 5 | 19 | 0 | 0
2017-05-14 20:00 | 5 | 20 | 0 | 0
2017-05-14 21:00 | 5 | 21 | 0 | 0
2017-05-14 22:00 | 5 | 22 | 0 | 0
2017-05-14 23:00 | 5 | 23 | 0 | 0
2017-05-15 | 5 | 0 | 0 | 0
2017-05-15 01:00 | 5 | 1 | 0 | 0
2017-05-15 02:00 | 5 | 2 | 0 | 0
2017-05-15 03:00 | 5 | 3 | 0 | 0
2017-05-15 04:00 | 5 | 4 | 0 | 0
2017-05-15 05:00 | 5 | 5 | 389.8902 | 389.8902
2017-05-15 06:00 | 5 | 6 | 805.3507 | 805.3507
2017-05-15 07:00 | 5 | 7 | 1280.3249 | 1280.3249
2017-05-15 08:00 | 5 | 8 | 2254.2139 | 2254.2139
2017-05-15 09:00 | 5 | 9 | 4101.2726 | 4101.2726
2017-05-15 10:00 | 5 | 10 | 828.6946 | 828.6946
2017-05-15 11:00 | 5 | 11 | 3257.8545 | 3257.8545
2017-05-15 12:00 | 5 | 12 | 3204.406 | 3204.406
2017-05-15 13:00 | 5 | 13 | 2914.6244 | 2914.6244
2017-05-15 14:00 | 5 | 14 | 3518.732 | 3518.732
2017-05-15 15:00 | 5 | 15 | 2409.7698 | 2409.7698
2017-05-15 16:00 | 5 | 16 | 2332.0689 | 2332.0689
2017-05-15 17:00 | 5 | 17 | 917.5562 | 917.5562
2017-05-15 18:00 | 5 | 18 | 155.4524 | 155.4524
2017-05-15 19:00 | 5 | 19 | 0 | 0
2017-05-15 20:00 | 5 | 20 | 0 | 0
2017-05-15 21:00 | 5 | 21 | 0 | 0
2017-05-15 22:00 | 5 | 22 | 0 | 0
2017-05-15 23:00 | 5 | 23 | 0 | 0
2017-05-16 | 5 | 0 | 0 | 0
2017-05-16 01:00 | 5 | 1 | 0 | 0
2017-05-16 02:00 | 5 | 2 | 0 | 0
2017-05-16 03:00 | 5 | 3 | 0 | 0
2017-05-16 04:00 | 5 | 4 | 0 | 0
2017-05-16 05:00 | 5 | 5 | 434.5597 | 434.5597
2017-05-16 06:00 | 5 | 6 | 1136.6956 | 1136.6956
2017-05-16 07:00 | 5 | 7 | 2472.2723 | 2472.2723
2017-05-16 08:00 | 5 | 8 | 2811.6292 | 2811.6292
2017-05-16 09:00 | 5 | 9 | 4611.5678 | 4611.5678
2017-05-16 10:00 | 5 | 10 | 4811.2032 | 4811.2032
2017-05-16 11:00 | 5 | 11 | 3162.9911 | 3162.9911
2017-05-16 12:00 | 5 | 12 | 2215.4531 | 2215.4531
2017-05-16 13:00 | 5 | 13 | 1998.1054 | 1998.1054
2017-05-16 14:00 | 5 | 14 | 1509.7154 | 1509.7154
2017-05-16 15:00 | 5 | 15 | 775.5209 | 775.5209
2017-05-16 16:00 | 5 | 16 | 176.3916 | 176.3916
2017-05-16 17:00 | 5 | 17 | 169.4191 | 169.4191
2017-05-16 18:00 | 5 | 18 | 0 | 0
2017-05-16 19:00 | 5 | 19 | 0 | 0
2017-05-16 20:00 | 5 | 20 | 0 | 0
2017-05-16 21:00 | 5 | 21 | 0 | 0
2017-05-16 22:00 | 5 | 22 | 0 | 0
2017-05-16 23:00 | 5 | 23 | 0 | 0
2017-05-17 | 5 | 0 | 0 | 0
2017-05-17 01:00 | 5 | 1 | 0 | 0
2017-05-17 02:00 | 5 | 2 | 0 | 0
2017-05-17 03:00 | 5 | 3 | 0 | 0
2017-05-17 04:00 | 5 | 4 | 0 | 0
2017-05-17 05:00 | 5 | 5 | 0 | 0
2017-05-17 06:00 | 5 | 6 | 735.1812 | 735.1812
2017-05-17 07:00 | 5 | 7 | 2325.2678 | 2325.2678
2017-05-17 08:00 | 5 | 8 | 2557.5505 | 2557.5505
2017-05-17 09:00 | 5 | 9 | 2314.9546 | 2314.9546
2017-05-17 10:00 | 5 | 10 | 7367.2887 | 7367.2887
2017-05-17 11:00 | 5 | 11 | 8553.4251 | 8553.4251
2017-05-17 12:00 | 5 | 12 | 6339.5889 | 6339.5889
2017-05-17 13:00 | 5 | 13 | 7771.9863 | 7771.9863
2017-05-17 14:00 | 5 | 14 | 6632.5296 | 6632.5296
2017-05-17 15:00 | 5 | 15 | 5043.7033 | 5043.7033
2017-05-17 16:00 | 5 | 16 | 3049.7471 | 3049.7471
2017-05-17 17:00 | 5 | 17 | 1109.9697 | 1109.9697
2017-05-17 18:00 | 5 | 18 | 173.5143 | 173.5143
2017-05-17 19:00 | 5 | 19 | 0 | 0
2017-05-17 20:00 | 5 | 20 | 0 | 0
2017-05-17 21:00 | 5 | 21 | 0 | 0
2017-05-17 22:00 | 5 | 22 | 0 | 0
2017-05-17 23:00 | 5 | 23 | 0 | 0
2017-05-18 | 5 | 0 | 0 | 0
2017-05-18 01:00 | 5 | 1 | 0 | 0
2017-05-18 02:00 | 5 | 2 | 0 | 0
2017-05-18 03:00 | 5 | 3 | 0 | 0
2017-05-18 04:00 | 5 | 4 | 0 | 0
2017-05-18 05:00 | 5 | 5 | 631.7399 | 631.7399
2017-05-18 06:00 | 5 | 6 | 2494.3189 | 2494.3189
2017-05-18 07:00 | 5 | 7 | 4610.9687 | 4610.9687
2017-05-18 08:00 | 5 | 8 | 6318.1598 | 6318.1598
2017-05-18 09:00 | 5 | 9 | 7536.3835 | 7536.3836
2017-05-18 10:00 | 5 | 10 | 8251.9411 | 8251.9411
2017-05-18 11:00 | 5 | 11 | 8427.3656 | 8427.3656
2017-05-18 12:00 | 5 | 12 | 4885.415 | 4885.415
2017-05-18 13:00 | 5 | 13 | 2901.3028 | 2901.3028
2017-05-18 14:00 | 5 | 14 | 2502.0159 | 2502.0159
2017-05-18 15:00 | 5 | 15 | 1817.6992 | 1817.6992
2017-05-18 16:00 | 5 | 16 | 269.192 | 269.192
2017-05-18 17:00 | 5 | 17 | 985.2107 | 985.2107
2017-05-18 18:00 | 5 | 18 | 194.0234 | 194.0234
2017-05-18 19:00 | 5 | 19 | 0 | 0
2017-05-18 20:00 | 5 | 20 | 0 | 0
2017-05-18 21:00 | 5 | 21 | 0 | 0
2017-05-18 22:00 | 5 | 22 | 0 | 0
2017-05-18 23:00 | 5 | 23 | 0 | 0
2017-05-19 | 5 | 0 | 0 | 0
2017-05-19 01:00 | 5 | 1 | 0 | 0
2017-05-19 02:00 | 5 | 2 | 0 | 0
2017-05-19 03:00 | 5 | 3 | 0 | 0
2017-05-19 04:00 | 5 | 4 | 15.3766 | 15.3767
2017-05-19 05:00 | 5 | 5 | 672.6603 | 672.6603
2017-05-19 06:00 | 5 | 6 | 2539.875 | 2539.875
2017-05-19 07:00 | 5 | 7 | 4749.0745 | 4749.0745
2017-05-19 08:00 | 5 | 8 | 6514.9386 | 6514.9386
2017-05-19 09:00 | 5 | 9 | 6542.5064 | 6542.5064
2017-05-19 10:00 | 5 | 10 | 5153.4628 | 5153.4628
2017-05-19 11:00 | 5 | 11 | 4858.1807 | 4858.1807
2017-05-19 12:00 | 5 | 12 | 6325.1886 | 6325.1886
2017-05-19 13:00 | 5 | 13 | 4096.9152 | 4096.9152
2017-05-19 14:00 | 5 | 14 | 4494.9475 | 4494.9475
2017-05-19 15:00 | 5 | 15 | 1421.1424 | 1421.1424
2017-05-19 16:00 | 5 | 16 | 2733.6546 | 2733.6546
2017-05-19 17:00 | 5 | 17 | 1092.5552 | 1092.5552
2017-05-19 18:00 | 5 | 18 | 169.0477 | 169.0477
2017-05-19 19:00 | 5 | 19 | 0 | 0
2017-05-19 20:00 | 5 | 20 | 0 | 0
2017-05-19 21:00 | 5 | 21 | 0 | 0
2017-05-19 22:00 | 5 | 22 | 0 | 0
2017-05-19 23:00 | 5 | 23 | 0 | 0
2017-05-20 | 5 | 0 | 0 | 0
2017-05-20 01:00 | 5 | 1 | 0 | 0
2017-05-20 02:00 | 5 | 2 | 0 | 0
2017-05-20 03:00 | 5 | 3 | 0 | 0
2017-05-20 04:00 | 5 | 4 | 23.5336 | 23.5336
2017-05-20 05:00 | 5 | 5 | 648.8519 | 648.8519
2017-05-20 06:00 | 5 | 6 | 2066.32 | 2066.32
2017-05-20 07:00 | 5 | 7 | 3939.5297 | 3939.5297
2017-05-20 08:00 | 5 | 8 | 6391.0813 | 6391.0813
2017-05-20 09:00 | 5 | 9 | 7580.8184 | 7580.8184
2017-05-20 10:00 | 5 | 10 | 8269.4832 | 8269.4832
2017-05-20 11:00 | 5 | 11 | 7332.3954 | 7332.3954
2017-05-20 12:00 | 5 | 12 | 7322.7101 | 7322.7101
2017-05-20 13:00 | 5 | 13 | 2881.9966 | 2881.9966
2017-05-20 14:00 | 5 | 14 | 2071.9964 | 2071.9964
2017-05-20 15:00 | 5 | 15 | 1707.405 | 1707.405
2017-05-20 16:00 | 5 | 16 | 1546.6488 | 1546.6488
2017-05-20 17:00 | 5 | 17 | 863.7627 | 863.7627
2017-05-20 18:00 | 5 | 18 | 159.7672 | 159.7672
2017-05-20 19:00 | 5 | 19 | 0 | 0
2017-05-20 20:00 | 5 | 20 | 0 | 0
2017-05-20 21:00 | 5 | 21 | 0 | 0
2017-05-20 22:00 | 5 | 22 | 0 | 0
2017-05-20 23:00 | 5 | 23 | 0 | 0
2017-05-21 | 5 | 0 | 0 | 0
2017-05-21 01:00 | 5 | 1 | 0 | 0
2017-05-21 02:00 | 5 | 2 | 0 | 0
2017-05-21 03:00 | 5 | 3 | 0 | 0
2017-05-21 04:00 | 5 | 4 | 31.9895 | 31.9895
2017-05-21 05:00 | 5 | 5 | 731.5472 | 731.5472
2017-05-21 06:00 | 5 | 6 | 2451.1985 | 2451.1985
2017-05-21 07:00 | 5 | 7 | 4485.4945 | 4485.4945
2017-05-21 08:00 | 5 | 8 | 6185.9765 | 6185.9765
2017-05-21 09:00 | 5 | 9 | 6014.2596 | 6014.2596
2017-05-21 10:00 | 5 | 10 | 8237.1521 | 8237.1521
2017-05-21 11:00 | 5 | 11 | 8441.8751 | 8441.8751
2017-05-21 12:00 | 5 | 12 | 8286.9954 | 8286.9954
2017-05-21 13:00 | 5 | 13 | 5146.4179 | 5146.4179
2017-05-21 14:00 | 5 | 14 | 6645.1289 | 6645.129
2017-05-21 15:00 | 5 | 15 | 5047.4811 | 5047.4811
2017-05-21 16:00 | 5 | 16 | 2020.113 | 2020.113
2017-05-21 17:00 | 5 | 17 | 394.7478 | 394.7478
2017-05-21 18:00 | 5 | 18 | 40.0648 | 40.0648
2017-05-21 19:00 | 5 | 19 | 0 | 0
2017-05-21 20:00 | 5 | 20 | 0 | 0
2017-05-21 21:00 | 5 | 21 | 0 | 0
2017-05-21 22:00 | 5 | 22 | 0 | 0
2017-05-21 23:00 | 5 | 23 | 0 | 0
2017-05-22 | 5 | 0 | 0 | 0
2017-05-22 01:00 | 5 | 1 | 0 | 0
2017-05-22 02:00 | 5 | 2 | 0 | 0
2017-05-22 03:00 | 5 | 3 | 0 | 0
2017-05-22 04:00 | 5 | 4 | 0 | 0
2017-05-22 05:00 | 5 | 5 | 674.3485 | 674.3485
2017-05-22 06:00 | 5 | 6 | 1713.7047 | 1713.7047
2017-05-22 07:00 | 5 | 7 | 3120.847 | 3120.847
2017-05-22 08:00 | 5 | 8 | 3034.1979 | 3034.1979
2017-05-22 09:00 | 5 | 9 | 4204.1481 | 4204.1481
2017-05-22 10:00 | 5 | 10 | 5110.5954 | 5110.5954
2017-05-22 11:00 | 5 | 11 | 6155.3957 | 6155.3957
2017-05-22 12:00 | 5 | 12 | 3965.6381 | 3965.6381
2017-05-22 13:00 | 5 | 13 | 5022.2535 | 5022.2535
2017-05-22 14:00 | 5 | 14 | 1132.566 | 1132.566
2017-05-22 15:00 | 5 | 15 | 2889.6027 | 2889.6027
2017-05-22 16:00 | 5 | 16 | 1582.3747 | 1582.3747
2017-05-22 17:00 | 5 | 17 | 987.0197 | 987.0197
2017-05-22 18:00 | 5 | 18 | 222.4284 | 222.4284
2017-05-22 19:00 | 5 | 19 | 0 | 0
2017-05-22 20:00 | 5 | 20 | 0 | 0
2017-05-22 21:00 | 5 | 21 | 0 | 0
2017-05-22 22:00 | 5 | 22 | 0 | 0
2017-05-22 23:00 | 5 | 23 | 0 | 0
2017-05-23 | 5 | 0 | 0 | 0
2017-05-23 01:00 | 5 | 1 | 0 | 0
2017-05-23 02:00 | 5 | 2 | 0 | 0
2017-05-23 03:00 | 5 | 3 | 0 | 0
2017-05-23 04:00 | 5 | 4 | 39.7164 | 39.7164
2017-05-23 05:00 | 5 | 5 | 615.7514 | 615.7514
2017-05-23 06:00 | 5 | 6 | 2505.39 | 2505.39
2017-05-23 07:00 | 5 | 7 | 4593.177 | 4593.177
2017-05-23 08:00 | 5 | 8 | 6293.9615 | 6293.9615
2017-05-23 09:00 | 5 | 9 | 7530.1758 | 7530.1758
2017-05-23 10:00 | 5 | 10 | 8261.8127 | 8261.8127
2017-05-23 11:00 | 5 | 11 | 8514.0871 | 8514.0871
2017-05-23 12:00 | 5 | 12 | 4670.8273 | 4670.8273
2017-05-23 13:00 | 5 | 13 | 7829.0102 | 7829.0102
2017-05-23 14:00 | 5 | 14 | 2418.1418 | 2418.1418
2017-05-23 15:00 | 5 | 15 | 4619.2797 | 4619.2797
2017-05-23 16:00 | 5 | 16 | 1966.1768 | 1966.1768
2017-05-23 17:00 | 5 | 17 | 934.1611 | 934.1611
2017-05-23 18:00 | 5 | 18 | 220.6263 | 220.6263
2017-05-23 19:00 | 5 | 19 | 0 | 0
2017-05-23 20:00 | 5 | 20 | 0 | 0
2017-05-23 21:00 | 5 | 21 | 0 | 0
2017-05-23 22:00 | 5 | 22 | 0 | 0
2017-05-23 23:00 | 5 | 23 | 0 | 0
2017-05-24 | 5 | 0 | 0 | 0
2017-05-24 01:00 | 5 | 1 | 0 | 0
2017-05-24 02:00 | 5 | 2 | 0 | 0
2017-05-24 03:00 | 5 | 3 | 0 | 0
2017-05-24 04:00 | 5 | 4 | 32.9383 | 32.9383
2017-05-24 05:00 | 5 | 5 | 653.7888 | 653.7888
2017-05-24 06:00 | 5 | 6 | 2083.907 | 2083.907
2017-05-24 07:00 | 5 | 7 | 3686.5147 | 3686.5147
2017-05-24 08:00 | 5 | 8 | 6254.0611 | 6254.0611
2017-05-24 09:00 | 5 | 9 | 5712.3398 | 5712.3398
2017-05-24 10:00 | 5 | 10 | 2685.1361 | 2685.1361
2017-05-24 11:00 | 5 | 11 | 5325.8949 | 5325.8949
2017-05-24 12:00 | 5 | 12 | 5076.0333 | 5076.0333
2017-05-24 13:00 | 5 | 13 | 6871.6962 | 6871.6962
2017-05-24 14:00 | 5 | 14 | 4826.9295 | 4826.9295
2017-05-24 15:00 | 5 | 15 | 1660.7426 | 1660.7426
2017-05-24 16:00 | 5 | 16 | 2319.7409 | 2319.7409
2017-05-24 17:00 | 5 | 17 | 1200.6253 | 1200.6253
2017-05-24 18:00 | 5 | 18 | 212.735 | 212.735
2017-05-24 19:00 | 5 | 19 | 0 | 0
2017-05-24 20:00 | 5 | 20 | 0 | 0
2017-05-24 21:00 | 5 | 21 | 0 | 0
2017-05-24 22:00 | 5 | 22 | 0 | 0
2017-05-24 23:00 | 5 | 23 | 0 | 0
2017-05-25 | 5 | 0 | 0 | 0
2017-05-25 01:00 | 5 | 1 | 0 | 0
2017-05-25 02:00 | 5 | 2 | 0 | 0
2017-05-25 03:00 | 5 | 3 | 0 | 0
2017-05-25 04:00 | 5 | 4 | 47.0074 | 47.0074
2017-05-25 05:00 | 5 | 5 | 660.3507 | 660.3507
2017-05-25 06:00 | 5 | 6 | 2512.1094 | 2512.1094
2017-05-25 07:00 | 5 | 7 | 4634.1665 | 4634.1665
2017-05-25 08:00 | 5 | 8 | 6332.4681 | 6332.4681
2017-05-25 09:00 | 5 | 9 | 7519.7982 | 7519.7982
2017-05-25 10:00 | 5 | 10 | 8229.9635 | 8229.9635
2017-05-25 11:00 | 5 | 11 | 8477.5159 | 8477.5159
2017-05-25 12:00 | 5 | 12 | 8293.4469 | 8293.4469
2017-05-25 13:00 | 5 | 13 | 7675.7796 | 7675.7796
2017-05-25 14:00 | 5 | 14 | 6594.7003 | 6594.7003
2017-05-25 15:00 | 5 | 15 | 5085.2287 | 5085.2287
2017-05-25 16:00 | 5 | 16 | 3210.3457 | 3210.3457
2017-05-25 17:00 | 5 | 17 | 1184.0527 | 1184.0527
2017-05-25 18:00 | 5 | 18 | 190.509 | 190.509
2017-05-25 19:00 | 5 | 19 | 0 | 0
2017-05-25 20:00 | 5 | 20 | 0 | 0
2017-05-25 21:00 | 5 | 21 | 0 | 0
2017-05-25 22:00 | 5 | 22 | 0 | 0
2017-05-25 23:00 | 5 | 23 | 0 | 0
2017-05-26 | 5 | 0 | 0 | 0
2017-05-26 01:00 | 5 | 1 | 0 | 0
2017-05-26 02:00 | 5 | 2 | 0 | 0
2017-05-26 03:00 | 5 | 3 | 0 | 0
2017-05-26 04:00 | 5 | 4 | 46.5497 | 46.5497
2017-05-26 05:00 | 5 | 5 | 626.2946 | 626.2946
2017-05-26 06:00 | 5 | 6 | 2062.5204 | 2062.5204
2017-05-26 07:00 | 5 | 7 | 3971.4479 | 3971.448
2017-05-26 08:00 | 5 | 8 | 6209.9931 | 6209.9931
2017-05-26 09:00 | 5 | 9 | 7289.0484 | 7289.0484
2017-05-26 10:00 | 5 | 10 | 8017.5573 | 8017.5574
2017-05-26 11:00 | 5 | 11 | 8277.5217 | 8277.5217
2017-05-26 12:00 | 5 | 12 | 8098.1056 | 8098.1056
2017-05-26 13:00 | 5 | 13 | 7496.0657 | 7496.0657
2017-05-26 14:00 | 5 | 14 | 6469.9368 | 6469.9368
2017-05-26 15:00 | 5 | 15 | 4463.1063 | 4463.1063
2017-05-26 16:00 | 5 | 16 | 1533.4951 | 1533.4951
2017-05-26 17:00 | 5 | 17 | 1200.5574 | 1200.5574
2017-05-26 18:00 | 5 | 18 | 241.761 | 241.761
2017-05-26 19:00 | 5 | 19 | 0 | 0
2017-05-26 20:00 | 5 | 20 | 0 | 0
2017-05-26 21:00 | 5 | 21 | 0 | 0
2017-05-26 22:00 | 5 | 22 | 0 | 0
2017-05-26 23:00 | 5 | 23 | 0 | 0
2017-05-27 | 5 | 0 | 0 | 0
2017-05-27 01:00 | 5 | 1 | 0 | 0
2017-05-27 02:00 | 5 | 2 | 0 | 0
2017-05-27 03:00 | 5 | 3 | 0 | 0
2017-05-27 04:00 | 5 | 4 | 0 | 0
2017-05-27 05:00 | 5 | 5 | 409.538 | 409.538
2017-05-27 06:00 | 5 | 6 | 683.077 | 683.077
2017-05-27 07:00 | 5 | 7 | 2680.8167 | 2680.8167
2017-05-27 08:00 | 5 | 8 | 2228.4424 | 2228.4424
2017-05-27 09:00 | 5 | 9 | 7067.678 | 7067.678
2017-05-27 10:00 | 5 | 10 | 7567.7141 | 7567.7141
2017-05-27 11:00 | 5 | 11 | 7807.7329 | 7807.7329
2017-05-27 12:00 | 5 | 12 | 7601.9623 | 7601.9623
2017-05-27 13:00 | 5 | 13 | 6322.7287 | 6322.7287
2017-05-27 14:00 | 5 | 14 | 2371.8451 | 2371.8451
2017-05-27 15:00 | 5 | 15 | 3636.216 | 3636.216
2017-05-27 16:00 | 5 | 16 | 403.9306 | 403.9306
2017-05-27 17:00 | 5 | 17 | 122.6463 | 122.6464
2017-05-27 18:00 | 5 | 18 | 251.4337 | 251.4337
2017-05-27 19:00 | 5 | 19 | 0 | 0
2017-05-27 20:00 | 5 | 20 | 0 | 0
2017-05-27 21:00 | 5 | 21 | 0 | 0
2017-05-27 22:00 | 5 | 22 | 0 | 0
2017-05-27 23:00 | 5 | 23 | 0 | 0
2017-05-28 | 5 | 0 | 0 | 0
2017-05-28 01:00 | 5 | 1 | 0 | 0
2017-05-28 02:00 | 5 | 2 | 0 | 0
2017-05-28 03:00 | 5 | 3 | 0 | 0
2017-05-28 04:00 | 5 | 4 | 132.0016 | 132.0016
2017-05-28 05:00 | 5 | 5 | 701.669 | 701.669
2017-05-28 06:00 | 5 | 6 | 2649.2895 | 2649.2895
2017-05-28 07:00 | 5 | 7 | 4804.6896 | 4804.6896
2017-05-28 08:00 | 5 | 8 | 6547.3203 | 6547.3203
2017-05-28 09:00 | 5 | 9 | 7753.7554 | 7753.7554
2017-05-28 10:00 | 5 | 10 | 8463.9091 | 8463.9091
2017-05-28 11:00 | 5 | 11 | 8711.3017 | 8711.3017
2017-05-28 12:00 | 5 | 12 | 8502.7757 | 8502.7757
2017-05-28 13:00 | 5 | 13 | 7863.8759 | 7863.8759
2017-05-28 14:00 | 5 | 14 | 6783.9351 | 6783.9351
2017-05-28 15:00 | 5 | 15 | 5240.2222 | 5240.2222
2017-05-28 16:00 | 5 | 16 | 3320.2213 | 3320.2213
2017-05-28 17:00 | 5 | 17 | 1253.0388 | 1253.0388
2017-05-28 18:00 | 5 | 18 | 218.3171 | 218.3171
2017-05-28 19:00 | 5 | 19 | 0 | 0
2017-05-28 20:00 | 5 | 20 | 0 | 0
2017-05-28 21:00 | 5 | 21 | 0 | 0
2017-05-28 22:00 | 5 | 22 | 0 | 0
2017-05-28 23:00 | 5 | 23 | 0 | 0
2017-05-29 | 5 | 0 | 0 | 0
2017-05-29 01:00 | 5 | 1 | 0 | 0
2017-05-29 02:00 | 5 | 2 | 0 | 0
2017-05-29 03:00 | 5 | 3 | 0 | 0
2017-05-29 04:00 | 5 | 4 | 64.7197 | 64.7197
2017-05-29 05:00 | 5 | 5 | 682.379 | 682.379
2017-05-29 06:00 | 5 | 6 | 2562.76 | 2562.76
2017-05-29 07:00 | 5 | 7 | 4618.9566 | 4618.9566
2017-05-29 08:00 | 5 | 8 | 6283.2941 | 6283.2941
2017-05-29 09:00 | 5 | 9 | 7461.6278 | 7461.6278
2017-05-29 10:00 | 5 | 10 | 8155.601 | 8155.601
2017-05-29 11:00 | 5 | 11 | 8391.8893 | 8391.8893
2017-05-29 12:00 | 5 | 12 | 8192.5666 | 8192.5666
2017-05-29 13:00 | 5 | 13 | 7592.5196 | 7592.5196
2017-05-29 14:00 | 5 | 14 | 6521.9409 | 6521.9409
2017-05-29 15:00 | 5 | 15 | 5057.593 | 5057.593
2017-05-29 16:00 | 5 | 16 | 3194.2457 | 3194.2457
2017-05-29 17:00 | 5 | 17 | 1234.2329 | 1234.2329
2017-05-29 18:00 | 5 | 18 | 213.0915 | 213.0916
2017-05-29 19:00 | 5 | 19 | 0 | 0
2017-05-29 20:00 | 5 | 20 | 0 | 0
2017-05-29 21:00 | 5 | 21 | 0 | 0
2017-05-29 22:00 | 5 | 22 | 0 | 0
2017-05-29 23:00 | 5 | 23 | 0 | 0
2017-05-30 | 5 | 0 | 0 | 0
2017-05-30 01:00 | 5 | 1 | 0 | 0
2017-05-30 02:00 | 5 | 2 | 0 | 0
2017-05-30 03:00 | 5 | 3 | 0 | 0
2017-05-30 04:00 | 5 | 4 | 62.8601 | 62.8601
2017-05-30 05:00 | 5 | 5 | 710.723 | 710.723
2017-05-30 06:00 | 5 | 6 | 2483.1501 | 2483.1501
2017-05-30 07:00 | 5 | 7 | 4521.9012 | 4521.9012
2017-05-30 08:00 | 5 | 8 | 6166.8865 | 6166.8865
2017-05-30 09:00 | 5 | 9 | 7321.1162 | 7321.1162
2017-05-30 10:00 | 5 | 10 | 7974.5278 | 7974.5278
2017-05-30 11:00 | 5 | 11 | 7286.9095 | 7286.9095
2017-05-30 12:00 | 5 | 12 | 7141.3735 | 7141.3735
2017-05-30 13:00 | 5 | 13 | 7489.3117 | 7489.3117
2017-05-30 14:00 | 5 | 14 | 6123.091 | 6123.091
2017-05-30 15:00 | 5 | 15 | 4326.6668 | 4326.6668
2017-05-30 16:00 | 5 | 16 | 3014.8182 | 3014.8182
2017-05-30 17:00 | 5 | 17 | 1133.8528 | 1133.8528
2017-05-30 18:00 | 5 | 18 | 212.482 | 212.482
2017-05-30 19:00 | 5 | 19 | 0 | 0
2017-05-30 20:00 | 5 | 20 | 0 | 0
2017-05-30 21:00 | 5 | 21 | 0 | 0
2017-05-30 22:00 | 5 | 22 | 0 | 0
2017-05-30 23:00 | 5 | 23 | 0 | 0
2017-05-31 | 5 | 0 | 0 | 0
2017-05-31 01:00 | 5 | 1 | 0 | 0
2017-05-31 02:00 | 5 | 2 | 0 | 0
2017-05-31 03:00 | 5 | 3 | 0 | 0
2017-05-31 04:00 | 5 | 4 | 79.9928 | 79.9928
2017-05-31 05:00 | 5 | 5 | 667.9464 | 667.9464
2017-05-31 06:00 | 5 | 6 | 2219.331 | 2219.331
2017-05-31 07:00 | 5 | 7 | 4148.027 | 4148.027
2017-05-31 08:00 | 5 | 8 | 4521.7425 | 4521.7425
2017-05-31 09:00 | 5 | 9 | 4869.9567 | 4869.9567
2017-05-31 10:00 | 5 | 10 | 6479.8291 | 6479.8291
2017-05-31 11:00 | 5 | 11 | 5645.7778 | 5645.7778
2017-05-31 12:00 | 5 | 12 | 2610.1285 | 2610.1285
2017-05-31 13:00 | 5 | 13 | 1766.5127 | 1766.5127
2017-05-31 14:00 | 5 | 14 | 1632.0788 | 1632.0788
2017-05-31 15:00 | 5 | 15 | 2528.1784 | 2528.1784
2017-05-31 16:00 | 5 | 16 | 2529.8436 | 2529.8436
2017-05-31 17:00 | 5 | 17 | 760.3478 | 760.3478
2017-05-31 18:00 | 5 | 18 | 296.7287 | 296.7287
2017-05-31 19:00 | 5 | 19 | 0 | 0
2017-05-31 20:00 | 5 | 20 | 0 | 0
2017-05-31 21:00 | 5 | 21 | 0 | 0
2017-05-31 22:00 | 5 | 22 | 0 | 0
2017-05-31 23:00 | 5 | 23 | 0 | 0
2017-06-01 | 6 | 0 | 0 | 0
2017-06-01 01:00 | 6 | 1 | 0 | 0
2017-06-01 02:00 | 6 | 2 | 0 | 0
2017-06-01 03:00 | 6 | 3 | 0 | 0
2017-06-01 04:00 | 6 | 4 | 11.5908 | 11.5908
2017-06-01 05:00 | 6 | 5 | 31.6491 | 31.6491
2017-06-01 06:00 | 6 | 6 | 111.8984 | 111.8984
2017-06-01 07:00 | 6 | 7 | 968.5196 | 968.5196
2017-06-01 08:00 | 6 | 8 | 1873.3477 | 1873.3477
2017-06-01 09:00 | 6 | 9 | 3188.7867 | 3188.7867
2017-06-01 10:00 | 6 | 10 | 4958.0398 | 4958.0398
2017-06-01 11:00 | 6 | 11 | 6745.9195 | 6745.9196
2017-06-01 12:00 | 6 | 12 | 3110.4245 | 3110.4245
2017-06-01 13:00 | 6 | 13 | 2591.9068 | 2591.9068
2017-06-01 14:00 | 6 | 14 | 1250.8147 | 1250.8147
2017-06-01 15:00 | 6 | 15 | 1188.2409 | 1188.2409
2017-06-01 16:00 | 6 | 16 | 287.0515 | 287.0515
2017-06-01 17:00 | 6 | 17 | 814.9693 | 814.9693
2017-06-01 18:00 | 6 | 18 | 247.2948 | 247.2948
2017-06-01 19:00 | 6 | 19 | 0 | 0
2017-06-01 20:00 | 6 | 20 | 0 | 0
2017-06-01 21:00 | 6 | 21 | 0 | 0
2017-06-01 22:00 | 6 | 22 | 0 | 0
2017-06-01 23:00 | 6 | 23 | 0 | 0
2017-06-02 | 6 | 0 | 0 | 0
2017-06-02 01:00 | 6 | 1 | 0 | 0
2017-06-02 02:00 | 6 | 2 | 0 | 0
2017-06-02 03:00 | 6 | 3 | 0 | 0
2017-06-02 04:00 | 6 | 4 | 0 | 0
2017-06-02 05:00 | 6 | 5 | 81.167 | 81.167
2017-06-02 06:00 | 6 | 6 | 1209.4079 | 1209.4079
2017-06-02 07:00 | 6 | 7 | 1244.9705 | 1244.9705
2017-06-02 08:00 | 6 | 8 | 1349.1869 | 1349.1869
2017-06-02 09:00 | 6 | 9 | 5333.4585 | 5333.4585
2017-06-02 10:00 | 6 | 10 | 7791.5467 | 7791.5467
2017-06-02 11:00 | 6 | 11 | 8004.5244 | 8004.5244
2017-06-02 12:00 | 6 | 12 | 2860.3133 | 2860.3133
2017-06-02 13:00 | 6 | 13 | 875.5778 | 875.5778
2017-06-02 14:00 | 6 | 14 | 2724.6812 | 2724.6812
2017-06-02 15:00 | 6 | 15 | 4493.8239 | 4493.8239
2017-06-02 16:00 | 6 | 16 | 16.1138 | 16.1138
2017-06-02 17:00 | 6 | 17 | 220.9817 | 220.9817
2017-06-02 18:00 | 6 | 18 | 305.9322 | 305.9322
2017-06-02 19:00 | 6 | 19 | 0 | 0
2017-06-02 20:00 | 6 | 20 | 0 | 0
2017-06-02 21:00 | 6 | 21 | 0 | 0
2017-06-02 22:00 | 6 | 22 | 0 | 0
2017-06-02 23:00 | 6 | 23 | 0 | 0
2017-06-03 | 6 | 0 | 0 | 0
2017-06-03 01:00 | 6 | 1 | 0 | 0
2017-06-03 02:00 | 6 | 2 | 0 | 0
2017-06-03 03:00 | 6 | 3 | 0 | 0
2017-06-03 04:00 | 6 | 4 | 0 | 0
2017-06-03 05:00 | 6 | 5 | 337.7297 | 337.7297
2017-06-03 06:00 | 6 | 6 | 188.0284 | 188.0284
2017-06-03 07:00 | 6 | 7 | 2761.9182 | 2761.9182
2017-06-03 08:00 | 6 | 8 | 6213.5247 | 6213.5247
2017-06-03 09:00 | 6 | 9 | 7335.0841 | 7335.0841
2017-06-03 10:00 | 6 | 10 | 8048.3049 | 8048.3049
2017-06-03 11:00 | 6 | 11 | 8288.533 | 8288.533
2017-06-03 12:00 | 6 | 12 | 8128.392 | 8128.392
2017-06-03 13:00 | 6 | 13 | 7496.0737 | 7496.0737
2017-06-03 14:00 | 6 | 14 | 577.7496 | 577.7496
2017-06-03 15:00 | 6 | 15 | 708.6277 | 708.6277
2017-06-03 16:00 | 6 | 16 | 3255.6983 | 3255.6983
2017-06-03 17:00 | 6 | 17 | 1208.282 | 1208.282
2017-06-03 18:00 | 6 | 18 | 299.5761 | 299.5761
2017-06-03 19:00 | 6 | 19 | 0 | 0
2017-06-03 20:00 | 6 | 20 | 0 | 0
2017-06-03 21:00 | 6 | 21 | 0 | 0
2017-06-03 22:00 | 6 | 22 | 0 | 0
2017-06-03 23:00 | 6 | 23 | 0 | 0
2017-06-04 | 6 | 0 | 0 | 0
2017-06-04 01:00 | 6 | 1 | 0 | 0
2017-06-04 02:00 | 6 | 2 | 0 | 0
2017-06-04 03:00 | 6 | 3 | 0 | 0
2017-06-04 04:00 | 6 | 4 | 80.0986 | 80.0986
2017-06-04 05:00 | 6 | 5 | 714.3708 | 714.3708
2017-06-04 06:00 | 6 | 6 | 2563.5489 | 2563.5489
2017-06-04 07:00 | 6 | 7 | 4599.1524 | 4599.1524
2017-06-04 08:00 | 6 | 8 | 6269.4297 | 6269.4297
2017-06-04 09:00 | 6 | 9 | 7471.3637 | 7471.3637
2017-06-04 10:00 | 6 | 10 | 8227.0494 | 8227.0494
2017-06-04 11:00 | 6 | 11 | 8473.1402 | 8473.1402
2017-06-04 12:00 | 6 | 12 | 8275.0251 | 8275.0251
2017-06-04 13:00 | 6 | 13 | 7685.8099 | 7685.8099
2017-06-04 14:00 | 6 | 14 | 6648.4421 | 6648.4421
2017-06-04 15:00 | 6 | 15 | 5184.5312 | 5184.5312
2017-06-04 16:00 | 6 | 16 | 3313.1937 | 3313.1937
2017-06-04 17:00 | 6 | 17 | 1234.0995 | 1234.0995
2017-06-04 18:00 | 6 | 18 | 229.2146 | 229.2146
2017-06-04 19:00 | 6 | 19 | 0 | 0
2017-06-04 20:00 | 6 | 20 | 0 | 0
2017-06-04 21:00 | 6 | 21 | 0 | 0
2017-06-04 22:00 | 6 | 22 | 0 | 0
2017-06-04 23:00 | 6 | 23 | 0 | 0
2017-06-05 | 6 | 0 | 0 | 0
2017-06-05 01:00 | 6 | 1 | 0 | 0
2017-06-05 02:00 | 6 | 2 | 0 | 0
2017-06-05 03:00 | 6 | 3 | 0 | 0
2017-06-05 04:00 | 6 | 4 | 31.2535 | 31.2535
2017-06-05 05:00 | 6 | 5 | 581.4952 | 581.4952
2017-06-05 06:00 | 6 | 6 | 1355.8212 | 1355.8212
2017-06-05 07:00 | 6 | 7 | 4070.111 | 4070.111
2017-06-05 08:00 | 6 | 8 | 5367.05 | 5367.05
2017-06-05 09:00 | 6 | 9 | 6113.3333 | 6113.3333
2017-06-05 10:00 | 6 | 10 | 7080.6512 | 7080.6512
2017-06-05 11:00 | 6 | 11 | 8489.515 | 8489.515
2017-06-05 12:00 | 6 | 12 | 8347.8178 | 8347.8178
2017-06-05 13:00 | 6 | 13 | 7733.0887 | 7733.0887
2017-06-05 14:00 | 6 | 14 | 6745.4653 | 6745.4653
2017-06-05 15:00 | 6 | 15 | 3953.7471 | 3953.7472
2017-06-05 16:00 | 6 | 16 | 3360.4736 | 3360.4736
2017-06-05 17:00 | 6 | 17 | 633.2222 | 633.2222
2017-06-05 18:00 | 6 | 18 | 139.1788 | 139.1788
2017-06-05 19:00 | 6 | 19 | 0 | 0
2017-06-05 20:00 | 6 | 20 | 0 | 0
2017-06-05 21:00 | 6 | 21 | 0 | 0
2017-06-05 22:00 | 6 | 22 | 0 | 0
2017-06-05 23:00 | 6 | 23 | 0 | 0
2017-06-06 | 6 | 0 | 0 | 0
2017-06-06 01:00 | 6 | 1 | 0 | 0
2017-06-06 02:00 | 6 | 2 | 0 | 0
2017-06-06 03:00 | 6 | 3 | 0 | 0
2017-06-06 04:00 | 6 | 4 | 0 | 0
2017-06-06 05:00 | 6 | 5 | 731.1228 | 731.1228
2017-06-06 06:00 | 6 | 6 | 948.658 | 948.658
2017-06-06 07:00 | 6 | 7 | 1612.7991 | 1612.7991
2017-06-06 08:00 | 6 | 8 | 1875.4533 | 1875.4533
2017-06-06 09:00 | 6 | 9 | 1693.9696 | 1693.9696
2017-06-06 10:00 | 6 | 10 | 3464.5624 | 3464.5624
2017-06-06 11:00 | 6 | 11 | 3311.2375 | 3311.2375
2017-06-06 12:00 | 6 | 12 | 2159.8645 | 2159.8645
2017-06-06 13:00 | 6 | 13 | 406.0765 | 406.0765
2017-06-06 14:00 | 6 | 14 | 1434.9171 | 1434.9171
2017-06-06 15:00 | 6 | 15 | 917.1307 | 917.1307
2017-06-06 16:00 | 6 | 16 | 635.8499 | 635.8499
2017-06-06 17:00 | 6 | 17 | 227.8897 | 227.8897
2017-06-06 18:00 | 6 | 18 | 230.2208 | 230.2208
2017-06-06 19:00 | 6 | 19 | 0 | 0
2017-06-06 20:00 | 6 | 20 | 0 | 0
2017-06-06 21:00 | 6 | 21 | 0 | 0
2017-06-06 22:00 | 6 | 22 | 0 | 0
2017-06-06 23:00 | 6 | 23 | 0 | 0
2017-06-07 | 6 | 0 | 0 | 0
2017-06-07 01:00 | 6 | 1 | 0 | 0
2017-06-07 02:00 | 6 | 2 | 0 | 0
2017-06-07 03:00 | 6 | 3 | 0 | 0
2017-06-07 04:00 | 6 | 4 | 103.6794 | 103.6794
2017-06-07 05:00 | 6 | 5 | 605.1932 | 605.1932
2017-06-07 06:00 | 6 | 6 | 473.0916 | 473.0916
2017-06-07 07:00 | 6 | 7 | 1469.7816 | 1469.7816
2017-06-07 08:00 | 6 | 8 | 1963.6031 | 1963.6031
2017-06-07 09:00 | 6 | 9 | 4116.9137 | 4116.9137
2017-06-07 10:00 | 6 | 10 | 6191.8576 | 6191.8576
2017-06-07 11:00 | 6 | 11 | 6027.2075 | 6027.2075
2017-06-07 12:00 | 6 | 12 | 7385.3517 | 7385.3517
2017-06-07 13:00 | 6 | 13 | 7336.6849 | 7336.6849
2017-06-07 14:00 | 6 | 14 | 6303.6445 | 6303.6445
2017-06-07 15:00 | 6 | 15 | 4894.5702 | 4894.5702
2017-06-07 16:00 | 6 | 16 | 2709.8818 | 2709.8818
2017-06-07 17:00 | 6 | 17 | 1424.3371 | 1424.3371
2017-06-07 18:00 | 6 | 18 | 348.7364 | 348.7364
2017-06-07 19:00 | 6 | 19 | 0 | 0
2017-06-07 20:00 | 6 | 20 | 0 | 0
2017-06-07 21:00 | 6 | 21 | 0 | 0
2017-06-07 22:00 | 6 | 22 | 0 | 0
2017-06-07 23:00 | 6 | 23 | 0 | 0
2017-06-08 | 6 | 0 | 0 | 0
2017-06-08 01:00 | 6 | 1 | 0 | 0
2017-06-08 02:00 | 6 | 2 | 0 | 0
2017-06-08 03:00 | 6 | 3 | 0 | 0
2017-06-08 04:00 | 6 | 4 | 57.0676 | 57.0676
2017-06-08 05:00 | 6 | 5 | 713.6336 | 713.6336
2017-06-08 06:00 | 6 | 6 | 1970.2582 | 1970.2582
2017-06-08 07:00 | 6 | 7 | 3906.7915 | 3906.7915
2017-06-08 08:00 | 6 | 8 | 5356.7391 | 5356.7391
2017-06-08 09:00 | 6 | 9 | 5894.5343 | 5894.5343
2017-06-08 10:00 | 6 | 10 | 6753.2784 | 6753.2784
2017-06-08 11:00 | 6 | 11 | 7573.0869 | 7573.0869
2017-06-08 12:00 | 6 | 12 | 7401.6323 | 7401.6323
2017-06-08 13:00 | 6 | 13 | 4254.594 | 4254.594
2017-06-08 14:00 | 6 | 14 | 3254.8691 | 3254.8691
2017-06-08 15:00 | 6 | 15 | 4685.5094 | 4685.5094
2017-06-08 16:00 | 6 | 16 | 2534.1078 | 2534.1078
2017-06-08 17:00 | 6 | 17 | 1255.5309 | 1255.5309
2017-06-08 18:00 | 6 | 18 | 326.0951 | 326.0951
2017-06-08 19:00 | 6 | 19 | 0 | 0
2017-06-08 20:00 | 6 | 20 | 0 | 0
2017-06-08 21:00 | 6 | 21 | 0 | 0
2017-06-08 22:00 | 6 | 22 | 0 | 0
2017-06-08 23:00 | 6 | 23 | 0 | 0
2017-06-09 | 6 | 0 | 0 | 0
2017-06-09 01:00 | 6 | 1 | 0 | 0
2017-06-09 02:00 | 6 | 2 | 0 | 0
2017-06-09 03:00 | 6 | 3 | 0 | 0
2017-06-09 04:00 | 6 | 4 | 80.5195 | 80.5195
2017-06-09 05:00 | 6 | 5 | 776.2316 | 776.2316
2017-06-09 06:00 | 6 | 6 | 2331.8492 | 2331.8492
2017-06-09 07:00 | 6 | 7 | 4089.431 | 4089.4311
2017-06-09 08:00 | 6 | 8 | 5582.8475 | 5582.8475
2017-06-09 09:00 | 6 | 9 | 6711.952 | 6711.952
2017-06-09 10:00 | 6 | 10 | 7325.0296 | 7325.0296
2017-06-09 11:00 | 6 | 11 | 6433.5278 | 6433.5278
2017-06-09 12:00 | 6 | 12 | 6057.4306 | 6057.4306
2017-06-09 13:00 | 6 | 13 | 5937.5845 | 5937.5845
2017-06-09 14:00 | 6 | 14 | 5475.9274 | 5475.9274
2017-06-09 15:00 | 6 | 15 | 3906.6213 | 3906.6213
2017-06-09 16:00 | 6 | 16 | 2521.5429 | 2521.5429
2017-06-09 17:00 | 6 | 17 | 1208.1118 | 1208.1118
2017-06-09 18:00 | 6 | 18 | 303.2722 | 303.2722
2017-06-09 19:00 | 6 | 19 | 0 | 0
2017-06-09 20:00 | 6 | 20 | 0 | 0
2017-06-09 21:00 | 6 | 21 | 0 | 0
2017-06-09 22:00 | 6 | 22 | 0 | 0
2017-06-09 23:00 | 6 | 23 | 0 | 0
2017-06-10 | 6 | 0 | 0 | 0
2017-06-10 01:00 | 6 | 1 | 0 | 0
2017-06-10 02:00 | 6 | 2 | 0 | 0
2017-06-10 03:00 | 6 | 3 | 0 | 0
2017-06-10 04:00 | 6 | 4 | 0 | 0
2017-06-10 05:00 | 6 | 5 | 0 | 0
2017-06-10 06:00 | 6 | 6 | 529.8556 | 529.8556
2017-06-10 07:00 | 6 | 7 | 1438.6212 | 1438.6212
2017-06-10 08:00 | 6 | 8 | 2159.8449 | 2159.8449
2017-06-10 09:00 | 6 | 9 | 3354.4442 | 3354.4442
2017-06-10 10:00 | 6 | 10 | 2746.5554 | 2746.5554
2017-06-10 11:00 | 6 | 11 | 1738.6781 | 1738.6781
2017-06-10 12:00 | 6 | 12 | 1936.0526 | 1936.0526
2017-06-10 13:00 | 6 | 13 | 4036.4229 | 4036.4229
2017-06-10 14:00 | 6 | 14 | 4965.6046 | 4965.6046
2017-06-10 15:00 | 6 | 15 | 4999.3593 | 4999.3593
2017-06-10 16:00 | 6 | 16 | 3224.0974 | 3224.0974
2017-06-10 17:00 | 6 | 17 | 892.3436 | 892.3437
2017-06-10 18:00 | 6 | 18 | 323.4076 | 323.4076
2017-06-10 19:00 | 6 | 19 | 0 | 0
2017-06-10 20:00 | 6 | 20 | 0 | 0
2017-06-10 21:00 | 6 | 21 | 0 | 0
2017-06-10 22:00 | 6 | 22 | 0 | 0
2017-06-10 23:00 | 6 | 23 | 0 | 0
2017-06-11 | 6 | 0 | 0 | 0
2017-06-11 01:00 | 6 | 1 | 0 | 0
2017-06-11 02:00 | 6 | 2 | 0 | 0
2017-06-11 03:00 | 6 | 3 | 0 | 0
2017-06-11 04:00 | 6 | 4 | 132.0533 | 132.0533
2017-06-11 05:00 | 6 | 5 | 713.4692 | 713.4692
2017-06-11 06:00 | 6 | 6 | 2586.8629 | 2586.8629
2017-06-11 07:00 | 6 | 7 | 4650.4148 | 4650.4148
2017-06-11 08:00 | 6 | 8 | 6328.3936 | 6328.3936
2017-06-11 09:00 | 6 | 9 | 6175.5184 | 6175.5184
2017-06-11 10:00 | 6 | 10 | 7371.2849 | 7371.2849
2017-06-11 11:00 | 6 | 11 | 8547.3049 | 8547.3049
2017-06-11 12:00 | 6 | 12 | 7475.33 | 7475.33
2017-06-11 13:00 | 6 | 13 | 7796.6722 | 7796.6723
2017-06-11 14:00 | 6 | 14 | 6791.3215 | 6791.3215
2017-06-11 15:00 | 6 | 15 | 5322.7922 | 5322.7922
2017-06-11 16:00 | 6 | 16 | 3440.7597 | 3440.7597
2017-06-11 17:00 | 6 | 17 | 1396.6577 | 1396.6577
2017-06-11 18:00 | 6 | 18 | 211.0537 | 211.0537
2017-06-11 19:00 | 6 | 19 | 0 | 0
2017-06-11 20:00 | 6 | 20 | 0 | 0
2017-06-11 21:00 | 6 | 21 | 0 | 0
2017-06-11 22:00 | 6 | 22 | 0 | 0
2017-06-11 23:00 | 6 | 23 | 0 | 0
2017-06-12 | 6 | 0 | 0 | 0
2017-06-12 01:00 | 6 | 1 | 0 | 0
2017-06-12 02:00 | 6 | 2 | 0 | 0
2017-06-12 03:00 | 6 | 3 | 0 | 0
2017-06-12 04:00 | 6 | 4 | 76.1277 | 76.1277
2017-06-12 05:00 | 6 | 5 | 650.8413 | 650.8413
2017-06-12 06:00 | 6 | 6 | 2551.4624 | 2551.4624
2017-06-12 07:00 | 6 | 7 | 4600.6244 | 4600.6244
2017-06-12 08:00 | 6 | 8 | 6267.3953 | 6267.3953
2017-06-12 09:00 | 6 | 9 | 7495.4746 | 7495.4746
2017-06-12 10:00 | 6 | 10 | 8215.6989 | 8215.6989
2017-06-12 11:00 | 6 | 11 | 8472.2581 | 8472.2581
2017-06-12 12:00 | 6 | 12 | 8344.1838 | 8344.1838
2017-06-12 13:00 | 6 | 13 | 7722.6099 | 7722.61
2017-06-12 14:00 | 6 | 14 | 6708.5146 | 6708.5146
2017-06-12 15:00 | 6 | 15 | 5253.7716 | 5253.7716
2017-06-12 16:00 | 6 | 16 | 3383.7255 | 3383.7255
2017-06-12 17:00 | 6 | 17 | 1372.548 | 1372.548
2017-06-12 18:00 | 6 | 18 | 209.0965 | 209.0965
2017-06-12 19:00 | 6 | 19 | 0 | 0
2017-06-12 20:00 | 6 | 20 | 0 | 0
2017-06-12 21:00 | 6 | 21 | 0 | 0
2017-06-12 22:00 | 6 | 22 | 0 | 0
2017-06-12 23:00 | 6 | 23 | 0 | 0
2017-06-13 | 6 | 0 | 0 | 0
2017-06-13 01:00 | 6 | 1 | 0 | 0
2017-06-13 02:00 | 6 | 2 | 0 | 0
2017-06-13 03:00 | 6 | 3 | 0 | 0
2017-06-13 04:00 | 6 | 4 | 157.9893 | 157.9893
2017-06-13 05:00 | 6 | 5 | 599.1442 | 599.1442
2017-06-13 06:00 | 6 | 6 | 2316.0034 | 2316.0034
2017-06-13 07:00 | 6 | 7 | 4534.1176 | 4534.1176
2017-06-13 08:00 | 6 | 8 | 6137.5166 | 6137.5166
2017-06-13 09:00 | 6 | 9 | 7267.8539 | 7267.8539
2017-06-13 10:00 | 6 | 10 | 7970.2463 | 7970.2463
2017-06-13 11:00 | 6 | 11 | 8220.9314 | 8220.9314
2017-06-13 12:00 | 6 | 12 | 6853.54 | 6853.54
2017-06-13 13:00 | 6 | 13 | 6797.7914 | 6797.7914
2017-06-13 14:00 | 6 | 14 | 5515.5507 | 5515.5507
2017-06-13 15:00 | 6 | 15 | 5242.1635 | 5242.1635
2017-06-13 16:00 | 6 | 16 | 3406.0608 | 3406.0608
2017-06-13 17:00 | 6 | 17 | 1336.9681 | 1336.9681
2017-06-13 18:00 | 6 | 18 | 246.1299 | 246.1299
2017-06-13 19:00 | 6 | 19 | 0 | 0
2017-06-13 20:00 | 6 | 20 | 0 | 0
2017-06-13 21:00 | 6 | 21 | 0 | 0
2017-06-13 22:00 | 6 | 22 | 0 | 0
2017-06-13 23:00 | 6 | 23 | 0 | 0
2017-06-14 | 6 | 0 | 0 | 0
2017-06-14 01:00 | 6 | 1 | 0 | 0
2017-06-14 02:00 | 6 | 2 | 0 | 0
2017-06-14 03:00 | 6 | 3 | 0 | 0
2017-06-14 04:00 | 6 | 4 | 137.7366 | 137.7366
2017-06-14 05:00 | 6 | 5 | 724.9657 | 724.9657
2017-06-14 06:00 | 6 | 6 | 1208.1808 | 1208.1808
2017-06-14 07:00 | 6 | 7 | 2023.847 | 2023.847
2017-06-14 08:00 | 6 | 8 | 1609.4825 | 1609.4825
2017-06-14 09:00 | 6 | 9 | 4725.3293 | 4725.3293
2017-06-14 10:00 | 6 | 10 | 3909.4652 | 3909.4652
2017-06-14 11:00 | 6 | 11 | 2292.8424 | 2292.8424
2017-06-14 12:00 | 6 | 12 | 1025.5677 | 1025.5677
2017-06-14 13:00 | 6 | 13 | 1507.0474 | 1507.0474
2017-06-14 14:00 | 6 | 14 | 1652.8731 | 1652.8731
2017-06-14 15:00 | 6 | 15 | 3463.1341 | 3463.1341
2017-06-14 16:00 | 6 | 16 | 1669.9943 | 1669.9944
2017-06-14 17:00 | 6 | 17 | 1105.265 | 1105.265
2017-06-14 18:00 | 6 | 18 | 360.4261 | 360.4261
2017-06-14 19:00 | 6 | 19 | 0 | 0
2017-06-14 20:00 | 6 | 20 | 0 | 0
2017-06-14 21:00 | 6 | 21 | 0 | 0
2017-06-14 22:00 | 6 | 22 | 0 | 0
2017-06-14 23:00 | 6 | 23 | 0 | 0
2017-06-15 | 6 | 0 | 0 | 0
2017-06-15 01:00 | 6 | 1 | 0 | 0
2017-06-15 02:00 | 6 | 2 | 0 | 0
2017-06-15 03:00 | 6 | 3 | 0 | 0
2017-06-15 04:00 | 6 | 4 | 0 | 0
2017-06-15 05:00 | 6 | 5 | 607.1402 | 607.1402
2017-06-15 06:00 | 6 | 6 | 1595.9332 | 1595.9332
2017-06-15 07:00 | 6 | 7 | 4172.2632 | 4172.2632
2017-06-15 08:00 | 6 | 8 | 5769.1889 | 5769.1889
2017-06-15 09:00 | 6 | 9 | 2373.47 | 2373.47
2017-06-15 10:00 | 6 | 10 | 7726.1933 | 7726.1933
2017-06-15 11:00 | 6 | 11 | 7878.3188 | 7878.3188
2017-06-15 12:00 | 6 | 12 | 6669.0374 | 6669.0374
2017-06-15 13:00 | 6 | 13 | 6184.079 | 6184.079
2017-06-15 14:00 | 6 | 14 | 5345.4438 | 5345.4438
2017-06-15 15:00 | 6 | 15 | 4883.4635 | 4883.4635
2017-06-15 16:00 | 6 | 16 | 3155.0503 | 3155.0503
2017-06-15 17:00 | 6 | 17 | 1330.3004 | 1330.3004
2017-06-15 18:00 | 6 | 18 | 254.219 | 254.219
2017-06-15 19:00 | 6 | 19 | 0 | 0
2017-06-15 20:00 | 6 | 20 | 0 | 0
2017-06-15 21:00 | 6 | 21 | 0 | 0
2017-06-15 22:00 | 6 | 22 | 0 | 0
2017-06-15 23:00 | 6 | 23 | 0 | 0
2017-06-16 | 6 | 0 | 0 | 0
2017-06-16 01:00 | 6 | 1 | 0 | 0
2017-06-16 02:00 | 6 | 2 | 0 | 0
2017-06-16 03:00 | 6 | 3 | 0 | 0
2017-06-16 04:00 | 6 | 4 | 83.843 | 83.843
2017-06-16 05:00 | 6 | 5 | 696.655 | 696.655
2017-06-16 06:00 | 6 | 6 | 2171.1218 | 2171.1218
2017-06-16 07:00 | 6 | 7 | 3838.9863 | 3838.9864
2017-06-16 08:00 | 6 | 8 | 5299.783 | 5299.783
2017-06-16 09:00 | 6 | 9 | 6222.7638 | 6222.7638
2017-06-16 10:00 | 6 | 10 | 7746.3954 | 7746.3954
2017-06-16 11:00 | 6 | 11 | 7966.533 | 7966.533
2017-06-16 12:00 | 6 | 12 | 7821.7112 | 7821.7112
2017-06-16 13:00 | 6 | 13 | 7261.7233 | 7261.7233
2017-06-16 14:00 | 6 | 14 | 6328.849 | 6328.849
2017-06-16 15:00 | 6 | 15 | 4945.8728 | 4945.8728
2017-06-16 16:00 | 6 | 16 | 3190.1713 | 3190.1713
2017-06-16 17:00 | 6 | 17 | 1365.6641 | 1365.6641
2017-06-16 18:00 | 6 | 18 | 266.2227 | 266.2227
2017-06-16 19:00 | 6 | 19 | 0 | 0
2017-06-16 20:00 | 6 | 20 | 0 | 0
2017-06-16 21:00 | 6 | 21 | 0 | 0
2017-06-16 22:00 | 6 | 22 | 0 | 0
2017-06-16 23:00 | 6 | 23 | 0 | 0
2017-06-17 | 6 | 0 | 0 | 0
2017-06-17 01:00 | 6 | 1 | 0 | 0
2017-06-17 02:00 | 6 | 2 | 0 | 0
2017-06-17 03:00 | 6 | 3 | 0 | 0
2017-06-17 04:00 | 6 | 4 | 38.5227 | 38.5227
2017-06-17 05:00 | 6 | 5 | 278.7174 | 278.7174
2017-06-17 06:00 | 6 | 6 | 896.6791 | 896.6791
2017-06-17 07:00 | 6 | 7 | 3108.6535 | 3108.6535
2017-06-17 08:00 | 6 | 8 | 1978.782 | 1978.782
2017-06-17 09:00 | 6 | 9 | 1168.8588 | 1168.8588
2017-06-17 10:00 | 6 | 10 | 6002.2422 | 6002.2422
2017-06-17 11:00 | 6 | 11 | 4605.1462 | 4605.1462
2017-06-17 12:00 | 6 | 12 | 4528.7552 | 4528.7552
2017-06-17 13:00 | 6 | 13 | 5374.9194 | 5374.9194
2017-06-17 14:00 | 6 | 14 | 2765.3797 | 2765.3797
2017-06-17 15:00 | 6 | 15 | 975.0689 | 975.0689
2017-06-17 16:00 | 6 | 16 | 783.2604 | 783.2604
2017-06-17 17:00 | 6 | 17 | 1143.6359 | 1143.6359
2017-06-17 18:00 | 6 | 18 | 299.8625 | 299.8625
2017-06-17 19:00 | 6 | 19 | 0 | 0
2017-06-17 20:00 | 6 | 20 | 0 | 0
2017-06-17 21:00 | 6 | 21 | 0 | 0
2017-06-17 22:00 | 6 | 22 | 0 | 0
2017-06-17 23:00 | 6 | 23 | 0 | 0
2017-06-18 | 6 | 0 | 0 | 0
2017-06-18 01:00 | 6 | 1 | 0 | 0
2017-06-18 02:00 | 6 | 2 | 0 | 0
2017-06-18 03:00 | 6 | 3 | 0 | 0
2017-06-18 04:00 | 6 | 4 | 29.3641 | 29.3641
2017-06-18 05:00 | 6 | 5 | 537.3007 | 537.3007
2017-06-18 06:00 | 6 | 6 | 493.7962 | 493.7962
2017-06-18 07:00 | 6 | 7 | 1091.8813 | 1091.8813
2017-06-18 08:00 | 6 | 8 | 938.7461 | 938.7461
2017-06-18 09:00 | 6 | 9 | 1254.5867 | 1254.5867
2017-06-18 10:00 | 6 | 10 | 1730.5878 | 1730.5878
2017-06-18 11:00 | 6 | 11 | 2673.7143 | 2673.7143
2017-06-18 12:00 | 6 | 12 | 2433.9175 | 2433.9175
2017-06-18 13:00 | 6 | 13 | 2530.8935 | 2530.8935
2017-06-18 14:00 | 6 | 14 | 972.3675 | 972.3675
2017-06-18 15:00 | 6 | 15 | 1368.9726 | 1368.9726
2017-06-18 16:00 | 6 | 16 | 1403.1023 | 1403.1023
2017-06-18 17:00 | 6 | 17 | 1482.9549 | 1482.9549
2017-06-18 18:00 | 6 | 18 | 370.5116 | 370.5116
2017-06-18 19:00 | 6 | 19 | 0 | 0
2017-06-18 20:00 | 6 | 20 | 0 | 0
2017-06-18 21:00 | 6 | 21 | 0 | 0
2017-06-18 22:00 | 6 | 22 | 0 | 0
2017-06-18 23:00 | 6 | 23 | 0 | 0
2017-06-19 | 6 | 0 | 0 | 0
2017-06-19 01:00 | 6 | 1 | 0 | 0
2017-06-19 02:00 | 6 | 2 | 0 | 0
2017-06-19 03:00 | 6 | 3 | 0 | 0
2017-06-19 04:00 | 6 | 4 | 10.0038 | 10.0038
2017-06-19 05:00 | 6 | 5 | 471.669 | 471.669
2017-06-19 06:00 | 6 | 6 | 1192.6052 | 1192.6052
2017-06-19 07:00 | 6 | 7 | 2217.1678 | 2217.1678
2017-06-19 08:00 | 6 | 8 | 3224.0538 | 3224.0538
2017-06-19 09:00 | 6 | 9 | 6865.5402 | 6865.5403
2017-06-19 10:00 | 6 | 10 | 5503.5918 | 5503.5918
2017-06-19 11:00 | 6 | 11 | 4403.6617 | 4403.6617
2017-06-19 12:00 | 6 | 12 | 3771.7527 | 3771.7527
2017-06-19 13:00 | 6 | 13 | 7278.266 | 7278.2661
2017-06-19 14:00 | 6 | 14 | 3817.2766 | 3817.2766
2017-06-19 15:00 | 6 | 15 | 4963.0113 | 4963.0113
2017-06-19 16:00 | 6 | 16 | 3225.2129 | 3225.2129
2017-06-19 17:00 | 6 | 17 | 1396.7037 | 1396.7037
2017-06-19 18:00 | 6 | 18 | 255.1689 | 255.1689
2017-06-19 19:00 | 6 | 19 | 0 | 0
2017-06-19 20:00 | 6 | 20 | 0 | 0
2017-06-19 21:00 | 6 | 21 | 0 | 0
2017-06-19 22:00 | 6 | 22 | 0 | 0
2017-06-19 23:00 | 6 | 23 | 0 | 0
2017-06-20 | 6 | 0 | 0 | 0
2017-06-20 01:00 | 6 | 1 | 0 | 0
2017-06-20 02:00 | 6 | 2 | 0 | 0
2017-06-20 03:00 | 6 | 3 | 0 | 0
2017-06-20 04:00 | 6 | 4 | 75.2548 | 75.2548
2017-06-20 05:00 | 6 | 5 | 624.4224 | 624.4224
2017-06-20 06:00 | 6 | 6 | 2533.0613 | 2533.0613
2017-06-20 07:00 | 6 | 7 | 4620.332 | 4620.332
2017-06-20 08:00 | 6 | 8 | 6311.8693 | 6311.8693
2017-06-20 09:00 | 6 | 9 | 7508.5926 | 7508.5927
2017-06-20 10:00 | 6 | 10 | 8237.7962 | 8237.7962
2017-06-20 11:00 | 6 | 11 | 8506.7696 | 8506.7696
2017-06-20 12:00 | 6 | 12 | 8326.7325 | 8326.7325
2017-06-20 13:00 | 6 | 13 | 7761.2936 | 7761.2936
2017-06-20 14:00 | 6 | 14 | 6749.6317 | 6749.6317
2017-06-20 15:00 | 6 | 15 | 5296.9149 | 5296.9149
2017-06-20 16:00 | 6 | 16 | 3469.2958 | 3469.2958
2017-06-20 17:00 | 6 | 17 | 1446.3814 | 1446.3814
2017-06-20 18:00 | 6 | 18 | 214.4336 | 214.4336
2017-06-20 19:00 | 6 | 19 | 0 | 0
2017-06-20 20:00 | 6 | 20 | 0 | 0
2017-06-20 21:00 | 6 | 21 | 0 | 0
2017-06-20 22:00 | 6 | 22 | 0 | 0
2017-06-20 23:00 | 6 | 23 | 0 | 0
2017-06-21 | 6 | 0 | 0 | 0
2017-06-21 01:00 | 6 | 1 | 0 | 0
2017-06-21 02:00 | 6 | 2 | 0 | 0
2017-06-21 03:00 | 6 | 3 | 0 | 0
2017-06-21 04:00 | 6 | 4 | 75.3054 | 75.3054
2017-06-21 05:00 | 6 | 5 | 613.065 | 613.065
2017-06-21 06:00 | 6 | 6 | 2464.5431 | 2464.5431
2017-06-21 07:00 | 6 | 7 | 4480.0964 | 4480.0964
2017-06-21 08:00 | 6 | 8 | 6099.7736 | 6099.7736
2017-06-21 09:00 | 6 | 9 | 7276.9826 | 7276.9826
2017-06-21 10:00 | 6 | 10 | 8002.6349 | 8002.6349
2017-06-21 11:00 | 6 | 11 | 8268.385 | 8268.385
2017-06-21 12:00 | 6 | 12 | 7208.2253 | 7208.2253
2017-06-21 13:00 | 6 | 13 | 6743.738 | 6743.738
2017-06-21 14:00 | 6 | 14 | 6613.7684 | 6613.7685
2017-06-21 15:00 | 6 | 15 | 4348.8112 | 4348.8112
2017-06-21 16:00 | 6 | 16 | 3438.6196 | 3438.6196
2017-06-21 17:00 | 6 | 17 | 1427.8342 | 1427.8342
2017-06-21 18:00 | 6 | 18 | 248.0274 | 248.0274
2017-06-21 19:00 | 6 | 19 | 0 | 0
2017-06-21 20:00 | 6 | 20 | 0 | 0
2017-06-21 21:00 | 6 | 21 | 0 | 0
2017-06-21 22:00 | 6 | 22 | 0 | 0
2017-06-21 23:00 | 6 | 23 | 0 | 0
2017-06-22 | 6 | 0 | 0 | 0
2017-06-22 01:00 | 6 | 1 | 0 | 0
2017-06-22 02:00 | 6 | 2 | 0 | 0
2017-06-22 03:00 | 6 | 3 | 0 | 0
2017-06-22 04:00 | 6 | 4 | 98.3469 | 98.3469
2017-06-22 05:00 | 6 | 5 | 710.5206 | 710.5206
2017-06-22 06:00 | 6 | 6 | 1444.2804 | 1444.2804
2017-06-22 07:00 | 6 | 7 | 2278.4053 | 2278.4053
2017-06-22 08:00 | 6 | 8 | 4931.3852 | 4931.3852
2017-06-22 09:00 | 6 | 9 | 5231.0326 | 5231.0326
2017-06-22 10:00 | 6 | 10 | 3588.5336 | 3588.5336
2017-06-22 11:00 | 6 | 11 | 4027.0148 | 4027.0148
2017-06-22 12:00 | 6 | 12 | 2882.7303 | 2882.7303
2017-06-22 13:00 | 6 | 13 | 3693.1065 | 3693.1065
2017-06-22 14:00 | 6 | 14 | 3035.7976 | 3035.7976
2017-06-22 15:00 | 6 | 15 | 2353.7717 | 2353.7717
2017-06-22 16:00 | 6 | 16 | 869.8381 | 869.8381
2017-06-22 17:00 | 6 | 17 | 869.638 | 869.638
2017-06-22 18:00 | 6 | 18 | 392.6376 | 392.6376
2017-06-22 19:00 | 6 | 19 | 0 | 0
2017-06-22 20:00 | 6 | 20 | 0 | 0
2017-06-22 21:00 | 6 | 21 | 0 | 0
2017-06-22 22:00 | 6 | 22 | 0 | 0
2017-06-22 23:00 | 6 | 23 | 0 | 0
2017-06-23 | 6 | 0 | 0 | 0
2017-06-23 01:00 | 6 | 1 | 0 | 0
2017-06-23 02:00 | 6 | 2 | 0 | 0
2017-06-23 03:00 | 6 | 3 | 0 | 0
2017-06-23 04:00 | 6 | 4 | 105.831 | 105.831
2017-06-23 05:00 | 6 | 5 | 600.7853 | 600.7853
2017-06-23 06:00 | 6 | 6 | 2125.5956 | 2125.5956
2017-06-23 07:00 | 6 | 7 | 4181.0975 | 4181.0975
2017-06-23 08:00 | 6 | 8 | 6041.4893 | 6041.4893
2017-06-23 09:00 | 6 | 9 | 7231.1586 | 7231.1586
2017-06-23 10:00 | 6 | 10 | 7949.1898 | 7949.1898
2017-06-23 11:00 | 6 | 11 | 8215.5655 | 8215.5655
2017-06-23 12:00 | 6 | 12 | 8085.7949 | 8085.7949
2017-06-23 13:00 | 6 | 13 | 7492.7399 | 7492.7399
2017-06-23 14:00 | 6 | 14 | 6522.9276 | 6522.9276
2017-06-23 15:00 | 6 | 15 | 5128.5273 | 5128.5273
2017-06-23 16:00 | 6 | 16 | 3327.2248 | 3327.2248
2017-06-23 17:00 | 6 | 17 | 1411.9999 | 1411.9999
2017-06-23 18:00 | 6 | 18 | 243.187 | 243.187
2017-06-23 19:00 | 6 | 19 | 0 | 0
2017-06-23 20:00 | 6 | 20 | 0 | 0
2017-06-23 21:00 | 6 | 21 | 0 | 0
2017-06-23 22:00 | 6 | 22 | 0 | 0
2017-06-23 23:00 | 6 | 23 | 0 | 0
2017-06-24 | 6 | 0 | 0 | 0
2017-06-24 01:00 | 6 | 1 | 0 | 0
2017-06-24 02:00 | 6 | 2 | 0 | 0
2017-06-24 03:00 | 6 | 3 | 0 | 0
2017-06-24 04:00 | 6 | 4 | 64.5495 | 64.5495
2017-06-24 05:00 | 6 | 5 | 604.5021 | 604.5021
2017-06-24 06:00 | 6 | 6 | 2364.837 | 2364.837
2017-06-24 07:00 | 6 | 7 | 4314.5815 | 4314.5815
2017-06-24 08:00 | 6 | 8 | 5888.092 | 5888.092
2017-06-24 09:00 | 6 | 9 | 6988.6408 | 6988.6408
2017-06-24 10:00 | 6 | 10 | 7650.7027 | 7650.7027
2017-06-24 11:00 | 6 | 11 | 7961.0578 | 7961.0578
2017-06-24 12:00 | 6 | 12 | 7838.1205 | 7838.1205
2017-06-24 13:00 | 6 | 13 | 7223.357 | 7223.357
2017-06-24 14:00 | 6 | 14 | 6294.7262 | 6294.7262
2017-06-24 15:00 | 6 | 15 | 4943.0036 | 4943.0036
2017-06-24 16:00 | 6 | 16 | 3206.9084 | 3206.9084
2017-06-24 17:00 | 6 | 17 | 1470.4026 | 1470.4026
2017-06-24 18:00 | 6 | 18 | 364.964 | 364.964
2017-06-24 19:00 | 6 | 19 | 0 | 0
2017-06-24 20:00 | 6 | 20 | 0 | 0
2017-06-24 21:00 | 6 | 21 | 0 | 0
2017-06-24 22:00 | 6 | 22 | 0 | 0
2017-06-24 23:00 | 6 | 23 | 0 | 0
2017-06-25 | 6 | 0 | 0 | 0
2017-06-25 01:00 | 6 | 1 | 0 | 0
2017-06-25 02:00 | 6 | 2 | 0 | 0
2017-06-25 03:00 | 6 | 3 | 0 | 0
2017-06-25 04:00 | 6 | 4 | 56.4397 | 56.4397
2017-06-25 05:00 | 6 | 5 | 803.559 | 803.559
2017-06-25 06:00 | 6 | 6 | 1793.5043 | 1793.5043
2017-06-25 07:00 | 6 | 7 | 2003.7255 | 2003.7255
2017-06-25 08:00 | 6 | 8 | 1781.3569 | 1781.3569
2017-06-25 09:00 | 6 | 9 | 4445.5343 | 4445.5343
2017-06-25 10:00 | 6 | 10 | 6183.2625 | 6183.2625
2017-06-25 11:00 | 6 | 11 | 5671.4504 | 5671.4504
2017-06-25 12:00 | 6 | 12 | 5418.1525 | 5418.1525
2017-06-25 13:00 | 6 | 13 | 5224.8847 | 5224.8847
2017-06-25 14:00 | 6 | 14 | 3366.9424 | 3366.9424
2017-06-25 15:00 | 6 | 15 | 2988.8339 | 2988.8339
2017-06-25 16:00 | 6 | 16 | 1574.0659 | 1574.0659
2017-06-25 17:00 | 6 | 17 | 1038.1671 | 1038.1671
2017-06-25 18:00 | 6 | 18 | 313.061 | 313.061
2017-06-25 19:00 | 6 | 19 | 0 | 0
2017-06-25 20:00 | 6 | 20 | 0 | 0
2017-06-25 21:00 | 6 | 21 | 0 | 0
2017-06-25 22:00 | 6 | 22 | 0 | 0
2017-06-25 23:00 | 6 | 23 | 0 | 0
2017-06-26 | 6 | 0 | 0 | 0
2017-06-26 01:00 | 6 | 1 | 0 | 0
2017-06-26 02:00 | 6 | 2 | 0 | 0
2017-06-26 03:00 | 6 | 3 | 0 | 0
2017-06-26 04:00 | 6 | 4 | 28.8098 | 28.8098
2017-06-26 05:00 | 6 | 5 | 317.1194 | 317.1194
2017-06-26 06:00 | 6 | 6 | 588.9575 | 588.9575
2017-06-26 07:00 | 6 | 7 | 2474.1893 | 2474.1893
2017-06-26 08:00 | 6 | 8 | 1357.6946 | 1357.6946
2017-06-26 09:00 | 6 | 9 | 1561.9691 | 1561.9691
2017-06-26 10:00 | 6 | 10 | 1515.892 | 1515.892
2017-06-26 11:00 | 6 | 11 | 1945.4837 | 1945.4837
2017-06-26 12:00 | 6 | 12 | 3587.2996 | 3587.2996
2017-06-26 13:00 | 6 | 13 | 4631.4329 | 4631.4329
2017-06-26 14:00 | 6 | 14 | 5427.8263 | 5427.8263
2017-06-26 15:00 | 6 | 15 | 4216.5705 | 4216.5705
2017-06-26 16:00 | 6 | 16 | 837.2241 | 837.2241
2017-06-26 17:00 | 6 | 17 | 1116.8075 | 1116.8075
2017-06-26 18:00 | 6 | 18 | 304.8408 | 304.8408
2017-06-26 19:00 | 6 | 19 | 0 | 0
2017-06-26 20:00 | 6 | 20 | 0 | 0
2017-06-26 21:00 | 6 | 21 | 0 | 0
2017-06-26 22:00 | 6 | 22 | 0 | 0
2017-06-26 23:00 | 6 | 23 | 0 | 0
2017-06-27 | 6 | 0 | 0 | 0
2017-06-27 01:00 | 6 | 1 | 0 | 0
2017-06-27 02:00 | 6 | 2 | 0 | 0
2017-06-27 03:00 | 6 | 3 | 0 | 0
2017-06-27 04:00 | 6 | 4 | 57.6345 | 57.6345
2017-06-27 05:00 | 6 | 5 | 578.5351 | 578.5351
2017-06-27 06:00 | 6 | 6 | 2404.3866 | 2404.3866
2017-06-27 07:00 | 6 | 7 | 4400.6153 | 4400.6153
2017-06-27 08:00 | 6 | 8 | 6086.5164 | 6086.5164
2017-06-27 09:00 | 6 | 9 | 7290.1467 | 7290.1467
2017-06-27 10:00 | 6 | 10 | 7993.3544 | 7993.3545
2017-06-27 11:00 | 6 | 11 | 8260.0521 | 8260.0521
2017-06-27 12:00 | 6 | 12 | 8116.0905 | 8116.0905
2017-06-27 13:00 | 6 | 13 | 7491.1897 | 7491.1897
2017-06-27 14:00 | 6 | 14 | 6544.2164 | 6544.2164
2017-06-27 15:00 | 6 | 15 | 5145.7544 | 5145.7544
2017-06-27 16:00 | 6 | 16 | 3369.0434 | 3369.0434
2017-06-27 17:00 | 6 | 17 | 1486.5958 | 1486.5958
2017-06-27 18:00 | 6 | 18 | 285.3667 | 285.3667
2017-06-27 19:00 | 6 | 19 | 0 | 0
2017-06-27 20:00 | 6 | 20 | 0 | 0
2017-06-27 21:00 | 6 | 21 | 0 | 0
2017-06-27 22:00 | 6 | 22 | 0 | 0
2017-06-27 23:00 | 6 | 23 | 0 | 0
2017-06-28 | 6 | 0 | 0 | 0
2017-06-28 01:00 | 6 | 1 | 0 | 0
2017-06-28 02:00 | 6 | 2 | 0 | 0
2017-06-28 03:00 | 6 | 3 | 0 | 0
2017-06-28 04:00 | 6 | 4 | 119.6092 | 119.6092
2017-06-28 05:00 | 6 | 5 | 616.7243 | 616.7243
2017-06-28 06:00 | 6 | 6 | 1682.7766 | 1682.7766
2017-06-28 07:00 | 6 | 7 | 3970.375 | 3970.375
2017-06-28 08:00 | 6 | 8 | 5658.8659 | 5658.8659
2017-06-28 09:00 | 6 | 9 | 5549.3411 | 5549.3411
2017-06-28 10:00 | 6 | 10 | 7191.8826 | 7191.8826
2017-06-28 11:00 | 6 | 11 | 6613.167 | 6613.167
2017-06-28 12:00 | 6 | 12 | 7110.3614 | 7110.3614
2017-06-28 13:00 | 6 | 13 | 5661.7662 | 5661.7662
2017-06-28 14:00 | 6 | 14 | 3379.7867 | 3379.7868
2017-06-28 15:00 | 6 | 15 | 3271.2198 | 3271.2198
2017-06-28 16:00 | 6 | 16 | 819.7913 | 819.7913
2017-06-28 17:00 | 6 | 17 | 84.8815 | 84.8815
2017-06-28 18:00 | 6 | 18 | 356.8438 | 356.8438
2017-06-28 19:00 | 6 | 19 | 0 | 0
2017-06-28 20:00 | 6 | 20 | 0 | 0
2017-06-28 21:00 | 6 | 21 | 0 | 0
2017-06-28 22:00 | 6 | 22 | 0 | 0
2017-06-28 23:00 | 6 | 23 | 0 | 0
2017-06-29 | 6 | 0 | 0 | 0
2017-06-29 01:00 | 6 | 1 | 0 | 0
2017-06-29 02:00 | 6 | 2 | 0 | 0
2017-06-29 03:00 | 6 | 3 | 0 | 0
2017-06-29 04:00 | 6 | 4 | 0 | 0
2017-06-29 05:00 | 6 | 5 | 68.8229 | 68.8229
2017-06-29 06:00 | 6 | 6 | 1669.823 | 1669.823
2017-06-29 07:00 | 6 | 7 | 1131.278 | 1131.278
2017-06-29 08:00 | 6 | 8 | 2062.6124 | 2062.6124
2017-06-29 09:00 | 6 | 9 | 1624.9086 | 1624.9086
2017-06-29 10:00 | 6 | 10 | 4493.4444 | 4493.4444
2017-06-29 11:00 | 6 | 11 | 8176.393 | 8176.3931
2017-06-29 12:00 | 6 | 12 | 6874.8518 | 6874.8518
2017-06-29 13:00 | 6 | 13 | 7419.0134 | 7419.0134
2017-06-29 14:00 | 6 | 14 | 6463.0092 | 6463.0092
2017-06-29 15:00 | 6 | 15 | 5080.363 | 5080.363
2017-06-29 16:00 | 6 | 16 | 3324.4717 | 3324.4717
2017-06-29 17:00 | 6 | 17 | 1439.5608 | 1439.5608
2017-06-29 18:00 | 6 | 18 | 273.3998 | 273.3998
2017-06-29 19:00 | 6 | 19 | 0 | 0
2017-06-29 20:00 | 6 | 20 | 0 | 0
2017-06-29 21:00 | 6 | 21 | 0 | 0
2017-06-29 22:00 | 6 | 22 | 0 | 0
2017-06-29 23:00 | 6 | 23 | 0 | 0
2017-06-30 | 6 | 0 | 0 | 0
2017-06-30 01:00 | 6 | 1 | 0 | 0
2017-06-30 02:00 | 6 | 2 | 0 | 0
2017-06-30 03:00 | 6 | 3 | 0 | 0
2017-06-30 04:00 | 6 | 4 | 48.3195 | 48.3195
2017-06-30 05:00 | 6 | 5 | 714.1833 | 714.1833
2017-06-30 06:00 | 6 | 6 | 2268.5141 | 2268.5141
2017-06-30 07:00 | 6 | 7 | 4177.0472 | 4177.0472
2017-06-30 08:00 | 6 | 8 | 5838.2694 | 5838.2694
2017-06-30 09:00 | 6 | 9 | 7060.2456 | 7060.2456
2017-06-30 10:00 | 6 | 10 | 7778.4079 | 7778.4079
2017-06-30 11:00 | 6 | 11 | 8109.9127 | 8109.9127
2017-06-30 12:00 | 6 | 12 | 7968.7226 | 7968.7226
2017-06-30 13:00 | 6 | 13 | 7409.7283 | 7409.7283
2017-06-30 14:00 | 6 | 14 | 4120.8709 | 4120.8709
2017-06-30 15:00 | 6 | 15 | 5109.5029 | 5109.5029
2017-06-30 16:00 | 6 | 16 | 3250.0196 | 3250.0196
2017-06-30 17:00 | 6 | 17 | 1502.4175 | 1502.4175
2017-06-30 18:00 | 6 | 18 | 370.0044 | 370.0044
2017-06-30 19:00 | 6 | 19 | 0 | 0
2017-06-30 20:00 | 6 | 20 | 0 | 0
2017-06-30 21:00 | 6 | 21 | 0 | 0
2017-06-30 22:00 | 6 | 22 | 0 | 0
2017-06-30 23:00 | 6 | 23 | 0 | 0
2017-07-01 | 7 | 0 | 0 | 0
2017-07-01 01:00 | 7 | 1 | 0 | 0
2017-07-01 02:00 | 7 | 2 | 0 | 0
2017-07-01 03:00 | 7 | 3 | 0 | 0
2017-07-01 04:00 | 7 | 4 | 75.5239 | 75.5239
2017-07-01 05:00 | 7 | 5 | 623.4897 | 623.4897
2017-07-01 06:00 | 7 | 6 | 1834.4259 | 1834.426
2017-07-01 07:00 | 7 | 7 | 3548.6102 | 3548.6102
2017-07-01 08:00 | 7 | 8 | 4502.7065 | 4502.7065
2017-07-01 09:00 | 7 | 9 | 5470.5224 | 5470.5224
2017-07-01 10:00 | 7 | 10 | 6447.8947 | 6447.8947
2017-07-01 11:00 | 7 | 11 | 6479.0252 | 6479.0252
2017-07-01 12:00 | 7 | 12 | 6047.2738 | 6047.2738
2017-07-01 13:00 | 7 | 13 | 5542.0455 | 5542.0455
2017-07-01 14:00 | 7 | 14 | 4321.7437 | 4321.7437
2017-07-01 15:00 | 7 | 15 | 4181.9554 | 4181.9554
2017-07-01 16:00 | 7 | 16 | 2798.2662 | 2798.2662
2017-07-01 17:00 | 7 | 17 | 1086.1991 | 1086.1991
2017-07-01 18:00 | 7 | 18 | 335.1065 | 335.1065
2017-07-01 19:00 | 7 | 19 | 0 | 0
2017-07-01 20:00 | 7 | 20 | 0 | 0
2017-07-01 21:00 | 7 | 21 | 0 | 0
2017-07-01 22:00 | 7 | 22 | 0 | 0
2017-07-01 23:00 | 7 | 23 | 0 | 0
2017-07-02 | 7 | 0 | 0 | 0
2017-07-02 01:00 | 7 | 1 | 0 | 0
2017-07-02 02:00 | 7 | 2 | 0 | 0
2017-07-02 03:00 | 7 | 3 | 0 | 0
2017-07-02 04:00 | 7 | 4 | 27.1664 | 27.1664
2017-07-02 05:00 | 7 | 5 | 625.6954 | 625.6954
2017-07-02 06:00 | 7 | 6 | 1441.4192 | 1441.4192
2017-07-02 07:00 | 7 | 7 | 3820.8175 | 3820.8175
2017-07-02 08:00 | 7 | 8 | 5335.3146 | 5335.3146
2017-07-02 09:00 | 7 | 9 | 6457.8043 | 6457.8043
2017-07-02 10:00 | 7 | 10 | 7178.4909 | 7178.4909
2017-07-02 11:00 | 7 | 11 | 7460.3927 | 7460.3927
2017-07-02 12:00 | 7 | 12 | 7390.6958 | 7390.6958
2017-07-02 13:00 | 7 | 13 | 6872.2976 | 6872.2976
2017-07-02 14:00 | 7 | 14 | 6000.4332 | 6000.4332
2017-07-02 15:00 | 7 | 15 | 3962.7378 | 3962.7378
2017-07-02 16:00 | 7 | 16 | 2666.2221 | 2666.2221
2017-07-02 17:00 | 7 | 17 | 538.3771 | 538.3771
2017-07-02 18:00 | 7 | 18 | 210.9203 | 210.9203
2017-07-02 19:00 | 7 | 19 | 0 | 0
2017-07-02 20:00 | 7 | 20 | 0 | 0
2017-07-02 21:00 | 7 | 21 | 0 | 0
2017-07-02 22:00 | 7 | 22 | 0 | 0
2017-07-02 23:00 | 7 | 23 | 0 | 0
2017-07-03 | 7 | 0 | 0 | 0
2017-07-03 01:00 | 7 | 1 | 0 | 0
2017-07-03 02:00 | 7 | 2 | 0 | 0
2017-07-03 03:00 | 7 | 3 | 0 | 0
2017-07-03 04:00 | 7 | 4 | 0 | 0
2017-07-03 05:00 | 7 | 5 | 630.1874 | 630.1874
2017-07-03 06:00 | 7 | 6 | 1967.0738 | 1967.0738
2017-07-03 07:00 | 7 | 7 | 3548.2249 | 3548.2249
2017-07-03 08:00 | 7 | 8 | 4910.9761 | 4910.9761
2017-07-03 09:00 | 7 | 9 | 1714.5315 | 1714.5315
2017-07-03 10:00 | 7 | 10 | 5067.2243 | 5067.2243
2017-07-03 11:00 | 7 | 11 | 7499.1707 | 7499.1707
2017-07-03 12:00 | 7 | 12 | 7370.2787 | 7370.2787
2017-07-03 13:00 | 7 | 13 | 6845.5176 | 6845.5176
2017-07-03 14:00 | 7 | 14 | 5949.1064 | 5949.1064
2017-07-03 15:00 | 7 | 15 | 4661.3732 | 4661.3732
2017-07-03 16:00 | 7 | 16 | 3107.921 | 3107.921
2017-07-03 17:00 | 7 | 17 | 1384.7702 | 1384.7702
2017-07-03 18:00 | 7 | 18 | 312.9185 | 312.9185
2017-07-03 19:00 | 7 | 19 | 0 | 0
2017-07-03 20:00 | 7 | 20 | 0 | 0
2017-07-03 21:00 | 7 | 21 | 0 | 0
2017-07-03 22:00 | 7 | 22 | 0 | 0
2017-07-03 23:00 | 7 | 23 | 0 | 0
2017-07-04 | 7 | 0 | 0 | 0
2017-07-04 01:00 | 7 | 1 | 0 | 0
2017-07-04 02:00 | 7 | 2 | 0 | 0
2017-07-04 03:00 | 7 | 3 | 0 | 0
2017-07-04 04:00 | 7 | 4 | 45.7481 | 45.7481
2017-07-04 05:00 | 7 | 5 | 607.0643 | 607.0643
2017-07-04 06:00 | 7 | 6 | 647.2959 | 647.2959
2017-07-04 07:00 | 7 | 7 | 2250.8708 | 2250.8708
2017-07-04 08:00 | 7 | 8 | 1942.9928 | 1942.9928
2017-07-04 09:00 | 7 | 9 | 3421.4984 | 3421.4984
2017-07-04 10:00 | 7 | 10 | 2575.5285 | 2575.5285
2017-07-04 11:00 | 7 | 11 | 1679.5439 | 1679.5439
2017-07-04 12:00 | 7 | 12 | 1327.6968 | 1327.6968
2017-07-04 13:00 | 7 | 13 | 1485.8655 | 1485.8655
2017-07-04 14:00 | 7 | 14 | 698.2524 | 698.2524
2017-07-04 15:00 | 7 | 15 | 515.9716 | 515.9716
2017-07-04 16:00 | 7 | 16 | 359.6188 | 359.6188
2017-07-04 17:00 | 7 | 17 | 435.3406 | 435.3406
2017-07-04 18:00 | 7 | 18 | 0 | 0
2017-07-04 19:00 | 7 | 19 | 0 | 0
2017-07-04 20:00 | 7 | 20 | 0 | 0
2017-07-04 21:00 | 7 | 21 | 0 | 0
2017-07-04 22:00 | 7 | 22 | 0 | 0
2017-07-04 23:00 | 7 | 23 | 0 | 0
2017-07-05 | 7 | 0 | 0 | 0
2017-07-05 01:00 | 7 | 1 | 0 | 0
2017-07-05 02:00 | 7 | 2 | 0 | 0
2017-07-05 03:00 | 7 | 3 | 0 | 0
2017-07-05 04:00 | 7 | 4 | 9.9992 | 9.9992
2017-07-05 05:00 | 7 | 5 | 629.4939 | 629.4939
2017-07-05 06:00 | 7 | 6 | 1853.11 | 1853.11
2017-07-05 07:00 | 7 | 7 | 4297.5293 | 4297.5293
2017-07-05 08:00 | 7 | 8 | 6008.8213 | 6008.8213
2017-07-05 09:00 | 7 | 9 | 7258.2997 | 7258.2998
2017-07-05 10:00 | 7 | 10 | 8049.6929 | 8049.6929
2017-07-05 11:00 | 7 | 11 | 8327.0568 | 8327.0568
2017-07-05 12:00 | 7 | 12 | 8221.3443 | 8221.3443
2017-07-05 13:00 | 7 | 13 | 6803.0768 | 6803.0768
2017-07-05 14:00 | 7 | 14 | 6155.6591 | 6155.6591
2017-07-05 15:00 | 7 | 15 | 5201.1498 | 5201.1498
2017-07-05 16:00 | 7 | 16 | 3402.643 | 3402.643
2017-07-05 17:00 | 7 | 17 | 1425.6285 | 1425.6285
2017-07-05 18:00 | 7 | 18 | 235.1002 | 235.1003
2017-07-05 19:00 | 7 | 19 | 0 | 0
2017-07-05 20:00 | 7 | 20 | 0 | 0
2017-07-05 21:00 | 7 | 21 | 0 | 0
2017-07-05 22:00 | 7 | 22 | 0 | 0
2017-07-05 23:00 | 7 | 23 | 0 | 0
2017-07-06 | 7 | 0 | 0 | 0
2017-07-06 01:00 | 7 | 1 | 0 | 0
2017-07-06 02:00 | 7 | 2 | 0 | 0
2017-07-06 03:00 | 7 | 3 | 0 | 0
2017-07-06 04:00 | 7 | 4 | 30.6728 | 30.6728
2017-07-06 05:00 | 7 | 5 | 499.614 | 499.614
2017-07-06 06:00 | 7 | 6 | 1876.2836 | 1876.2836
2017-07-06 07:00 | 7 | 7 | 4115.0013 | 4115.0013
2017-07-06 08:00 | 7 | 8 | 5346.2545 | 5346.2545
2017-07-06 09:00 | 7 | 9 | 7054.4231 | 7054.4231
2017-07-06 10:00 | 7 | 10 | 7784.266 | 7784.2661
2017-07-06 11:00 | 7 | 11 | 8074.0603 | 8074.0603
2017-07-06 12:00 | 7 | 12 | 7979.0507 | 7979.0507
2017-07-06 13:00 | 7 | 13 | 7423.2281 | 7423.2281
2017-07-06 14:00 | 7 | 14 | 6514.1623 | 6514.1623
2017-07-06 15:00 | 7 | 15 | 5143.0564 | 5143.0564
2017-07-06 16:00 | 7 | 16 | 3365.5831 | 3365.5831
2017-07-06 17:00 | 7 | 17 | 1435.6945 | 1435.6945
2017-07-06 18:00 | 7 | 18 | 263.0613 | 263.0613
2017-07-06 19:00 | 7 | 19 | 0 | 0
2017-07-06 20:00 | 7 | 20 | 0 | 0
2017-07-06 21:00 | 7 | 21 | 0 | 0
2017-07-06 22:00 | 7 | 22 | 0 | 0
2017-07-06 23:00 | 7 | 23 | 0 | 0
2017-07-07 | 7 | 0 | 0 | 0
2017-07-07 01:00 | 7 | 1 | 0 | 0
2017-07-07 02:00 | 7 | 2 | 0 | 0
2017-07-07 03:00 | 7 | 3 | 0 | 0
2017-07-07 04:00 | 7 | 4 | 0 | 0
2017-07-07 05:00 | 7 | 5 | 417.3074 | 417.3074
2017-07-07 06:00 | 7 | 6 | 916.9985 | 916.9985
2017-07-07 07:00 | 7 | 7 | 1406.1763 | 1406.1763
2017-07-07 08:00 | 7 | 8 | 4763.8106 | 4763.8106
2017-07-07 09:00 | 7 | 9 | 6643.4108 | 6643.4108
2017-07-07 10:00 | 7 | 10 | 7435.5435 | 7435.5435
2017-07-07 11:00 | 7 | 11 | 7709.8978 | 7709.8978
2017-07-07 12:00 | 7 | 12 | 7562.9221 | 7562.9221
2017-07-07 13:00 | 7 | 13 | 7045.3784 | 7045.3784
2017-07-07 14:00 | 7 | 14 | 6137.3304 | 6137.3304
2017-07-07 15:00 | 7 | 15 | 4786.3149 | 4786.3149
2017-07-07 16:00 | 7 | 16 | 3130.6243 | 3130.6243
2017-07-07 17:00 | 7 | 17 | 14.7763 | 14.7763
2017-07-07 18:00 | 7 | 18 | 0 | 0
2017-07-07 19:00 | 7 | 19 | 0 | 0
2017-07-07 20:00 | 7 | 20 | 0 | 0
2017-07-07 21:00 | 7 | 21 | 0 | 0
2017-07-07 22:00 | 7 | 22 | 0 | 0
2017-07-07 23:00 | 7 | 23 | 0 | 0
2017-07-08 | 7 | 0 | 0 | 0
2017-07-08 01:00 | 7 | 1 | 0 | 0
2017-07-08 02:00 | 7 | 2 | 0 | 0
2017-07-08 03:00 | 7 | 3 | 0 | 0
2017-07-08 04:00 | 7 | 4 | 8.4697 | 8.4697
2017-07-08 05:00 | 7 | 5 | 603.9616 | 603.9616
2017-07-08 06:00 | 7 | 6 | 1910.5398 | 1910.5398
2017-07-08 07:00 | 7 | 7 | 3852.2389 | 3852.2389
2017-07-08 08:00 | 7 | 8 | 5401.4546 | 5401.4546
2017-07-08 09:00 | 7 | 9 | 4148.3582 | 4148.3582
2017-07-08 10:00 | 7 | 10 | 6250.1844 | 6250.1844
2017-07-08 11:00 | 7 | 11 | 6696.0544 | 6696.0544
2017-07-08 12:00 | 7 | 12 | 6759.7759 | 6759.7759
2017-07-08 13:00 | 7 | 13 | 5897.2782 | 5897.2782
2017-07-08 14:00 | 7 | 14 | 5939.175 | 5939.175
2017-07-08 15:00 | 7 | 15 | 4288.8698 | 4288.8698
2017-07-08 16:00 | 7 | 16 | 2761.4225 | 2761.4225
2017-07-08 17:00 | 7 | 17 | 1426.6658 | 1426.6658
2017-07-08 18:00 | 7 | 18 | 335.1825 | 335.1825
2017-07-08 19:00 | 7 | 19 | 0 | 0
2017-07-08 20:00 | 7 | 20 | 0 | 0
2017-07-08 21:00 | 7 | 21 | 0 | 0
2017-07-08 22:00 | 7 | 22 | 0 | 0
2017-07-08 23:00 | 7 | 23 | 0 | 0
2017-07-09 | 7 | 0 | 0 | 0
2017-07-09 01:00 | 7 | 1 | 0 | 0
2017-07-09 02:00 | 7 | 2 | 0 | 0
2017-07-09 03:00 | 7 | 3 | 0 | 0
2017-07-09 04:00 | 7 | 4 | 27.1803 | 27.1803
2017-07-09 05:00 | 7 | 5 | 544.6664 | 544.6664
2017-07-09 06:00 | 7 | 6 | 1681.5978 | 1681.5978
2017-07-09 07:00 | 7 | 7 | 3981.3483 | 3981.3483
2017-07-09 08:00 | 7 | 8 | 5600.3539 | 5600.3539
2017-07-09 09:00 | 7 | 9 | 6754.7918 | 6754.7918
2017-07-09 10:00 | 7 | 10 | 7548.0813 | 7548.0813
2017-07-09 11:00 | 7 | 11 | 6599.4601 | 6599.4602
2017-07-09 12:00 | 7 | 12 | 6423.3491 | 6423.3491
2017-07-09 13:00 | 7 | 13 | 7219.7632 | 7219.7633
2017-07-09 14:00 | 7 | 14 | 6279.5968 | 6279.5968
2017-07-09 15:00 | 7 | 15 | 4929.7199 | 4929.7199
2017-07-09 16:00 | 7 | 16 | 3211.2749 | 3211.2749
2017-07-09 17:00 | 7 | 17 | 1236.8215 | 1236.8215
2017-07-09 18:00 | 7 | 18 | 334.113 | 334.113
2017-07-09 19:00 | 7 | 19 | 0 | 0
2017-07-09 20:00 | 7 | 20 | 0 | 0
2017-07-09 21:00 | 7 | 21 | 0 | 0
2017-07-09 22:00 | 7 | 22 | 0 | 0
2017-07-09 23:00 | 7 | 23 | 0 | 0
2017-07-10 | 7 | 0 | 0 | 0
2017-07-10 01:00 | 7 | 1 | 0 | 0
2017-07-10 02:00 | 7 | 2 | 0 | 0
2017-07-10 03:00 | 7 | 3 | 0 | 0
2017-07-10 04:00 | 7 | 4 | 0 | 0
2017-07-10 05:00 | 7 | 5 | 576.8308 | 576.8308
2017-07-10 06:00 | 7 | 6 | 1905.167 | 1905.167
2017-07-10 07:00 | 7 | 7 | 3588.1116 | 3588.1116
2017-07-10 08:00 | 7 | 8 | 5475.9561 | 5475.9561
2017-07-10 09:00 | 7 | 9 | 5476.1723 | 5476.1723
2017-07-10 10:00 | 7 | 10 | 6467.5275 | 6467.5275
2017-07-10 11:00 | 7 | 11 | 7389.8563 | 7389.8563
2017-07-10 12:00 | 7 | 12 | 5228.1645 | 5228.1645
2017-07-10 13:00 | 7 | 13 | 4712.3803 | 4712.3803
2017-07-10 14:00 | 7 | 14 | 4933.5322 | 4933.5322
2017-07-10 15:00 | 7 | 15 | 5082.8309 | 5082.8309
2017-07-10 16:00 | 7 | 16 | 3294.9558 | 3294.9558
2017-07-10 17:00 | 7 | 17 | 1393.325 | 1393.325
2017-07-10 18:00 | 7 | 18 | 244.0139 | 244.0139
2017-07-10 19:00 | 7 | 19 | 0 | 0
2017-07-10 20:00 | 7 | 20 | 0 | 0
2017-07-10 21:00 | 7 | 21 | 0 | 0
2017-07-10 22:00 | 7 | 22 | 0 | 0
2017-07-10 23:00 | 7 | 23 | 0 | 0
2017-07-11 | 7 | 0 | 0 | 0
2017-07-11 01:00 | 7 | 1 | 0 | 0
2017-07-11 02:00 | 7 | 2 | 0 | 0
2017-07-11 03:00 | 7 | 3 | 0 | 0
2017-07-11 04:00 | 7 | 4 | 18.7278 | 18.7278
2017-07-11 05:00 | 7 | 5 | 583.6192 | 583.6192
2017-07-11 06:00 | 7 | 6 | 1726.3466 | 1726.3466
2017-07-11 07:00 | 7 | 7 | 4057.3035 | 4057.3035
2017-07-11 08:00 | 7 | 8 | 5692.4333 | 5692.4333
2017-07-11 09:00 | 7 | 9 | 6882.3659 | 6882.3659
2017-07-11 10:00 | 7 | 10 | 7640.401 | 7640.401
2017-07-11 11:00 | 7 | 11 | 7967.4265 | 7967.4265
2017-07-11 12:00 | 7 | 12 | 7846.5247 | 7846.5247
2017-07-11 13:00 | 7 | 13 | 7316.0412 | 7316.0412
2017-07-11 14:00 | 7 | 14 | 6380.1851 | 6380.1851
2017-07-11 15:00 | 7 | 15 | 4993.2966 | 4993.2966
2017-07-11 16:00 | 7 | 16 | 3263.0249 | 3263.0249
2017-07-11 17:00 | 7 | 17 | 1441.7619 | 1441.7619
2017-07-11 18:00 | 7 | 18 | 266.762 | 266.762
2017-07-11 19:00 | 7 | 19 | 0 | 0
2017-07-11 20:00 | 7 | 20 | 0 | 0
2017-07-11 21:00 | 7 | 21 | 0 | 0
2017-07-11 22:00 | 7 | 22 | 0 | 0
2017-07-11 23:00 | 7 | 23 | 0 | 0
2017-07-12 | 7 | 0 | 0 | 0
2017-07-12 01:00 | 7 | 1 | 0 | 0
2017-07-12 02:00 | 7 | 2 | 0 | 0
2017-07-12 03:00 | 7 | 3 | 0 | 0
2017-07-12 04:00 | 7 | 4 | 0 | 0
2017-07-12 05:00 | 7 | 5 | 482.9689 | 482.9689
2017-07-12 06:00 | 7 | 6 | 2115.9287 | 2115.9287
2017-07-12 07:00 | 7 | 7 | 4069.919 | 4069.919
2017-07-12 08:00 | 7 | 8 | 5680.6297 | 5680.6297
2017-07-12 09:00 | 7 | 9 | 6864.8652 | 6864.8652
2017-07-12 10:00 | 7 | 10 | 7614.641 | 7614.6411
2017-07-12 11:00 | 7 | 11 | 7935.2794 | 7935.2794
2017-07-12 12:00 | 7 | 12 | 7793.9456 | 7793.9456
2017-07-12 13:00 | 7 | 13 | 6365.0407 | 6365.0407
2017-07-12 14:00 | 7 | 14 | 6333.6066 | 6333.6066
2017-07-12 15:00 | 7 | 15 | 4932.6168 | 4932.6168
2017-07-12 16:00 | 7 | 16 | 3217.6345 | 3217.6345
2017-07-12 17:00 | 7 | 17 | 1399.2924 | 1399.2924
2017-07-12 18:00 | 7 | 18 | 271.883 | 271.883
2017-07-12 19:00 | 7 | 19 | 0 | 0
2017-07-12 20:00 | 7 | 20 | 0 | 0
2017-07-12 21:00 | 7 | 21 | 0 | 0
2017-07-12 22:00 | 7 | 22 | 0 | 0
2017-07-12 23:00 | 7 | 23 | 0 | 0
2017-07-13 | 7 | 0 | 0 | 0
2017-07-13 01:00 | 7 | 1 | 0 | 0
2017-07-13 02:00 | 7 | 2 | 0 | 0
2017-07-13 03:00 | 7 | 3 | 0 | 0
2017-07-13 04:00 | 7 | 4 | 0 | 0
2017-07-13 05:00 | 7 | 5 | 561.7037 | 561.7037
2017-07-13 06:00 | 7 | 6 | 2041.9653 | 2041.9653
2017-07-13 07:00 | 7 | 7 | 3769.7609 | 3769.7609
2017-07-13 08:00 | 7 | 8 | 5343.9051 | 5343.9051
2017-07-13 09:00 | 7 | 9 | 6544.7604 | 6544.7604
2017-07-13 10:00 | 7 | 10 | 7317.289 | 7317.289
2017-07-13 11:00 | 7 | 11 | 7638.9704 | 7638.9704
2017-07-13 12:00 | 7 | 12 | 7479.102 | 7479.102
2017-07-13 13:00 | 7 | 13 | 6954.1259 | 6954.1259
2017-07-13 14:00 | 7 | 14 | 6062.4722 | 6062.4722
2017-07-13 15:00 | 7 | 15 | 4769.2168 | 4769.2168
2017-07-13 16:00 | 7 | 16 | 1200.1216 | 1200.1216
2017-07-13 17:00 | 7 | 17 | 1305.8721 | 1305.8721
2017-07-13 18:00 | 7 | 18 | 319.7149 | 319.7149
2017-07-13 19:00 | 7 | 19 | 0 | 0
2017-07-13 20:00 | 7 | 20 | 0 | 0
2017-07-13 21:00 | 7 | 21 | 0 | 0
2017-07-13 22:00 | 7 | 22 | 0 | 0
2017-07-13 23:00 | 7 | 23 | 0 | 0
2017-07-14 | 7 | 0 | 0 | 0
2017-07-14 01:00 | 7 | 1 | 0 | 0
2017-07-14 02:00 | 7 | 2 | 0 | 0
2017-07-14 03:00 | 7 | 3 | 0 | 0
2017-07-14 04:00 | 7 | 4 | 0 | 0
2017-07-14 05:00 | 7 | 5 | 330.8469 | 330.8469
2017-07-14 06:00 | 7 | 6 | 724.761 | 724.761
2017-07-14 07:00 | 7 | 7 | 2309.0263 | 2309.0263
2017-07-14 08:00 | 7 | 8 | 5325.2211 | 5325.2211
2017-07-14 09:00 | 7 | 9 | 6481.5288 | 6481.5288
2017-07-14 10:00 | 7 | 10 | 6101.1732 | 6101.1732
2017-07-14 11:00 | 7 | 11 | 6078.4929 | 6078.4929
2017-07-14 12:00 | 7 | 12 | 3229.982 | 3229.982
2017-07-14 13:00 | 7 | 13 | 1973.822 | 1973.822
2017-07-14 14:00 | 7 | 14 | 5104.1232 | 5104.1232
2017-07-14 15:00 | 7 | 15 | 2690.3525 | 2690.3525
2017-07-14 16:00 | 7 | 16 | 205.4601 | 205.4601
2017-07-14 17:00 | 7 | 17 | 1234.2432 | 1234.2432
2017-07-14 18:00 | 7 | 18 | 332.8974 | 332.8974
2017-07-14 19:00 | 7 | 19 | 0 | 0
2017-07-14 20:00 | 7 | 20 | 0 | 0
2017-07-14 21:00 | 7 | 21 | 0 | 0
2017-07-14 22:00 | 7 | 22 | 0 | 0
2017-07-14 23:00 | 7 | 23 | 0 | 0
2017-07-15 | 7 | 0 | 0 | 0
2017-07-15 01:00 | 7 | 1 | 0 | 0
2017-07-15 02:00 | 7 | 2 | 0 | 0
2017-07-15 03:00 | 7 | 3 | 0 | 0
2017-07-15 04:00 | 7 | 4 | 0 | 0
2017-07-15 05:00 | 7 | 5 | 300.733 | 300.733
2017-07-15 06:00 | 7 | 6 | 530.3489 | 530.3489
2017-07-15 07:00 | 7 | 7 | 3473.4497 | 3473.4497
2017-07-15 08:00 | 7 | 8 | 3246.2269 | 3246.2269
2017-07-15 09:00 | 7 | 9 | 3462.9225 | 3462.9226
2017-07-15 10:00 | 7 | 10 | 4577.3369 | 4577.3369
2017-07-15 11:00 | 7 | 11 | 6485.6688 | 6485.6688
2017-07-15 12:00 | 7 | 12 | 4146.9276 | 4146.9276
2017-07-15 13:00 | 7 | 13 | 1650.7894 | 1650.7893
2017-07-15 14:00 | 7 | 14 | 2749.9524 | 2749.9524
2017-07-15 15:00 | 7 | 15 | 3491.7645 | 3491.7645
2017-07-15 16:00 | 7 | 16 | 709.3947 | 709.3947
2017-07-15 17:00 | 7 | 17 | 1426.6049 | 1426.6049
2017-07-15 18:00 | 7 | 18 | 328.8575 | 328.8575
2017-07-15 19:00 | 7 | 19 | 0 | 0
2017-07-15 20:00 | 7 | 20 | 0 | 0
2017-07-15 21:00 | 7 | 21 | 0 | 0
2017-07-15 22:00 | 7 | 22 | 0 | 0
2017-07-15 23:00 | 7 | 23 | 0 | 0
2017-07-16 | 7 | 0 | 0 | 0
2017-07-16 01:00 | 7 | 1 | 0 | 0
2017-07-16 02:00 | 7 | 2 | 0 | 0
2017-07-16 03:00 | 7 | 3 | 0 | 0
2017-07-16 04:00 | 7 | 4 | 0 | 0
2017-07-16 05:00 | 7 | 5 | 500.9273 | 500.9273
2017-07-16 06:00 | 7 | 6 | 813.2639 | 813.2639
2017-07-16 07:00 | 7 | 7 | 528.0363 | 528.0363
2017-07-16 08:00 | 7 | 8 | 344.8356 | 344.8356
2017-07-16 09:00 | 7 | 9 | 1835.8623 | 1835.8623
2017-07-16 10:00 | 7 | 10 | 4534.3741 | 4534.3741
2017-07-16 11:00 | 7 | 11 | 1478.0697 | 1478.0697
2017-07-16 12:00 | 7 | 12 | 3128.1253 | 3128.1253
2017-07-16 13:00 | 7 | 13 | 2820.6774 | 2820.6774
2017-07-16 14:00 | 7 | 14 | 1600.9564 | 1600.9564
2017-07-16 15:00 | 7 | 15 | 1901.2766 | 1901.2766
2017-07-16 16:00 | 7 | 16 | 957.6268 | 957.6268
2017-07-16 17:00 | 7 | 17 | 1079.7614 | 1079.7614
2017-07-16 18:00 | 7 | 18 | 306.6199 | 306.6199
2017-07-16 19:00 | 7 | 19 | 0 | 0
2017-07-16 20:00 | 7 | 20 | 0 | 0
2017-07-16 21:00 | 7 | 21 | 0 | 0
2017-07-16 22:00 | 7 | 22 | 0 | 0
2017-07-16 23:00 | 7 | 23 | 0 | 0
2017-07-17 | 7 | 0 | 0 | 0
2017-07-17 01:00 | 7 | 1 | 0 | 0
2017-07-17 02:00 | 7 | 2 | 0 | 0
2017-07-17 03:00 | 7 | 3 | 0 | 0
2017-07-17 04:00 | 7 | 4 | 0 | 0
2017-07-17 05:00 | 7 | 5 | 537.4008 | 537.4008
2017-07-17 06:00 | 7 | 6 | 1309.1105 | 1309.1105
2017-07-17 07:00 | 7 | 7 | 2938.5467 | 2938.5467
2017-07-17 08:00 | 7 | 8 | 5528.7251 | 5528.7251
2017-07-17 09:00 | 7 | 9 | 5815.8927 | 5815.8927
2017-07-17 10:00 | 7 | 10 | 6994.8635 | 6994.8635
2017-07-17 11:00 | 7 | 11 | 6735.2487 | 6735.2487
2017-07-17 12:00 | 7 | 12 | 6516.4129 | 6516.4129
2017-07-17 13:00 | 7 | 13 | 5995.1673 | 5995.1673
2017-07-17 14:00 | 7 | 14 | 5676.9646 | 5676.9646
2017-07-17 15:00 | 7 | 15 | 4453.36 | 4453.36
2017-07-17 16:00 | 7 | 16 | 2516.6634 | 2516.6634
2017-07-17 17:00 | 7 | 17 | 1308.4758 | 1308.4758
2017-07-17 18:00 | 7 | 18 | 237.8418 | 237.8418
2017-07-17 19:00 | 7 | 19 | 0 | 0
2017-07-17 20:00 | 7 | 20 | 0 | 0
2017-07-17 21:00 | 7 | 21 | 0 | 0
2017-07-17 22:00 | 7 | 22 | 0 | 0
2017-07-17 23:00 | 7 | 23 | 0 | 0
2017-07-18 | 7 | 0 | 0 | 0
2017-07-18 01:00 | 7 | 1 | 0 | 0
2017-07-18 02:00 | 7 | 2 | 0 | 0
2017-07-18 03:00 | 7 | 3 | 0 | 0
2017-07-18 04:00 | 7 | 4 | 0 | 0
2017-07-18 05:00 | 7 | 5 | 455.8887 | 455.8887
2017-07-18 06:00 | 7 | 6 | 2046.4411 | 2046.4411
2017-07-18 07:00 | 7 | 7 | 4019.6226 | 4019.6226
2017-07-18 08:00 | 7 | 8 | 5708.8104 | 5708.8104
2017-07-18 09:00 | 7 | 9 | 6913.5401 | 6913.5401
2017-07-18 10:00 | 7 | 10 | 7597.2772 | 7597.2772
2017-07-18 11:00 | 7 | 11 | 6738.9321 | 6738.9321
2017-07-18 12:00 | 7 | 12 | 7811.6349 | 7811.6349
2017-07-18 13:00 | 7 | 13 | 7082.6706 | 7082.6706
2017-07-18 14:00 | 7 | 14 | 6122.347 | 6122.347
2017-07-18 15:00 | 7 | 15 | 4780.3304 | 4780.3304
2017-07-18 16:00 | 7 | 16 | 3115.5087 | 3115.5087
2017-07-18 17:00 | 7 | 17 | 1378.1473 | 1378.1473
2017-07-18 18:00 | 7 | 18 | 252.0156 | 252.0156
2017-07-18 19:00 | 7 | 19 | 0 | 0
2017-07-18 20:00 | 7 | 20 | 0 | 0
2017-07-18 21:00 | 7 | 21 | 0 | 0
2017-07-18 22:00 | 7 | 22 | 0 | 0
2017-07-18 23:00 | 7 | 23 | 0 | 0
2017-07-19 | 7 | 0 | 0 | 0
2017-07-19 01:00 | 7 | 1 | 0 | 0
2017-07-19 02:00 | 7 | 2 | 0 | 0
2017-07-19 03:00 | 7 | 3 | 0 | 0
2017-07-19 04:00 | 7 | 4 | 0 | 0
2017-07-19 05:00 | 7 | 5 | 475.9033 | 475.9033
2017-07-19 06:00 | 7 | 6 | 1905.0773 | 1905.0774
2017-07-19 07:00 | 7 | 7 | 2670.3805 | 2670.3805
2017-07-19 08:00 | 7 | 8 | 4610.8537 | 4610.8537
2017-07-19 09:00 | 7 | 9 | 5304.6855 | 5304.6855
2017-07-19 10:00 | 7 | 10 | 4581.447 | 4581.447
2017-07-19 11:00 | 7 | 11 | 6064.3697 | 6064.3697
2017-07-19 12:00 | 7 | 12 | 4504.2383 | 4504.2383
2017-07-19 13:00 | 7 | 13 | 5648.6321 | 5648.6321
2017-07-19 14:00 | 7 | 14 | 2864.8535 | 2864.8535
2017-07-19 15:00 | 7 | 15 | 2496.7006 | 2496.7006
2017-07-19 16:00 | 7 | 16 | 1526.0523 | 1526.0523
2017-07-19 17:00 | 7 | 17 | 850.3594 | 850.3594
2017-07-19 18:00 | 7 | 18 | 235.7672 | 235.7672
2017-07-19 19:00 | 7 | 19 | 0 | 0
2017-07-19 20:00 | 7 | 20 | 0 | 0
2017-07-19 21:00 | 7 | 21 | 0 | 0
2017-07-19 22:00 | 7 | 22 | 0 | 0
2017-07-19 23:00 | 7 | 23 | 0 | 0
2017-07-20 | 7 | 0 | 0 | 0
2017-07-20 01:00 | 7 | 1 | 0 | 0
2017-07-20 02:00 | 7 | 2 | 0 | 0
2017-07-20 03:00 | 7 | 3 | 0 | 0
2017-07-20 04:00 | 7 | 4 | 0 | 0
2017-07-20 05:00 | 7 | 5 | 501.3747 | 501.3747
2017-07-20 06:00 | 7 | 6 | 1416.179 | 1416.179
2017-07-20 07:00 | 7 | 7 | 1584.8483 | 1584.8483
2017-07-20 08:00 | 7 | 8 | 1380.8809 | 1380.8809
2017-07-20 09:00 | 7 | 9 | 4285.176 | 4285.176
2017-07-20 10:00 | 7 | 10 | 2995.5924 | 2995.5924
2017-07-20 11:00 | 7 | 11 | 5786.0352 | 5786.0352
2017-07-20 12:00 | 7 | 12 | 6394.4508 | 6394.4508
2017-07-20 13:00 | 7 | 13 | 7307.215 | 7307.215
2017-07-20 14:00 | 7 | 14 | 5048.1113 | 5048.1113
2017-07-20 15:00 | 7 | 15 | 4359.2383 | 4359.2383
2017-07-20 16:00 | 7 | 16 | 3213.4013 | 3213.4013
2017-07-20 17:00 | 7 | 17 | 1359.2908 | 1359.2908
2017-07-20 18:00 | 7 | 18 | 241.6483 | 241.6483
2017-07-20 19:00 | 7 | 19 | 0 | 0
2017-07-20 20:00 | 7 | 20 | 0 | 0
2017-07-20 21:00 | 7 | 21 | 0 | 0
2017-07-20 22:00 | 7 | 22 | 0 | 0
2017-07-20 23:00 | 7 | 23 | 0 | 0
2017-07-21 | 7 | 0 | 0 | 0
2017-07-21 01:00 | 7 | 1 | 0 | 0
2017-07-21 02:00 | 7 | 2 | 0 | 0
2017-07-21 03:00 | 7 | 3 | 0 | 0
2017-07-21 04:00 | 7 | 4 | 0 | 0
2017-07-21 05:00 | 7 | 5 | 477.4236 | 477.4236
2017-07-21 06:00 | 7 | 6 | 1973.2896 | 1973.2896
2017-07-21 07:00 | 7 | 7 | 3845.6701 | 3845.6701
2017-07-21 08:00 | 7 | 8 | 5491.1051 | 5491.1051
2017-07-21 09:00 | 7 | 9 | 6722.862 | 6722.862
2017-07-21 10:00 | 7 | 10 | 7507.1816 | 7507.1816
2017-07-21 11:00 | 7 | 11 | 7817.7931 | 7817.7931
2017-07-21 12:00 | 7 | 12 | 7733.6672 | 7733.6672
2017-07-21 13:00 | 7 | 13 | 7234.8581 | 7234.8581
2017-07-21 14:00 | 7 | 14 | 6279.2369 | 6279.2369
2017-07-21 15:00 | 7 | 15 | 4906.0518 | 4906.0518
2017-07-21 16:00 | 7 | 16 | 3178.5045 | 3178.5045
2017-07-21 17:00 | 7 | 17 | 1343.2851 | 1343.2851
2017-07-21 18:00 | 7 | 18 | 232.6887 | 232.6887
2017-07-21 19:00 | 7 | 19 | 0 | 0
2017-07-21 20:00 | 7 | 20 | 0 | 0
2017-07-21 21:00 | 7 | 21 | 0 | 0
2017-07-21 22:00 | 7 | 22 | 0 | 0
2017-07-21 23:00 | 7 | 23 | 0 | 0
2017-07-22 | 7 | 0 | 0 | 0
2017-07-22 01:00 | 7 | 1 | 0 | 0
2017-07-22 02:00 | 7 | 2 | 0 | 0
2017-07-22 03:00 | 7 | 3 | 0 | 0
2017-07-22 04:00 | 7 | 4 | 0 | 0
2017-07-22 05:00 | 7 | 5 | 469.3598 | 469.3598
2017-07-22 06:00 | 7 | 6 | 1882.0934 | 1882.0934
2017-07-22 07:00 | 7 | 7 | 3693.5125 | 3693.5125
2017-07-22 08:00 | 7 | 8 | 5223.5909 | 5223.5909
2017-07-22 09:00 | 7 | 9 | 6390.2395 | 6390.2395
2017-07-22 10:00 | 7 | 10 | 7125.4023 | 7125.4023
2017-07-22 11:00 | 7 | 11 | 7454.6749 | 7454.6749
2017-07-22 12:00 | 7 | 12 | 7315.3133 | 7315.3133
2017-07-22 13:00 | 7 | 13 | 6790.221 | 6790.221
2017-07-22 14:00 | 7 | 14 | 5862.0353 | 5862.0353
2017-07-22 15:00 | 7 | 15 | 1319.0086 | 1319.0086
2017-07-22 16:00 | 7 | 16 | 2989.3387 | 2989.3387
2017-07-22 17:00 | 7 | 17 | 1330.3913 | 1330.3913
2017-07-22 18:00 | 7 | 18 | 260.6187 | 260.6187
2017-07-22 19:00 | 7 | 19 | 0 | 0
2017-07-22 20:00 | 7 | 20 | 0 | 0
2017-07-22 21:00 | 7 | 21 | 0 | 0
2017-07-22 22:00 | 7 | 22 | 0 | 0
2017-07-22 23:00 | 7 | 23 | 0 | 0
2017-07-23 | 7 | 0 | 0 | 0
2017-07-23 01:00 | 7 | 1 | 0 | 0
2017-07-23 02:00 | 7 | 2 | 0 | 0
2017-07-23 03:00 | 7 | 3 | 0 | 0
2017-07-23 04:00 | 7 | 4 | 0 | 0
2017-07-23 05:00 | 7 | 5 | 531.5081 | 531.5081
2017-07-23 06:00 | 7 | 6 | 1863.4623 | 1863.4623
2017-07-23 07:00 | 7 | 7 | 3528.2115 | 3528.2115
2017-07-23 08:00 | 7 | 8 | 5056.6109 | 5056.6109
2017-07-23 09:00 | 7 | 9 | 6275.5948 | 6275.5948
2017-07-23 10:00 | 7 | 10 | 7255.9641 | 7255.9641
2017-07-23 11:00 | 7 | 11 | 7530.6335 | 7530.6336
2017-07-23 12:00 | 7 | 12 | 7474.0547 | 7474.0547
2017-07-23 13:00 | 7 | 13 | 6923.8889 | 6923.8889
2017-07-23 14:00 | 7 | 14 | 6020.7054 | 6020.7054
2017-07-23 15:00 | 7 | 15 | 4677.7722 | 4677.7722
2017-07-23 16:00 | 7 | 16 | 2911.7942 | 2911.7942
2017-07-23 17:00 | 7 | 17 | 1312.9194 | 1312.9194
2017-07-23 18:00 | 7 | 18 | 266.2273 | 266.2273
2017-07-23 19:00 | 7 | 19 | 0 | 0
2017-07-23 20:00 | 7 | 20 | 0 | 0
2017-07-23 21:00 | 7 | 21 | 0 | 0
2017-07-23 22:00 | 7 | 22 | 0 | 0
2017-07-23 23:00 | 7 | 23 | 0 | 0
2017-07-24 | 7 | 0 | 0 | 0
2017-07-24 01:00 | 7 | 1 | 0 | 0
2017-07-24 02:00 | 7 | 2 | 0 | 0
2017-07-24 03:00 | 7 | 3 | 0 | 0
2017-07-24 04:00 | 7 | 4 | 0 | 0
2017-07-24 05:00 | 7 | 5 | 464.186 | 464.186
2017-07-24 06:00 | 7 | 6 | 1893.6739 | 1893.6739
2017-07-24 07:00 | 7 | 7 | 1595.0764 | 1595.0764
2017-07-24 08:00 | 7 | 8 | 762.642 | 762.642
2017-07-24 09:00 | 7 | 9 | 1850.1315 | 1850.1315
2017-07-24 10:00 | 7 | 10 | 2215.2461 | 2215.2461
2017-07-24 11:00 | 7 | 11 | 4224.9769 | 4224.9769
2017-07-24 12:00 | 7 | 12 | 5517.0732 | 5517.0732
2017-07-24 13:00 | 7 | 13 | 6049 | 6049
2017-07-24 14:00 | 7 | 14 | 4511.1659 | 4511.1659
2017-07-24 15:00 | 7 | 15 | 2977.7364 | 2977.7364
2017-07-24 16:00 | 7 | 16 | 3019.6677 | 3019.6677
2017-07-24 17:00 | 7 | 17 | 1241.6573 | 1241.6573
2017-07-24 18:00 | 7 | 18 | 210.6834 | 210.6834
2017-07-24 19:00 | 7 | 19 | 0 | 0
2017-07-24 20:00 | 7 | 20 | 0 | 0
2017-07-24 21:00 | 7 | 21 | 0 | 0
2017-07-24 22:00 | 7 | 22 | 0 | 0
2017-07-24 23:00 | 7 | 23 | 0 | 0
2017-07-25 | 7 | 0 | 0 | 0
2017-07-25 01:00 | 7 | 1 | 0 | 0
2017-07-25 02:00 | 7 | 2 | 0 | 0
2017-07-25 03:00 | 7 | 3 | 0 | 0
2017-07-25 04:00 | 7 | 4 | 0 | 0
2017-07-25 05:00 | 7 | 5 | 376.0672 | 376.0672
2017-07-25 06:00 | 7 | 6 | 1995.9193 | 1995.9193
2017-07-25 07:00 | 7 | 7 | 4017.6285 | 4017.6285
2017-07-25 08:00 | 7 | 8 | 5673.9827 | 5673.9827
2017-07-25 09:00 | 7 | 9 | 6840.9026 | 6840.9026
2017-07-25 10:00 | 7 | 10 | 7500.7439 | 7500.7439
2017-07-25 11:00 | 7 | 11 | 7768.411 | 7768.411
2017-07-25 12:00 | 7 | 12 | 7662.1406 | 7662.1406
2017-07-25 13:00 | 7 | 13 | 6921.4923 | 6921.4923
2017-07-25 14:00 | 7 | 14 | 5982.7209 | 5982.7209
2017-07-25 15:00 | 7 | 15 | 4661.4158 | 4661.4158
2017-07-25 16:00 | 7 | 16 | 2992.9405 | 2992.9405
2017-07-25 17:00 | 7 | 17 | 1294.7827 | 1294.7827
2017-07-25 18:00 | 7 | 18 | 210.6651 | 210.6651
2017-07-25 19:00 | 7 | 19 | 0 | 0
2017-07-25 20:00 | 7 | 20 | 0 | 0
2017-07-25 21:00 | 7 | 21 | 0 | 0
2017-07-25 22:00 | 7 | 22 | 0 | 0
2017-07-25 23:00 | 7 | 23 | 0 | 0
2017-07-26 | 7 | 0 | 0 | 0
2017-07-26 01:00 | 7 | 1 | 0 | 0
2017-07-26 02:00 | 7 | 2 | 0 | 0
2017-07-26 03:00 | 7 | 3 | 0 | 0
2017-07-26 04:00 | 7 | 4 | 0 | 0
2017-07-26 05:00 | 7 | 5 | 449.5247 | 449.5247
2017-07-26 06:00 | 7 | 6 | 1439.7517 | 1439.7517
2017-07-26 07:00 | 7 | 7 | 3154.9238 | 3154.9238
2017-07-26 08:00 | 7 | 8 | 4603.3465 | 4603.3465
2017-07-26 09:00 | 7 | 9 | 6629.9581 | 6629.9581
2017-07-26 10:00 | 7 | 10 | 7456.723 | 7456.723
2017-07-26 11:00 | 7 | 11 | 7796.6205 | 7796.6205
2017-07-26 12:00 | 7 | 12 | 7660.7526 | 7660.7526
2017-07-26 13:00 | 7 | 13 | 6107.351 | 6107.351
2017-07-26 14:00 | 7 | 14 | 4249.2787 | 4249.2787
2017-07-26 15:00 | 7 | 15 | 3909.5963 | 3909.5963
2017-07-26 16:00 | 7 | 16 | 2787.7932 | 2787.7932
2017-07-26 17:00 | 7 | 17 | 1312.8457 | 1312.8457
2017-07-26 18:00 | 7 | 18 | 255.5829 | 255.5829
2017-07-26 19:00 | 7 | 19 | 0 | 0
2017-07-26 20:00 | 7 | 20 | 0 | 0
2017-07-26 21:00 | 7 | 21 | 0 | 0
2017-07-26 22:00 | 7 | 22 | 0 | 0
2017-07-26 23:00 | 7 | 23 | 0 | 0
2017-07-27 | 7 | 0 | 0 | 0
2017-07-27 01:00 | 7 | 1 | 0 | 0
2017-07-27 02:00 | 7 | 2 | 0 | 0
2017-07-27 03:00 | 7 | 3 | 0 | 0
2017-07-27 04:00 | 7 | 4 | 0 | 0
2017-07-27 05:00 | 7 | 5 | 438.0798 | 438.0798
2017-07-27 06:00 | 7 | 6 | 1091.6432 | 1091.6432
2017-07-27 07:00 | 7 | 7 | 2283.4205 | 2283.4205
2017-07-27 08:00 | 7 | 8 | 5193.3494 | 5193.3494
2017-07-27 09:00 | 7 | 9 | 3911.8572 | 3911.8572
2017-07-27 10:00 | 7 | 10 | 527.6234 | 527.6234
2017-07-27 11:00 | 7 | 11 | 963.4389 | 963.4389
2017-07-27 12:00 | 7 | 12 | 2347.334 | 2347.334
2017-07-27 13:00 | 7 | 13 | 3937.002 | 3937.002
2017-07-27 14:00 | 7 | 14 | 3361.3683 | 3361.3683
2017-07-27 15:00 | 7 | 15 | 3211.4509 | 3211.4509
2017-07-27 16:00 | 7 | 16 | 3016.7248 | 3016.7248
2017-07-27 17:00 | 7 | 17 | 1211.7677 | 1211.7677
2017-07-27 18:00 | 7 | 18 | 192.717 | 192.717
2017-07-27 19:00 | 7 | 19 | 0 | 0
2017-07-27 20:00 | 7 | 20 | 0 | 0
2017-07-27 21:00 | 7 | 21 | 0 | 0
2017-07-27 22:00 | 7 | 22 | 0 | 0
2017-07-27 23:00 | 7 | 23 | 0 | 0
2017-07-28 | 7 | 0 | 0 | 0
2017-07-28 01:00 | 7 | 1 | 0 | 0
2017-07-28 02:00 | 7 | 2 | 0 | 0
2017-07-28 03:00 | 7 | 3 | 0 | 0
2017-07-28 04:00 | 7 | 4 | 0 | 0
2017-07-28 05:00 | 7 | 5 | 353.5031 | 353.5031
2017-07-28 06:00 | 7 | 6 | 718.8328 | 718.8328
2017-07-28 07:00 | 7 | 7 | 158.516 | 158.516
2017-07-28 08:00 | 7 | 8 | 3162.9036 | 3162.9036
2017-07-28 09:00 | 7 | 9 | 5466.3283 | 5466.3283
2017-07-28 10:00 | 7 | 10 | 4889.8391 | 4889.8391
2017-07-28 11:00 | 7 | 11 | 7675.9545 | 7675.9545
2017-07-28 12:00 | 7 | 12 | 5817.7971 | 5817.7971
2017-07-28 13:00 | 7 | 13 | 7073.9766 | 7073.9766
2017-07-28 14:00 | 7 | 14 | 6106.1745 | 6106.1745
2017-07-28 15:00 | 7 | 15 | 4767.6263 | 4767.6263
2017-07-28 16:00 | 7 | 16 | 3030.856 | 3030.856
2017-07-28 17:00 | 7 | 17 | 1277.0117 | 1277.0117
2017-07-28 18:00 | 7 | 18 | 244.314 | 244.3141
2017-07-28 19:00 | 7 | 19 | 0 | 0
2017-07-28 20:00 | 7 | 20 | 0 | 0
2017-07-28 21:00 | 7 | 21 | 0 | 0
2017-07-28 22:00 | 7 | 22 | 0 | 0
2017-07-28 23:00 | 7 | 23 | 0 | 0
2017-07-29 | 7 | 0 | 0 | 0
2017-07-29 01:00 | 7 | 1 | 0 | 0
2017-07-29 02:00 | 7 | 2 | 0 | 0
2017-07-29 03:00 | 7 | 3 | 0 | 0
2017-07-29 04:00 | 7 | 4 | 0 | 0
2017-07-29 05:00 | 7 | 5 | 323.7629 | 323.7629
2017-07-29 06:00 | 7 | 6 | 1557.6382 | 1557.6382
2017-07-29 07:00 | 7 | 7 | 3950.9043 | 3950.9043
2017-07-29 08:00 | 7 | 8 | 5652.112 | 5652.112
2017-07-29 09:00 | 7 | 9 | 6913.8299 | 6913.8299
2017-07-29 10:00 | 7 | 10 | 7675.7095 | 7675.7095
2017-07-29 11:00 | 7 | 11 | 7977.0635 | 7977.0636
2017-07-29 12:00 | 7 | 12 | 7860.4811 | 7860.4811
2017-07-29 13:00 | 7 | 13 | 5225.677 | 5225.677
2017-07-29 14:00 | 7 | 14 | 2296.5891 | 2296.5891
2017-07-29 15:00 | 7 | 15 | 1982.6885 | 1982.6885
2017-07-29 16:00 | 7 | 16 | 2199.8775 | 2199.8775
2017-07-29 17:00 | 7 | 17 | 1099.3586 | 1099.3586
2017-07-29 18:00 | 7 | 18 | 225.8048 | 225.8048
2017-07-29 19:00 | 7 | 19 | 0 | 0
2017-07-29 20:00 | 7 | 20 | 0 | 0
2017-07-29 21:00 | 7 | 21 | 0 | 0
2017-07-29 22:00 | 7 | 22 | 0 | 0
2017-07-29 23:00 | 7 | 23 | 0 | 0
2017-07-30 | 7 | 0 | 0 | 0
2017-07-30 01:00 | 7 | 1 | 0 | 0
2017-07-30 02:00 | 7 | 2 | 0 | 0
2017-07-30 03:00 | 7 | 3 | 0 | 0
2017-07-30 04:00 | 7 | 4 | 0 | 0
2017-07-30 05:00 | 7 | 5 | 349.8219 | 349.8219
2017-07-30 06:00 | 7 | 6 | 1614.7725 | 1614.7725
2017-07-30 07:00 | 7 | 7 | 3698.4081 | 3698.408
2017-07-30 08:00 | 7 | 8 | 5364.5246 | 5364.5246
2017-07-30 09:00 | 7 | 9 | 6576.6533 | 6576.6533
2017-07-30 10:00 | 7 | 10 | 3876.4119 | 3876.412
2017-07-30 11:00 | 7 | 11 | 5935.9378 | 5935.9378
2017-07-30 12:00 | 7 | 12 | 7639.4546 | 7639.4546
2017-07-30 13:00 | 7 | 13 | 6401.5635 | 6401.5635
2017-07-30 14:00 | 7 | 14 | 6072.2334 | 6072.2334
2017-07-30 15:00 | 7 | 15 | 4696.3194 | 4696.3194
2017-07-30 16:00 | 7 | 16 | 2166.0307 | 2166.0307
2017-07-30 17:00 | 7 | 17 | 1294.1433 | 1294.1433
2017-07-30 18:00 | 7 | 18 | 218.5357 | 218.5356
2017-07-30 19:00 | 7 | 19 | 0 | 0
2017-07-30 20:00 | 7 | 20 | 0 | 0
2017-07-30 21:00 | 7 | 21 | 0 | 0
2017-07-30 22:00 | 7 | 22 | 0 | 0
2017-07-30 23:00 | 7 | 23 | 0 | 0
2017-07-31 | 7 | 0 | 0 | 0
2017-07-31 01:00 | 7 | 1 | 0 | 0
2017-07-31 02:00 | 7 | 2 | 0 | 0
2017-07-31 03:00 | 7 | 3 | 0 | 0
2017-07-31 04:00 | 7 | 4 | 0 | 0
2017-07-31 05:00 | 7 | 5 | 430.2518 | 430.2518
2017-07-31 06:00 | 7 | 6 | 1825.0741 | 1825.0741
2017-07-31 07:00 | 7 | 7 | 3662.3636 | 3662.3636
2017-07-31 08:00 | 7 | 8 | 5290.7452 | 5290.7452
2017-07-31 09:00 | 7 | 9 | 6513.2527 | 6513.2527
2017-07-31 10:00 | 7 | 10 | 7231.1712 | 7231.1712
2017-07-31 11:00 | 7 | 11 | 6687.6904 | 6687.6904
2017-07-31 12:00 | 7 | 12 | 6651.0054 | 6651.0054
2017-07-31 13:00 | 7 | 13 | 3905.2114 | 3905.2114
2017-07-31 14:00 | 7 | 14 | 6084.3855 | 6084.3855
2017-07-31 15:00 | 7 | 15 | 4652.1145 | 4652.1145
2017-07-31 16:00 | 7 | 16 | 2960.1793 | 2960.1793
2017-07-31 17:00 | 7 | 17 | 1270.4062 | 1270.4062
2017-07-31 18:00 | 7 | 18 | 203.1797 | 203.1797
2017-07-31 19:00 | 7 | 19 | 0 | 0
2017-07-31 20:00 | 7 | 20 | 0 | 0
2017-07-31 21:00 | 7 | 21 | 0 | 0
2017-07-31 22:00 | 7 | 22 | 0 | 0
2017-07-31 23:00 | 7 | 23 | 0 | 0
2017-08-01 | 8 | 0 | 0 | 0
2017-08-01 01:00 | 8 | 1 | 0 | 0
2017-08-01 02:00 | 8 | 2 | 0 | 0
2017-08-01 03:00 | 8 | 3 | 0 | 0
2017-08-01 04:00 | 8 | 4 | 0 | 0
2017-08-01 05:00 | 8 | 5 | 313.4705 | 313.4705
2017-08-01 06:00 | 8 | 6 | 1912.7375 | 1912.7375
2017-08-01 07:00 | 8 | 7 | 4003.3121 | 4003.3121
2017-08-01 08:00 | 8 | 8 | 5760.5248 | 5760.5248
2017-08-01 09:00 | 8 | 9 | 7026.1688 | 7026.1688
2017-08-01 10:00 | 8 | 10 | 7848.7764 | 7848.7764
2017-08-01 11:00 | 8 | 11 | 8172.0219 | 8172.0219
2017-08-01 12:00 | 8 | 12 | 8079.9782 | 8079.9782
2017-08-01 13:00 | 8 | 13 | 7544.3013 | 7544.3013
2017-08-01 14:00 | 8 | 14 | 6541.3449 | 6541.3449
2017-08-01 15:00 | 8 | 15 | 5081.7821 | 5081.7821
2017-08-01 16:00 | 8 | 16 | 3201.1446 | 3201.1446
2017-08-01 17:00 | 8 | 17 | 1207.945 | 1207.945
2017-08-01 18:00 | 8 | 18 | 133.0791 | 133.0791
2017-08-01 19:00 | 8 | 19 | 0 | 0
2017-08-01 20:00 | 8 | 20 | 0 | 0
2017-08-01 21:00 | 8 | 21 | 0 | 0
2017-08-01 22:00 | 8 | 22 | 0 | 0
2017-08-01 23:00 | 8 | 23 | 0 | 0
2017-08-02 | 8 | 0 | 0 | 0
2017-08-02 01:00 | 8 | 1 | 0 | 0
2017-08-02 02:00 | 8 | 2 | 0 | 0
2017-08-02 03:00 | 8 | 3 | 0 | 0
2017-08-02 04:00 | 8 | 4 | 0 | 0
2017-08-02 05:00 | 8 | 5 | 307.6871 | 307.6871
2017-08-02 06:00 | 8 | 6 | 1873.1775 | 1873.1775
2017-08-02 07:00 | 8 | 7 | 3921.3011 | 3921.3011
2017-08-02 08:00 | 8 | 8 | 5616.1446 | 5616.1446
2017-08-02 09:00 | 8 | 9 | 6863.4576 | 6863.4576
2017-08-02 10:00 | 8 | 10 | 7638.7059 | 7638.706
2017-08-02 11:00 | 8 | 11 | 7984.6972 | 7984.6972
2017-08-02 12:00 | 8 | 12 | 7848.8995 | 7848.8995
2017-08-02 13:00 | 8 | 13 | 7319.3912 | 7319.3912
2017-08-02 14:00 | 8 | 14 | 6340.2398 | 6340.2398
2017-08-02 15:00 | 8 | 15 | 4926.8933 | 4926.8933
2017-08-02 16:00 | 8 | 16 | 3107.2149 | 3107.2149
2017-08-02 17:00 | 8 | 17 | 1183.3097 | 1183.3097
2017-08-02 18:00 | 8 | 18 | 143.0462 | 143.0462
2017-08-02 19:00 | 8 | 19 | 0 | 0
2017-08-02 20:00 | 8 | 20 | 0 | 0
2017-08-02 21:00 | 8 | 21 | 0 | 0
2017-08-02 22:00 | 8 | 22 | 0 | 0
2017-08-02 23:00 | 8 | 23 | 0 | 0
2017-08-03 | 8 | 0 | 0 | 0
2017-08-03 01:00 | 8 | 1 | 0 | 0
2017-08-03 02:00 | 8 | 2 | 0 | 0
2017-08-03 03:00 | 8 | 3 | 0 | 0
2017-08-03 04:00 | 8 | 4 | 0 | 0
2017-08-03 05:00 | 8 | 5 | 366.551 | 366.551
2017-08-03 06:00 | 8 | 6 | 1717.5319 | 1717.5319
2017-08-03 07:00 | 8 | 7 | 3860.8892 | 3860.8892
2017-08-03 08:00 | 8 | 8 | 5557.766 | 5557.766
2017-08-03 09:00 | 8 | 9 | 6792.2231 | 6792.2231
2017-08-03 10:00 | 8 | 10 | 7563.6454 | 7563.6454
2017-08-03 11:00 | 8 | 11 | 7906.0315 | 7906.0315
2017-08-03 12:00 | 8 | 12 | 7764.8471 | 7764.8471
2017-08-03 13:00 | 8 | 13 | 7224.5795 | 7224.5795
2017-08-03 14:00 | 8 | 14 | 6253.2009 | 6253.2009
2017-08-03 15:00 | 8 | 15 | 4817.611 | 4817.611
2017-08-03 16:00 | 8 | 16 | 3013.4232 | 3013.4232
2017-08-03 17:00 | 8 | 17 | 1051.6037 | 1051.6037
2017-08-03 18:00 | 8 | 18 | 161.9487 | 161.9487
2017-08-03 19:00 | 8 | 19 | 0 | 0
2017-08-03 20:00 | 8 | 20 | 0 | 0
2017-08-03 21:00 | 8 | 21 | 0 | 0
2017-08-03 22:00 | 8 | 22 | 0 | 0
2017-08-03 23:00 | 8 | 23 | 0 | 0
2017-08-04 | 8 | 0 | 0 | 0
2017-08-04 01:00 | 8 | 1 | 0 | 0
2017-08-04 02:00 | 8 | 2 | 0 | 0
2017-08-04 03:00 | 8 | 3 | 0 | 0
2017-08-04 04:00 | 8 | 4 | 0 | 0
2017-08-04 05:00 | 8 | 5 | 350.9857 | 350.9857
2017-08-04 06:00 | 8 | 6 | 1795.2167 | 1795.2167
2017-08-04 07:00 | 8 | 7 | 3547.045 | 3547.045
2017-08-04 08:00 | 8 | 8 | 4051.6685 | 4051.6685
2017-08-04 09:00 | 8 | 9 | 5254.4926 | 5254.4926
2017-08-04 10:00 | 8 | 10 | 5510.1629 | 5510.1629
2017-08-04 11:00 | 8 | 11 | 6297.4701 | 6297.4701
2017-08-04 12:00 | 8 | 12 | 7132.4679 | 7132.4679
2017-08-04 13:00 | 8 | 13 | 6831.3967 | 6831.3967
2017-08-04 14:00 | 8 | 14 | 6217.7027 | 6217.7027
2017-08-04 15:00 | 8 | 15 | 4837.598 | 4837.598
2017-08-04 16:00 | 8 | 16 | 3044.9734 | 3044.9734
2017-08-04 17:00 | 8 | 17 | 1157.4899 | 1157.4899
2017-08-04 18:00 | 8 | 18 | 134.8478 | 134.8478
2017-08-04 19:00 | 8 | 19 | 0 | 0
2017-08-04 20:00 | 8 | 20 | 0 | 0
2017-08-04 21:00 | 8 | 21 | 0 | 0
2017-08-04 22:00 | 8 | 22 | 0 | 0
2017-08-04 23:00 | 8 | 23 | 0 | 0
2017-08-05 | 8 | 0 | 0 | 0
2017-08-05 01:00 | 8 | 1 | 0 | 0
2017-08-05 02:00 | 8 | 2 | 0 | 0
2017-08-05 03:00 | 8 | 3 | 0 | 0
2017-08-05 04:00 | 8 | 4 | 0 | 0
2017-08-05 05:00 | 8 | 5 | 348.7823 | 348.7823
2017-08-05 06:00 | 8 | 6 | 1583.8168 | 1583.8168
2017-08-05 07:00 | 8 | 7 | 2945.7031 | 2945.7031
2017-08-05 08:00 | 8 | 8 | 4723.0661 | 4723.0661
2017-08-05 09:00 | 8 | 9 | 5200.3483 | 5200.3483
2017-08-05 10:00 | 8 | 10 | 6406.3085 | 6406.3085
2017-08-05 11:00 | 8 | 11 | 6195.3789 | 6195.3789
2017-08-05 12:00 | 8 | 12 | 6243.9169 | 6243.9169
2017-08-05 13:00 | 8 | 13 | 5707.3753 | 5707.3753
2017-08-05 14:00 | 8 | 14 | 5484.9756 | 5484.9756
2017-08-05 15:00 | 8 | 15 | 4552.0231 | 4552.0231
2017-08-05 16:00 | 8 | 16 | 2278.6572 | 2278.6572
2017-08-05 17:00 | 8 | 17 | 1140.601 | 1140.601
2017-08-05 18:00 | 8 | 18 | 146.2823 | 146.2823
2017-08-05 19:00 | 8 | 19 | 0 | 0
2017-08-05 20:00 | 8 | 20 | 0 | 0
2017-08-05 21:00 | 8 | 21 | 0 | 0
2017-08-05 22:00 | 8 | 22 | 0 | 0
2017-08-05 23:00 | 8 | 23 | 0 | 0
2017-08-06 | 8 | 0 | 0 | 0
2017-08-06 01:00 | 8 | 1 | 0 | 0
2017-08-06 02:00 | 8 | 2 | 0 | 0
2017-08-06 03:00 | 8 | 3 | 0 | 0
2017-08-06 04:00 | 8 | 4 | 0 | 0
2017-08-06 05:00 | 8 | 5 | 324.1298 | 324.1298
2017-08-06 06:00 | 8 | 6 | 1418.2858 | 1418.2858
2017-08-06 07:00 | 8 | 7 | 3366.0684 | 3366.0684
2017-08-06 08:00 | 8 | 8 | 4581.5068 | 4581.5068
2017-08-06 09:00 | 8 | 9 | 5281.9097 | 5281.9097
2017-08-06 10:00 | 8 | 10 | 6514.2072 | 6514.2072
2017-08-06 11:00 | 8 | 11 | 7624.0365 | 7624.0365
2017-08-06 12:00 | 8 | 12 | 7475.7682 | 7475.7682
2017-08-06 13:00 | 8 | 13 | 4528.4873 | 4528.4873
2017-08-06 14:00 | 8 | 14 | 4961.0712 | 4961.0712
2017-08-06 15:00 | 8 | 15 | 915.469 | 915.469
2017-08-06 16:00 | 8 | 16 | 707.8227 | 707.8227
2017-08-06 17:00 | 8 | 17 | 265.8179 | 265.8179
2017-08-06 18:00 | 8 | 18 | 0 | 0
2017-08-06 19:00 | 8 | 19 | 0 | 0
2017-08-06 20:00 | 8 | 20 | 0 | 0
2017-08-06 21:00 | 8 | 21 | 0 | 0
2017-08-06 22:00 | 8 | 22 | 0 | 0
2017-08-06 23:00 | 8 | 23 | 0 | 0
2017-08-07 | 8 | 0 | 0 | 0
2017-08-07 01:00 | 8 | 1 | 0 | 0
2017-08-07 02:00 | 8 | 2 | 0 | 0
2017-08-07 03:00 | 8 | 3 | 0 | 0
2017-08-07 04:00 | 8 | 4 | 0 | 0
2017-08-07 05:00 | 8 | 5 | 0 | 0
2017-08-07 06:00 | 8 | 6 | 1316.0761 | 1316.0761
2017-08-07 07:00 | 8 | 7 | 2810.5275 | 2810.5275
2017-08-07 08:00 | 8 | 8 | 3659.2436 | 3659.2436
2017-08-07 09:00 | 8 | 9 | 4081.9319 | 4081.9319
2017-08-07 10:00 | 8 | 10 | 3712.2954 | 3712.2954
2017-08-07 11:00 | 8 | 11 | 4740.055 | 4740.055
2017-08-07 12:00 | 8 | 12 | 2894.8018 | 2894.8018
2017-08-07 13:00 | 8 | 13 | 5846.5563 | 5846.5563
2017-08-07 14:00 | 8 | 14 | 3170.8306 | 3170.8306
2017-08-07 15:00 | 8 | 15 | 2556.1671 | 2556.1671
2017-08-07 16:00 | 8 | 16 | 626.9099 | 626.9099
2017-08-07 17:00 | 8 | 17 | 790.5468 | 790.5468
2017-08-07 18:00 | 8 | 18 | 82.923 | 82.923
2017-08-07 19:00 | 8 | 19 | 0 | 0
2017-08-07 20:00 | 8 | 20 | 0 | 0
2017-08-07 21:00 | 8 | 21 | 0 | 0
2017-08-07 22:00 | 8 | 22 | 0 | 0
2017-08-07 23:00 | 8 | 23 | 0 | 0
2017-08-08 | 8 | 0 | 0 | 0
2017-08-08 01:00 | 8 | 1 | 0 | 0
2017-08-08 02:00 | 8 | 2 | 0 | 0
2017-08-08 03:00 | 8 | 3 | 0 | 0
2017-08-08 04:00 | 8 | 4 | 0 | 0
2017-08-08 05:00 | 8 | 5 | 312.0375 | 312.0375
2017-08-08 06:00 | 8 | 6 | 1699.8518 | 1699.8518
2017-08-08 07:00 | 8 | 7 | 3581.1471 | 3581.1471
2017-08-08 08:00 | 8 | 8 | 5258.5314 | 5258.5314
2017-08-08 09:00 | 8 | 9 | 6492.0559 | 6492.0559
2017-08-08 10:00 | 8 | 10 | 7258.9426 | 7258.9426
2017-08-08 11:00 | 8 | 11 | 7620.8303 | 7620.8303
2017-08-08 12:00 | 8 | 12 | 7505.3071 | 7505.3071
2017-08-08 13:00 | 8 | 13 | 7016.2098 | 7016.2098
2017-08-08 14:00 | 8 | 14 | 6042.0045 | 6042.0045
2017-08-08 15:00 | 8 | 15 | 4649.5121 | 4649.5121
2017-08-08 16:00 | 8 | 16 | 2888.785 | 2888.785
2017-08-08 17:00 | 8 | 17 | 1089.7802 | 1089.7802
2017-08-08 18:00 | 8 | 18 | 110.0147 | 110.0148
2017-08-08 19:00 | 8 | 19 | 0 | 0
2017-08-08 20:00 | 8 | 20 | 0 | 0
2017-08-08 21:00 | 8 | 21 | 0 | 0
2017-08-08 22:00 | 8 | 22 | 0 | 0
2017-08-08 23:00 | 8 | 23 | 0 | 0
2017-08-09 | 8 | 0 | 0 | 0
2017-08-09 01:00 | 8 | 1 | 0 | 0
2017-08-09 02:00 | 8 | 2 | 0 | 0
2017-08-09 03:00 | 8 | 3 | 0 | 0
2017-08-09 04:00 | 8 | 4 | 0 | 0
2017-08-09 05:00 | 8 | 5 | 280.2423 | 280.2423
2017-08-09 06:00 | 8 | 6 | 1724.6584 | 1724.6584
2017-08-09 07:00 | 8 | 7 | 3703.9867 | 3703.9867
2017-08-09 08:00 | 8 | 8 | 5382.3358 | 5382.3358
2017-08-09 09:00 | 8 | 9 | 6633.108 | 6633.108
2017-08-09 10:00 | 8 | 10 | 7361.1718 | 7361.1719
2017-08-09 11:00 | 8 | 11 | 7660.7618 | 7660.7618
2017-08-09 12:00 | 8 | 12 | 7564.1434 | 7564.1434
2017-08-09 13:00 | 8 | 13 | 7040.2252 | 7040.2253
2017-08-09 14:00 | 8 | 14 | 6113.6633 | 6113.6633
2017-08-09 15:00 | 8 | 15 | 4689.2837 | 4689.2837
2017-08-09 16:00 | 8 | 16 | 2894.8375 | 2894.8375
2017-08-09 17:00 | 8 | 17 | 1047.3602 | 1047.3602
2017-08-09 18:00 | 8 | 18 | 102.3879 | 102.3879
2017-08-09 19:00 | 8 | 19 | 0 | 0
2017-08-09 20:00 | 8 | 20 | 0 | 0
2017-08-09 21:00 | 8 | 21 | 0 | 0
2017-08-09 22:00 | 8 | 22 | 0 | 0
2017-08-09 23:00 | 8 | 23 | 0 | 0
2017-08-10 | 8 | 0 | 0 | 0
2017-08-10 01:00 | 8 | 1 | 0 | 0
2017-08-10 02:00 | 8 | 2 | 0 | 0
2017-08-10 03:00 | 8 | 3 | 0 | 0
2017-08-10 04:00 | 8 | 4 | 0 | 0
2017-08-10 05:00 | 8 | 5 | 316.9009 | 316.9009
2017-08-10 06:00 | 8 | 6 | 1663.4267 | 1663.4267
2017-08-10 07:00 | 8 | 7 | 3535.936 | 3535.936
2017-08-10 08:00 | 8 | 8 | 5220.6573 | 5220.6573
2017-08-10 09:00 | 8 | 9 | 6422.4176 | 6422.4176
2017-08-10 10:00 | 8 | 10 | 7202.8134 | 7202.8134
2017-08-10 11:00 | 8 | 11 | 7565.9822 | 7565.9822
2017-08-10 12:00 | 8 | 12 | 7491.79 | 7491.79
2017-08-10 13:00 | 8 | 13 | 4428.9915 | 4428.9915
2017-08-10 14:00 | 8 | 14 | 3127.5342 | 3127.5342
2017-08-10 15:00 | 8 | 15 | 4614.59 | 4614.59
2017-08-10 16:00 | 8 | 16 | 2787.2722 | 2787.2722
2017-08-10 17:00 | 8 | 17 | 1030.0849 | 1030.0849
2017-08-10 18:00 | 8 | 18 | 100.1431 | 100.1431
2017-08-10 19:00 | 8 | 19 | 0 | 0
2017-08-10 20:00 | 8 | 20 | 0 | 0
2017-08-10 21:00 | 8 | 21 | 0 | 0
2017-08-10 22:00 | 8 | 22 | 0 | 0
2017-08-10 23:00 | 8 | 23 | 0 | 0
2017-08-11 | 8 | 0 | 0 | 0
2017-08-11 01:00 | 8 | 1 | 0 | 0
2017-08-11 02:00 | 8 | 2 | 0 | 0
2017-08-11 03:00 | 8 | 3 | 0 | 0
2017-08-11 04:00 | 8 | 4 | 0 | 0
2017-08-11 05:00 | 8 | 5 | 160.4365 | 160.4365
2017-08-11 06:00 | 8 | 6 | 533.7966 | 533.7966
2017-08-11 07:00 | 8 | 7 | 2535.7742 | 2535.7742
2017-08-11 08:00 | 8 | 8 | 2118.2551 | 2118.2551
2017-08-11 09:00 | 8 | 9 | 2547.2005 | 2547.2005
2017-08-11 10:00 | 8 | 10 | 3629.7864 | 3629.7864
2017-08-11 11:00 | 8 | 11 | 4030.183 | 4030.183
2017-08-11 12:00 | 8 | 12 | 5315.7335 | 5315.7335
2017-08-11 13:00 | 8 | 13 | 4433.6789 | 4433.6789
2017-08-11 14:00 | 8 | 14 | 5904.4254 | 5904.4254
2017-08-11 15:00 | 8 | 15 | 3081.724 | 3081.724
2017-08-11 16:00 | 8 | 16 | 60.8143 | 60.8143
2017-08-11 17:00 | 8 | 17 | 911.7913 | 911.7913
2017-08-11 18:00 | 8 | 18 | 92.2024 | 92.2024
2017-08-11 19:00 | 8 | 19 | 0 | 0
2017-08-11 20:00 | 8 | 20 | 0 | 0
2017-08-11 21:00 | 8 | 21 | 0 | 0
2017-08-11 22:00 | 8 | 22 | 0 | 0
2017-08-11 23:00 | 8 | 23 | 0 | 0
2017-08-12 | 8 | 0 | 0 | 0
2017-08-12 01:00 | 8 | 1 | 0 | 0
2017-08-12 02:00 | 8 | 2 | 0 | 0
2017-08-12 03:00 | 8 | 3 | 0 | 0
2017-08-12 04:00 | 8 | 4 | 0 | 0
2017-08-12 05:00 | 8 | 5 | 0 | 0
2017-08-12 06:00 | 8 | 6 | 852.9193 | 852.9193
2017-08-12 07:00 | 8 | 7 | 2475.7246 | 2475.7246
2017-08-12 08:00 | 8 | 8 | 1516.3601 | 1516.3601
2017-08-12 09:00 | 8 | 9 | 988.1271 | 988.1271
2017-08-12 10:00 | 8 | 10 | 3596.3375 | 3596.3375
2017-08-12 11:00 | 8 | 11 | 2077.8706 | 2077.8706
2017-08-12 12:00 | 8 | 12 | 1370.8678 | 1370.8678
2017-08-12 13:00 | 8 | 13 | 1519.9561 | 1519.9561
2017-08-12 14:00 | 8 | 14 | 1729.1572 | 1729.1572
2017-08-12 15:00 | 8 | 15 | 2027.4189 | 2027.4189
2017-08-12 16:00 | 8 | 16 | 899.9992 | 899.9992
2017-08-12 17:00 | 8 | 17 | 418.6092 | 418.6092
2017-08-12 18:00 | 8 | 18 | 142.9565 | 142.9565
2017-08-12 19:00 | 8 | 19 | 0 | 0
2017-08-12 20:00 | 8 | 20 | 0 | 0
2017-08-12 21:00 | 8 | 21 | 0 | 0
2017-08-12 22:00 | 8 | 22 | 0 | 0
2017-08-12 23:00 | 8 | 23 | 0 | 0
2017-08-13 | 8 | 0 | 0 | 0
2017-08-13 01:00 | 8 | 1 | 0 | 0
2017-08-13 02:00 | 8 | 2 | 0 | 0
2017-08-13 03:00 | 8 | 3 | 0 | 0
2017-08-13 04:00 | 8 | 4 | 0 | 0
2017-08-13 05:00 | 8 | 5 | 218.4919 | 218.492
2017-08-13 06:00 | 8 | 6 | 1315.7092 | 1315.7092
2017-08-13 07:00 | 8 | 7 | 3916.7562 | 3916.7562
2017-08-13 08:00 | 8 | 8 | 5681.0954 | 5681.0954
2017-08-13 09:00 | 8 | 9 | 6972.1199 | 6972.1199
2017-08-13 10:00 | 8 | 10 | 7746.3724 | 7746.3724
2017-08-13 11:00 | 8 | 11 | 6096.1937 | 6096.1937
2017-08-13 12:00 | 8 | 12 | 8005.1948 | 8005.1948
2017-08-13 13:00 | 8 | 13 | 3984.3843 | 3984.3843
2017-08-13 14:00 | 8 | 14 | 6426.292 | 6426.292
2017-08-13 15:00 | 8 | 15 | 4864.8036 | 4864.8036
2017-08-13 16:00 | 8 | 16 | 2944.8613 | 2944.8613
2017-08-13 17:00 | 8 | 17 | 992.8605 | 992.8605
2017-08-13 18:00 | 8 | 18 | 52.9977 | 52.9977
2017-08-13 19:00 | 8 | 19 | 0 | 0
2017-08-13 20:00 | 8 | 20 | 0 | 0
2017-08-13 21:00 | 8 | 21 | 0 | 0
2017-08-13 22:00 | 8 | 22 | 0 | 0
2017-08-13 23:00 | 8 | 23 | 0 | 0
2017-08-14 | 8 | 0 | 0 | 0
2017-08-14 01:00 | 8 | 1 | 0 | 0
2017-08-14 02:00 | 8 | 2 | 0 | 0
2017-08-14 03:00 | 8 | 3 | 0 | 0
2017-08-14 04:00 | 8 | 4 | 0 | 0
2017-08-14 05:00 | 8 | 5 | 244.5199 | 244.5199
2017-08-14 06:00 | 8 | 6 | 1722.493 | 1722.493
2017-08-14 07:00 | 8 | 7 | 2851.4376 | 2851.4376
2017-08-14 08:00 | 8 | 8 | 4850.4401 | 4850.4401
2017-08-14 09:00 | 8 | 9 | 5739.727 | 5739.727
2017-08-14 10:00 | 8 | 10 | 7546.7841 | 7546.7841
2017-08-14 11:00 | 8 | 11 | 6493.6981 | 6493.6981
2017-08-14 12:00 | 8 | 12 | 7229.3036 | 7229.3036
2017-08-14 13:00 | 8 | 13 | 7121.9051 | 7121.9052
2017-08-14 14:00 | 8 | 14 | 3728.921 | 3728.921
2017-08-14 15:00 | 8 | 15 | 3565.3542 | 3565.3542
2017-08-14 16:00 | 8 | 16 | 2794.7748 | 2794.7748
2017-08-14 17:00 | 8 | 17 | 890.9073 | 890.9073
2017-08-14 18:00 | 8 | 18 | 65.0061 | 65.0061
2017-08-14 19:00 | 8 | 19 | 0 | 0
2017-08-14 20:00 | 8 | 20 | 0 | 0
2017-08-14 21:00 | 8 | 21 | 0 | 0
2017-08-14 22:00 | 8 | 22 | 0 | 0
2017-08-14 23:00 | 8 | 23 | 0 | 0
2017-08-15 | 8 | 0 | 0 | 0
2017-08-15 01:00 | 8 | 1 | 0 | 0
2017-08-15 02:00 | 8 | 2 | 0 | 0
2017-08-15 03:00 | 8 | 3 | 0 | 0
2017-08-15 04:00 | 8 | 4 | 0 | 0
2017-08-15 05:00 | 8 | 5 | 0 | 0
2017-08-15 06:00 | 8 | 6 | 1033.5602 | 1033.5602
2017-08-15 07:00 | 8 | 7 | 430.4024 | 430.4024
2017-08-15 08:00 | 8 | 8 | 1289.0085 | 1289.0085
2017-08-15 09:00 | 8 | 9 | 3105.2725 | 3105.2725
2017-08-15 10:00 | 8 | 10 | 7305.8097 | 7305.8097
2017-08-15 11:00 | 8 | 11 | 7527.9563 | 7527.9563
2017-08-15 12:00 | 8 | 12 | 7463.0423 | 7463.0423
2017-08-15 13:00 | 8 | 13 | 6890.6769 | 6890.6769
2017-08-15 14:00 | 8 | 14 | 5947.6562 | 5947.6562
2017-08-15 15:00 | 8 | 15 | 4509.9458 | 4509.9458
2017-08-15 16:00 | 8 | 16 | 2717.8525 | 2717.8525
2017-08-15 17:00 | 8 | 17 | 937.9457 | 937.9458
2017-08-15 18:00 | 8 | 18 | 44.513 | 44.513
2017-08-15 19:00 | 8 | 19 | 0 | 0
2017-08-15 20:00 | 8 | 20 | 0 | 0
2017-08-15 21:00 | 8 | 21 | 0 | 0
2017-08-15 22:00 | 8 | 22 | 0 | 0
2017-08-15 23:00 | 8 | 23 | 0 | 0
2017-08-16 | 8 | 0 | 0 | 0
2017-08-16 01:00 | 8 | 1 | 0 | 0
2017-08-16 02:00 | 8 | 2 | 0 | 0
2017-08-16 03:00 | 8 | 3 | 0 | 0
2017-08-16 04:00 | 8 | 4 | 0 | 0
2017-08-16 05:00 | 8 | 5 | 0 | 0
2017-08-16 06:00 | 8 | 6 | 735.1099 | 735.1099
2017-08-16 07:00 | 8 | 7 | 963.7356 | 963.7356
2017-08-16 08:00 | 8 | 8 | 4276.2186 | 4276.2186
2017-08-16 09:00 | 8 | 9 | 5413.61 | 5413.61
2017-08-16 10:00 | 8 | 10 | 7006.2289 | 7006.2289
2017-08-16 11:00 | 8 | 11 | 7304.6551 | 7304.6551
2017-08-16 12:00 | 8 | 12 | 7212.5884 | 7212.5884
2017-08-16 13:00 | 8 | 13 | 6645.1565 | 6645.1565
2017-08-16 14:00 | 8 | 14 | 5192.5099 | 5192.5099
2017-08-16 15:00 | 8 | 15 | 3859.055 | 3859.055
2017-08-16 16:00 | 8 | 16 | 2317.5007 | 2317.5007
2017-08-16 17:00 | 8 | 17 | 864.0605 | 864.0605
2017-08-16 18:00 | 8 | 18 | 0 | 0
2017-08-16 19:00 | 8 | 19 | 0 | 0
2017-08-16 20:00 | 8 | 20 | 0 | 0
2017-08-16 21:00 | 8 | 21 | 0 | 0
2017-08-16 22:00 | 8 | 22 | 0 | 0
2017-08-16 23:00 | 8 | 23 | 0 | 0
2017-08-17 | 8 | 0 | 0 | 0
2017-08-17 01:00 | 8 | 1 | 0 | 0
2017-08-17 02:00 | 8 | 2 | 0 | 0
2017-08-17 03:00 | 8 | 3 | 0 | 0
2017-08-17 04:00 | 8 | 4 | 0 | 0
2017-08-17 05:00 | 8 | 5 | 229.042 | 229.042
2017-08-17 06:00 | 8 | 6 | 835.2266 | 835.2266
2017-08-17 07:00 | 8 | 7 | 1331.6183 | 1331.6183
2017-08-17 08:00 | 8 | 8 | 2018.3236 | 2018.3236
2017-08-17 09:00 | 8 | 9 | 1748.9108 | 1748.9108
2017-08-17 10:00 | 8 | 10 | 1623.325 | 1623.325
2017-08-17 11:00 | 8 | 11 | 1483.6679 | 1483.6679
2017-08-17 12:00 | 8 | 12 | 2067.8506 | 2067.8506
2017-08-17 13:00 | 8 | 13 | 1339.7477 | 1339.7477
2017-08-17 14:00 | 8 | 14 | 1610.6843 | 1610.6843
2017-08-17 15:00 | 8 | 15 | 1329.8692 | 1329.8692
2017-08-17 16:00 | 8 | 16 | 1073.8999 | 1073.8999
2017-08-17 17:00 | 8 | 17 | 590.8872 | 590.8872
2017-08-17 18:00 | 8 | 18 | 0 | 0
2017-08-17 19:00 | 8 | 19 | 0 | 0
2017-08-17 20:00 | 8 | 20 | 0 | 0
2017-08-17 21:00 | 8 | 21 | 0 | 0
2017-08-17 22:00 | 8 | 22 | 0 | 0
2017-08-17 23:00 | 8 | 23 | 0 | 0
2017-08-18 | 8 | 0 | 0 | 0
2017-08-18 01:00 | 8 | 1 | 0 | 0
2017-08-18 02:00 | 8 | 2 | 0 | 0
2017-08-18 03:00 | 8 | 3 | 0 | 0
2017-08-18 04:00 | 8 | 4 | 0 | 0
2017-08-18 05:00 | 8 | 5 | 227.6183 | 227.6184
2017-08-18 06:00 | 8 | 6 | 1574.7904 | 1574.7904
2017-08-18 07:00 | 8 | 7 | 3522.887 | 3522.887
2017-08-18 08:00 | 8 | 8 | 5219.6211 | 5219.6211
2017-08-18 09:00 | 8 | 9 | 6439.9183 | 6439.9183
2017-08-18 10:00 | 8 | 10 | 7135.5004 | 7135.5004
2017-08-18 11:00 | 8 | 11 | 7425.7305 | 7425.7305
2017-08-18 12:00 | 8 | 12 | 7288.8552 | 7288.8552
2017-08-18 13:00 | 8 | 13 | 3174.3645 | 3174.3645
2017-08-18 14:00 | 8 | 14 | 3092.2488 | 3092.2488
2017-08-18 15:00 | 8 | 15 | 1395.9562 | 1395.9562
2017-08-18 16:00 | 8 | 16 | 1117.5332 | 1117.5332
2017-08-18 17:00 | 8 | 17 | 612.1519 | 612.1519
2017-08-18 18:00 | 8 | 18 | 0 | 0
2017-08-18 19:00 | 8 | 19 | 0 | 0
2017-08-18 20:00 | 8 | 20 | 0 | 0
2017-08-18 21:00 | 8 | 21 | 0 | 0
2017-08-18 22:00 | 8 | 22 | 0 | 0
2017-08-18 23:00 | 8 | 23 | 0 | 0
2017-08-19 | 8 | 0 | 0 | 0
2017-08-19 01:00 | 8 | 1 | 0 | 0
2017-08-19 02:00 | 8 | 2 | 0 | 0
2017-08-19 03:00 | 8 | 3 | 0 | 0
2017-08-19 04:00 | 8 | 4 | 0 | 0
2017-08-19 05:00 | 8 | 5 | 180.7834 | 180.7834
2017-08-19 06:00 | 8 | 6 | 1719.1557 | 1719.1557
2017-08-19 07:00 | 8 | 7 | 2718.1411 | 2718.1411
2017-08-19 08:00 | 8 | 8 | 5779.7643 | 5779.7643
2017-08-19 09:00 | 8 | 9 | 7090.0283 | 7090.0283
2017-08-19 10:00 | 8 | 10 | 7891.1183 | 7891.1183
2017-08-19 11:00 | 8 | 11 | 8252.7737 | 8252.7737
2017-08-19 12:00 | 8 | 12 | 8081.165 | 8081.165
2017-08-19 13:00 | 8 | 13 | 7487.8041 | 7487.8041
2017-08-19 14:00 | 8 | 14 | 6410.9959 | 6410.9959
2017-08-19 15:00 | 8 | 15 | 4890.6752 | 4890.6752
2017-08-19 16:00 | 8 | 16 | 2895.0422 | 2895.0422
2017-08-19 17:00 | 8 | 17 | 863.7822 | 863.7822
2017-08-19 18:00 | 8 | 18 | 0 | 0
2017-08-19 19:00 | 8 | 19 | 0 | 0
2017-08-19 20:00 | 8 | 20 | 0 | 0
2017-08-19 21:00 | 8 | 21 | 0 | 0
2017-08-19 22:00 | 8 | 22 | 0 | 0
2017-08-19 23:00 | 8 | 23 | 0 | 0
2017-08-20 | 8 | 0 | 0 | 0
2017-08-20 01:00 | 8 | 1 | 0 | 0
2017-08-20 02:00 | 8 | 2 | 0 | 0
2017-08-20 03:00 | 8 | 3 | 0 | 0
2017-08-20 04:00 | 8 | 4 | 0 | 0
2017-08-20 05:00 | 8 | 5 | 182.4233 | 182.4233
2017-08-20 06:00 | 8 | 6 | 1706.93 | 1706.93
2017-08-20 07:00 | 8 | 7 | 3868.5034 | 3868.5034
2017-08-20 08:00 | 8 | 8 | 5681.7095 | 5681.7095
2017-08-20 09:00 | 8 | 9 | 6998.7919 | 6998.7919
2017-08-20 10:00 | 8 | 10 | 7798.9458 | 7798.9458
2017-08-20 11:00 | 8 | 11 | 8114.6472 | 8114.6472
2017-08-20 12:00 | 8 | 12 | 7988.1633 | 7988.1633
2017-08-20 13:00 | 8 | 13 | 7386.3465 | 7386.3465
2017-08-20 14:00 | 8 | 14 | 6312.3052 | 6312.3052
2017-08-20 15:00 | 8 | 15 | 4769.3478 | 4769.3478
2017-08-20 16:00 | 8 | 16 | 2807.0672 | 2807.0672
2017-08-20 17:00 | 8 | 17 | 828.1046 | 828.1046
2017-08-20 18:00 | 8 | 18 | 0 | 0
2017-08-20 19:00 | 8 | 19 | 0 | 0
2017-08-20 20:00 | 8 | 20 | 0 | 0
2017-08-20 21:00 | 8 | 21 | 0 | 0
2017-08-20 22:00 | 8 | 22 | 0 | 0
2017-08-20 23:00 | 8 | 23 | 0 | 0
2017-08-21 | 8 | 0 | 0 | 0
2017-08-21 01:00 | 8 | 1 | 0 | 0
2017-08-21 02:00 | 8 | 2 | 0 | 0
2017-08-21 03:00 | 8 | 3 | 0 | 0
2017-08-21 04:00 | 8 | 4 | 0 | 0
2017-08-21 05:00 | 8 | 5 | 189.7017 | 189.7017
2017-08-21 06:00 | 8 | 6 | 1599.2015 | 1599.2015
2017-08-21 07:00 | 8 | 7 | 2380.0216 | 2380.0216
2017-08-21 08:00 | 8 | 8 | 4029.0871 | 4029.0871
2017-08-21 09:00 | 8 | 9 | 2181.7961 | 2181.7961
2017-08-21 10:00 | 8 | 10 | 5756.325 | 5756.325
2017-08-21 11:00 | 8 | 11 | 7836.2782 | 7836.2783
2017-08-21 12:00 | 8 | 12 | 7623.8962 | 7623.8962
2017-08-21 13:00 | 8 | 13 | 7064.9422 | 7064.9422
2017-08-21 14:00 | 8 | 14 | 6012.2414 | 6012.2414
2017-08-21 15:00 | 8 | 15 | 1717.8688 | 1717.8688
2017-08-21 16:00 | 8 | 16 | 2660.1386 | 2660.1386
2017-08-21 17:00 | 8 | 17 | 639.3839 | 639.3839
2017-08-21 18:00 | 8 | 18 | 0 | 0
2017-08-21 19:00 | 8 | 19 | 0 | 0
2017-08-21 20:00 | 8 | 20 | 0 | 0
2017-08-21 21:00 | 8 | 21 | 0 | 0
2017-08-21 22:00 | 8 | 22 | 0 | 0
2017-08-21 23:00 | 8 | 23 | 0 | 0
2017-08-22 | 8 | 0 | 0 | 0
2017-08-22 01:00 | 8 | 1 | 0 | 0
2017-08-22 02:00 | 8 | 2 | 0 | 0
2017-08-22 03:00 | 8 | 3 | 0 | 0
2017-08-22 04:00 | 8 | 4 | 0 | 0
2017-08-22 05:00 | 8 | 5 | 184.5623 | 184.5623
2017-08-22 06:00 | 8 | 6 | 1587.5554 | 1587.5554
2017-08-22 07:00 | 8 | 7 | 3622.5943 | 3622.5943
2017-08-22 08:00 | 8 | 8 | 5398.0724 | 5398.0724
2017-08-22 09:00 | 8 | 9 | 6696.7214 | 6696.7214
2017-08-22 10:00 | 8 | 10 | 7499.7077 | 7499.7077
2017-08-22 11:00 | 8 | 11 | 7849.5435 | 7849.5435
2017-08-22 12:00 | 8 | 12 | 7696.9419 | 7696.9419
2017-08-22 13:00 | 8 | 13 | 7084.0517 | 7084.0518
2017-08-22 14:00 | 8 | 14 | 6075.895 | 6075.895
2017-08-22 15:00 | 8 | 15 | 4522.2692 | 4522.2692
2017-08-22 16:00 | 8 | 16 | 2607.9608 | 2607.9608
2017-08-22 17:00 | 8 | 17 | 759.7441 | 759.7441
2017-08-22 18:00 | 8 | 18 | 0 | 0
2017-08-22 19:00 | 8 | 19 | 0 | 0
2017-08-22 20:00 | 8 | 20 | 0 | 0
2017-08-22 21:00 | 8 | 21 | 0 | 0
2017-08-22 22:00 | 8 | 22 | 0 | 0
2017-08-22 23:00 | 8 | 23 | 0 | 0
2017-08-23 | 8 | 0 | 0 | 0
2017-08-23 01:00 | 8 | 1 | 0 | 0
2017-08-23 02:00 | 8 | 2 | 0 | 0
2017-08-23 03:00 | 8 | 3 | 0 | 0
2017-08-23 04:00 | 8 | 4 | 0 | 0
2017-08-23 05:00 | 8 | 5 | 173.7765 | 173.7765
2017-08-23 06:00 | 8 | 6 | 747.7357 | 747.7357
2017-08-23 07:00 | 8 | 7 | 1573.591 | 1573.591
2017-08-23 08:00 | 8 | 8 | 1698.6339 | 1698.6339
2017-08-23 09:00 | 8 | 9 | 2404.2245 | 2404.2245
2017-08-23 10:00 | 8 | 10 | 4282.8128 | 4282.8128
2017-08-23 11:00 | 8 | 11 | 4178.7791 | 4178.7791
2017-08-23 12:00 | 8 | 12 | 3607.1096 | 3607.1096
2017-08-23 13:00 | 8 | 13 | 4527.9134 | 4527.9134
2017-08-23 14:00 | 8 | 14 | 4460.7338 | 4460.7338
2017-08-23 15:00 | 8 | 15 | 1360.7766 | 1360.7766
2017-08-23 16:00 | 8 | 16 | 1170.8334 | 1170.8334
2017-08-23 17:00 | 8 | 17 | 545.246 | 545.246
2017-08-23 18:00 | 8 | 18 | 0 | 0
2017-08-23 19:00 | 8 | 19 | 0 | 0
2017-08-23 20:00 | 8 | 20 | 0 | 0
2017-08-23 21:00 | 8 | 21 | 0 | 0
2017-08-23 22:00 | 8 | 22 | 0 | 0
2017-08-23 23:00 | 8 | 23 | 0 | 0
2017-08-24 | 8 | 0 | 0 | 0
2017-08-24 01:00 | 8 | 1 | 0 | 0
2017-08-24 02:00 | 8 | 2 | 0 | 0
2017-08-24 03:00 | 8 | 3 | 0 | 0
2017-08-24 04:00 | 8 | 4 | 0 | 0
2017-08-24 05:00 | 8 | 5 | 185.2604 | 185.2604
2017-08-24 06:00 | 8 | 6 | 1488.0356 | 1488.0356
2017-08-24 07:00 | 8 | 7 | 3416.6074 | 3416.6075
2017-08-24 08:00 | 8 | 8 | 5148.0842 | 5148.0842
2017-08-24 09:00 | 8 | 9 | 6427.4615 | 6427.4615
2017-08-24 10:00 | 8 | 10 | 7189.6631 | 7189.6631
2017-08-24 11:00 | 8 | 11 | 6599.1577 | 6599.1577
2017-08-24 12:00 | 8 | 12 | 7265.0261 | 7265.0261
2017-08-24 13:00 | 8 | 13 | 6053.9657 | 6053.9657
2017-08-24 14:00 | 8 | 14 | 5573.6348 | 5573.6348
2017-08-24 15:00 | 8 | 15 | 2878.2832 | 2878.2832
2017-08-24 16:00 | 8 | 16 | 1344.9871 | 1344.9871
2017-08-24 17:00 | 8 | 17 | 61.5813 | 61.5814
2017-08-24 18:00 | 8 | 18 | 0 | 0
2017-08-24 19:00 | 8 | 19 | 0 | 0
2017-08-24 20:00 | 8 | 20 | 0 | 0
2017-08-24 21:00 | 8 | 21 | 0 | 0
2017-08-24 22:00 | 8 | 22 | 0 | 0
2017-08-24 23:00 | 8 | 23 | 0 | 0
2017-08-25 | 8 | 0 | 0 | 0
2017-08-25 01:00 | 8 | 1 | 0 | 0
2017-08-25 02:00 | 8 | 2 | 0 | 0
2017-08-25 03:00 | 8 | 3 | 0 | 0
2017-08-25 04:00 | 8 | 4 | 0 | 0
2017-08-25 05:00 | 8 | 5 | 8.0695 | 8.0695
2017-08-25 06:00 | 8 | 6 | 839.5172 | 839.5172
2017-08-25 07:00 | 8 | 7 | 3389.2811 | 3389.2811
2017-08-25 08:00 | 8 | 8 | 5067.3278 | 5067.3278
2017-08-25 09:00 | 8 | 9 | 2623.4087 | 2623.4087
2017-08-25 10:00 | 8 | 10 | 1437.7725 | 1437.7725
2017-08-25 11:00 | 8 | 11 | 1833.0586 | 1833.0586
2017-08-25 12:00 | 8 | 12 | 5345.3265 | 5345.3265
2017-08-25 13:00 | 8 | 13 | 6749.925 | 6749.925
2017-08-25 14:00 | 8 | 14 | 2026.4782 | 2026.4782
2017-08-25 15:00 | 8 | 15 | 3200.5972 | 3200.5972
2017-08-25 16:00 | 8 | 16 | 1617.69 | 1617.69
2017-08-25 17:00 | 8 | 17 | 491.9355 | 491.9355
2017-08-25 18:00 | 8 | 18 | 0 | 0
2017-08-25 19:00 | 8 | 19 | 0 | 0
2017-08-25 20:00 | 8 | 20 | 0 | 0
2017-08-25 21:00 | 8 | 21 | 0 | 0
2017-08-25 22:00 | 8 | 22 | 0 | 0
2017-08-25 23:00 | 8 | 23 | 0 | 0
2017-08-26 | 8 | 0 | 0 | 0
2017-08-26 01:00 | 8 | 1 | 0 | 0
2017-08-26 02:00 | 8 | 2 | 0 | 0
2017-08-26 03:00 | 8 | 3 | 0 | 0
2017-08-26 04:00 | 8 | 4 | 0 | 0
2017-08-26 05:00 | 8 | 5 | 0 | 0
2017-08-26 06:00 | 8 | 6 | 499.9303 | 499.9303
2017-08-26 07:00 | 8 | 7 | 2253.4859 | 2253.4859
2017-08-26 08:00 | 8 | 8 | 1766.5392 | 1766.5392
2017-08-26 09:00 | 8 | 9 | 2032.7101 | 2032.7101
2017-08-26 10:00 | 8 | 10 | 6502.2667 | 6502.2667
2017-08-26 11:00 | 8 | 11 | 1591.1158 | 1591.1158
2017-08-26 12:00 | 8 | 12 | 3584.8087 | 3584.8087
2017-08-26 13:00 | 8 | 13 | 4025.5796 | 4025.5796
2017-08-26 14:00 | 8 | 14 | 3980.9423 | 3980.9423
2017-08-26 15:00 | 8 | 15 | 2787.9657 | 2787.9657
2017-08-26 16:00 | 8 | 16 | 1764.0126 | 1764.0126
2017-08-26 17:00 | 8 | 17 | 406.6205 | 406.6205
2017-08-26 18:00 | 8 | 18 | 0 | 0
2017-08-26 19:00 | 8 | 19 | 0 | 0
2017-08-26 20:00 | 8 | 20 | 0 | 0
2017-08-26 21:00 | 8 | 21 | 0 | 0
2017-08-26 22:00 | 8 | 22 | 0 | 0
2017-08-26 23:00 | 8 | 23 | 0 | 0
2017-08-27 | 8 | 0 | 0 | 0
2017-08-27 01:00 | 8 | 1 | 0 | 0
2017-08-27 02:00 | 8 | 2 | 0 | 0
2017-08-27 03:00 | 8 | 3 | 0 | 0
2017-08-27 04:00 | 8 | 4 | 0 | 0
2017-08-27 05:00 | 8 | 5 | 161.4071 | 161.4071
2017-08-27 06:00 | 8 | 6 | 1145.661 | 1145.661
2017-08-27 07:00 | 8 | 7 | 3284.607 | 3284.607
2017-08-27 08:00 | 8 | 8 | 5357.4923 | 5357.4923
2017-08-27 09:00 | 8 | 9 | 6631.0714 | 6631.0714
2017-08-27 10:00 | 8 | 10 | 7413.521 | 7413.521
2017-08-27 11:00 | 8 | 11 | 7707.8819 | 7707.8819
2017-08-27 12:00 | 8 | 12 | 7537.6221 | 7537.6221
2017-08-27 13:00 | 8 | 13 | 6945.4365 | 6945.4365
2017-08-27 14:00 | 8 | 14 | 5952.3241 | 5952.3241
2017-08-27 15:00 | 8 | 15 | 4407.5417 | 4407.5417
2017-08-27 16:00 | 8 | 16 | 2482.6269 | 2482.6269
2017-08-27 17:00 | 8 | 17 | 633.175 | 633.175
2017-08-27 18:00 | 8 | 18 | 0 | 0
2017-08-27 19:00 | 8 | 19 | 0 | 0
2017-08-27 20:00 | 8 | 20 | 0 | 0
2017-08-27 21:00 | 8 | 21 | 0 | 0
2017-08-27 22:00 | 8 | 22 | 0 | 0
2017-08-27 23:00 | 8 | 23 | 0 | 0
2017-08-28 | 8 | 0 | 0 | 0
2017-08-28 01:00 | 8 | 1 | 0 | 0
2017-08-28 02:00 | 8 | 2 | 0 | 0
2017-08-28 03:00 | 8 | 3 | 0 | 0
2017-08-28 04:00 | 8 | 4 | 0 | 0
2017-08-28 05:00 | 8 | 5 | 131.2414 | 131.2414
2017-08-28 06:00 | 8 | 6 | 1517.0006 | 1517.0006
2017-08-28 07:00 | 8 | 7 | 3601.1088 | 3601.1088
2017-08-28 08:00 | 8 | 8 | 5343.9936 | 5343.9936
2017-08-28 09:00 | 8 | 9 | 6587.4817 | 6587.4817
2017-08-28 10:00 | 8 | 10 | 7367.6187 | 7367.6187
2017-08-28 11:00 | 8 | 11 | 7635.7366 | 7635.7366
2017-08-28 12:00 | 8 | 12 | 7512.1392 | 7512.1392
2017-08-28 13:00 | 8 | 13 | 6920.8368 | 6920.8368
2017-08-28 14:00 | 8 | 14 | 3275.6692 | 3275.6692
2017-08-28 15:00 | 8 | 15 | 3763.7269 | 3763.7269
2017-08-28 16:00 | 8 | 16 | 2417.7565 | 2417.7565
2017-08-28 17:00 | 8 | 17 | 612.0058 | 612.0058
2017-08-28 18:00 | 8 | 18 | 0 | 0
2017-08-28 19:00 | 8 | 19 | 0 | 0
2017-08-28 20:00 | 8 | 20 | 0 | 0
2017-08-28 21:00 | 8 | 21 | 0 | 0
2017-08-28 22:00 | 8 | 22 | 0 | 0
2017-08-28 23:00 | 8 | 23 | 0 | 0
2017-08-29 | 8 | 0 | 0 | 0
2017-08-29 01:00 | 8 | 1 | 0 | 0
2017-08-29 02:00 | 8 | 2 | 0 | 0
2017-08-29 03:00 | 8 | 3 | 0 | 0
2017-08-29 04:00 | 8 | 4 | 0 | 0
2017-08-29 05:00 | 8 | 5 | 0 | 0
2017-08-29 06:00 | 8 | 6 | 259.5711 | 259.5711
2017-08-29 07:00 | 8 | 7 | 400.3357 | 400.3357
2017-08-29 08:00 | 8 | 8 | 1312.2638 | 1312.2638
2017-08-29 09:00 | 8 | 9 | 1758.7858 | 1758.7858
2017-08-29 10:00 | 8 | 10 | 2199.3531 | 2199.3531
2017-08-29 11:00 | 8 | 11 | 1434.909 | 1434.909
2017-08-29 12:00 | 8 | 12 | 4249.3282 | 4249.3282
2017-08-29 13:00 | 8 | 13 | 2551.1991 | 2551.1991
2017-08-29 14:00 | 8 | 14 | 4581.3435 | 4581.3435
2017-08-29 15:00 | 8 | 15 | 3813.2033 | 3813.2033
2017-08-29 16:00 | 8 | 16 | 87.6035 | 87.6035
2017-08-29 17:00 | 8 | 17 | 621.4082 | 621.4082
2017-08-29 18:00 | 8 | 18 | 0 | 0
2017-08-29 19:00 | 8 | 19 | 0 | 0
2017-08-29 20:00 | 8 | 20 | 0 | 0
2017-08-29 21:00 | 8 | 21 | 0 | 0
2017-08-29 22:00 | 8 | 22 | 0 | 0
2017-08-29 23:00 | 8 | 23 | 0 | 0
2017-08-30 | 8 | 0 | 0 | 0
2017-08-30 01:00 | 8 | 1 | 0 | 0
2017-08-30 02:00 | 8 | 2 | 0 | 0
2017-08-30 03:00 | 8 | 3 | 0 | 0
2017-08-30 04:00 | 8 | 4 | 0 | 0
2017-08-30 05:00 | 8 | 5 | 129.2197 | 129.2197
2017-08-30 06:00 | 8 | 6 | 1433.7027 | 1433.7027
2017-08-30 07:00 | 8 | 7 | 3382.641 | 3382.641
2017-08-30 08:00 | 8 | 8 | 5084.1741 | 5084.1741
2017-08-30 09:00 | 8 | 9 | 3387.026 | 3387.026
2017-08-30 10:00 | 8 | 10 | 5086.7984 | 5086.7984
2017-08-30 11:00 | 8 | 11 | 5750.552 | 5750.552
2017-08-30 12:00 | 8 | 12 | 4710.3827 | 4710.3827
2017-08-30 13:00 | 8 | 13 | 4556.6761 | 4556.6761
2017-08-30 14:00 | 8 | 14 | 5361.5783 | 5361.5783
2017-08-30 15:00 | 8 | 15 | 3890.4281 | 3890.4281
2017-08-30 16:00 | 8 | 16 | 2145.0433 | 2145.0433
2017-08-30 17:00 | 8 | 17 | 579.792 | 579.792
2017-08-30 18:00 | 8 | 18 | 0 | 0
2017-08-30 19:00 | 8 | 19 | 0 | 0
2017-08-30 20:00 | 8 | 20 | 0 | 0
2017-08-30 21:00 | 8 | 21 | 0 | 0
2017-08-30 22:00 | 8 | 22 | 0 | 0
2017-08-30 23:00 | 8 | 23 | 0 | 0
2017-08-31 | 8 | 0 | 0 | 0
2017-08-31 01:00 | 8 | 1 | 0 | 0
2017-08-31 02:00 | 8 | 2 | 0 | 0
2017-08-31 03:00 | 8 | 3 | 0 | 0
2017-08-31 04:00 | 8 | 4 | 0 | 0
2017-08-31 05:00 | 8 | 5 | 87.7691 | 87.7691
2017-08-31 06:00 | 8 | 6 | 481.965 | 481.965
2017-08-31 07:00 | 8 | 7 | 794.7949 | 794.7949
2017-08-31 08:00 | 8 | 8 | 848.723 | 848.723
2017-08-31 09:00 | 8 | 9 | 1621.0595 | 1621.0595
2017-08-31 10:00 | 8 | 10 | 2892.9124 | 2892.9124
2017-08-31 11:00 | 8 | 11 | 3671.0944 | 3671.0944
2017-08-31 12:00 | 8 | 12 | 4007.6568 | 4007.6568
2017-08-31 13:00 | 8 | 13 | 6601.7348 | 6601.7348
2017-08-31 14:00 | 8 | 14 | 5486.6546 | 5486.6546
2017-08-31 15:00 | 8 | 15 | 4055.2726 | 4055.2726
2017-08-31 16:00 | 8 | 16 | 2265.3677 | 2265.3677
2017-08-31 17:00 | 8 | 17 | 557.6442 | 557.6442
2017-08-31 18:00 | 8 | 18 | 0 | 0
2017-08-31 19:00 | 8 | 19 | 0 | 0
2017-08-31 20:00 | 8 | 20 | 0 | 0
2017-08-31 21:00 | 8 | 21 | 0 | 0
2017-08-31 22:00 | 8 | 22 | 0 | 0
2017-08-31 23:00 | 8 | 23 | 0 | 0
2017-09-01 | 9 | 0 | 0 | 0
2017-09-01 01:00 | 9 | 1 | 0 | 0
2017-09-01 02:00 | 9 | 2 | 0 | 0
2017-09-01 03:00 | 9 | 3 | 0 | 0
2017-09-01 04:00 | 9 | 4 | 0 | 0
2017-09-01 05:00 | 9 | 5 | 121.3307 | 121.3307
2017-09-01 06:00 | 9 | 6 | 1557.6451 | 1557.6451
2017-09-01 07:00 | 9 | 7 | 3747.9846 | 3747.9846
2017-09-01 08:00 | 9 | 8 | 5617.4176 | 5617.4176
2017-09-01 09:00 | 9 | 9 | 6937.2726 | 6937.2727
2017-09-01 10:00 | 9 | 10 | 7791.5869 | 7791.5869
2017-09-01 11:00 | 9 | 11 | 8084.477 | 8084.477
2017-09-01 12:00 | 9 | 12 | 7935.5255 | 7935.5256
2017-09-01 13:00 | 9 | 13 | 7231.4633 | 7231.4633
2017-09-01 14:00 | 9 | 14 | 6145.4482 | 6145.4482
2017-09-01 15:00 | 9 | 15 | 4481.4557 | 4481.4557
2017-09-01 16:00 | 9 | 16 | 2431.9016 | 2431.9016
2017-09-01 17:00 | 9 | 17 | 533.2515 | 533.2515
2017-09-01 18:00 | 9 | 18 | 0 | 0
2017-09-01 19:00 | 9 | 19 | 0 | 0
2017-09-01 20:00 | 9 | 20 | 0 | 0
2017-09-01 21:00 | 9 | 21 | 0 | 0
2017-09-01 22:00 | 9 | 22 | 0 | 0
2017-09-01 23:00 | 9 | 23 | 0 | 0
2017-09-02 | 9 | 0 | 0 | 0
2017-09-02 01:00 | 9 | 1 | 0 | 0
2017-09-02 02:00 | 9 | 2 | 0 | 0
2017-09-02 03:00 | 9 | 3 | 0 | 0
2017-09-02 04:00 | 9 | 4 | 0 | 0
2017-09-02 05:00 | 9 | 5 | 102.4305 | 102.4305
2017-09-02 06:00 | 9 | 6 | 1514.8973 | 1514.8973
2017-09-02 07:00 | 9 | 7 | 3635.6732 | 3635.6732
2017-09-02 08:00 | 9 | 8 | 5489.0581 | 5489.0581
2017-09-02 09:00 | 9 | 9 | 6831.7486 | 6831.7486
2017-09-02 10:00 | 9 | 10 | 7637.7445 | 7637.7446
2017-09-02 11:00 | 9 | 11 | 7930.3402 | 7930.3402
2017-09-02 12:00 | 9 | 12 | 7782.0097 | 7782.0097
2017-09-02 13:00 | 9 | 13 | 7123.9728 | 7123.9729
2017-09-02 14:00 | 9 | 14 | 5980.4059 | 5980.4059
2017-09-02 15:00 | 9 | 15 | 4351.1204 | 4351.1204
2017-09-02 16:00 | 9 | 16 | 2332.2908 | 2332.2908
2017-09-02 17:00 | 9 | 17 | 508.1896 | 508.1896
2017-09-02 18:00 | 9 | 18 | 0 | 0
2017-09-02 19:00 | 9 | 19 | 0 | 0
2017-09-02 20:00 | 9 | 20 | 0 | 0
2017-09-02 21:00 | 9 | 21 | 0 | 0
2017-09-02 22:00 | 9 | 22 | 0 | 0
2017-09-02 23:00 | 9 | 23 | 0 | 0
2017-09-03 | 9 | 0 | 0 | 0
2017-09-03 01:00 | 9 | 1 | 0 | 0
2017-09-03 02:00 | 9 | 2 | 0 | 0
2017-09-03 03:00 | 9 | 3 | 0 | 0
2017-09-03 04:00 | 9 | 4 | 0 | 0
2017-09-03 05:00 | 9 | 5 | 147.5254 | 147.5254
2017-09-03 06:00 | 9 | 6 | 1460.4586 | 1460.4586
2017-09-03 07:00 | 9 | 7 | 3324.5154 | 3324.5154
2017-09-03 08:00 | 9 | 8 | 4696.953 | 4696.953
2017-09-03 09:00 | 9 | 9 | 5843.3202 | 5843.3202
2017-09-03 10:00 | 9 | 10 | 4782.1094 | 4782.1094
2017-09-03 11:00 | 9 | 11 | 6070.1726 | 6070.1726
2017-09-03 12:00 | 9 | 12 | 4758.1399 | 4758.1399
2017-09-03 13:00 | 9 | 13 | 7154.5548 | 7154.5548
2017-09-03 14:00 | 9 | 14 | 5981.3754 | 5981.3754
2017-09-03 15:00 | 9 | 15 | 4361.2105 | 4361.2105
2017-09-03 16:00 | 9 | 16 | 2182.0664 | 2182.0664
2017-09-03 17:00 | 9 | 17 | 467.2024 | 467.2024
2017-09-03 18:00 | 9 | 18 | 0 | 0
2017-09-03 19:00 | 9 | 19 | 0 | 0
2017-09-03 20:00 | 9 | 20 | 0 | 0
2017-09-03 21:00 | 9 | 21 | 0 | 0
2017-09-03 22:00 | 9 | 22 | 0 | 0
2017-09-03 23:00 | 9 | 23 | 0 | 0
2017-09-04 | 9 | 0 | 0 | 0
2017-09-04 01:00 | 9 | 1 | 0 | 0
2017-09-04 02:00 | 9 | 2 | 0 | 0
2017-09-04 03:00 | 9 | 3 | 0 | 0
2017-09-04 04:00 | 9 | 4 | 0 | 0
2017-09-04 05:00 | 9 | 5 | 73.4022 | 73.4022
2017-09-04 06:00 | 9 | 6 | 1447.1393 | 1447.1393
2017-09-04 07:00 | 9 | 7 | 3552.7295 | 3552.7295
2017-09-04 08:00 | 9 | 8 | 5379.5792 | 5379.5792
2017-09-04 09:00 | 9 | 9 | 6672.0734 | 6672.0734
2017-09-04 10:00 | 9 | 10 | 7498.0276 | 7498.0276
2017-09-04 11:00 | 9 | 11 | 7827.8303 | 7827.8303
2017-09-04 12:00 | 9 | 12 | 7619.3514 | 7619.3514
2017-09-04 13:00 | 9 | 13 | 6903.7467 | 6903.7467
2017-09-04 14:00 | 9 | 14 | 5777.5563 | 5777.5563
2017-09-04 15:00 | 9 | 15 | 4168.0301 | 4168.0301
2017-09-04 16:00 | 9 | 16 | 2211.7777 | 2211.7777
2017-09-04 17:00 | 9 | 17 | 451.1772 | 451.1772
2017-09-04 18:00 | 9 | 18 | 0 | 0
2017-09-04 19:00 | 9 | 19 | 0 | 0
2017-09-04 20:00 | 9 | 20 | 0 | 0
2017-09-04 21:00 | 9 | 21 | 0 | 0
2017-09-04 22:00 | 9 | 22 | 0 | 0
2017-09-04 23:00 | 9 | 23 | 0 | 0
2017-09-05 | 9 | 0 | 0 | 0
2017-09-05 01:00 | 9 | 1 | 0 | 0
2017-09-05 02:00 | 9 | 2 | 0 | 0
2017-09-05 03:00 | 9 | 3 | 0 | 0
2017-09-05 04:00 | 9 | 4 | 0 | 0
2017-09-05 05:00 | 9 | 5 | 72.4557 | 72.4557
2017-09-05 06:00 | 9 | 6 | 381.8701 | 381.8701
2017-09-05 07:00 | 9 | 7 | 2032.3846 | 2032.3846
2017-09-05 08:00 | 9 | 8 | 5237.1207 | 5237.1207
2017-09-05 09:00 | 9 | 9 | 4006.6655 | 4006.6655
2017-09-05 10:00 | 9 | 10 | 7331.4685 | 7331.4685
2017-09-05 11:00 | 9 | 11 | 7593.9019 | 7593.9019
2017-09-05 12:00 | 9 | 12 | 7422.5715 | 7422.5715
2017-09-05 13:00 | 9 | 13 | 6738.1398 | 6738.1398
2017-09-05 14:00 | 9 | 14 | 5609.7356 | 5609.7356
2017-09-05 15:00 | 9 | 15 | 4022.0824 | 4022.0825
2017-09-05 16:00 | 9 | 16 | 2124.3317 | 2124.3317
2017-09-05 17:00 | 9 | 17 | 418.7115 | 418.7115
2017-09-05 18:00 | 9 | 18 | 0 | 0
2017-09-05 19:00 | 9 | 19 | 0 | 0
2017-09-05 20:00 | 9 | 20 | 0 | 0
2017-09-05 21:00 | 9 | 21 | 0 | 0
2017-09-05 22:00 | 9 | 22 | 0 | 0
2017-09-05 23:00 | 9 | 23 | 0 | 0
2017-09-06 | 9 | 0 | 0 | 0
2017-09-06 01:00 | 9 | 1 | 0 | 0
2017-09-06 02:00 | 9 | 2 | 0 | 0
2017-09-06 03:00 | 9 | 3 | 0 | 0
2017-09-06 04:00 | 9 | 4 | 0 | 0
2017-09-06 05:00 | 9 | 5 | 76.5152 | 76.5152
2017-09-06 06:00 | 9 | 6 | 1455.9299 | 1455.9299
2017-09-06 07:00 | 9 | 7 | 3676.55 | 3676.55
2017-09-06 08:00 | 9 | 8 | 5602.7551 | 5602.7551
2017-09-06 09:00 | 9 | 9 | 6945.4733 | 6945.4733
2017-09-06 10:00 | 9 | 10 | 7782.2144 | 7782.2144
2017-09-06 11:00 | 9 | 11 | 8124.0301 | 8124.0301
2017-09-06 12:00 | 9 | 12 | 7964.5193 | 7964.5193
2017-09-06 13:00 | 9 | 13 | 7290.6251 | 7290.6251
2017-09-06 14:00 | 9 | 14 | 6144.7133 | 6144.7133
2017-09-06 15:00 | 9 | 15 | 4474.5074 | 4474.5074
2017-09-06 16:00 | 9 | 16 | 2341.753 | 2341.753
2017-09-06 17:00 | 9 | 17 | 413.9862 | 413.9862
2017-09-06 18:00 | 9 | 18 | 0 | 0
2017-09-06 19:00 | 9 | 19 | 0 | 0
2017-09-06 20:00 | 9 | 20 | 0 | 0
2017-09-06 21:00 | 9 | 21 | 0 | 0
2017-09-06 22:00 | 9 | 22 | 0 | 0
2017-09-06 23:00 | 9 | 23 | 0 | 0
2017-09-07 | 9 | 0 | 0 | 0
2017-09-07 01:00 | 9 | 1 | 0 | 0
2017-09-07 02:00 | 9 | 2 | 0 | 0
2017-09-07 03:00 | 9 | 3 | 0 | 0
2017-09-07 04:00 | 9 | 4 | 0 | 0
2017-09-07 05:00 | 9 | 5 | 65.1555 | 65.1555
2017-09-07 06:00 | 9 | 6 | 1064.5872 | 1064.5872
2017-09-07 07:00 | 9 | 7 | 3605.511 | 3605.511
2017-09-07 08:00 | 9 | 8 | 5478.7368 | 5478.7368
2017-09-07 09:00 | 9 | 9 | 5794.5165 | 5794.5165
2017-09-07 10:00 | 9 | 10 | 6553.1991 | 6553.1991
2017-09-07 11:00 | 9 | 11 | 6430.7218 | 6430.7218
2017-09-07 12:00 | 9 | 12 | 6584.2813 | 6584.2813
2017-09-07 13:00 | 9 | 13 | 5500.4132 | 5500.4132
2017-09-07 14:00 | 9 | 14 | 5474.7509 | 5474.7509
2017-09-07 15:00 | 9 | 15 | 4005.5098 | 4005.5098
2017-09-07 16:00 | 9 | 16 | 2013.8949 | 2013.8949
2017-09-07 17:00 | 9 | 17 | 377.2322 | 377.2322
2017-09-07 18:00 | 9 | 18 | 0 | 0
2017-09-07 19:00 | 9 | 19 | 0 | 0
2017-09-07 20:00 | 9 | 20 | 0 | 0
2017-09-07 21:00 | 9 | 21 | 0 | 0
2017-09-07 22:00 | 9 | 22 | 0 | 0
2017-09-07 23:00 | 9 | 23 | 0 | 0
2017-09-08 | 9 | 0 | 0 | 0
2017-09-08 01:00 | 9 | 1 | 0 | 0
2017-09-08 02:00 | 9 | 2 | 0 | 0
2017-09-08 03:00 | 9 | 3 | 0 | 0
2017-09-08 04:00 | 9 | 4 | 0 | 0
2017-09-08 05:00 | 9 | 5 | 0.1909 | 0.1909
2017-09-08 06:00 | 9 | 6 | 990.0729 | 990.0729
2017-09-08 07:00 | 9 | 7 | 2473.0255 | 2473.0255
2017-09-08 08:00 | 9 | 8 | 3326.9258 | 3326.9258
2017-09-08 09:00 | 9 | 9 | 4720.4717 | 4720.4717
2017-09-08 10:00 | 9 | 10 | 6159.9474 | 6159.9474
2017-09-08 11:00 | 9 | 11 | 6192.9202 | 6192.9202
2017-09-08 12:00 | 9 | 12 | 6323.8247 | 6323.8247
2017-09-08 13:00 | 9 | 13 | 5537.9457 | 5537.9457
2017-09-08 14:00 | 9 | 14 | 4298.0146 | 4298.0146
2017-09-08 15:00 | 9 | 15 | 3572.3968 | 3572.3968
2017-09-08 16:00 | 9 | 16 | 888.4152 | 888.4152
2017-09-08 17:00 | 9 | 17 | 299.2369 | 299.2369
2017-09-08 18:00 | 9 | 18 | 0 | 0
2017-09-08 19:00 | 9 | 19 | 0 | 0
2017-09-08 20:00 | 9 | 20 | 0 | 0
2017-09-08 21:00 | 9 | 21 | 0 | 0
2017-09-08 22:00 | 9 | 22 | 0 | 0
2017-09-08 23:00 | 9 | 23 | 0 | 0
2017-09-09 | 9 | 0 | 0 | 0
2017-09-09 01:00 | 9 | 1 | 0 | 0
2017-09-09 02:00 | 9 | 2 | 0 | 0
2017-09-09 03:00 | 9 | 3 | 0 | 0
2017-09-09 04:00 | 9 | 4 | 0 | 0
2017-09-09 05:00 | 9 | 5 | 0 | 0
2017-09-09 06:00 | 9 | 6 | 405.6751 | 405.6751
2017-09-09 07:00 | 9 | 7 | 1310.9885 | 1310.9885
2017-09-09 08:00 | 9 | 8 | 4090.7087 | 4090.7087
2017-09-09 09:00 | 9 | 9 | 2930.2299 | 2930.2299
2017-09-09 10:00 | 9 | 10 | 6043.1488 | 6043.1488
2017-09-09 11:00 | 9 | 11 | 6179.1995 | 6179.1995
2017-09-09 12:00 | 9 | 12 | 6708.9988 | 6708.9988
2017-09-09 13:00 | 9 | 13 | 6767.474 | 6767.474
2017-09-09 14:00 | 9 | 14 | 5379.953 | 5379.953
2017-09-09 15:00 | 9 | 15 | 3872.9711 | 3872.9711
2017-09-09 16:00 | 9 | 16 | 1711.2713 | 1711.2713
2017-09-09 17:00 | 9 | 17 | 365.1802 | 365.1802
2017-09-09 18:00 | 9 | 18 | 0 | 0
2017-09-09 19:00 | 9 | 19 | 0 | 0
2017-09-09 20:00 | 9 | 20 | 0 | 0
2017-09-09 21:00 | 9 | 21 | 0 | 0
2017-09-09 22:00 | 9 | 22 | 0 | 0
2017-09-09 23:00 | 9 | 23 | 0 | 0
2017-09-10 | 9 | 0 | 0 | 0
2017-09-10 01:00 | 9 | 1 | 0 | 0
2017-09-10 02:00 | 9 | 2 | 0 | 0
2017-09-10 03:00 | 9 | 3 | 0 | 0
2017-09-10 04:00 | 9 | 4 | 0 | 0
2017-09-10 05:00 | 9 | 5 | 50.9945 | 50.9945
2017-09-10 06:00 | 9 | 6 | 1400.4758 | 1400.4758
2017-09-10 07:00 | 9 | 7 | 2238.5026 | 2238.5026
2017-09-10 08:00 | 9 | 8 | 4954.1471 | 4954.1471
2017-09-10 09:00 | 9 | 9 | 5737.3281 | 5737.3281
2017-09-10 10:00 | 9 | 10 | 5811.8976 | 5811.8976
2017-09-10 11:00 | 9 | 11 | 6288.5208 | 6288.5208
2017-09-10 12:00 | 9 | 12 | 6214.9438 | 6214.9438
2017-09-10 13:00 | 9 | 13 | 4942.7011 | 4942.7011
2017-09-10 14:00 | 9 | 14 | 4655.139 | 4655.139
2017-09-10 15:00 | 9 | 15 | 3423.6282 | 3423.6282
2017-09-10 16:00 | 9 | 16 | 1780.8233 | 1780.8233
2017-09-10 17:00 | 9 | 17 | 291.617 | 291.617
2017-09-10 18:00 | 9 | 18 | 0 | 0
2017-09-10 19:00 | 9 | 19 | 0 | 0
2017-09-10 20:00 | 9 | 20 | 0 | 0
2017-09-10 21:00 | 9 | 21 | 0 | 0
2017-09-10 22:00 | 9 | 22 | 0 | 0
2017-09-10 23:00 | 9 | 23 | 0 | 0
2017-09-11 | 9 | 0 | 0 | 0
2017-09-11 01:00 | 9 | 1 | 0 | 0
2017-09-11 02:00 | 9 | 2 | 0 | 0
2017-09-11 03:00 | 9 | 3 | 0 | 0
2017-09-11 04:00 | 9 | 4 | 0 | 0
2017-09-11 05:00 | 9 | 5 | 0 | 0
2017-09-11 06:00 | 9 | 6 | 59.0145 | 59.0145
2017-09-11 07:00 | 9 | 7 | 532.412 | 532.412
2017-09-11 08:00 | 9 | 8 | 622.6733 | 622.6733
2017-09-11 09:00 | 9 | 9 | 791.8992 | 791.8992
2017-09-11 10:00 | 9 | 10 | 1537.2705 | 1537.2705
2017-09-11 11:00 | 9 | 11 | 2054.1587 | 2054.1587
2017-09-11 12:00 | 9 | 12 | 2680.0462 | 2680.0462
2017-09-11 13:00 | 9 | 13 | 2359.685 | 2359.685
2017-09-11 14:00 | 9 | 14 | 1963.1903 | 1963.1903
2017-09-11 15:00 | 9 | 15 | 389.16 | 389.16
2017-09-11 16:00 | 9 | 16 | 76.989 | 76.989
2017-09-11 17:00 | 9 | 17 | 38.9045 | 38.9045
2017-09-11 18:00 | 9 | 18 | 0 | 0
2017-09-11 19:00 | 9 | 19 | 0 | 0
2017-09-11 20:00 | 9 | 20 | 0 | 0
2017-09-11 21:00 | 9 | 21 | 0 | 0
2017-09-11 22:00 | 9 | 22 | 0 | 0
2017-09-11 23:00 | 9 | 23 | 0 | 0
2017-09-12 | 9 | 0 | 0 | 0
2017-09-12 01:00 | 9 | 1 | 0 | 0
2017-09-12 02:00 | 9 | 2 | 0 | 0
2017-09-12 03:00 | 9 | 3 | 0 | 0
2017-09-12 04:00 | 9 | 4 | 0 | 0
2017-09-12 05:00 | 9 | 5 | 0 | 0
2017-09-12 06:00 | 9 | 6 | 895.0404 | 895.0404
2017-09-12 07:00 | 9 | 7 | 428.1082 | 428.1082
2017-09-12 08:00 | 9 | 8 | 47.1649 | 47.1649
2017-09-12 09:00 | 9 | 9 | 75.7792 | 75.7792
2017-09-12 10:00 | 9 | 10 | 719.3089 | 719.3089
2017-09-12 11:00 | 9 | 11 | 665.321 | 665.321
2017-09-12 12:00 | 9 | 12 | 924.8599 | 924.8599
2017-09-12 13:00 | 9 | 13 | 1095.6004 | 1095.6004
2017-09-12 14:00 | 9 | 14 | 1029.534 | 1029.534
2017-09-12 15:00 | 9 | 15 | 510.0181 | 510.0181
2017-09-12 16:00 | 9 | 16 | 76.2484 | 76.2484
2017-09-12 17:00 | 9 | 17 | 0 | 0
2017-09-12 18:00 | 9 | 18 | 0 | 0
2017-09-12 19:00 | 9 | 19 | 0 | 0
2017-09-12 20:00 | 9 | 20 | 0 | 0
2017-09-12 21:00 | 9 | 21 | 0 | 0
2017-09-12 22:00 | 9 | 22 | 0 | 0
2017-09-12 23:00 | 9 | 23 | 0 | 0
2017-09-13 | 9 | 0 | 0 | 0
2017-09-13 01:00 | 9 | 1 | 0 | 0
2017-09-13 02:00 | 9 | 2 | 0 | 0
2017-09-13 03:00 | 9 | 3 | 0 | 0
2017-09-13 04:00 | 9 | 4 | 0 | 0
2017-09-13 05:00 | 9 | 5 | 0 | 0
2017-09-13 06:00 | 9 | 6 | 562.8295 | 562.8295
2017-09-13 07:00 | 9 | 7 | 1497.4978 | 1497.4978
2017-09-13 08:00 | 9 | 8 | 1992.4244 | 1992.4244
2017-09-13 09:00 | 9 | 9 | 6537.4234 | 6537.4234
2017-09-13 10:00 | 9 | 10 | 7223.0016 | 7223.0017
2017-09-13 11:00 | 9 | 11 | 7499.5824 | 7499.5824
2017-09-13 12:00 | 9 | 12 | 7320.4779 | 7320.4779
2017-09-13 13:00 | 9 | 13 | 6654.5095 | 6654.5095
2017-09-13 14:00 | 9 | 14 | 5452.6778 | 5452.6778
2017-09-13 15:00 | 9 | 15 | 2094.6146 | 2094.6146
2017-09-13 16:00 | 9 | 16 | 602.0687 | 602.0687
2017-09-13 17:00 | 9 | 17 | 65.366 | 65.366
2017-09-13 18:00 | 9 | 18 | 0 | 0
2017-09-13 19:00 | 9 | 19 | 0 | 0
2017-09-13 20:00 | 9 | 20 | 0 | 0
2017-09-13 21:00 | 9 | 21 | 0 | 0
2017-09-13 22:00 | 9 | 22 | 0 | 0
2017-09-13 23:00 | 9 | 23 | 0 | 0
2017-09-14 | 9 | 0 | 0 | 0
2017-09-14 01:00 | 9 | 1 | 0 | 0
2017-09-14 02:00 | 9 | 2 | 0 | 0
2017-09-14 03:00 | 9 | 3 | 0 | 0
2017-09-14 04:00 | 9 | 4 | 0 | 0
2017-09-14 05:00 | 9 | 5 | 0 | 0
2017-09-14 06:00 | 9 | 6 | 938.6461 | 938.6461
2017-09-14 07:00 | 9 | 7 | 2991.181 | 2991.181
2017-09-14 08:00 | 9 | 8 | 5285.653 | 5285.653
2017-09-14 09:00 | 9 | 9 | 6605.8967 | 6605.8967
2017-09-14 10:00 | 9 | 10 | 7364.01 | 7364.01
2017-09-14 11:00 | 9 | 11 | 7627.1116 | 7627.1116
2017-09-14 12:00 | 9 | 12 | 7409.1084 | 7409.1084
2017-09-14 13:00 | 9 | 13 | 6754.9574 | 6754.9574
2017-09-14 14:00 | 9 | 14 | 5575.0896 | 5575.0896
2017-09-14 15:00 | 9 | 15 | 2797.8373 | 2797.8373
2017-09-14 16:00 | 9 | 16 | 1761.1054 | 1761.1054
2017-09-14 17:00 | 9 | 17 | 218.132 | 218.132
2017-09-14 18:00 | 9 | 18 | 0 | 0
2017-09-14 19:00 | 9 | 19 | 0 | 0
2017-09-14 20:00 | 9 | 20 | 0 | 0
2017-09-14 21:00 | 9 | 21 | 0 | 0
2017-09-14 22:00 | 9 | 22 | 0 | 0
2017-09-14 23:00 | 9 | 23 | 0 | 0
2017-09-15 | 9 | 0 | 0 | 0
2017-09-15 01:00 | 9 | 1 | 0 | 0
2017-09-15 02:00 | 9 | 2 | 0 | 0
2017-09-15 03:00 | 9 | 3 | 0 | 0
2017-09-15 04:00 | 9 | 4 | 0 | 0
2017-09-15 05:00 | 9 | 5 | 0 | 0
2017-09-15 06:00 | 9 | 6 | 1246.7794 | 1246.7794
2017-09-15 07:00 | 9 | 7 | 3364.9425 | 3364.9425
2017-09-15 08:00 | 9 | 8 | 5208.5317 | 5208.5317
2017-09-15 09:00 | 9 | 9 | 6556.3386 | 6556.3386
2017-09-15 10:00 | 9 | 10 | 7335.9696 | 7335.9696
2017-09-15 11:00 | 9 | 11 | 7665.21 | 7665.21
2017-09-15 12:00 | 9 | 12 | 7474.203 | 7474.203
2017-09-15 13:00 | 9 | 13 | 6780.178 | 6780.178
2017-09-15 14:00 | 9 | 14 | 5623.9807 | 5623.9807
2017-09-15 15:00 | 9 | 15 | 3925.1075 | 3925.1075
2017-09-15 16:00 | 9 | 16 | 1843.9951 | 1843.9951
2017-09-15 17:00 | 9 | 17 | 218.876 | 218.876
2017-09-15 18:00 | 9 | 18 | 0 | 0
2017-09-15 19:00 | 9 | 19 | 0 | 0
2017-09-15 20:00 | 9 | 20 | 0 | 0
2017-09-15 21:00 | 9 | 21 | 0 | 0
2017-09-15 22:00 | 9 | 22 | 0 | 0
2017-09-15 23:00 | 9 | 23 | 0 | 0
2017-09-16 | 9 | 0 | 0 | 0
2017-09-16 01:00 | 9 | 1 | 0 | 0
2017-09-16 02:00 | 9 | 2 | 0 | 0
2017-09-16 03:00 | 9 | 3 | 0 | 0
2017-09-16 04:00 | 9 | 4 | 0 | 0
2017-09-16 05:00 | 9 | 5 | 0 | 0
2017-09-16 06:00 | 9 | 6 | 652.4525 | 652.4525
2017-09-16 07:00 | 9 | 7 | 261.3076 | 261.3076
2017-09-16 08:00 | 9 | 8 | 633.5948 | 633.5948
2017-09-16 09:00 | 9 | 9 | 787.8339 | 787.8339
2017-09-16 10:00 | 9 | 10 | 2509.4541 | 2509.4541
2017-09-16 11:00 | 9 | 11 | 2623.3397 | 2623.3397
2017-09-16 12:00 | 9 | 12 | 2327.1676 | 2327.1676
2017-09-16 13:00 | 9 | 13 | 2077.0265 | 2077.0265
2017-09-16 14:00 | 9 | 14 | 3231.4828 | 3231.4828
2017-09-16 15:00 | 9 | 15 | 1826.0735 | 1826.0735
2017-09-16 16:00 | 9 | 16 | 1199.956 | 1199.956
2017-09-16 17:00 | 9 | 17 | 209.1332 | 209.1332
2017-09-16 18:00 | 9 | 18 | 0 | 0
2017-09-16 19:00 | 9 | 19 | 0 | 0
2017-09-16 20:00 | 9 | 20 | 0 | 0
2017-09-16 21:00 | 9 | 21 | 0 | 0
2017-09-16 22:00 | 9 | 22 | 0 | 0
2017-09-16 23:00 | 9 | 23 | 0 | 0
2017-09-17 | 9 | 0 | 0 | 0
2017-09-17 01:00 | 9 | 1 | 0 | 0
2017-09-17 02:00 | 9 | 2 | 0 | 0
2017-09-17 03:00 | 9 | 3 | 0 | 0
2017-09-17 04:00 | 9 | 4 | 0 | 0
2017-09-17 05:00 | 9 | 5 | 0 | 0
2017-09-17 06:00 | 9 | 6 | 217.9963 | 217.9963
2017-09-17 07:00 | 9 | 7 | 850.034 | 850.034
2017-09-17 08:00 | 9 | 8 | 1956.8584 | 1956.8584
2017-09-17 09:00 | 9 | 9 | 2422.705 | 2422.705
2017-09-17 10:00 | 9 | 10 | 2983.33 | 2983.33
2017-09-17 11:00 | 9 | 11 | 3720.043 | 3720.043
2017-09-17 12:00 | 9 | 12 | 2361.3904 | 2361.3904
2017-09-17 13:00 | 9 | 13 | 1376.9157 | 1376.9157
2017-09-17 14:00 | 9 | 14 | 2146.0265 | 2146.0265
2017-09-17 15:00 | 9 | 15 | 693.4132 | 693.4132
2017-09-17 16:00 | 9 | 16 | 281.8627 | 281.8627
2017-09-17 17:00 | 9 | 17 | 180.5845 | 180.5845
2017-09-17 18:00 | 9 | 18 | 0 | 0
2017-09-17 19:00 | 9 | 19 | 0 | 0
2017-09-17 20:00 | 9 | 20 | 0 | 0
2017-09-17 21:00 | 9 | 21 | 0 | 0
2017-09-17 22:00 | 9 | 22 | 0 | 0
2017-09-17 23:00 | 9 | 23 | 0 | 0
2017-09-18 | 9 | 0 | 0 | 0
2017-09-18 01:00 | 9 | 1 | 0 | 0
2017-09-18 02:00 | 9 | 2 | 0 | 0
2017-09-18 03:00 | 9 | 3 | 0 | 0
2017-09-18 04:00 | 9 | 4 | 0 | 0
2017-09-18 05:00 | 9 | 5 | 0 | 0
2017-09-18 06:00 | 9 | 6 | 1266.1189 | 1266.1189
2017-09-18 07:00 | 9 | 7 | 3454.6287 | 3454.6287
2017-09-18 08:00 | 9 | 8 | 5322.4564 | 5322.4564
2017-09-18 09:00 | 9 | 9 | 6680.4627 | 6680.4627
2017-09-18 10:00 | 9 | 10 | 7421.6101 | 7421.6101
2017-09-18 11:00 | 9 | 11 | 7641.9363 | 7641.9363
2017-09-18 12:00 | 9 | 12 | 7342.9202 | 7342.9202
2017-09-18 13:00 | 9 | 13 | 6597.8225 | 6597.8225
2017-09-18 14:00 | 9 | 14 | 1607.7598 | 1607.7598
2017-09-18 15:00 | 9 | 15 | 1465.7382 | 1465.7382
2017-09-18 16:00 | 9 | 16 | 1768.3021 | 1768.3021
2017-09-18 17:00 | 9 | 17 | 161.9418 | 161.9418
2017-09-18 18:00 | 9 | 18 | 0 | 0
2017-09-18 19:00 | 9 | 19 | 0 | 0
2017-09-18 20:00 | 9 | 20 | 0 | 0
2017-09-18 21:00 | 9 | 21 | 0 | 0
2017-09-18 22:00 | 9 | 22 | 0 | 0
2017-09-18 23:00 | 9 | 23 | 0 | 0
2017-09-19 | 9 | 0 | 0 | 0
2017-09-19 01:00 | 9 | 1 | 0 | 0
2017-09-19 02:00 | 9 | 2 | 0 | 0
2017-09-19 03:00 | 9 | 3 | 0 | 0
2017-09-19 04:00 | 9 | 4 | 0 | 0
2017-09-19 05:00 | 9 | 5 | 0 | 0
2017-09-19 06:00 | 9 | 6 | 1339.2555 | 1339.2555
2017-09-19 07:00 | 9 | 7 | 3672.9229 | 3672.9229
2017-09-19 08:00 | 9 | 8 | 5652.7583 | 5652.7583
2017-09-19 09:00 | 9 | 9 | 7040.4495 | 7040.4495
2017-09-19 10:00 | 9 | 10 | 7862.213 | 7862.2131
2017-09-19 11:00 | 9 | 11 | 8123.9404 | 8123.9404
2017-09-19 12:00 | 9 | 12 | 7859.683 | 7859.683
2017-09-19 13:00 | 9 | 13 | 7113.9138 | 7113.9138
2017-09-19 14:00 | 9 | 14 | 5834.3617 | 5834.3617
2017-09-19 15:00 | 9 | 15 | 4021.2015 | 4021.2015
2017-09-19 16:00 | 9 | 16 | 1814.3159 | 1814.3159
2017-09-19 17:00 | 9 | 17 | 153.8631 | 153.8631
2017-09-19 18:00 | 9 | 18 | 0 | 0
2017-09-19 19:00 | 9 | 19 | 0 | 0
2017-09-19 20:00 | 9 | 20 | 0 | 0
2017-09-19 21:00 | 9 | 21 | 0 | 0
2017-09-19 22:00 | 9 | 22 | 0 | 0
2017-09-19 23:00 | 9 | 23 | 0 | 0
2017-09-20 | 9 | 0 | 0 | 0
2017-09-20 01:00 | 9 | 1 | 0 | 0
2017-09-20 02:00 | 9 | 2 | 0 | 0
2017-09-20 03:00 | 9 | 3 | 0 | 0
2017-09-20 04:00 | 9 | 4 | 0 | 0
2017-09-20 05:00 | 9 | 5 | 0 | 0
2017-09-20 06:00 | 9 | 6 | 1278.1572 | 1278.1572
2017-09-20 07:00 | 9 | 7 | 3572.7429 | 3572.7429
2017-09-20 08:00 | 9 | 8 | 5508.7461 | 5508.7461
2017-09-20 09:00 | 9 | 9 | 6838.958 | 6838.958
2017-09-20 10:00 | 9 | 10 | 7654.7266 | 7654.7266
2017-09-20 11:00 | 9 | 11 | 7929.1304 | 7929.1304
2017-09-20 12:00 | 9 | 12 | 7673.6613 | 7673.6613
2017-09-20 13:00 | 9 | 13 | 6904.7449 | 6904.7449
2017-09-20 14:00 | 9 | 14 | 5641.1996 | 5641.1996
2017-09-20 15:00 | 9 | 15 | 3874.9744 | 3874.9745
2017-09-20 16:00 | 9 | 16 | 1714.1566 | 1714.1566
2017-09-20 17:00 | 9 | 17 | 122.506 | 122.506
2017-09-20 18:00 | 9 | 18 | 0 | 0
2017-09-20 19:00 | 9 | 19 | 0 | 0
2017-09-20 20:00 | 9 | 20 | 0 | 0
2017-09-20 21:00 | 9 | 21 | 0 | 0
2017-09-20 22:00 | 9 | 22 | 0 | 0
2017-09-20 23:00 | 9 | 23 | 0 | 0
2017-09-21 | 9 | 0 | 0 | 0
2017-09-21 01:00 | 9 | 1 | 0 | 0
2017-09-21 02:00 | 9 | 2 | 0 | 0
2017-09-21 03:00 | 9 | 3 | 0 | 0
2017-09-21 04:00 | 9 | 4 | 0 | 0
2017-09-21 05:00 | 9 | 5 | 0 | 0
2017-09-21 06:00 | 9 | 6 | 1255.6781 | 1255.6781
2017-09-21 07:00 | 9 | 7 | 3488.6894 | 3488.6894
2017-09-21 08:00 | 9 | 8 | 5426.49 | 5426.49
2017-09-21 09:00 | 9 | 9 | 6742.2257 | 6742.2257
2017-09-21 10:00 | 9 | 10 | 7466.6337 | 7466.6337
2017-09-21 11:00 | 9 | 11 | 7728.3795 | 7728.3795
2017-09-21 12:00 | 9 | 12 | 7515.7767 | 7515.7767
2017-09-21 13:00 | 9 | 13 | 6814.8379 | 6814.8379
2017-09-21 14:00 | 9 | 14 | 5574.2225 | 5574.2225
2017-09-21 15:00 | 9 | 15 | 3789.3305 | 3789.3305
2017-09-21 16:00 | 9 | 16 | 1670.0748 | 1670.0749
2017-09-21 17:00 | 9 | 17 | 104.09 | 104.09
2017-09-21 18:00 | 9 | 18 | 0 | 0
2017-09-21 19:00 | 9 | 19 | 0 | 0
2017-09-21 20:00 | 9 | 20 | 0 | 0
2017-09-21 21:00 | 9 | 21 | 0 | 0
2017-09-21 22:00 | 9 | 22 | 0 | 0
2017-09-21 23:00 | 9 | 23 | 0 | 0
2017-09-22 | 9 | 0 | 0 | 0
2017-09-22 01:00 | 9 | 1 | 0 | 0
2017-09-22 02:00 | 9 | 2 | 0 | 0
2017-09-22 03:00 | 9 | 3 | 0 | 0
2017-09-22 04:00 | 9 | 4 | 0 | 0
2017-09-22 05:00 | 9 | 5 | 0 | 0
2017-09-22 06:00 | 9 | 6 | 233.6444 | 233.6443
2017-09-22 07:00 | 9 | 7 | 1593.8299 | 1593.8299
2017-09-22 08:00 | 9 | 8 | 3543.5743 | 3543.5743
2017-09-22 09:00 | 9 | 9 | 4862.3645 | 4862.3645
2017-09-22 10:00 | 9 | 10 | 5864.5124 | 5864.5124
2017-09-22 11:00 | 9 | 11 | 5675.0154 | 5675.0154
2017-09-22 12:00 | 9 | 12 | 5098.9873 | 5098.9873
2017-09-22 13:00 | 9 | 13 | 2983.9176 | 2983.9176
2017-09-22 14:00 | 9 | 14 | 2242.63 | 2242.63
2017-09-22 15:00 | 9 | 15 | 998.7474 | 998.7474
2017-09-22 16:00 | 9 | 16 | 724.2988 | 724.2988
2017-09-22 17:00 | 9 | 17 | 0 | 0
2017-09-22 18:00 | 9 | 18 | 0 | 0
2017-09-22 19:00 | 9 | 19 | 0 | 0
2017-09-22 20:00 | 9 | 20 | 0 | 0
2017-09-22 21:00 | 9 | 21 | 0 | 0
2017-09-22 22:00 | 9 | 22 | 0 | 0
2017-09-22 23:00 | 9 | 23 | 0 | 0
2017-09-23 | 9 | 0 | 0 | 0
2017-09-23 01:00 | 9 | 1 | 0 | 0
2017-09-23 02:00 | 9 | 2 | 0 | 0
2017-09-23 03:00 | 9 | 3 | 0 | 0
2017-09-23 04:00 | 9 | 4 | 0 | 0
2017-09-23 05:00 | 9 | 5 | 0 | 0
2017-09-23 06:00 | 9 | 6 | 1008.7363 | 1008.7363
2017-09-23 07:00 | 9 | 7 | 1615.0163 | 1615.0163
2017-09-23 08:00 | 9 | 8 | 1590.8249 | 1590.8249
2017-09-23 09:00 | 9 | 9 | 3810.4295 | 3810.4295
2017-09-23 10:00 | 9 | 10 | 4827.8507 | 4827.8507
2017-09-23 11:00 | 9 | 11 | 4859.9782 | 4859.9782
2017-09-23 12:00 | 9 | 12 | 5918.8936 | 5918.8936
2017-09-23 13:00 | 9 | 13 | 6212.6737 | 6212.6737
2017-09-23 14:00 | 9 | 14 | 4228.811 | 4228.811
2017-09-23 15:00 | 9 | 15 | 3169.5334 | 3169.5334
2017-09-23 16:00 | 9 | 16 | 217.3603 | 217.3603
2017-09-23 17:00 | 9 | 17 | 0 | 0
2017-09-23 18:00 | 9 | 18 | 0 | 0
2017-09-23 19:00 | 9 | 19 | 0 | 0
2017-09-23 20:00 | 9 | 20 | 0 | 0
2017-09-23 21:00 | 9 | 21 | 0 | 0
2017-09-23 22:00 | 9 | 22 | 0 | 0
2017-09-23 23:00 | 9 | 23 | 0 | 0
2017-09-24 | 9 | 0 | 0 | 0
2017-09-24 01:00 | 9 | 1 | 0 | 0
2017-09-24 02:00 | 9 | 2 | 0 | 0
2017-09-24 03:00 | 9 | 3 | 0 | 0
2017-09-24 04:00 | 9 | 4 | 0 | 0
2017-09-24 05:00 | 9 | 5 | 0 | 0
2017-09-24 06:00 | 9 | 6 | 1001.4706 | 1001.4706
2017-09-24 07:00 | 9 | 7 | 3008.9623 | 3008.9623
2017-09-24 08:00 | 9 | 8 | 4880.9956 | 4880.9956
2017-09-24 09:00 | 9 | 9 | 441.9737 | 441.9737
2017-09-24 10:00 | 9 | 10 | 2513.7608 | 2513.7608
2017-09-24 11:00 | 9 | 11 | 3530.6081 | 3530.6081
2017-09-24 12:00 | 9 | 12 | 935.6135 | 935.6135
2017-09-24 13:00 | 9 | 13 | 2381.2602 | 2381.2602
2017-09-24 14:00 | 9 | 14 | 2492.3674 | 2492.3674
2017-09-24 15:00 | 9 | 15 | 3566.1523 | 3566.1523
2017-09-24 16:00 | 9 | 16 | 1159.806 | 1159.806
2017-09-24 17:00 | 9 | 17 | 0 | 0
2017-09-24 18:00 | 9 | 18 | 0 | 0
2017-09-24 19:00 | 9 | 19 | 0 | 0
2017-09-24 20:00 | 9 | 20 | 0 | 0
2017-09-24 21:00 | 9 | 21 | 0 | 0
2017-09-24 22:00 | 9 | 22 | 0 | 0
2017-09-24 23:00 | 9 | 23 | 0 | 0
2017-09-25 | 9 | 0 | 0 | 0
2017-09-25 01:00 | 9 | 1 | 0 | 0
2017-09-25 02:00 | 9 | 2 | 0 | 0
2017-09-25 03:00 | 9 | 3 | 0 | 0
2017-09-25 04:00 | 9 | 4 | 0 | 0
2017-09-25 05:00 | 9 | 5 | 0 | 0
2017-09-25 06:00 | 9 | 6 | 1189.0241 | 1189.0241
2017-09-25 07:00 | 9 | 7 | 3505.7301 | 3505.7301
2017-09-25 08:00 | 9 | 8 | 5634.3755 | 5634.3755
2017-09-25 09:00 | 9 | 9 | 6889.8949 | 6889.8949
2017-09-25 10:00 | 9 | 10 | 7686.8415 | 7686.8415
2017-09-25 11:00 | 9 | 11 | 5513.8429 | 5513.8429
2017-09-25 12:00 | 9 | 12 | 3321.4093 | 3321.4093
2017-09-25 13:00 | 9 | 13 | 7026.577 | 7026.577
2017-09-25 14:00 | 9 | 14 | 5650.6078 | 5650.6078
2017-09-25 15:00 | 9 | 15 | 3766.6548 | 3766.6548
2017-09-25 16:00 | 9 | 16 | 1561.5954 | 1561.5954
2017-09-25 17:00 | 9 | 17 | 0 | 0
2017-09-25 18:00 | 9 | 18 | 0 | 0
2017-09-25 19:00 | 9 | 19 | 0 | 0
2017-09-25 20:00 | 9 | 20 | 0 | 0
2017-09-25 21:00 | 9 | 21 | 0 | 0
2017-09-25 22:00 | 9 | 22 | 0 | 0
2017-09-25 23:00 | 9 | 23 | 0 | 0
2017-09-26 | 9 | 0 | 0 | 0
2017-09-26 01:00 | 9 | 1 | 0 | 0
2017-09-26 02:00 | 9 | 2 | 0 | 0
2017-09-26 03:00 | 9 | 3 | 0 | 0
2017-09-26 04:00 | 9 | 4 | 0 | 0
2017-09-26 05:00 | 9 | 5 | 0 | 0
2017-09-26 06:00 | 9 | 6 | 1203.8821 | 1203.8821
2017-09-26 07:00 | 9 | 7 | 3510.6383 | 3510.6383
2017-09-26 08:00 | 9 | 8 | 5509.8961 | 5509.8961
2017-09-26 09:00 | 9 | 9 | 6895.6771 | 6895.6772
2017-09-26 10:00 | 9 | 10 | 7714.3081 | 7714.3081
2017-09-26 11:00 | 9 | 11 | 7970.4752 | 7970.4752
2017-09-26 12:00 | 9 | 12 | 7726.076 | 7726.0761
2017-09-26 13:00 | 9 | 13 | 6906.3917 | 6906.3917
2017-09-26 14:00 | 9 | 14 | 5621.4104 | 5621.4104
2017-09-26 15:00 | 9 | 15 | 3731.0014 | 3731.0014
2017-09-26 16:00 | 9 | 16 | 1514.458 | 1514.458
2017-09-26 17:00 | 9 | 17 | 0 | 0
2017-09-26 18:00 | 9 | 18 | 0 | 0
2017-09-26 19:00 | 9 | 19 | 0 | 0
2017-09-26 20:00 | 9 | 20 | 0 | 0
2017-09-26 21:00 | 9 | 21 | 0 | 0
2017-09-26 22:00 | 9 | 22 | 0 | 0
2017-09-26 23:00 | 9 | 23 | 0 | 0
2017-09-27 | 9 | 0 | 0 | 0
2017-09-27 01:00 | 9 | 1 | 0 | 0
2017-09-27 02:00 | 9 | 2 | 0 | 0
2017-09-27 03:00 | 9 | 3 | 0 | 0
2017-09-27 04:00 | 9 | 4 | 0 | 0
2017-09-27 05:00 | 9 | 5 | 0 | 0
2017-09-27 06:00 | 9 | 6 | 39.8578 | 39.8578
2017-09-27 07:00 | 9 | 7 | 29.6596 | 29.6596
2017-09-27 08:00 | 9 | 8 | 571.0164 | 571.0164
2017-09-27 09:00 | 9 | 9 | 939.6351 | 939.6351
2017-09-27 10:00 | 9 | 10 | 1513.5897 | 1513.5897
2017-09-27 11:00 | 9 | 11 | 1028.5841 | 1028.5841
2017-09-27 12:00 | 9 | 12 | 1183.3017 | 1183.3017
2017-09-27 13:00 | 9 | 13 | 775.1034 | 775.1034
2017-09-27 14:00 | 9 | 14 | 561.1896 | 561.1896
2017-09-27 15:00 | 9 | 15 | 950.9534 | 950.9534
2017-09-27 16:00 | 9 | 16 | 422.6871 | 422.6871
2017-09-27 17:00 | 9 | 17 | 0 | 0
2017-09-27 18:00 | 9 | 18 | 0 | 0
2017-09-27 19:00 | 9 | 19 | 0 | 0
2017-09-27 20:00 | 9 | 20 | 0 | 0
2017-09-27 21:00 | 9 | 21 | 0 | 0
2017-09-27 22:00 | 9 | 22 | 0 | 0
2017-09-27 23:00 | 9 | 23 | 0 | 0
2017-09-28 | 9 | 0 | 0 | 0
2017-09-28 01:00 | 9 | 1 | 0 | 0
2017-09-28 02:00 | 9 | 2 | 0 | 0
2017-09-28 03:00 | 9 | 3 | 0 | 0
2017-09-28 04:00 | 9 | 4 | 0 | 0
2017-09-28 05:00 | 9 | 5 | 0 | 0
2017-09-28 06:00 | 9 | 6 | 1026.9661 | 1026.9661
2017-09-28 07:00 | 9 | 7 | 3163.9754 | 3163.9754
2017-09-28 08:00 | 9 | 8 | 5050.7919 | 5050.7919
2017-09-28 09:00 | 9 | 9 | 6399.2865 | 6399.2865
2017-09-28 10:00 | 9 | 10 | 7185.6025 | 7185.6025
2017-09-28 11:00 | 9 | 11 | 7406.1012 | 7406.1012
2017-09-28 12:00 | 9 | 12 | 7097.7758 | 7097.7758
2017-09-28 13:00 | 9 | 13 | 6362.5739 | 6362.5739
2017-09-28 14:00 | 9 | 14 | 5048.5414 | 5048.5414
2017-09-28 15:00 | 9 | 15 | 3213.1345 | 3213.1345
2017-09-28 16:00 | 9 | 16 | 1150.8613 | 1150.8613
2017-09-28 17:00 | 9 | 17 | 0 | 0
2017-09-28 18:00 | 9 | 18 | 0 | 0
2017-09-28 19:00 | 9 | 19 | 0 | 0
2017-09-28 20:00 | 9 | 20 | 0 | 0
2017-09-28 21:00 | 9 | 21 | 0 | 0
2017-09-28 22:00 | 9 | 22 | 0 | 0
2017-09-28 23:00 | 9 | 23 | 0 | 0
2017-09-29 | 9 | 0 | 0 | 0
2017-09-29 01:00 | 9 | 1 | 0 | 0
2017-09-29 02:00 | 9 | 2 | 0 | 0
2017-09-29 03:00 | 9 | 3 | 0 | 0
2017-09-29 04:00 | 9 | 4 | 0 | 0
2017-09-29 05:00 | 9 | 5 | 0 | 0
2017-09-29 06:00 | 9 | 6 | 1044.6393 | 1044.6393
2017-09-29 07:00 | 9 | 7 | 3199.4299 | 3199.4299
2017-09-29 08:00 | 9 | 8 | 5117.6391 | 5117.6391
2017-09-29 09:00 | 9 | 9 | 6517.5203 | 6517.5203
2017-09-29 10:00 | 9 | 10 | 7315.0189 | 7315.0189
2017-09-29 11:00 | 9 | 11 | 7557.1744 | 7557.1744
2017-09-29 12:00 | 9 | 12 | 7319.1163 | 7319.1163
2017-09-29 13:00 | 9 | 13 | 4070.6251 | 4070.6251
2017-09-29 14:00 | 9 | 14 | 4707.4916 | 4707.4916
2017-09-29 15:00 | 9 | 15 | 583.2478 | 583.2478
2017-09-29 16:00 | 9 | 16 | 387.6236 | 387.6236
2017-09-29 17:00 | 9 | 17 | 0 | 0
2017-09-29 18:00 | 9 | 18 | 0 | 0
2017-09-29 19:00 | 9 | 19 | 0 | 0
2017-09-29 20:00 | 9 | 20 | 0 | 0
2017-09-29 21:00 | 9 | 21 | 0 | 0
2017-09-29 22:00 | 9 | 22 | 0 | 0
2017-09-29 23:00 | 9 | 23 | 0 | 0
2017-09-30 | 9 | 0 | 0 | 0
2017-09-30 01:00 | 9 | 1 | 0 | 0
2017-09-30 02:00 | 9 | 2 | 0 | 0
2017-09-30 03:00 | 9 | 3 | 0 | 0
2017-09-30 04:00 | 9 | 4 | 0 | 0
2017-09-30 05:00 | 9 | 5 | 0 | 0
2017-09-30 06:00 | 9 | 6 | 40.7687 | 40.7687
2017-09-30 07:00 | 9 | 7 | 197.0479 | 197.0479
2017-09-30 08:00 | 9 | 8 | 302.8168 | 302.8168
2017-09-30 09:00 | 9 | 9 | 2009.3421 | 2009.3421
2017-09-30 10:00 | 9 | 10 | 1983.3567 | 1983.3567
2017-09-30 11:00 | 9 | 11 | 7735.7395 | 7735.7395
2017-09-30 12:00 | 9 | 12 | 1965.6214 | 1965.6214
2017-09-30 13:00 | 9 | 13 | 2030.8241 | 2030.8241
2017-09-30 14:00 | 9 | 14 | 2605.1571 | 2605.1571
2017-09-30 15:00 | 9 | 15 | 711.9224 | 711.9224
2017-09-30 16:00 | 9 | 16 | 355.3534 | 355.3534
2017-09-30 17:00 | 9 | 17 | 0 | 0
2017-09-30 18:00 | 9 | 18 | 0 | 0
2017-09-30 19:00 | 9 | 19 | 0 | 0
2017-09-30 20:00 | 9 | 20 | 0 | 0
2017-09-30 21:00 | 9 | 21 | 0 | 0
2017-09-30 22:00 | 9 | 22 | 0 | 0
2017-09-30 23:00 | 9 | 23 | 0 | 0
2017-10-01 | 10 | 0 | 0 | 0
2017-10-01 01:00 | 10 | 1 | 0 | 0
2017-10-01 02:00 | 10 | 2 | 0 | 0
2017-10-01 03:00 | 10 | 3 | 0 | 0
2017-10-01 04:00 | 10 | 4 | 0 | 0
2017-10-01 05:00 | 10 | 5 | 0 | 0
2017-10-01 06:00 | 10 | 6 | 384.6048 | 384.6048
2017-10-01 07:00 | 10 | 7 | 820.4123 | 820.4123
2017-10-01 08:00 | 10 | 8 | 2337.7372 | 2337.7372
2017-10-01 09:00 | 10 | 9 | 3292.9997 | 3292.9997
2017-10-01 10:00 | 10 | 10 | 4326.4633 | 4326.4633
2017-10-01 11:00 | 10 | 11 | 2538.2202 | 2538.2202
2017-10-01 12:00 | 10 | 12 | 3674.9446 | 3674.9446
2017-10-01 13:00 | 10 | 13 | 2688.1997 | 2688.1997
2017-10-01 14:00 | 10 | 14 | 2911.7551 | 2911.7551
2017-10-01 15:00 | 10 | 15 | 363.914 | 363.914
2017-10-01 16:00 | 10 | 16 | 449.029 | 449.029
2017-10-01 17:00 | 10 | 17 | 0 | 0
2017-10-01 18:00 | 10 | 18 | 0 | 0
2017-10-01 19:00 | 10 | 19 | 0 | 0
2017-10-01 20:00 | 10 | 20 | 0 | 0
2017-10-01 21:00 | 10 | 21 | 0 | 0
2017-10-01 22:00 | 10 | 22 | 0 | 0
2017-10-01 23:00 | 10 | 23 | 0 | 0
2017-10-02 | 10 | 0 | 0 | 0
2017-10-02 01:00 | 10 | 1 | 0 | 0
2017-10-02 02:00 | 10 | 2 | 0 | 0
2017-10-02 03:00 | 10 | 3 | 0 | 0
2017-10-02 04:00 | 10 | 4 | 0 | 0
2017-10-02 05:00 | 10 | 5 | 0 | 0
2017-10-02 06:00 | 10 | 6 | 120.7293 | 120.7293
2017-10-02 07:00 | 10 | 7 | 358.8356 | 358.8356
2017-10-02 08:00 | 10 | 8 | 1643.3718 | 1643.3718
2017-10-02 09:00 | 10 | 9 | 723.7594 | 723.7594
2017-10-02 10:00 | 10 | 10 | 1367.0981 | 1367.0981
2017-10-02 11:00 | 10 | 11 | 2441.6156 | 2441.6156
2017-10-02 12:00 | 10 | 12 | 1529.5851 | 1529.5851
2017-10-02 13:00 | 10 | 13 | 1587.0506 | 1587.0506
2017-10-02 14:00 | 10 | 14 | 1526.2616 | 1526.2616
2017-10-02 15:00 | 10 | 15 | 1476.9289 | 1476.9289
2017-10-02 16:00 | 10 | 16 | 109.3546 | 109.3546
2017-10-02 17:00 | 10 | 17 | 0 | 0
2017-10-02 18:00 | 10 | 18 | 0 | 0
2017-10-02 19:00 | 10 | 19 | 0 | 0
2017-10-02 20:00 | 10 | 20 | 0 | 0
2017-10-02 21:00 | 10 | 21 | 0 | 0
2017-10-02 22:00 | 10 | 22 | 0 | 0
2017-10-02 23:00 | 10 | 23 | 0 | 0
2017-10-03 | 10 | 0 | 0 | 0
2017-10-03 01:00 | 10 | 1 | 0 | 0
2017-10-03 02:00 | 10 | 2 | 0 | 0
2017-10-03 03:00 | 10 | 3 | 0 | 0
2017-10-03 04:00 | 10 | 4 | 0 | 0
2017-10-03 05:00 | 10 | 5 | 0 | 0
2017-10-03 06:00 | 10 | 6 | 71.4886 | 71.4886
2017-10-03 07:00 | 10 | 7 | 428.1461 | 428.1461
2017-10-03 08:00 | 10 | 8 | 812.8499 | 812.8499
2017-10-03 09:00 | 10 | 9 | 1191.1631 | 1191.1631
2017-10-03 10:00 | 10 | 10 | 1592.5763 | 1592.5763
2017-10-03 11:00 | 10 | 11 | 1290.5208 | 1290.5208
2017-10-03 12:00 | 10 | 12 | 2092.456 | 2092.456
2017-10-03 13:00 | 10 | 13 | 1890.2423 | 1890.2423
2017-10-03 14:00 | 10 | 14 | 1753.1152 | 1753.1152
2017-10-03 15:00 | 10 | 15 | 739.6478 | 739.6478
2017-10-03 16:00 | 10 | 16 | 1119.4238 | 1119.4238
2017-10-03 17:00 | 10 | 17 | 0 | 0
2017-10-03 18:00 | 10 | 18 | 0 | 0
2017-10-03 19:00 | 10 | 19 | 0 | 0
2017-10-03 20:00 | 10 | 20 | 0 | 0
2017-10-03 21:00 | 10 | 21 | 0 | 0
2017-10-03 22:00 | 10 | 22 | 0 | 0
2017-10-03 23:00 | 10 | 23 | 0 | 0
2017-10-04 | 10 | 0 | 0 | 0
2017-10-04 01:00 | 10 | 1 | 0 | 0
2017-10-04 02:00 | 10 | 2 | 0 | 0
2017-10-04 03:00 | 10 | 3 | 0 | 0
2017-10-04 04:00 | 10 | 4 | 0 | 0
2017-10-04 05:00 | 10 | 5 | 0 | 0
2017-10-04 06:00 | 10 | 6 | 335.7034 | 335.7034
2017-10-04 07:00 | 10 | 7 | 3230.925 | 3230.925
2017-10-04 08:00 | 10 | 8 | 3806.3321 | 3806.3321
2017-10-04 09:00 | 10 | 9 | 4913.9488 | 4913.9488
2017-10-04 10:00 | 10 | 10 | 3381.414 | 3381.414
2017-10-04 11:00 | 10 | 11 | 3563.6004 | 3563.6004
2017-10-04 12:00 | 10 | 12 | 2471.5869 | 2471.5869
2017-10-04 13:00 | 10 | 13 | 1433.7866 | 1433.7866
2017-10-04 14:00 | 10 | 14 | 1370.2319 | 1370.2319
2017-10-04 15:00 | 10 | 15 | 1948.7727 | 1948.7727
2017-10-04 16:00 | 10 | 16 | 412.0013 | 412.0013
2017-10-04 17:00 | 10 | 17 | 0 | 0
2017-10-04 18:00 | 10 | 18 | 0 | 0
2017-10-04 19:00 | 10 | 19 | 0 | 0
2017-10-04 20:00 | 10 | 20 | 0 | 0
2017-10-04 21:00 | 10 | 21 | 0 | 0
2017-10-04 22:00 | 10 | 22 | 0 | 0
2017-10-04 23:00 | 10 | 23 | 0 | 0
2017-10-05 | 10 | 0 | 0 | 0
2017-10-05 01:00 | 10 | 1 | 0 | 0
2017-10-05 02:00 | 10 | 2 | 0 | 0
2017-10-05 03:00 | 10 | 3 | 0 | 0
2017-10-05 04:00 | 10 | 4 | 0 | 0
2017-10-05 05:00 | 10 | 5 | 0 | 0
2017-10-05 06:00 | 10 | 6 | 883.4588 | 883.4588
2017-10-05 07:00 | 10 | 7 | 3089.782 | 3089.782
2017-10-05 08:00 | 10 | 8 | 5044.3991 | 5044.3991
2017-10-05 09:00 | 10 | 9 | 4927.8063 | 4927.8063
2017-10-05 10:00 | 10 | 10 | 4255.3737 | 4255.3737
2017-10-05 11:00 | 10 | 11 | 4296.4046 | 4296.4046
2017-10-05 12:00 | 10 | 12 | 2901.9893 | 2901.9893
2017-10-05 13:00 | 10 | 13 | 2542.3728 | 2542.3728
2017-10-05 14:00 | 10 | 14 | 1142.6952 | 1142.6952
2017-10-05 15:00 | 10 | 15 | 1624.7648 | 1624.7648
2017-10-05 16:00 | 10 | 16 | 174.3319 | 174.3319
2017-10-05 17:00 | 10 | 17 | 0 | 0
2017-10-05 18:00 | 10 | 18 | 0 | 0
2017-10-05 19:00 | 10 | 19 | 0 | 0
2017-10-05 20:00 | 10 | 20 | 0 | 0
2017-10-05 21:00 | 10 | 21 | 0 | 0
2017-10-05 22:00 | 10 | 22 | 0 | 0
2017-10-05 23:00 | 10 | 23 | 0 | 0
2017-10-06 | 10 | 0 | 0 | 0
2017-10-06 01:00 | 10 | 1 | 0 | 0
2017-10-06 02:00 | 10 | 2 | 0 | 0
2017-10-06 03:00 | 10 | 3 | 0 | 0
2017-10-06 04:00 | 10 | 4 | 0 | 0
2017-10-06 05:00 | 10 | 5 | 0 | 0
2017-10-06 06:00 | 10 | 6 | 948.6718 | 948.6718
2017-10-06 07:00 | 10 | 7 | 3146.8255 | 3146.8255
2017-10-06 08:00 | 10 | 8 | 5072.1256 | 5072.1256
2017-10-06 09:00 | 10 | 9 | 6385.4865 | 6385.4865
2017-10-06 10:00 | 10 | 10 | 7179.4051 | 7179.4052
2017-10-06 11:00 | 10 | 11 | 7464.5269 | 7464.5269
2017-10-06 12:00 | 10 | 12 | 7176.3519 | 7176.3519
2017-10-06 13:00 | 10 | 13 | 6359.3976 | 6359.3976
2017-10-06 14:00 | 10 | 14 | 5079.4177 | 5079.4177
2017-10-06 15:00 | 10 | 15 | 3194.3228 | 3194.3228
2017-10-06 16:00 | 10 | 16 | 1051.8969 | 1051.8969
2017-10-06 17:00 | 10 | 17 | 0 | 0
2017-10-06 18:00 | 10 | 18 | 0 | 0
2017-10-06 19:00 | 10 | 19 | 0 | 0
2017-10-06 20:00 | 10 | 20 | 0 | 0
2017-10-06 21:00 | 10 | 21 | 0 | 0
2017-10-06 22:00 | 10 | 22 | 0 | 0
2017-10-06 23:00 | 10 | 23 | 0 | 0
2017-10-07 | 10 | 0 | 0 | 0
2017-10-07 01:00 | 10 | 1 | 0 | 0
2017-10-07 02:00 | 10 | 2 | 0 | 0
2017-10-07 03:00 | 10 | 3 | 0 | 0
2017-10-07 04:00 | 10 | 4 | 0 | 0
2017-10-07 05:00 | 10 | 5 | 0 | 0
2017-10-07 06:00 | 10 | 6 | 479.8662 | 479.8662
2017-10-07 07:00 | 10 | 7 | 3050.1991 | 3050.1991
2017-10-07 08:00 | 10 | 8 | 4944.1467 | 4944.1467
2017-10-07 09:00 | 10 | 9 | 6316.7602 | 6316.7602
2017-10-07 10:00 | 10 | 10 | 7141.7863 | 7141.7863
2017-10-07 11:00 | 10 | 11 | 7365.3463 | 7365.3463
2017-10-07 12:00 | 10 | 12 | 7059.7039 | 7059.7039
2017-10-07 13:00 | 10 | 13 | 6240.6785 | 6240.6785
2017-10-07 14:00 | 10 | 14 | 4953.4962 | 4953.4962
2017-10-07 15:00 | 10 | 15 | 3075.0425 | 3075.0425
2017-10-07 16:00 | 10 | 16 | 976.4362 | 976.4362
2017-10-07 17:00 | 10 | 17 | 0 | 0
2017-10-07 18:00 | 10 | 18 | 0 | 0
2017-10-07 19:00 | 10 | 19 | 0 | 0
2017-10-07 20:00 | 10 | 20 | 0 | 0
2017-10-07 21:00 | 10 | 21 | 0 | 0
2017-10-07 22:00 | 10 | 22 | 0 | 0
2017-10-07 23:00 | 10 | 23 | 0 | 0
2017-10-08 | 10 | 0 | 0 | 0
2017-10-08 01:00 | 10 | 1 | 0 | 0
2017-10-08 02:00 | 10 | 2 | 0 | 0
2017-10-08 03:00 | 10 | 3 | 0 | 0
2017-10-08 04:00 | 10 | 4 | 0 | 0
2017-10-08 05:00 | 10 | 5 | 0 | 0
2017-10-08 06:00 | 10 | 6 | 942.1892 | 942.1892
2017-10-08 07:00 | 10 | 7 | 3213.2713 | 3213.2713
2017-10-08 08:00 | 10 | 8 | 5203.244 | 5203.244
2017-10-08 09:00 | 10 | 9 | 6604.5857 | 6604.5857
2017-10-08 10:00 | 10 | 10 | 7398.5123 | 7398.5123
2017-10-08 11:00 | 10 | 11 | 7618.8834 | 7618.8834
2017-10-08 12:00 | 10 | 12 | 7324.6869 | 7324.687
2017-10-08 13:00 | 10 | 13 | 6449.7589 | 6449.7589
2017-10-08 14:00 | 10 | 14 | 5108.9785 | 5108.9785
2017-10-08 15:00 | 10 | 15 | 3162.799 | 3162.799
2017-10-08 16:00 | 10 | 16 | 979.5171 | 979.5171
2017-10-08 17:00 | 10 | 17 | 0 | 0
2017-10-08 18:00 | 10 | 18 | 0 | 0
2017-10-08 19:00 | 10 | 19 | 0 | 0
2017-10-08 20:00 | 10 | 20 | 0 | 0
2017-10-08 21:00 | 10 | 21 | 0 | 0
2017-10-08 22:00 | 10 | 22 | 0 | 0
2017-10-08 23:00 | 10 | 23 | 0 | 0
2017-10-09 | 10 | 0 | 0 | 0
2017-10-09 01:00 | 10 | 1 | 0 | 0
2017-10-09 02:00 | 10 | 2 | 0 | 0
2017-10-09 03:00 | 10 | 3 | 0 | 0
2017-10-09 04:00 | 10 | 4 | 0 | 0
2017-10-09 05:00 | 10 | 5 | 0 | 0
2017-10-09 06:00 | 10 | 6 | 128.4792 | 128.4792
2017-10-09 07:00 | 10 | 7 | 2572.4614 | 2572.4614
2017-10-09 08:00 | 10 | 8 | 4377.4014 | 4377.4014
2017-10-09 09:00 | 10 | 9 | 2826.056 | 2826.056
2017-10-09 10:00 | 10 | 10 | 1218.7654 | 1218.7654
2017-10-09 11:00 | 10 | 11 | 992.366 | 992.366
2017-10-09 12:00 | 10 | 12 | 2799.3036 | 2799.3036
2017-10-09 13:00 | 10 | 13 | 2858.7539 | 2858.7539
2017-10-09 14:00 | 10 | 14 | 1010.1393 | 1010.1393
2017-10-09 15:00 | 10 | 15 | 246.1759 | 246.1759
2017-10-09 16:00 | 10 | 16 | 316.7019 | 316.7019
2017-10-09 17:00 | 10 | 17 | 0 | 0
2017-10-09 18:00 | 10 | 18 | 0 | 0
2017-10-09 19:00 | 10 | 19 | 0 | 0
2017-10-09 20:00 | 10 | 20 | 0 | 0
2017-10-09 21:00 | 10 | 21 | 0 | 0
2017-10-09 22:00 | 10 | 22 | 0 | 0
2017-10-09 23:00 | 10 | 23 | 0 | 0
2017-10-10 | 10 | 0 | 0 | 0
2017-10-10 01:00 | 10 | 1 | 0 | 0
2017-10-10 02:00 | 10 | 2 | 0 | 0
2017-10-10 03:00 | 10 | 3 | 0 | 0
2017-10-10 04:00 | 10 | 4 | 0 | 0
2017-10-10 05:00 | 10 | 5 | 0 | 0
2017-10-10 06:00 | 10 | 6 | 932.8547 | 932.8547
2017-10-10 07:00 | 10 | 7 | 3258.6446 | 3258.6446
2017-10-10 08:00 | 10 | 8 | 5343.9798 | 5343.9798
2017-10-10 09:00 | 10 | 9 | 6712.0463 | 6712.0463
2017-10-10 10:00 | 10 | 10 | 7510.1543 | 7510.1543
2017-10-10 11:00 | 10 | 11 | 7758.3784 | 7758.3784
2017-10-10 12:00 | 10 | 12 | 7421.8378 | 7421.8378
2017-10-10 13:00 | 10 | 13 | 6503.2201 | 6503.2201
2017-10-10 14:00 | 10 | 14 | 5099.8843 | 5099.8843
2017-10-10 15:00 | 10 | 15 | 3122.6766 | 3122.6766
2017-10-10 16:00 | 10 | 16 | 935.6457 | 935.6457
2017-10-10 17:00 | 10 | 17 | 0 | 0
2017-10-10 18:00 | 10 | 18 | 0 | 0
2017-10-10 19:00 | 10 | 19 | 0 | 0
2017-10-10 20:00 | 10 | 20 | 0 | 0
2017-10-10 21:00 | 10 | 21 | 0 | 0
2017-10-10 22:00 | 10 | 22 | 0 | 0
2017-10-10 23:00 | 10 | 23 | 0 | 0
2017-10-11 | 10 | 0 | 0 | 0
2017-10-11 01:00 | 10 | 1 | 0 | 0
2017-10-11 02:00 | 10 | 2 | 0 | 0
2017-10-11 03:00 | 10 | 3 | 0 | 0
2017-10-11 04:00 | 10 | 4 | 0 | 0
2017-10-11 05:00 | 10 | 5 | 0 | 0
2017-10-11 06:00 | 10 | 6 | 791.024 | 791.024
2017-10-11 07:00 | 10 | 7 | 2243.1279 | 2243.1279
2017-10-11 08:00 | 10 | 8 | 4584.6693 | 4584.6693
2017-10-11 09:00 | 10 | 9 | 5177.1401 | 5177.1401
2017-10-11 10:00 | 10 | 10 | 7115.9631 | 7115.9631
2017-10-11 11:00 | 10 | 11 | 7324.7836 | 7324.7836
2017-10-11 12:00 | 10 | 12 | 6996.2849 | 6996.2849
2017-10-11 13:00 | 10 | 13 | 6152.5172 | 6152.5172
2017-10-11 14:00 | 10 | 14 | 4768.2967 | 4768.2967
2017-10-11 15:00 | 10 | 15 | 2876.6548 | 2876.6548
2017-10-11 16:00 | 10 | 16 | 790.6376 | 790.6376
2017-10-11 17:00 | 10 | 17 | 0 | 0
2017-10-11 18:00 | 10 | 18 | 0 | 0
2017-10-11 19:00 | 10 | 19 | 0 | 0
2017-10-11 20:00 | 10 | 20 | 0 | 0
2017-10-11 21:00 | 10 | 21 | 0 | 0
2017-10-11 22:00 | 10 | 22 | 0 | 0
2017-10-11 23:00 | 10 | 23 | 0 | 0
2017-10-12 | 10 | 0 | 0 | 0
2017-10-12 01:00 | 10 | 1 | 0 | 0
2017-10-12 02:00 | 10 | 2 | 0 | 0
2017-10-12 03:00 | 10 | 3 | 0 | 0
2017-10-12 04:00 | 10 | 4 | 0 | 0
2017-10-12 05:00 | 10 | 5 | 0 | 0
2017-10-12 06:00 | 10 | 6 | 778.726 | 778.726
2017-10-12 07:00 | 10 | 7 | 2963.167 | 2963.167
2017-10-12 08:00 | 10 | 8 | 4889.6723 | 4889.6723
2017-10-12 09:00 | 10 | 9 | 6170.3664 | 6170.3664
2017-10-12 10:00 | 10 | 10 | 6880.6949 | 6880.6949
2017-10-12 11:00 | 10 | 11 | 7084.4174 | 7084.4174
2017-10-12 12:00 | 10 | 12 | 6796.5471 | 6796.5472
2017-10-12 13:00 | 10 | 13 | 5963.3951 | 5963.3951
2017-10-12 14:00 | 10 | 14 | 4627.8047 | 4627.8047
2017-10-12 15:00 | 10 | 15 | 2801.6289 | 2801.6289
2017-10-12 16:00 | 10 | 16 | 758.3261 | 758.3261
2017-10-12 17:00 | 10 | 17 | 0 | 0
2017-10-12 18:00 | 10 | 18 | 0 | 0
2017-10-12 19:00 | 10 | 19 | 0 | 0
2017-10-12 20:00 | 10 | 20 | 0 | 0
2017-10-12 21:00 | 10 | 21 | 0 | 0
2017-10-12 22:00 | 10 | 22 | 0 | 0
2017-10-12 23:00 | 10 | 23 | 0 | 0
2017-10-13 | 10 | 0 | 0 | 0
2017-10-13 01:00 | 10 | 1 | 0 | 0
2017-10-13 02:00 | 10 | 2 | 0 | 0
2017-10-13 03:00 | 10 | 3 | 0 | 0
2017-10-13 04:00 | 10 | 4 | 0 | 0
2017-10-13 05:00 | 10 | 5 | 0 | 0
2017-10-13 06:00 | 10 | 6 | 188.0192 | 188.0192
2017-10-13 07:00 | 10 | 7 | 1678.3629 | 1678.3629
2017-10-13 08:00 | 10 | 8 | 315.7773 | 315.7773
2017-10-13 09:00 | 10 | 9 | 1995.8192 | 1995.8192
2017-10-13 10:00 | 10 | 10 | 3970.0771 | 3970.0771
2017-10-13 11:00 | 10 | 11 | 3992.524 | 3992.524
2017-10-13 12:00 | 10 | 12 | 4414.099 | 4414.099
2017-10-13 13:00 | 10 | 13 | 3012.7102 | 3012.7102
2017-10-13 14:00 | 10 | 14 | 3624.5481 | 3624.5481
2017-10-13 15:00 | 10 | 15 | 1841.3627 | 1841.3627
2017-10-13 16:00 | 10 | 16 | 651.5037 | 651.5037
2017-10-13 17:00 | 10 | 17 | 0 | 0
2017-10-13 18:00 | 10 | 18 | 0 | 0
2017-10-13 19:00 | 10 | 19 | 0 | 0
2017-10-13 20:00 | 10 | 20 | 0 | 0
2017-10-13 21:00 | 10 | 21 | 0 | 0
2017-10-13 22:00 | 10 | 22 | 0 | 0
2017-10-13 23:00 | 10 | 23 | 0 | 0
2017-10-14 | 10 | 0 | 0 | 0
2017-10-14 01:00 | 10 | 1 | 0 | 0
2017-10-14 02:00 | 10 | 2 | 0 | 0
2017-10-14 03:00 | 10 | 3 | 0 | 0
2017-10-14 04:00 | 10 | 4 | 0 | 0
2017-10-14 05:00 | 10 | 5 | 0 | 0
2017-10-14 06:00 | 10 | 6 | 752.9027 | 752.9027
2017-10-14 07:00 | 10 | 7 | 2310.1177 | 2310.1177
2017-10-14 08:00 | 10 | 8 | 4823.284 | 4823.284
2017-10-14 09:00 | 10 | 9 | 6168.0192 | 6168.0192
2017-10-14 10:00 | 10 | 10 | 5953.7144 | 5953.7144
2017-10-14 11:00 | 10 | 11 | 3039.2269 | 3039.2269
2017-10-14 12:00 | 10 | 12 | 4011.4714 | 4011.4714
2017-10-14 13:00 | 10 | 13 | 3520.9147 | 3520.9147
2017-10-14 14:00 | 10 | 14 | 4663.9998 | 4663.9998
2017-10-14 15:00 | 10 | 15 | 2732.3068 | 2732.3068
2017-10-14 16:00 | 10 | 16 | 699.6623 | 699.6623
2017-10-14 17:00 | 10 | 17 | 0 | 0
2017-10-14 18:00 | 10 | 18 | 0 | 0
2017-10-14 19:00 | 10 | 19 | 0 | 0
2017-10-14 20:00 | 10 | 20 | 0 | 0
2017-10-14 21:00 | 10 | 21 | 0 | 0
2017-10-14 22:00 | 10 | 22 | 0 | 0
2017-10-14 23:00 | 10 | 23 | 0 | 0
2017-10-15 | 10 | 0 | 0 | 0
2017-10-15 01:00 | 10 | 1 | 0 | 0
2017-10-15 02:00 | 10 | 2 | 0 | 0
2017-10-15 03:00 | 10 | 3 | 0 | 0
2017-10-15 04:00 | 10 | 4 | 0 | 0
2017-10-15 05:00 | 10 | 5 | 0 | 0
2017-10-15 06:00 | 10 | 6 | 816.5632 | 816.5632
2017-10-15 07:00 | 10 | 7 | 3075.9268 | 3075.9268
2017-10-15 08:00 | 10 | 8 | 5108.039 | 5108.039
2017-10-15 09:00 | 10 | 9 | 6475.6327 | 6475.6327
2017-10-15 10:00 | 10 | 10 | 7280.0336 | 7280.0336
2017-10-15 11:00 | 10 | 11 | 7504.8506 | 7504.8506
2017-10-15 12:00 | 10 | 12 | 7159.1628 | 7159.1628
2017-10-15 13:00 | 10 | 13 | 6299.0307 | 6299.0307
2017-10-15 14:00 | 10 | 14 | 4883.9672 | 4883.9672
2017-10-15 15:00 | 10 | 15 | 2888.2181 | 2888.2181
2017-10-15 16:00 | 10 | 16 | 753.8986 | 753.8986
2017-10-15 17:00 | 10 | 17 | 0 | 0
2017-10-15 18:00 | 10 | 18 | 0 | 0
2017-10-15 19:00 | 10 | 19 | 0 | 0
2017-10-15 20:00 | 10 | 20 | 0 | 0
2017-10-15 21:00 | 10 | 21 | 0 | 0
2017-10-15 22:00 | 10 | 22 | 0 | 0
2017-10-15 23:00 | 10 | 23 | 0 | 0
2017-10-16 | 10 | 0 | 0 | 0
2017-10-16 01:00 | 10 | 1 | 0 | 0
2017-10-16 02:00 | 10 | 2 | 0 | 0
2017-10-16 03:00 | 10 | 3 | 0 | 0
2017-10-16 04:00 | 10 | 4 | 0 | 0
2017-10-16 05:00 | 10 | 5 | 0 | 0
2017-10-16 06:00 | 10 | 6 | 41.0021 | 41.0021
2017-10-16 07:00 | 10 | 7 | 1408.3785 | 1408.3785
2017-10-16 08:00 | 10 | 8 | 668.8009 | 668.8009
2017-10-16 09:00 | 10 | 9 | 1828.3114 | 1828.3114
2017-10-16 10:00 | 10 | 10 | 4892.7463 | 4892.7463
2017-10-16 11:00 | 10 | 11 | 7390.8257 | 7390.8258
2017-10-16 12:00 | 10 | 12 | 7035.8219 | 7035.8219
2017-10-16 13:00 | 10 | 13 | 3465.1535 | 3465.1535
2017-10-16 14:00 | 10 | 14 | 4845.1547 | 4845.1547
2017-10-16 15:00 | 10 | 15 | 2818.1037 | 2818.1037
2017-10-16 16:00 | 10 | 16 | 722.7359 | 722.7359
2017-10-16 17:00 | 10 | 17 | 0 | 0
2017-10-16 18:00 | 10 | 18 | 0 | 0
2017-10-16 19:00 | 10 | 19 | 0 | 0
2017-10-16 20:00 | 10 | 20 | 0 | 0
2017-10-16 21:00 | 10 | 21 | 0 | 0
2017-10-16 22:00 | 10 | 22 | 0 | 0
2017-10-16 23:00 | 10 | 23 | 0 | 0
2017-10-17 | 10 | 0 | 0 | 0
2017-10-17 01:00 | 10 | 1 | 0 | 0
2017-10-17 02:00 | 10 | 2 | 0 | 0
2017-10-17 03:00 | 10 | 3 | 0 | 0
2017-10-17 04:00 | 10 | 4 | 0 | 0
2017-10-17 05:00 | 10 | 5 | 0 | 0
2017-10-17 06:00 | 10 | 6 | 505.8792 | 505.8792
2017-10-17 07:00 | 10 | 7 | 2169.7418 | 2169.7418
2017-10-17 08:00 | 10 | 8 | 5043.7804 | 5043.7804
2017-10-17 09:00 | 10 | 9 | 6500.4152 | 6500.4152
2017-10-17 10:00 | 10 | 10 | 7364.7782 | 7364.7783
2017-10-17 11:00 | 10 | 11 | 7630.764 | 7630.764
2017-10-17 12:00 | 10 | 12 | 7315.5801 | 7315.5801
2017-10-17 13:00 | 10 | 13 | 1011.0374 | 1011.0375
2017-10-17 14:00 | 10 | 14 | 1324.0513 | 1324.0513
2017-10-17 15:00 | 10 | 15 | 1298.4558 | 1298.4558
2017-10-17 16:00 | 10 | 16 | 213.6953 | 213.6953
2017-10-17 17:00 | 10 | 17 | 0 | 0
2017-10-17 18:00 | 10 | 18 | 0 | 0
2017-10-17 19:00 | 10 | 19 | 0 | 0
2017-10-17 20:00 | 10 | 20 | 0 | 0
2017-10-17 21:00 | 10 | 21 | 0 | 0
2017-10-17 22:00 | 10 | 22 | 0 | 0
2017-10-17 23:00 | 10 | 23 | 0 | 0
2017-10-18 | 10 | 0 | 0 | 0
2017-10-18 01:00 | 10 | 1 | 0 | 0
2017-10-18 02:00 | 10 | 2 | 0 | 0
2017-10-18 03:00 | 10 | 3 | 0 | 0
2017-10-18 04:00 | 10 | 4 | 0 | 0
2017-10-18 05:00 | 10 | 5 | 0 | 0
2017-10-18 06:00 | 10 | 6 | 814.5841 | 814.5841
2017-10-18 07:00 | 10 | 7 | 3161.1441 | 3161.1441
2017-10-18 08:00 | 10 | 8 | 5273.2054 | 5273.2054
2017-10-18 09:00 | 10 | 9 | 6764.0435 | 6764.0435
2017-10-18 10:00 | 10 | 10 | 7599.8037 | 7599.8037
2017-10-18 11:00 | 10 | 11 | 7859.7394 | 7859.7394
2017-10-18 12:00 | 10 | 12 | 1673.074 | 1673.074
2017-10-18 13:00 | 10 | 13 | 2896.1117 | 2896.1117
2017-10-18 14:00 | 10 | 14 | 3420.6738 | 3420.6739
2017-10-18 15:00 | 10 | 15 | 1719.2201 | 1719.2201
2017-10-18 16:00 | 10 | 16 | 680.677 | 680.677
2017-10-18 17:00 | 10 | 17 | 0 | 0
2017-10-18 18:00 | 10 | 18 | 0 | 0
2017-10-18 19:00 | 10 | 19 | 0 | 0
2017-10-18 20:00 | 10 | 20 | 0 | 0
2017-10-18 21:00 | 10 | 21 | 0 | 0
2017-10-18 22:00 | 10 | 22 | 0 | 0
2017-10-18 23:00 | 10 | 23 | 0 | 0
2017-10-19 | 10 | 0 | 0 | 0
2017-10-19 01:00 | 10 | 1 | 0 | 0
2017-10-19 02:00 | 10 | 2 | 0 | 0
2017-10-19 03:00 | 10 | 3 | 0 | 0
2017-10-19 04:00 | 10 | 4 | 0 | 0
2017-10-19 05:00 | 10 | 5 | 0 | 0
2017-10-19 06:00 | 10 | 6 | 805.598 | 805.598
2017-10-19 07:00 | 10 | 7 | 3147.5224 | 3147.5224
2017-10-19 08:00 | 10 | 8 | 5242.5579 | 5242.5579
2017-10-19 09:00 | 10 | 9 | 6712.5695 | 6712.5695
2017-10-19 10:00 | 10 | 10 | 7529.8193 | 7529.8193
2017-10-19 11:00 | 10 | 11 | 7725.7506 | 7725.7506
2017-10-19 12:00 | 10 | 12 | 7344.6762 | 7344.6762
2017-10-19 13:00 | 10 | 13 | 6395.3075 | 6395.3075
2017-10-19 14:00 | 10 | 14 | 4897.0059 | 4897.0059
2017-10-19 15:00 | 10 | 15 | 2810.0825 | 2810.0825
2017-10-19 16:00 | 10 | 16 | 656.5937 | 656.5937
2017-10-19 17:00 | 10 | 17 | 0 | 0
2017-10-19 18:00 | 10 | 18 | 0 | 0
2017-10-19 19:00 | 10 | 19 | 0 | 0
2017-10-19 20:00 | 10 | 20 | 0 | 0
2017-10-19 21:00 | 10 | 21 | 0 | 0
2017-10-19 22:00 | 10 | 22 | 0 | 0
2017-10-19 23:00 | 10 | 23 | 0 | 0
2017-10-20 | 10 | 0 | 0 | 0
2017-10-20 01:00 | 10 | 1 | 0 | 0
2017-10-20 02:00 | 10 | 2 | 0 | 0
2017-10-20 03:00 | 10 | 3 | 0 | 0
2017-10-20 04:00 | 10 | 4 | 0 | 0
2017-10-20 05:00 | 10 | 5 | 0 | 0
2017-10-20 06:00 | 10 | 6 | 52.5872 | 52.5872
2017-10-20 07:00 | 10 | 7 | 133.4518 | 133.4518
2017-10-20 08:00 | 10 | 8 | 717.5747 | 717.5747
2017-10-20 09:00 | 10 | 9 | 2823.1074 | 2823.1074
2017-10-20 10:00 | 10 | 10 | 3705.5898 | 3705.5898
2017-10-20 11:00 | 10 | 11 | 2727.2434 | 2727.2434
2017-10-20 12:00 | 10 | 12 | 2269.6112 | 2269.6112
2017-10-20 13:00 | 10 | 13 | 1940.9298 | 1940.9298
2017-10-20 14:00 | 10 | 14 | 4247.3387 | 4247.3387
2017-10-20 15:00 | 10 | 15 | 1043.9286 | 1043.9286
2017-10-20 16:00 | 10 | 16 | 404.0444 | 404.0444
2017-10-20 17:00 | 10 | 17 | 0 | 0
2017-10-20 18:00 | 10 | 18 | 0 | 0
2017-10-20 19:00 | 10 | 19 | 0 | 0
2017-10-20 20:00 | 10 | 20 | 0 | 0
2017-10-20 21:00 | 10 | 21 | 0 | 0
2017-10-20 22:00 | 10 | 22 | 0 | 0
2017-10-20 23:00 | 10 | 23 | 0 | 0
2017-10-21 | 10 | 0 | 0 | 0
2017-10-21 01:00 | 10 | 1 | 0 | 0
2017-10-21 02:00 | 10 | 2 | 0 | 0
2017-10-21 03:00 | 10 | 3 | 0 | 0
2017-10-21 04:00 | 10 | 4 | 0 | 0
2017-10-21 05:00 | 10 | 5 | 0 | 0
2017-10-21 06:00 | 10 | 6 | 0 | 0
2017-10-21 07:00 | 10 | 7 | 0.7751 | 0.7751
2017-10-21 08:00 | 10 | 8 | 741.1842 | 741.1842
2017-10-21 09:00 | 10 | 9 | 982.4944 | 982.4944
2017-10-21 10:00 | 10 | 10 | 1128.5571 | 1128.5571
2017-10-21 11:00 | 10 | 11 | 2666.1439 | 2666.1439
2017-10-21 12:00 | 10 | 12 | 3036.5957 | 3036.5957
2017-10-21 13:00 | 10 | 13 | 2293.4416 | 2293.4416
2017-10-21 14:00 | 10 | 14 | 1479.759 | 1479.759
2017-10-21 15:00 | 10 | 15 | 240.956 | 240.956
2017-10-21 16:00 | 10 | 16 | 0 | 0
2017-10-21 17:00 | 10 | 17 | 0 | 0
2017-10-21 18:00 | 10 | 18 | 0 | 0
2017-10-21 19:00 | 10 | 19 | 0 | 0
2017-10-21 20:00 | 10 | 20 | 0 | 0
2017-10-21 21:00 | 10 | 21 | 0 | 0
2017-10-21 22:00 | 10 | 22 | 0 | 0
2017-10-21 23:00 | 10 | 23 | 0 | 0
2017-10-22 | 10 | 0 | 0 | 0
2017-10-22 01:00 | 10 | 1 | 0 | 0
2017-10-22 02:00 | 10 | 2 | 0 | 0
2017-10-22 03:00 | 10 | 3 | 0 | 0
2017-10-22 04:00 | 10 | 4 | 0 | 0
2017-10-22 05:00 | 10 | 5 | 0 | 0
2017-10-22 06:00 | 10 | 6 | 169.3858 | 169.3858
2017-10-22 07:00 | 10 | 7 | 1861.298 | 1861.298
2017-10-22 08:00 | 10 | 8 | 3000.3638 | 3000.3638
2017-10-22 09:00 | 10 | 9 | 1453.6644 | 1453.6644
2017-10-22 10:00 | 10 | 10 | 5143.4428 | 5143.4428
2017-10-22 11:00 | 10 | 11 | 3588.2633 | 3588.2633
2017-10-22 12:00 | 10 | 12 | 5530.8169 | 5530.8169
2017-10-22 13:00 | 10 | 13 | 4538.521 | 4538.521
2017-10-22 14:00 | 10 | 14 | 2243.1555 | 2243.1555
2017-10-22 15:00 | 10 | 15 | 943.667 | 943.667
2017-10-22 16:00 | 10 | 16 | 66.2895 | 66.2895
2017-10-22 17:00 | 10 | 17 | 0 | 0
2017-10-22 18:00 | 10 | 18 | 0 | 0
2017-10-22 19:00 | 10 | 19 | 0 | 0
2017-10-22 20:00 | 10 | 20 | 0 | 0
2017-10-22 21:00 | 10 | 21 | 0 | 0
2017-10-22 22:00 | 10 | 22 | 0 | 0
2017-10-22 23:00 | 10 | 23 | 0 | 0
2017-10-23 | 10 | 0 | 0 | 0
2017-10-23 01:00 | 10 | 1 | 0 | 0
2017-10-23 02:00 | 10 | 2 | 0 | 0
2017-10-23 03:00 | 10 | 3 | 0 | 0
2017-10-23 04:00 | 10 | 4 | 0 | 0
2017-10-23 05:00 | 10 | 5 | 0 | 0
2017-10-23 06:00 | 10 | 6 | 601.0004 | 601.0004
2017-10-23 07:00 | 10 | 7 | 2790.6026 | 2790.6026
2017-10-23 08:00 | 10 | 8 | 4882.0616 | 4882.0616
2017-10-23 09:00 | 10 | 9 | 6347.6642 | 6347.6642
2017-10-23 10:00 | 10 | 10 | 7161.51 | 7161.51
2017-10-23 11:00 | 10 | 11 | 7416.0786 | 7416.0786
2017-10-23 12:00 | 10 | 12 | 5960.7444 | 5960.7444
2017-10-23 13:00 | 10 | 13 | 6189.2379 | 6189.2379
2017-10-23 14:00 | 10 | 14 | 4653.1334 | 4653.1334
2017-10-23 15:00 | 10 | 15 | 2595.9847 | 2595.9847
2017-10-23 16:00 | 10 | 16 | 489.3756 | 489.3756
2017-10-23 17:00 | 10 | 17 | 0 | 0
2017-10-23 18:00 | 10 | 18 | 0 | 0
2017-10-23 19:00 | 10 | 19 | 0 | 0
2017-10-23 20:00 | 10 | 20 | 0 | 0
2017-10-23 21:00 | 10 | 21 | 0 | 0
2017-10-23 22:00 | 10 | 22 | 0 | 0
2017-10-23 23:00 | 10 | 23 | 0 | 0
2017-10-24 | 10 | 0 | 0 | 0
2017-10-24 01:00 | 10 | 1 | 0 | 0
2017-10-24 02:00 | 10 | 2 | 0 | 0
2017-10-24 03:00 | 10 | 3 | 0 | 0
2017-10-24 04:00 | 10 | 4 | 0 | 0
2017-10-24 05:00 | 10 | 5 | 0 | 0
2017-10-24 06:00 | 10 | 6 | 0 | 0
2017-10-24 07:00 | 10 | 7 | 537.7112 | 537.7112
2017-10-24 08:00 | 10 | 8 | 1219.9625 | 1219.9625
2017-10-24 09:00 | 10 | 9 | 1510.0788 | 1510.0788
2017-10-24 10:00 | 10 | 10 | 1717.4571 | 1717.4571
2017-10-24 11:00 | 10 | 11 | 1006.9446 | 1006.9446
2017-10-24 12:00 | 10 | 12 | 2985.2263 | 2985.2263
2017-10-24 13:00 | 10 | 13 | 2121.106 | 2121.106
2017-10-24 14:00 | 10 | 14 | 1124.3676 | 1124.3676
2017-10-24 15:00 | 10 | 15 | 580.8121 | 580.8121
2017-10-24 16:00 | 10 | 16 | 22.057 | 22.057
2017-10-24 17:00 | 10 | 17 | 0 | 0
2017-10-24 18:00 | 10 | 18 | 0 | 0
2017-10-24 19:00 | 10 | 19 | 0 | 0
2017-10-24 20:00 | 10 | 20 | 0 | 0
2017-10-24 21:00 | 10 | 21 | 0 | 0
2017-10-24 22:00 | 10 | 22 | 0 | 0
2017-10-24 23:00 | 10 | 23 | 0 | 0
2017-10-25 | 10 | 0 | 0 | 0
2017-10-25 01:00 | 10 | 1 | 0 | 0
2017-10-25 02:00 | 10 | 2 | 0 | 0
2017-10-25 03:00 | 10 | 3 | 0 | 0
2017-10-25 04:00 | 10 | 4 | 0 | 0
2017-10-25 05:00 | 10 | 5 | 0 | 0
2017-10-25 06:00 | 10 | 6 | 0 | 0
2017-10-25 07:00 | 10 | 7 | 280.0399 | 280.0399
2017-10-25 08:00 | 10 | 8 | 813.8573 | 813.8573
2017-10-25 09:00 | 10 | 9 | 1343.1689 | 1343.1689
2017-10-25 10:00 | 10 | 10 | 1219.7866 | 1219.7866
2017-10-25 11:00 | 10 | 11 | 1382.3793 | 1382.3793
2017-10-25 12:00 | 10 | 12 | 2848.803 | 2848.803
2017-10-25 13:00 | 10 | 13 | 1630.9909 | 1630.9909
2017-10-25 14:00 | 10 | 14 | 1862.7965 | 1862.7965
2017-10-25 15:00 | 10 | 15 | 435.3934 | 435.3934
2017-10-25 16:00 | 10 | 16 | 0.29785 | 0.29785
2017-10-25 17:00 | 10 | 17 | 0 | 0
2017-10-25 18:00 | 10 | 18 | 0 | 0
2017-10-25 19:00 | 10 | 19 | 0 | 0
2017-10-25 20:00 | 10 | 20 | 0 | 0
2017-10-25 21:00 | 10 | 21 | 0 | 0
2017-10-25 22:00 | 10 | 22 | 0 | 0
2017-10-25 23:00 | 10 | 23 | 0 | 0
2017-10-26 | 10 | 0 | 0 | 0
2017-10-26 01:00 | 10 | 1 | 0 | 0
2017-10-26 02:00 | 10 | 2 | 0 | 0
2017-10-26 03:00 | 10 | 3 | 0 | 0
2017-10-26 04:00 | 10 | 4 | 0 | 0
2017-10-26 05:00 | 10 | 5 | 0 | 0
2017-10-26 06:00 | 10 | 6 | 573.3383 | 573.3383
2017-10-26 07:00 | 10 | 7 | 2763.4396 | 2763.4396
2017-10-26 08:00 | 10 | 8 | 4867.0381 | 4867.0381
2017-10-26 09:00 | 10 | 9 | 6315.1571 | 6315.1571
2017-10-26 10:00 | 10 | 10 | 7193.0982 | 7193.0982
2017-10-26 11:00 | 10 | 11 | 7416.0889 | 7416.0889
2017-10-26 12:00 | 10 | 12 | 7046.625 | 7046.625
2017-10-26 13:00 | 10 | 13 | 6095.115 | 6095.115
2017-10-26 14:00 | 10 | 14 | 4617.5225 | 4617.5225
2017-10-26 15:00 | 10 | 15 | 2520.2951 | 2520.2951
2017-10-26 16:00 | 10 | 16 | 431.1729 | 431.1729
2017-10-26 17:00 | 10 | 17 | 0 | 0
2017-10-26 18:00 | 10 | 18 | 0 | 0
2017-10-26 19:00 | 10 | 19 | 0 | 0
2017-10-26 20:00 | 10 | 20 | 0 | 0
2017-10-26 21:00 | 10 | 21 | 0 | 0
2017-10-26 22:00 | 10 | 22 | 0 | 0
2017-10-26 23:00 | 10 | 23 | 0 | 0
2017-10-27 | 10 | 0 | 0 | 0
2017-10-27 01:00 | 10 | 1 | 0 | 0
2017-10-27 02:00 | 10 | 2 | 0 | 0
2017-10-27 03:00 | 10 | 3 | 0 | 0
2017-10-27 04:00 | 10 | 4 | 0 | 0
2017-10-27 05:00 | 10 | 5 | 0 | 0
2017-10-27 06:00 | 10 | 6 | 514.1662 | 514.1662
2017-10-27 07:00 | 10 | 7 | 2668.8383 | 2668.8383
2017-10-27 08:00 | 10 | 8 | 4713.6303 | 4713.6303
2017-10-27 09:00 | 10 | 9 | 4563.0287 | 4563.0287
2017-10-27 10:00 | 10 | 10 | 6938.9965 | 6938.9965
2017-10-27 11:00 | 10 | 11 | 5529.0264 | 5529.0264
2017-10-27 12:00 | 10 | 12 | 5579.6011 | 5579.6011
2017-10-27 13:00 | 10 | 13 | 5281.6705 | 5281.6705
2017-10-27 14:00 | 10 | 14 | 3821.5328 | 3821.5328
2017-10-27 15:00 | 10 | 15 | 1632.1789 | 1632.1789
2017-10-27 16:00 | 10 | 16 | 70.0626 | 70.0626
2017-10-27 17:00 | 10 | 17 | 0 | 0
2017-10-27 18:00 | 10 | 18 | 0 | 0
2017-10-27 19:00 | 10 | 19 | 0 | 0
2017-10-27 20:00 | 10 | 20 | 0 | 0
2017-10-27 21:00 | 10 | 21 | 0 | 0
2017-10-27 22:00 | 10 | 22 | 0 | 0
2017-10-27 23:00 | 10 | 23 | 0 | 0
2017-10-28 | 10 | 0 | 0 | 0
2017-10-28 01:00 | 10 | 1 | 0 | 0
2017-10-28 02:00 | 10 | 2 | 0 | 0
2017-10-28 03:00 | 10 | 3 | 0 | 0
2017-10-28 04:00 | 10 | 4 | 0 | 0
2017-10-28 05:00 | 10 | 5 | 0 | 0
2017-10-28 06:00 | 10 | 6 | 72.9203 | 72.9203
2017-10-28 07:00 | 10 | 7 | 692.0251 | 692.0251
2017-10-28 08:00 | 10 | 8 | 1251.7566 | 1251.7566
2017-10-28 09:00 | 10 | 9 | 3393.9283 | 3393.9283
2017-10-28 10:00 | 10 | 10 | 2991.6019 | 2991.6019
2017-10-28 11:00 | 10 | 11 | 1900.2002 | 1900.2002
2017-10-28 12:00 | 10 | 12 | 714.2408 | 714.2408
2017-10-28 13:00 | 10 | 13 | 803.1669 | 803.1669
2017-10-28 14:00 | 10 | 14 | 865.4693 | 865.4693
2017-10-28 15:00 | 10 | 15 | 345.161 | 345.161
2017-10-28 16:00 | 10 | 16 | 0 | 0
2017-10-28 17:00 | 10 | 17 | 0 | 0
2017-10-28 18:00 | 10 | 18 | 0 | 0
2017-10-28 19:00 | 10 | 19 | 0 | 0
2017-10-28 20:00 | 10 | 20 | 0 | 0
2017-10-28 21:00 | 10 | 21 | 0 | 0
2017-10-28 22:00 | 10 | 22 | 0 | 0
2017-10-28 23:00 | 10 | 23 | 0 | 0
2017-10-29 | 10 | 0 | 0 | 0
2017-10-29 01:00 | 10 | 1 | 0 | 0
2017-10-29 02:00 | 10 | 2 | 0 | 0
2017-10-29 03:00 | 10 | 3 | 0 | 0
2017-10-29 04:00 | 10 | 4 | 0 | 0
2017-10-29 05:00 | 10 | 5 | 0 | 0
2017-10-29 06:00 | 10 | 6 | 0 | 0
2017-10-29 07:00 | 10 | 7 | 76.0322 | 76.0322
2017-10-29 08:00 | 10 | 8 | 1498.3994 | 1498.3994
2017-10-29 09:00 | 10 | 9 | 3292.7237 | 3292.7237
2017-10-29 10:00 | 10 | 10 | 6288.2931 | 6288.2931
2017-10-29 11:00 | 10 | 11 | 6571.2656 | 6571.2656
2017-10-29 12:00 | 10 | 12 | 5139.6007 | 5139.6007
2017-10-29 13:00 | 10 | 13 | 4122.244 | 4122.244
2017-10-29 14:00 | 10 | 14 | 2540.396 | 2540.396
2017-10-29 15:00 | 10 | 15 | 1739.3371 | 1739.3371
2017-10-29 16:00 | 10 | 16 | 46.1552 | 46.1552
2017-10-29 17:00 | 10 | 17 | 0 | 0
2017-10-29 18:00 | 10 | 18 | 0 | 0
2017-10-29 19:00 | 10 | 19 | 0 | 0
2017-10-29 20:00 | 10 | 20 | 0 | 0
2017-10-29 21:00 | 10 | 21 | 0 | 0
2017-10-29 22:00 | 10 | 22 | 0 | 0
2017-10-29 23:00 | 10 | 23 | 0 | 0
2017-10-30 | 10 | 0 | 0 | 0
2017-10-30 01:00 | 10 | 1 | 0 | 0
2017-10-30 02:00 | 10 | 2 | 0 | 0
2017-10-30 03:00 | 10 | 3 | 0 | 0
2017-10-30 04:00 | 10 | 4 | 0 | 0
2017-10-30 05:00 | 10 | 5 | 0 | 0
2017-10-30 06:00 | 10 | 6 | 377.7083 | 377.7083
2017-10-30 07:00 | 10 | 7 | 2464.4868 | 2464.4868
2017-10-30 08:00 | 10 | 8 | 4490.7845 | 4490.7845
2017-10-30 09:00 | 10 | 9 | 5939.6005 | 5939.6005
2017-10-30 10:00 | 10 | 10 | 6910.6593 | 6910.6593
2017-10-30 11:00 | 10 | 11 | 7128.6234 | 7128.6234
2017-10-30 12:00 | 10 | 12 | 6764.7117 | 6764.7117
2017-10-30 13:00 | 10 | 13 | 5884.5592 | 5884.5592
2017-10-30 14:00 | 10 | 14 | 4408.1685 | 4408.1685
2017-10-30 15:00 | 10 | 15 | 2332.3886 | 2332.3886
2017-10-30 16:00 | 10 | 16 | 292.9567 | 292.9567
2017-10-30 17:00 | 10 | 17 | 0 | 0
2017-10-30 18:00 | 10 | 18 | 0 | 0
2017-10-30 19:00 | 10 | 19 | 0 | 0
2017-10-30 20:00 | 10 | 20 | 0 | 0
2017-10-30 21:00 | 10 | 21 | 0 | 0
2017-10-30 22:00 | 10 | 22 | 0 | 0
2017-10-30 23:00 | 10 | 23 | 0 | 0
2017-10-31 | 10 | 0 | 0 | 0
2017-10-31 01:00 | 10 | 1 | 0 | 0
2017-10-31 02:00 | 10 | 2 | 0 | 0
2017-10-31 03:00 | 10 | 3 | 0 | 0
2017-10-31 04:00 | 10 | 4 | 0 | 0
2017-10-31 05:00 | 10 | 5 | 0 | 0
2017-10-31 06:00 | 10 | 6 | 408.4984 | 408.4984
2017-10-31 07:00 | 10 | 7 | 2587.247 | 2587.247
2017-10-31 08:00 | 10 | 8 | 4690.7189 | 4690.7189
2017-10-31 09:00 | 10 | 9 | 6113.2447 | 6113.2447
2017-10-31 10:00 | 10 | 10 | 6936.9311 | 6936.9311
2017-10-31 11:00 | 10 | 11 | 7109.1597 | 7109.1597
2017-10-31 12:00 | 10 | 12 | 6081.6519 | 6081.6519
2017-10-31 13:00 | 10 | 13 | 4607.7257 | 4607.7257
2017-10-31 14:00 | 10 | 14 | 3630.9789 | 3630.9789
2017-10-31 15:00 | 10 | 15 | 2227.5235 | 2227.5235
2017-10-31 16:00 | 10 | 16 | 0 | 0
2017-10-31 17:00 | 10 | 17 | 0 | 0
2017-10-31 18:00 | 10 | 18 | 0 | 0
2017-10-31 19:00 | 10 | 19 | 0 | 0
2017-10-31 20:00 | 10 | 20 | 0 | 0
2017-10-31 21:00 | 10 | 21 | 0 | 0
2017-10-31 22:00 | 10 | 22 | 0 | 0
2017-10-31 23:00 | 10 | 23 | 0 | 0
2017-11-01 | 11 | 0 | 0 | 0
2017-11-01 01:00 | 11 | 1 | 0 | 0
2017-11-01 02:00 | 11 | 2 | 0 | 0
2017-11-01 03:00 | 11 | 3 | 0 | 0
2017-11-01 04:00 | 11 | 4 | 0 | 0
2017-11-01 05:00 | 11 | 5 | 0 | 0
2017-11-01 06:00 | 11 | 6 | 20.9369 | 20.9369
2017-11-01 07:00 | 11 | 7 | 1687.9608 | 1687.9608
2017-11-01 08:00 | 11 | 8 | 2286.8888 | 2286.8888
2017-11-01 09:00 | 11 | 9 | 4414.2819 | 4414.2819
2017-11-01 10:00 | 11 | 10 | 3831.486 | 3831.486
2017-11-01 11:00 | 11 | 11 | 4416.6739 | 4416.6739
2017-11-01 12:00 | 11 | 12 | 4551.7862 | 4551.7862
2017-11-01 13:00 | 11 | 13 | 3348.9288 | 3348.9288
2017-11-01 14:00 | 11 | 14 | 2403.5471 | 2403.5471
2017-11-01 15:00 | 11 | 15 | 779.0272 | 779.0272
2017-11-01 16:00 | 11 | 16 | 0 | 0
2017-11-01 17:00 | 11 | 17 | 0 | 0
2017-11-01 18:00 | 11 | 18 | 0 | 0
2017-11-01 19:00 | 11 | 19 | 0 | 0
2017-11-01 20:00 | 11 | 20 | 0 | 0
2017-11-01 21:00 | 11 | 21 | 0 | 0
2017-11-01 22:00 | 11 | 22 | 0 | 0
2017-11-01 23:00 | 11 | 23 | 0 | 0
2017-11-02 | 11 | 0 | 0 | 0
2017-11-02 01:00 | 11 | 1 | 0 | 0
2017-11-02 02:00 | 11 | 2 | 0 | 0
2017-11-02 03:00 | 11 | 3 | 0 | 0
2017-11-02 04:00 | 11 | 4 | 0 | 0
2017-11-02 05:00 | 11 | 5 | 0 | 0
2017-11-02 06:00 | 11 | 6 | 1.2696 | 1.2696
2017-11-02 07:00 | 11 | 7 | 1294.0214 | 1294.0214
2017-11-02 08:00 | 11 | 8 | 3523.7736 | 3523.7737
2017-11-02 09:00 | 11 | 9 | 4943.6177 | 4943.6177
2017-11-02 10:00 | 11 | 10 | 6126.2581 | 6126.2581
2017-11-02 11:00 | 11 | 11 | 6408.3313 | 6408.3313
2017-11-02 12:00 | 11 | 12 | 1604.6743 | 1604.6743
2017-11-02 13:00 | 11 | 13 | 221.3899 | 221.3899
2017-11-02 14:00 | 11 | 14 | 304.0692 | 304.0692
2017-11-02 15:00 | 11 | 15 | 109.1591 | 109.1591
2017-11-02 16:00 | 11 | 16 | 0 | 0
2017-11-02 17:00 | 11 | 17 | 0 | 0
2017-11-02 18:00 | 11 | 18 | 0 | 0
2017-11-02 19:00 | 11 | 19 | 0 | 0
2017-11-02 20:00 | 11 | 20 | 0 | 0
2017-11-02 21:00 | 11 | 21 | 0 | 0
2017-11-02 22:00 | 11 | 22 | 0 | 0
2017-11-02 23:00 | 11 | 23 | 0 | 0
2017-11-03 | 11 | 0 | 0 | 0
2017-11-03 01:00 | 11 | 1 | 0 | 0
2017-11-03 02:00 | 11 | 2 | 0 | 0
2017-11-03 03:00 | 11 | 3 | 0 | 0
2017-11-03 04:00 | 11 | 4 | 0 | 0
2017-11-03 05:00 | 11 | 5 | 0 | 0
2017-11-03 06:00 | 11 | 6 | 0 | 0
2017-11-03 07:00 | 11 | 7 | 189.5407 | 189.5407
2017-11-03 08:00 | 11 | 8 | 1185.175 | 1185.175
2017-11-03 09:00 | 11 | 9 | 3627.5818 | 3627.5818
2017-11-03 10:00 | 11 | 10 | 5809.2377 | 5809.2377
2017-11-03 11:00 | 11 | 11 | 5990.0038 | 5990.0038
2017-11-03 12:00 | 11 | 12 | 5614.3471 | 5614.3471
2017-11-03 13:00 | 11 | 13 | 4750.1129 | 4750.1129
2017-11-03 14:00 | 11 | 14 | 3290.2259 | 3290.2259
2017-11-03 15:00 | 11 | 15 | 926.8574 | 926.8574
2017-11-03 16:00 | 11 | 16 | 0 | 0
2017-11-03 17:00 | 11 | 17 | 0 | 0
2017-11-03 18:00 | 11 | 18 | 0 | 0
2017-11-03 19:00 | 11 | 19 | 0 | 0
2017-11-03 20:00 | 11 | 20 | 0 | 0
2017-11-03 21:00 | 11 | 21 | 0 | 0
2017-11-03 22:00 | 11 | 22 | 0 | 0
2017-11-03 23:00 | 11 | 23 | 0 | 0
2017-11-04 | 11 | 0 | 0 | 0
2017-11-04 01:00 | 11 | 1 | 0 | 0
2017-11-04 02:00 | 11 | 2 | 0 | 0
2017-11-04 03:00 | 11 | 3 | 0 | 0
2017-11-04 04:00 | 11 | 4 | 0 | 0
2017-11-04 05:00 | 11 | 5 | 0 | 0
2017-11-04 06:00 | 11 | 6 | 0 | 0
2017-11-04 07:00 | 11 | 7 | 202.9669 | 202.9669
2017-11-04 08:00 | 11 | 8 | 292.6336 | 292.6336
2017-11-04 09:00 | 11 | 9 | 412.0542 | 412.0542
2017-11-04 10:00 | 11 | 10 | 599.7135 | 599.7135
2017-11-04 11:00 | 11 | 11 | 1373.2817 | 1373.2817
2017-11-04 12:00 | 11 | 12 | 864.5251 | 864.5251
2017-11-04 13:00 | 11 | 13 | 392.2098 | 392.2098
2017-11-04 14:00 | 11 | 14 | 244.9466 | 244.9466
2017-11-04 15:00 | 11 | 15 | 1484.504 | 1484.504
2017-11-04 16:00 | 11 | 16 | 0 | 0
2017-11-04 17:00 | 11 | 17 | 0 | 0
2017-11-04 18:00 | 11 | 18 | 0 | 0
2017-11-04 19:00 | 11 | 19 | 0 | 0
2017-11-04 20:00 | 11 | 20 | 0 | 0
2017-11-04 21:00 | 11 | 21 | 0 | 0
2017-11-04 22:00 | 11 | 22 | 0 | 0
2017-11-04 23:00 | 11 | 23 | 0 | 0
2017-11-05 | 11 | 0 | 0 | 0
2017-11-05 01:00 | 11 | 1 | 0 | 0
2017-11-05 02:00 | 11 | 2 | 0 | 0
2017-11-05 03:00 | 11 | 3 | 0 | 0
2017-11-05 04:00 | 11 | 4 | 0 | 0
2017-11-05 05:00 | 11 | 5 | 0 | 0
2017-11-05 06:00 | 11 | 6 | 0 | 0
2017-11-05 07:00 | 11 | 7 | 0 | 0
2017-11-05 08:00 | 11 | 8 | 32.1206 | 32.1206
2017-11-05 09:00 | 11 | 9 | 706.5128 | 706.5128
2017-11-05 10:00 | 11 | 10 | 475.2628 | 475.2628
2017-11-05 11:00 | 11 | 11 | 1284.0555 | 1284.0555
2017-11-05 12:00 | 11 | 12 | 1882.2521 | 1882.2521
2017-11-05 13:00 | 11 | 13 | 1316.0427 | 1316.0427
2017-11-05 14:00 | 11 | 14 | 698.5755 | 698.5755
2017-11-05 15:00 | 11 | 15 | 316.3961 | 316.3961
2017-11-05 16:00 | 11 | 16 | 0 | 0
2017-11-05 17:00 | 11 | 17 | 0 | 0
2017-11-05 18:00 | 11 | 18 | 0 | 0
2017-11-05 19:00 | 11 | 19 | 0 | 0
2017-11-05 20:00 | 11 | 20 | 0 | 0
2017-11-05 21:00 | 11 | 21 | 0 | 0
2017-11-05 22:00 | 11 | 22 | 0 | 0
2017-11-05 23:00 | 11 | 23 | 0 | 0
2017-11-06 | 11 | 0 | 0 | 0
2017-11-06 01:00 | 11 | 1 | 0 | 0
2017-11-06 02:00 | 11 | 2 | 0 | 0
2017-11-06 03:00 | 11 | 3 | 0 | 0
2017-11-06 04:00 | 11 | 4 | 0 | 0
2017-11-06 05:00 | 11 | 5 | 0 | 0
2017-11-06 06:00 | 11 | 6 | 0 | 0
2017-11-06 07:00 | 11 | 7 | 972.4929 | 972.4929
2017-11-06 08:00 | 11 | 8 | 1469.9863 | 1469.9863
2017-11-06 09:00 | 11 | 9 | 2068.9075 | 2068.9075
2017-11-06 10:00 | 11 | 10 | 2842.9162 | 2842.9162
2017-11-06 11:00 | 11 | 11 | 2904.7206 | 2904.7206
2017-11-06 12:00 | 11 | 12 | 1677.9351 | 1677.9351
2017-11-06 13:00 | 11 | 13 | 1371.6636 | 1371.6636
2017-11-06 14:00 | 11 | 14 | 294.0377 | 294.0377
2017-11-06 15:00 | 11 | 15 | 289.3837 | 289.3837
2017-11-06 16:00 | 11 | 16 | 0 | 0
2017-11-06 17:00 | 11 | 17 | 0 | 0
2017-11-06 18:00 | 11 | 18 | 0 | 0
2017-11-06 19:00 | 11 | 19 | 0 | 0
2017-11-06 20:00 | 11 | 20 | 0 | 0
2017-11-06 21:00 | 11 | 21 | 0 | 0
2017-11-06 22:00 | 11 | 22 | 0 | 0
2017-11-06 23:00 | 11 | 23 | 0 | 0
2017-11-07 | 11 | 0 | 0 | 0
2017-11-07 01:00 | 11 | 1 | 0 | 0
2017-11-07 02:00 | 11 | 2 | 0 | 0
2017-11-07 03:00 | 11 | 3 | 0 | 0
2017-11-07 04:00 | 11 | 4 | 0 | 0
2017-11-07 05:00 | 11 | 5 | 0 | 0
2017-11-07 06:00 | 11 | 6 | 0 | 0
2017-11-07 07:00 | 11 | 7 | 93.8032 | 93.8032
2017-11-07 08:00 | 11 | 8 | 3860.5235 | 3860.5235
2017-11-07 09:00 | 11 | 9 | 5406.1454 | 5406.1454
2017-11-07 10:00 | 11 | 10 | 6478.3628 | 6478.3628
2017-11-07 11:00 | 11 | 11 | 6751.1359 | 6751.1359
2017-11-07 12:00 | 11 | 12 | 6452.4315 | 6452.4315
2017-11-07 13:00 | 11 | 13 | 5522.0217 | 5522.0217
2017-11-07 14:00 | 11 | 14 | 3986.6164 | 3986.6164
2017-11-07 15:00 | 11 | 15 | 1951.5511 | 1951.5511
2017-11-07 16:00 | 11 | 16 | 0 | 0
2017-11-07 17:00 | 11 | 17 | 0 | 0
2017-11-07 18:00 | 11 | 18 | 0 | 0
2017-11-07 19:00 | 11 | 19 | 0 | 0
2017-11-07 20:00 | 11 | 20 | 0 | 0
2017-11-07 21:00 | 11 | 21 | 0 | 0
2017-11-07 22:00 | 11 | 22 | 0 | 0
2017-11-07 23:00 | 11 | 23 | 0 | 0
2017-11-08 | 11 | 0 | 0 | 0
2017-11-08 01:00 | 11 | 1 | 0 | 0
2017-11-08 02:00 | 11 | 2 | 0 | 0
2017-11-08 03:00 | 11 | 3 | 0 | 0
2017-11-08 04:00 | 11 | 4 | 0 | 0
2017-11-08 05:00 | 11 | 5 | 0 | 0
2017-11-08 06:00 | 11 | 6 | 0 | 0
2017-11-08 07:00 | 11 | 7 | 2292.0523 | 2292.0523
2017-11-08 08:00 | 11 | 8 | 4538.6923 | 4538.6923
2017-11-08 09:00 | 11 | 9 | 6199.7742 | 6199.7742
2017-11-08 10:00 | 11 | 10 | 7207.0569 | 7207.0569
2017-11-08 11:00 | 11 | 11 | 7608.4011 | 7608.4011
2017-11-08 12:00 | 11 | 12 | 7288.0157 | 7288.0158
2017-11-08 13:00 | 11 | 13 | 6313.0354 | 6313.0354
2017-11-08 14:00 | 11 | 14 | 4623.36 | 4623.36
2017-11-08 15:00 | 11 | 15 | 2297.4194 | 2297.4194
2017-11-08 16:00 | 11 | 16 | 0 | 0
2017-11-08 17:00 | 11 | 17 | 0 | 0
2017-11-08 18:00 | 11 | 18 | 0 | 0
2017-11-08 19:00 | 11 | 19 | 0 | 0
2017-11-08 20:00 | 11 | 20 | 0 | 0
2017-11-08 21:00 | 11 | 21 | 0 | 0
2017-11-08 22:00 | 11 | 22 | 0 | 0
2017-11-08 23:00 | 11 | 23 | 0 | 0
2017-11-09 | 11 | 0 | 0 | 0
2017-11-09 01:00 | 11 | 1 | 0 | 0
2017-11-09 02:00 | 11 | 2 | 0 | 0
2017-11-09 03:00 | 11 | 3 | 0 | 0
2017-11-09 04:00 | 11 | 4 | 0 | 0
2017-11-09 05:00 | 11 | 5 | 0 | 0
2017-11-09 06:00 | 11 | 6 | 0 | 0
2017-11-09 07:00 | 11 | 7 | 2437.7827 | 2437.7827
2017-11-09 08:00 | 11 | 8 | 4687.8151 | 4687.8151
2017-11-09 09:00 | 11 | 9 | 6235.2218 | 6235.2218
2017-11-09 10:00 | 11 | 10 | 7103.9789 | 7103.9789
2017-11-09 11:00 | 11 | 11 | 7337.5163 | 7337.5163
2017-11-09 12:00 | 11 | 12 | 6947.0281 | 6947.0281
2017-11-09 13:00 | 11 | 13 | 5916.4234 | 5916.4234
2017-11-09 14:00 | 11 | 14 | 4322.6108 | 4322.6108
2017-11-09 15:00 | 11 | 15 | 2108.4813 | 2108.4813
2017-11-09 16:00 | 11 | 16 | 0 | 0
2017-11-09 17:00 | 11 | 17 | 0 | 0
2017-11-09 18:00 | 11 | 18 | 0 | 0
2017-11-09 19:00 | 11 | 19 | 0 | 0
2017-11-09 20:00 | 11 | 20 | 0 | 0
2017-11-09 21:00 | 11 | 21 | 0 | 0
2017-11-09 22:00 | 11 | 22 | 0 | 0
2017-11-09 23:00 | 11 | 23 | 0 | 0
2017-11-10 | 11 | 0 | 0 | 0
2017-11-10 01:00 | 11 | 1 | 0 | 0
2017-11-10 02:00 | 11 | 2 | 0 | 0
2017-11-10 03:00 | 11 | 3 | 0 | 0
2017-11-10 04:00 | 11 | 4 | 0 | 0
2017-11-10 05:00 | 11 | 5 | 0 | 0
2017-11-10 06:00 | 11 | 6 | 0 | 0
2017-11-10 07:00 | 11 | 7 | 2215.1196 | 2215.1196
2017-11-10 08:00 | 11 | 8 | 4377.3565 | 4377.3565
2017-11-10 09:00 | 11 | 9 | 5937.8352 | 5937.8352
2017-11-10 10:00 | 11 | 10 | 6780.7047 | 6780.7047
2017-11-10 11:00 | 11 | 11 | 6983.7591 | 6983.7591
2017-11-10 12:00 | 11 | 12 | 6653.6746 | 6653.6746
2017-11-10 13:00 | 11 | 13 | 5665.6532 | 5665.6532
2017-11-10 14:00 | 11 | 14 | 3407.8559 | 3407.8559
2017-11-10 15:00 | 11 | 15 | 1310.7355 | 1310.7355
2017-11-10 16:00 | 11 | 16 | 0 | 0
2017-11-10 17:00 | 11 | 17 | 0 | 0
2017-11-10 18:00 | 11 | 18 | 0 | 0
2017-11-10 19:00 | 11 | 19 | 0 | 0
2017-11-10 20:00 | 11 | 20 | 0 | 0
2017-11-10 21:00 | 11 | 21 | 0 | 0
2017-11-10 22:00 | 11 | 22 | 0 | 0
2017-11-10 23:00 | 11 | 23 | 0 | 0
2017-11-11 | 11 | 0 | 0 | 0
2017-11-11 01:00 | 11 | 1 | 0 | 0
2017-11-11 02:00 | 11 | 2 | 0 | 0
2017-11-11 03:00 | 11 | 3 | 0 | 0
2017-11-11 04:00 | 11 | 4 | 0 | 0
2017-11-11 05:00 | 11 | 5 | 0 | 0
2017-11-11 06:00 | 11 | 6 | 0 | 0
2017-11-11 07:00 | 11 | 7 | 1903.9653 | 1903.9653
2017-11-11 08:00 | 11 | 8 | 3791.8456 | 3791.8455
2017-11-11 09:00 | 11 | 9 | 3089.3577 | 3089.3577
2017-11-11 10:00 | 11 | 10 | 2029.0749 | 2029.0749
2017-11-11 11:00 | 11 | 11 | 1222.7271 | 1222.7271
2017-11-11 12:00 | 11 | 12 | 1042.2151 | 1042.2151
2017-11-11 13:00 | 11 | 13 | 925.3176 | 925.3176
2017-11-11 14:00 | 11 | 14 | 774.3709 | 774.3709
2017-11-11 15:00 | 11 | 15 | 267.3313 | 267.3313
2017-11-11 16:00 | 11 | 16 | 0 | 0
2017-11-11 17:00 | 11 | 17 | 0 | 0
2017-11-11 18:00 | 11 | 18 | 0 | 0
2017-11-11 19:00 | 11 | 19 | 0 | 0
2017-11-11 20:00 | 11 | 20 | 0 | 0
2017-11-11 21:00 | 11 | 21 | 0 | 0
2017-11-11 22:00 | 11 | 22 | 0 | 0
2017-11-11 23:00 | 11 | 23 | 0 | 0
2017-11-12 | 11 | 0 | 0 | 0
2017-11-12 01:00 | 11 | 1 | 0 | 0
2017-11-12 02:00 | 11 | 2 | 0 | 0
2017-11-12 03:00 | 11 | 3 | 0 | 0
2017-11-12 04:00 | 11 | 4 | 0 | 0
2017-11-12 05:00 | 11 | 5 | 0 | 0
2017-11-12 06:00 | 11 | 6 | 0 | 0
2017-11-12 07:00 | 11 | 7 | 134.3959 | 134.3959
2017-11-12 08:00 | 11 | 8 | 910.2008 | 910.2008
2017-11-12 09:00 | 11 | 9 | 997.9447 | 997.9447
2017-11-12 10:00 | 11 | 10 | 642.022 | 642.022
2017-11-12 11:00 | 11 | 11 | 2749.4315 | 2749.4315
2017-11-12 12:00 | 11 | 12 | 3457.2875 | 3457.2875
2017-11-12 13:00 | 11 | 13 | 4689.6655 | 4689.6655
2017-11-12 14:00 | 11 | 14 | 3193.0497 | 3193.0497
2017-11-12 15:00 | 11 | 15 | 1359.1183 | 1359.1183
2017-11-12 16:00 | 11 | 16 | 0 | 0
2017-11-12 17:00 | 11 | 17 | 0 | 0
2017-11-12 18:00 | 11 | 18 | 0 | 0
2017-11-12 19:00 | 11 | 19 | 0 | 0
2017-11-12 20:00 | 11 | 20 | 0 | 0
2017-11-12 21:00 | 11 | 21 | 0 | 0
2017-11-12 22:00 | 11 | 22 | 0 | 0
2017-11-12 23:00 | 11 | 23 | 0 | 0
2017-11-13 | 11 | 0 | 0 | 0
2017-11-13 01:00 | 11 | 1 | 0 | 0
2017-11-13 02:00 | 11 | 2 | 0 | 0
2017-11-13 03:00 | 11 | 3 | 0 | 0
2017-11-13 04:00 | 11 | 4 | 0 | 0
2017-11-13 05:00 | 11 | 5 | 0 | 0
2017-11-13 06:00 | 11 | 6 | 0 | 0
2017-11-13 07:00 | 11 | 7 | 0 | 0
2017-11-13 08:00 | 11 | 8 | 759.2162 | 759.2162
2017-11-13 09:00 | 11 | 9 | 2737.5992 | 2737.5992
2017-11-13 10:00 | 11 | 10 | 2915.3937 | 2915.3937
2017-11-13 11:00 | 11 | 11 | 4285.4853 | 4285.4853
2017-11-13 12:00 | 11 | 12 | 197.578 | 197.578
2017-11-13 13:00 | 11 | 13 | 2701.91 | 2701.91
2017-11-13 14:00 | 11 | 14 | 280.3274 | 280.3274
2017-11-13 15:00 | 11 | 15 | 297.6625 | 297.6625
2017-11-13 16:00 | 11 | 16 | 0 | 0
2017-11-13 17:00 | 11 | 17 | 0 | 0
2017-11-13 18:00 | 11 | 18 | 0 | 0
2017-11-13 19:00 | 11 | 19 | 0 | 0
2017-11-13 20:00 | 11 | 20 | 0 | 0
2017-11-13 21:00 | 11 | 21 | 0 | 0
2017-11-13 22:00 | 11 | 22 | 0 | 0
2017-11-13 23:00 | 11 | 23 | 0 | 0
2017-11-14 | 11 | 0 | 0 | 0
2017-11-14 01:00 | 11 | 1 | 0 | 0
2017-11-14 02:00 | 11 | 2 | 0 | 0
2017-11-14 03:00 | 11 | 3 | 0 | 0
2017-11-14 04:00 | 11 | 4 | 0 | 0
2017-11-14 05:00 | 11 | 5 | 0 | 0
2017-11-14 06:00 | 11 | 6 | 0 | 0
2017-11-14 07:00 | 11 | 7 | 1899.3066 | 1899.3066
2017-11-14 08:00 | 11 | 8 | 2583.6486 | 2583.6486
2017-11-14 09:00 | 11 | 9 | 4807.6222 | 4807.6222
2017-11-14 10:00 | 11 | 10 | 7011.3407 | 7011.3407
2017-11-14 11:00 | 11 | 11 | 7344.782 | 7344.782
2017-11-14 12:00 | 11 | 12 | 6967.827 | 6967.827
2017-11-14 13:00 | 11 | 13 | 5989.2299 | 5989.2299
2017-11-14 14:00 | 11 | 14 | 4274.0475 | 4274.0475
2017-11-14 15:00 | 11 | 15 | 1971.1575 | 1971.1575
2017-11-14 16:00 | 11 | 16 | 0 | 0
2017-11-14 17:00 | 11 | 17 | 0 | 0
2017-11-14 18:00 | 11 | 18 | 0 | 0
2017-11-14 19:00 | 11 | 19 | 0 | 0
2017-11-14 20:00 | 11 | 20 | 0 | 0
2017-11-14 21:00 | 11 | 21 | 0 | 0
2017-11-14 22:00 | 11 | 22 | 0 | 0
2017-11-14 23:00 | 11 | 23 | 0 | 0
2017-11-15 | 11 | 0 | 0 | 0
2017-11-15 01:00 | 11 | 1 | 0 | 0
2017-11-15 02:00 | 11 | 2 | 0 | 0
2017-11-15 03:00 | 11 | 3 | 0 | 0
2017-11-15 04:00 | 11 | 4 | 0 | 0
2017-11-15 05:00 | 11 | 5 | 0 | 0
2017-11-15 06:00 | 11 | 6 | 0 | 0
2017-11-15 07:00 | 11 | 7 | 2106.7459 | 2106.7459
2017-11-15 08:00 | 11 | 8 | 4463.5134 | 4463.5134
2017-11-15 09:00 | 11 | 9 | 6105.5788 | 6105.5788
2017-11-15 10:00 | 11 | 10 | 7055.5179 | 7055.5179
2017-11-15 11:00 | 11 | 11 | 7325.5356 | 7325.5356
2017-11-15 12:00 | 11 | 12 | 6941.5541 | 6941.5541
2017-11-15 13:00 | 11 | 13 | 5893.0163 | 5893.0163
2017-11-15 14:00 | 11 | 14 | 4265.0487 | 4265.0487
2017-11-15 15:00 | 11 | 15 | 1960.3659 | 1960.3659
2017-11-15 16:00 | 11 | 16 | 0 | 0
2017-11-15 17:00 | 11 | 17 | 0 | 0
2017-11-15 18:00 | 11 | 18 | 0 | 0
2017-11-15 19:00 | 11 | 19 | 0 | 0
2017-11-15 20:00 | 11 | 20 | 0 | 0
2017-11-15 21:00 | 11 | 21 | 0 | 0
2017-11-15 22:00 | 11 | 22 | 0 | 0
2017-11-15 23:00 | 11 | 23 | 0 | 0
2017-11-16 | 11 | 0 | 0 | 0
2017-11-16 01:00 | 11 | 1 | 0 | 0
2017-11-16 02:00 | 11 | 2 | 0 | 0
2017-11-16 03:00 | 11 | 3 | 0 | 0
2017-11-16 04:00 | 11 | 4 | 0 | 0
2017-11-16 05:00 | 11 | 5 | 0 | 0
2017-11-16 06:00 | 11 | 6 | 0 | 0
2017-11-16 07:00 | 11 | 7 | 1986.9895 | 1986.9895
2017-11-16 08:00 | 11 | 8 | 4177.0863 | 4177.0863
2017-11-16 09:00 | 11 | 9 | 5681.054 | 5681.054
2017-11-16 10:00 | 11 | 10 | 6521.9938 | 6521.9938
2017-11-16 11:00 | 11 | 11 | 6766.8058 | 6766.8058
2017-11-16 12:00 | 11 | 12 | 6389.1895 | 6389.1895
2017-11-16 13:00 | 11 | 13 | 5477.6742 | 5477.6742
2017-11-16 14:00 | 11 | 14 | 3888.8687 | 3888.8688
2017-11-16 15:00 | 11 | 15 | 1760.566 | 1760.566
2017-11-16 16:00 | 11 | 16 | 0 | 0
2017-11-16 17:00 | 11 | 17 | 0 | 0
2017-11-16 18:00 | 11 | 18 | 0 | 0
2017-11-16 19:00 | 11 | 19 | 0 | 0
2017-11-16 20:00 | 11 | 20 | 0 | 0
2017-11-16 21:00 | 11 | 21 | 0 | 0
2017-11-16 22:00 | 11 | 22 | 0 | 0
2017-11-16 23:00 | 11 | 23 | 0 | 0
2017-11-17 | 11 | 0 | 0 | 0
2017-11-17 01:00 | 11 | 1 | 0 | 0
2017-11-17 02:00 | 11 | 2 | 0 | 0
2017-11-17 03:00 | 11 | 3 | 0 | 0
2017-11-17 04:00 | 11 | 4 | 0 | 0
2017-11-17 05:00 | 11 | 5 | 0 | 0
2017-11-17 06:00 | 11 | 6 | 0 | 0
2017-11-17 07:00 | 11 | 7 | 230.7544 | 230.7544
2017-11-17 08:00 | 11 | 8 | 916.6799 | 916.6799
2017-11-17 09:00 | 11 | 9 | 1459.9802 | 1459.9802
2017-11-17 10:00 | 11 | 10 | 1097.4795 | 1097.4795
2017-11-17 11:00 | 11 | 11 | 1741.6727 | 1741.6727
2017-11-17 12:00 | 11 | 12 | 51.4912 | 51.4912
2017-11-17 13:00 | 11 | 13 | 164.7605 | 164.7605
2017-11-17 14:00 | 11 | 14 | 898.1741 | 898.1741
2017-11-17 15:00 | 11 | 15 | 1319.426 | 1319.426
2017-11-17 16:00 | 11 | 16 | 0 | 0
2017-11-17 17:00 | 11 | 17 | 0 | 0
2017-11-17 18:00 | 11 | 18 | 0 | 0
2017-11-17 19:00 | 11 | 19 | 0 | 0
2017-11-17 20:00 | 11 | 20 | 0 | 0
2017-11-17 21:00 | 11 | 21 | 0 | 0
2017-11-17 22:00 | 11 | 22 | 0 | 0
2017-11-17 23:00 | 11 | 23 | 0 | 0
2017-11-18 | 11 | 0 | 0 | 0
2017-11-18 01:00 | 11 | 1 | 0 | 0
2017-11-18 02:00 | 11 | 2 | 0 | 0
2017-11-18 03:00 | 11 | 3 | 0 | 0
2017-11-18 04:00 | 11 | 4 | 0 | 0
2017-11-18 05:00 | 11 | 5 | 0 | 0
2017-11-18 06:00 | 11 | 6 | 0 | 0
2017-11-18 07:00 | 11 | 7 | 1541.8222 | 1541.8222
2017-11-18 08:00 | 11 | 8 | 3588.4197 | 3588.4197
2017-11-18 09:00 | 11 | 9 | 5105.3284 | 5105.3284
2017-11-18 10:00 | 11 | 10 | 6181.442 | 6181.442
2017-11-18 11:00 | 11 | 11 | 6422.919 | 6422.919
2017-11-18 12:00 | 11 | 12 | 6085.7632 | 6085.7632
2017-11-18 13:00 | 11 | 13 | 5141.4844 | 5141.4844
2017-11-18 14:00 | 11 | 14 | 3625.9005 | 3625.9005
2017-11-18 15:00 | 11 | 15 | 1578.2669 | 1578.2669
2017-11-18 16:00 | 11 | 16 | 0 | 0
2017-11-18 17:00 | 11 | 17 | 0 | 0
2017-11-18 18:00 | 11 | 18 | 0 | 0
2017-11-18 19:00 | 11 | 19 | 0 | 0
2017-11-18 20:00 | 11 | 20 | 0 | 0
2017-11-18 21:00 | 11 | 21 | 0 | 0
2017-11-18 22:00 | 11 | 22 | 0 | 0
2017-11-18 23:00 | 11 | 23 | 0 | 0
2017-11-19 | 11 | 0 | 0 | 0
2017-11-19 01:00 | 11 | 1 | 0 | 0
2017-11-19 02:00 | 11 | 2 | 0 | 0
2017-11-19 03:00 | 11 | 3 | 0 | 0
2017-11-19 04:00 | 11 | 4 | 0 | 0
2017-11-19 05:00 | 11 | 5 | 0 | 0
2017-11-19 06:00 | 11 | 6 | 0 | 0
2017-11-19 07:00 | 11 | 7 | 113.3808 | 113.3808
2017-11-19 08:00 | 11 | 8 | 414.6359 | 414.6359
2017-11-19 09:00 | 11 | 9 | 965.0478 | 965.0478
2017-11-19 10:00 | 11 | 10 | 1018.7884 | 1018.7884
2017-11-19 11:00 | 11 | 11 | 1192.6811 | 1192.6811
2017-11-19 12:00 | 11 | 12 | 1452.3971 | 1452.3971
2017-11-19 13:00 | 11 | 13 | 1104.2449 | 1104.2449
2017-11-19 14:00 | 11 | 14 | 236.6562 | 236.6562
2017-11-19 15:00 | 11 | 15 | 129.8649 | 129.8649
2017-11-19 16:00 | 11 | 16 | 0 | 0
2017-11-19 17:00 | 11 | 17 | 0 | 0
2017-11-19 18:00 | 11 | 18 | 0 | 0
2017-11-19 19:00 | 11 | 19 | 0 | 0
2017-11-19 20:00 | 11 | 20 | 0 | 0
2017-11-19 21:00 | 11 | 21 | 0 | 0
2017-11-19 22:00 | 11 | 22 | 0 | 0
2017-11-19 23:00 | 11 | 23 | 0 | 0
2017-11-20 | 11 | 0 | 0 | 0
2017-11-20 01:00 | 11 | 1 | 0 | 0
2017-11-20 02:00 | 11 | 2 | 0 | 0
2017-11-20 03:00 | 11 | 3 | 0 | 0
2017-11-20 04:00 | 11 | 4 | 0 | 0
2017-11-20 05:00 | 11 | 5 | 0 | 0
2017-11-20 06:00 | 11 | 6 | 0 | 0
2017-11-20 07:00 | 11 | 7 | 0 | 0
2017-11-20 08:00 | 11 | 8 | 11.3102 | 11.3102
2017-11-20 09:00 | 11 | 9 | 1094.0617 | 1094.0617
2017-11-20 10:00 | 11 | 10 | 3749.1437 | 3749.1438
2017-11-20 11:00 | 11 | 11 | 1185.374 | 1185.374
2017-11-20 12:00 | 11 | 12 | 698.9343 | 698.9343
2017-11-20 13:00 | 11 | 13 | 941.9431 | 941.9431
2017-11-20 14:00 | 11 | 14 | 3540.1013 | 3540.1013
2017-11-20 15:00 | 11 | 15 | 1484.3993 | 1484.3993
2017-11-20 16:00 | 11 | 16 | 0 | 0
2017-11-20 17:00 | 11 | 17 | 0 | 0
2017-11-20 18:00 | 11 | 18 | 0 | 0
2017-11-20 19:00 | 11 | 19 | 0 | 0
2017-11-20 20:00 | 11 | 20 | 0 | 0
2017-11-20 21:00 | 11 | 21 | 0 | 0
2017-11-20 22:00 | 11 | 22 | 0 | 0
2017-11-20 23:00 | 11 | 23 | 0 | 0
2017-11-21 | 11 | 0 | 0 | 0
2017-11-21 01:00 | 11 | 1 | 0 | 0
2017-11-21 02:00 | 11 | 2 | 0 | 0
2017-11-21 03:00 | 11 | 3 | 0 | 0
2017-11-21 04:00 | 11 | 4 | 0 | 0
2017-11-21 05:00 | 11 | 5 | 0 | 0
2017-11-21 06:00 | 11 | 6 | 0 | 0
2017-11-21 07:00 | 11 | 7 | 0 | 0
2017-11-21 08:00 | 11 | 8 | 439.5254 | 439.5254
2017-11-21 09:00 | 11 | 9 | 697.3025 | 697.3025
2017-11-21 10:00 | 11 | 10 | 1731.3365 | 1731.3365
2017-11-21 11:00 | 11 | 11 | 1547.3457 | 1547.3457
2017-11-21 12:00 | 11 | 12 | 922.2264 | 922.2264
2017-11-21 13:00 | 11 | 13 | 735.6332 | 735.6332
2017-11-21 14:00 | 11 | 14 | 3619.441 | 3619.441
2017-11-21 15:00 | 11 | 15 | 1556.7906 | 1556.7906
2017-11-21 16:00 | 11 | 16 | 0 | 0
2017-11-21 17:00 | 11 | 17 | 0 | 0
2017-11-21 18:00 | 11 | 18 | 0 | 0
2017-11-21 19:00 | 11 | 19 | 0 | 0
2017-11-21 20:00 | 11 | 20 | 0 | 0
2017-11-21 21:00 | 11 | 21 | 0 | 0
2017-11-21 22:00 | 11 | 22 | 0 | 0
2017-11-21 23:00 | 11 | 23 | 0 | 0
2017-11-22 | 11 | 0 | 0 | 0
2017-11-22 01:00 | 11 | 1 | 0 | 0
2017-11-22 02:00 | 11 | 2 | 0 | 0
2017-11-22 03:00 | 11 | 3 | 0 | 0
2017-11-22 04:00 | 11 | 4 | 0 | 0
2017-11-22 05:00 | 11 | 5 | 0 | 0
2017-11-22 06:00 | 11 | 6 | 0 | 0
2017-11-22 07:00 | 11 | 7 | 1586.5779 | 1586.5779
2017-11-22 08:00 | 11 | 8 | 3753.6207 | 3753.6207
2017-11-22 09:00 | 11 | 9 | 5374.1846 | 5374.1846
2017-11-22 10:00 | 11 | 10 | 4648.6335 | 4648.6335
2017-11-22 11:00 | 11 | 11 | 6582.3792 | 6582.3792
2017-11-22 12:00 | 11 | 12 | 6211.595 | 6211.595
2017-11-22 13:00 | 11 | 13 | 5318.9018 | 5318.9018
2017-11-22 14:00 | 11 | 14 | 3777.3774 | 3777.3774
2017-11-22 15:00 | 11 | 15 | 1679.0506 | 1679.0506
2017-11-22 16:00 | 11 | 16 | 0 | 0
2017-11-22 17:00 | 11 | 17 | 0 | 0
2017-11-22 18:00 | 11 | 18 | 0 | 0
2017-11-22 19:00 | 11 | 19 | 0 | 0
2017-11-22 20:00 | 11 | 20 | 0 | 0
2017-11-22 21:00 | 11 | 21 | 0 | 0
2017-11-22 22:00 | 11 | 22 | 0 | 0
2017-11-22 23:00 | 11 | 23 | 0 | 0
2017-11-23 | 11 | 0 | 0 | 0
2017-11-23 01:00 | 11 | 1 | 0 | 0
2017-11-23 02:00 | 11 | 2 | 0 | 0
2017-11-23 03:00 | 11 | 3 | 0 | 0
2017-11-23 04:00 | 11 | 4 | 0 | 0
2017-11-23 05:00 | 11 | 5 | 0 | 0
2017-11-23 06:00 | 11 | 6 | 0 | 0
2017-11-23 07:00 | 11 | 7 | 1445.8846 | 1445.8846
2017-11-23 08:00 | 11 | 8 | 3465.2536 | 3465.2536
2017-11-23 09:00 | 11 | 9 | 4257.7048 | 4257.7048
2017-11-23 10:00 | 11 | 10 | 4928.5516 | 4928.5516
2017-11-23 11:00 | 11 | 11 | 6551.0658 | 6551.0658
2017-11-23 12:00 | 11 | 12 | 5077.1511 | 5077.1511
2017-11-23 13:00 | 11 | 13 | 5310.2285 | 5310.2285
2017-11-23 14:00 | 11 | 14 | 3719.0896 | 3719.0897
2017-11-23 15:00 | 11 | 15 | 1629.5074 | 1629.5074
2017-11-23 16:00 | 11 | 16 | 0 | 0
2017-11-23 17:00 | 11 | 17 | 0 | 0
2017-11-23 18:00 | 11 | 18 | 0 | 0
2017-11-23 19:00 | 11 | 19 | 0 | 0
2017-11-23 20:00 | 11 | 20 | 0 | 0
2017-11-23 21:00 | 11 | 21 | 0 | 0
2017-11-23 22:00 | 11 | 22 | 0 | 0
2017-11-23 23:00 | 11 | 23 | 0 | 0
2017-11-24 | 11 | 0 | 0 | 0
2017-11-24 01:00 | 11 | 1 | 0 | 0
2017-11-24 02:00 | 11 | 2 | 0 | 0
2017-11-24 03:00 | 11 | 3 | 0 | 0
2017-11-24 04:00 | 11 | 4 | 0 | 0
2017-11-24 05:00 | 11 | 5 | 0 | 0
2017-11-24 06:00 | 11 | 6 | 0 | 0
2017-11-24 07:00 | 11 | 7 | 1517.6469 | 1517.6469
2017-11-24 08:00 | 11 | 8 | 1700.2451 | 1700.2451
2017-11-24 09:00 | 11 | 9 | 2478.2293 | 2478.2293
2017-11-24 10:00 | 11 | 10 | 3011.191 | 3011.191
2017-11-24 11:00 | 11 | 11 | 6571.7704 | 6571.7704
2017-11-24 12:00 | 11 | 12 | 6157.2541 | 6157.2541
2017-11-24 13:00 | 11 | 13 | 5205.5842 | 5205.5842
2017-11-24 14:00 | 11 | 14 | 3648.0771 | 3648.0771
2017-11-24 15:00 | 11 | 15 | 1573.9325 | 1573.9325
2017-11-24 16:00 | 11 | 16 | 0 | 0
2017-11-24 17:00 | 11 | 17 | 0 | 0
2017-11-24 18:00 | 11 | 18 | 0 | 0
2017-11-24 19:00 | 11 | 19 | 0 | 0
2017-11-24 20:00 | 11 | 20 | 0 | 0
2017-11-24 21:00 | 11 | 21 | 0 | 0
2017-11-24 22:00 | 11 | 22 | 0 | 0
2017-11-24 23:00 | 11 | 23 | 0 | 0
2017-11-25 | 11 | 0 | 0 | 0
2017-11-25 01:00 | 11 | 1 | 0 | 0
2017-11-25 02:00 | 11 | 2 | 0 | 0
2017-11-25 03:00 | 11 | 3 | 0 | 0
2017-11-25 04:00 | 11 | 4 | 0 | 0
2017-11-25 05:00 | 11 | 5 | 0 | 0
2017-11-25 06:00 | 11 | 6 | 0 | 0
2017-11-25 07:00 | 11 | 7 | 1559.4644 | 1559.4644
2017-11-25 08:00 | 11 | 8 | 3801.7367 | 3801.7367
2017-11-25 09:00 | 11 | 9 | 5425.2549 | 5425.2549
2017-11-25 10:00 | 11 | 10 | 6355.6521 | 6355.6521
2017-11-25 11:00 | 11 | 11 | 6630.4181 | 6630.4181
2017-11-25 12:00 | 11 | 12 | 4002.6325 | 4002.6325
2017-11-25 13:00 | 11 | 13 | 3261.776 | 3261.776
2017-11-25 14:00 | 11 | 14 | 3807.0152 | 3807.0152
2017-11-25 15:00 | 11 | 15 | 1606.9755 | 1606.9755
2017-11-25 16:00 | 11 | 16 | 0 | 0
2017-11-25 17:00 | 11 | 17 | 0 | 0
2017-11-25 18:00 | 11 | 18 | 0 | 0
2017-11-25 19:00 | 11 | 19 | 0 | 0
2017-11-25 20:00 | 11 | 20 | 0 | 0
2017-11-25 21:00 | 11 | 21 | 0 | 0
2017-11-25 22:00 | 11 | 22 | 0 | 0
2017-11-25 23:00 | 11 | 23 | 0 | 0
2017-11-26 | 11 | 0 | 0 | 0
2017-11-26 01:00 | 11 | 1 | 0 | 0
2017-11-26 02:00 | 11 | 2 | 0 | 0
2017-11-26 03:00 | 11 | 3 | 0 | 0
2017-11-26 04:00 | 11 | 4 | 0 | 0
2017-11-26 05:00 | 11 | 5 | 0 | 0
2017-11-26 06:00 | 11 | 6 | 0 | 0
2017-11-26 07:00 | 11 | 7 | 420.3135 | 420.3135
2017-11-26 08:00 | 11 | 8 | 3698.147 | 3698.147
2017-11-26 09:00 | 11 | 9 | 4264.1954 | 4264.1954
2017-11-26 10:00 | 11 | 10 | 4366.6535 | 4366.6535
2017-11-26 11:00 | 11 | 11 | 1920.5862 | 1920.5862
2017-11-26 12:00 | 11 | 12 | 4392.663 | 4392.663
2017-11-26 13:00 | 11 | 13 | 1410.2887 | 1410.2887
2017-11-26 14:00 | 11 | 14 | 2826.432 | 2826.432
2017-11-26 15:00 | 11 | 15 | 1176.7892 | 1176.7892
2017-11-26 16:00 | 11 | 16 | 0 | 0
2017-11-26 17:00 | 11 | 17 | 0 | 0
2017-11-26 18:00 | 11 | 18 | 0 | 0
2017-11-26 19:00 | 11 | 19 | 0 | 0
2017-11-26 20:00 | 11 | 20 | 0 | 0
2017-11-26 21:00 | 11 | 21 | 0 | 0
2017-11-26 22:00 | 11 | 22 | 0 | 0
2017-11-26 23:00 | 11 | 23 | 0 | 0
2017-11-27 | 11 | 0 | 0 | 0
2017-11-27 01:00 | 11 | 1 | 0 | 0
2017-11-27 02:00 | 11 | 2 | 0 | 0
2017-11-27 03:00 | 11 | 3 | 0 | 0
2017-11-27 04:00 | 11 | 4 | 0 | 0
2017-11-27 05:00 | 11 | 5 | 0 | 0
2017-11-27 06:00 | 11 | 6 | 0 | 0
2017-11-27 07:00 | 11 | 7 | 391.5117 | 391.5117
2017-11-27 08:00 | 11 | 8 | 3110.8753 | 3110.8753
2017-11-27 09:00 | 11 | 9 | 3872.8136 | 3872.8136
2017-11-27 10:00 | 11 | 10 | 6015.6511 | 6015.6511
2017-11-27 11:00 | 11 | 11 | 6282.5949 | 6282.5949
2017-11-27 12:00 | 11 | 12 | 4363.0712 | 4363.0712
2017-11-27 13:00 | 11 | 13 | 3428.0258 | 3428.0258
2017-11-27 14:00 | 11 | 14 | 3527.1845 | 3527.1845
2017-11-27 15:00 | 11 | 15 | 1413.6674 | 1413.6674
2017-11-27 16:00 | 11 | 16 | 0 | 0
2017-11-27 17:00 | 11 | 17 | 0 | 0
2017-11-27 18:00 | 11 | 18 | 0 | 0
2017-11-27 19:00 | 11 | 19 | 0 | 0
2017-11-27 20:00 | 11 | 20 | 0 | 0
2017-11-27 21:00 | 11 | 21 | 0 | 0
2017-11-27 22:00 | 11 | 22 | 0 | 0
2017-11-27 23:00 | 11 | 23 | 0 | 0
2017-11-28 | 11 | 0 | 0 | 0
2017-11-28 01:00 | 11 | 1 | 0 | 0
2017-11-28 02:00 | 11 | 2 | 0 | 0
2017-11-28 03:00 | 11 | 3 | 0 | 0
2017-11-28 04:00 | 11 | 4 | 0 | 0
2017-11-28 05:00 | 11 | 5 | 0 | 0
2017-11-28 06:00 | 11 | 6 | 0 | 0
2017-11-28 07:00 | 11 | 7 | 0 | 0
2017-11-28 08:00 | 11 | 8 | 124.2575 | 124.2575
2017-11-28 09:00 | 11 | 9 | 284.387 | 284.387
2017-11-28 10:00 | 11 | 10 | 364.213 | 364.213
2017-11-28 11:00 | 11 | 11 | 411.8794 | 411.8794
2017-11-28 12:00 | 11 | 12 | 958.2409 | 958.2409
2017-11-28 13:00 | 11 | 13 | 289.3032 | 289.3032
2017-11-28 14:00 | 11 | 14 | 259.5768 | 259.5768
2017-11-28 15:00 | 11 | 15 | 70.9745 | 70.9745
2017-11-28 16:00 | 11 | 16 | 0 | 0
2017-11-28 17:00 | 11 | 17 | 0 | 0
2017-11-28 18:00 | 11 | 18 | 0 | 0
2017-11-28 19:00 | 11 | 19 | 0 | 0
2017-11-28 20:00 | 11 | 20 | 0 | 0
2017-11-28 21:00 | 11 | 21 | 0 | 0
2017-11-28 22:00 | 11 | 22 | 0 | 0
2017-11-28 23:00 | 11 | 23 | 0 | 0
2017-11-29 | 11 | 0 | 0 | 0
2017-11-29 01:00 | 11 | 1 | 0 | 0
2017-11-29 02:00 | 11 | 2 | 0 | 0
2017-11-29 03:00 | 11 | 3 | 0 | 0
2017-11-29 04:00 | 11 | 4 | 0 | 0
2017-11-29 05:00 | 11 | 5 | 0 | 0
2017-11-29 06:00 | 11 | 6 | 0 | 0
2017-11-29 07:00 | 11 | 7 | 0 | 0
2017-11-29 08:00 | 11 | 8 | 534.0473 | 534.0473
2017-11-29 09:00 | 11 | 9 | 2496.673 | 2496.673
2017-11-29 10:00 | 11 | 10 | 2618.6914 | 2618.6914
2017-11-29 11:00 | 11 | 11 | 6230.777 | 6230.777
2017-11-29 12:00 | 11 | 12 | 2356.2108 | 2356.2108
2017-11-29 13:00 | 11 | 13 | 3404.1173 | 3404.1173
2017-11-29 14:00 | 11 | 14 | 222.5422 | 222.5422
2017-11-29 15:00 | 11 | 15 | 281.8765 | 281.8765
2017-11-29 16:00 | 11 | 16 | 0 | 0
2017-11-29 17:00 | 11 | 17 | 0 | 0
2017-11-29 18:00 | 11 | 18 | 0 | 0
2017-11-29 19:00 | 11 | 19 | 0 | 0
2017-11-29 20:00 | 11 | 20 | 0 | 0
2017-11-29 21:00 | 11 | 21 | 0 | 0
2017-11-29 22:00 | 11 | 22 | 0 | 0
2017-11-29 23:00 | 11 | 23 | 0 | 0
2017-11-30 | 11 | 0 | 0 | 0
2017-11-30 01:00 | 11 | 1 | 0 | 0
2017-11-30 02:00 | 11 | 2 | 0 | 0
2017-11-30 03:00 | 11 | 3 | 0 | 0
2017-11-30 04:00 | 11 | 4 | 0 | 0
2017-11-30 05:00 | 11 | 5 | 0 | 0
2017-11-30 06:00 | 11 | 6 | 0 | 0
2017-11-30 07:00 | 11 | 7 | 24.1316 | 24.1316
2017-11-30 08:00 | 11 | 8 | 2681.8644 | 2681.8644
2017-11-30 09:00 | 11 | 9 | 3798.2487 | 3798.2487
2017-11-30 10:00 | 11 | 10 | 3361.412 | 3361.412
2017-11-30 11:00 | 11 | 11 | 6380.8037 | 6380.8037
2017-11-30 12:00 | 11 | 12 | 6006.7559 | 6006.7559
2017-11-30 13:00 | 11 | 13 | 5081.9558 | 5081.9558
2017-11-30 14:00 | 11 | 14 | 3518.6642 | 3518.6642
2017-11-30 15:00 | 11 | 15 | 774.579 | 774.579
2017-11-30 16:00 | 11 | 16 | 0 | 0
2017-11-30 17:00 | 11 | 17 | 0 | 0
2017-11-30 18:00 | 11 | 18 | 0 | 0
2017-11-30 19:00 | 11 | 19 | 0 | 0
2017-11-30 20:00 | 11 | 20 | 0 | 0
2017-11-30 21:00 | 11 | 21 | 0 | 0
2017-11-30 22:00 | 11 | 22 | 0 | 0
2017-11-30 23:00 | 11 | 23 | 0 | 0
2017-12-01 | 12 | 0 | 0 | 0
2017-12-01 01:00 | 12 | 1 | 0 | 0
2017-12-01 02:00 | 12 | 2 | 0 | 0
2017-12-01 03:00 | 12 | 3 | 0 | 0
2017-12-01 04:00 | 12 | 4 | 0 | 0
2017-12-01 05:00 | 12 | 5 | 0 | 0
2017-12-01 06:00 | 12 | 6 | 0 | 0
2017-12-01 07:00 | 12 | 7 | 219.3084 | 219.3084
2017-12-01 08:00 | 12 | 8 | 469.9981 | 469.9981
2017-12-01 09:00 | 12 | 9 | 423.5002 | 423.5002
2017-12-01 10:00 | 12 | 10 | 5555.3694 | 5555.3694
2017-12-01 11:00 | 12 | 11 | 6524.2283 | 6524.2283
2017-12-01 12:00 | 12 | 12 | 6264.1753 | 6264.1753
2017-12-01 13:00 | 12 | 13 | 5351.2582 | 5351.2582
2017-12-01 14:00 | 12 | 14 | 1686.8361 | 1686.8361
2017-12-01 15:00 | 12 | 15 | 1556.4756 | 1556.4756
2017-12-01 16:00 | 12 | 16 | 0 | 0
2017-12-01 17:00 | 12 | 17 | 0 | 0
2017-12-01 18:00 | 12 | 18 | 0 | 0
2017-12-01 19:00 | 12 | 19 | 0 | 0
2017-12-01 20:00 | 12 | 20 | 0 | 0
2017-12-01 21:00 | 12 | 21 | 0 | 0
2017-12-01 22:00 | 12 | 22 | 0 | 0
2017-12-01 23:00 | 12 | 23 | 0 | 0
2017-12-02 | 12 | 0 | 0 | 0
2017-12-02 01:00 | 12 | 1 | 0 | 0
2017-12-02 02:00 | 12 | 2 | 0 | 0
2017-12-02 03:00 | 12 | 3 | 0 | 0
2017-12-02 04:00 | 12 | 4 | 0 | 0
2017-12-02 05:00 | 12 | 5 | 0 | 0
2017-12-02 06:00 | 12 | 6 | 0 | 0
2017-12-02 07:00 | 12 | 7 | 1110.9851 | 1110.9851
2017-12-02 08:00 | 12 | 8 | 870.55 | 870.55
2017-12-02 09:00 | 12 | 9 | 1162.6316 | 1162.6316
2017-12-02 10:00 | 12 | 10 | 2997.3657 | 2997.3657
2017-12-02 11:00 | 12 | 11 | 4239.935 | 4239.935
2017-12-02 12:00 | 12 | 12 | 42.7214 | 42.7214
2017-12-02 13:00 | 12 | 13 | 3822.4034 | 3822.4033
2017-12-02 14:00 | 12 | 14 | 1723.3911 | 1723.3911
2017-12-02 15:00 | 12 | 15 | 0 | 0
2017-12-02 16:00 | 12 | 16 | 0 | 0
2017-12-02 17:00 | 12 | 17 | 0 | 0
2017-12-02 18:00 | 12 | 18 | 0 | 0
2017-12-02 19:00 | 12 | 19 | 0 | 0
2017-12-02 20:00 | 12 | 20 | 0 | 0
2017-12-02 21:00 | 12 | 21 | 0 | 0
2017-12-02 22:00 | 12 | 22 | 0 | 0
2017-12-02 23:00 | 12 | 23 | 0 | 0
2017-12-03 | 12 | 0 | 0 | 0
2017-12-03 01:00 | 12 | 1 | 0 | 0
2017-12-03 02:00 | 12 | 2 | 0 | 0
2017-12-03 03:00 | 12 | 3 | 0 | 0
2017-12-03 04:00 | 12 | 4 | 0 | 0
2017-12-03 05:00 | 12 | 5 | 0 | 0
2017-12-03 06:00 | 12 | 6 | 0 | 0
2017-12-03 07:00 | 12 | 7 | 1338.3412 | 1338.3412
2017-12-03 08:00 | 12 | 8 | 3693.6436 | 3693.6436
2017-12-03 09:00 | 12 | 9 | 5441.838 | 5441.838
2017-12-03 10:00 | 12 | 10 | 6492.7114 | 6492.7114
2017-12-03 11:00 | 12 | 11 | 6786.1937 | 6786.1937
2017-12-03 12:00 | 12 | 12 | 6474.0756 | 6474.0756
2017-12-03 13:00 | 12 | 13 | 5566.5175 | 5566.5175
2017-12-03 14:00 | 12 | 14 | 3937.301 | 3937.301
2017-12-03 15:00 | 12 | 15 | 1692.8425 | 1692.8425
2017-12-03 16:00 | 12 | 16 | 0 | 0
2017-12-03 17:00 | 12 | 17 | 0 | 0
2017-12-03 18:00 | 12 | 18 | 0 | 0
2017-12-03 19:00 | 12 | 19 | 0 | 0
2017-12-03 20:00 | 12 | 20 | 0 | 0
2017-12-03 21:00 | 12 | 21 | 0 | 0
2017-12-03 22:00 | 12 | 22 | 0 | 0
2017-12-03 23:00 | 12 | 23 | 0 | 0
2017-12-04 | 12 | 0 | 0 | 0
2017-12-04 01:00 | 12 | 1 | 0 | 0
2017-12-04 02:00 | 12 | 2 | 0 | 0
2017-12-04 03:00 | 12 | 3 | 0 | 0
2017-12-04 04:00 | 12 | 4 | 0 | 0
2017-12-04 05:00 | 12 | 5 | 0 | 0
2017-12-04 06:00 | 12 | 6 | 0 | 0
2017-12-04 07:00 | 12 | 7 | 322.0425 | 322.0425
2017-12-04 08:00 | 12 | 8 | 3144.0482 | 3144.0482
2017-12-04 09:00 | 12 | 9 | 4836.9609 | 4836.9609
2017-12-04 10:00 | 12 | 10 | 6046.9875 | 6046.9875
2017-12-04 11:00 | 12 | 11 | 1429.1142 | 1429.1142
2017-12-04 12:00 | 12 | 12 | 3751.0389 | 3751.0389
2017-12-04 13:00 | 12 | 13 | 4190.1871 | 4190.1871
2017-12-04 14:00 | 12 | 14 | 2362.7348 | 2362.7348
2017-12-04 15:00 | 12 | 15 | 586.178 | 586.178
2017-12-04 16:00 | 12 | 16 | 0 | 0
2017-12-04 17:00 | 12 | 17 | 0 | 0
2017-12-04 18:00 | 12 | 18 | 0 | 0
2017-12-04 19:00 | 12 | 19 | 0 | 0
2017-12-04 20:00 | 12 | 20 | 0 | 0
2017-12-04 21:00 | 12 | 21 | 0 | 0
2017-12-04 22:00 | 12 | 22 | 0 | 0
2017-12-04 23:00 | 12 | 23 | 0 | 0
2017-12-05 | 12 | 0 | 0 | 0
2017-12-05 01:00 | 12 | 1 | 0 | 0
2017-12-05 02:00 | 12 | 2 | 0 | 0
2017-12-05 03:00 | 12 | 3 | 0 | 0
2017-12-05 04:00 | 12 | 4 | 0 | 0
2017-12-05 05:00 | 12 | 5 | 0 | 0
2017-12-05 06:00 | 12 | 6 | 0 | 0
2017-12-05 07:00 | 12 | 7 | 762.1084 | 762.1084
2017-12-05 08:00 | 12 | 8 | 2360.6395 | 2360.6395
2017-12-05 09:00 | 12 | 9 | 4203.6812 | 4203.6812
2017-12-05 10:00 | 12 | 10 | 4460.3118 | 4460.3118
2017-12-05 11:00 | 12 | 11 | 4865.3878 | 4865.3878
2017-12-05 12:00 | 12 | 12 | 2996.2019 | 2996.2019
2017-12-05 13:00 | 12 | 13 | 1875.6454 | 1875.6454
2017-12-05 14:00 | 12 | 14 | 1964.0827 | 1964.0827
2017-12-05 15:00 | 12 | 15 | 710.0077 | 710.0077
2017-12-05 16:00 | 12 | 16 | 0 | 0
2017-12-05 17:00 | 12 | 17 | 0 | 0
2017-12-05 18:00 | 12 | 18 | 0 | 0
2017-12-05 19:00 | 12 | 19 | 0 | 0
2017-12-05 20:00 | 12 | 20 | 0 | 0
2017-12-05 21:00 | 12 | 21 | 0 | 0
2017-12-05 22:00 | 12 | 22 | 0 | 0
2017-12-05 23:00 | 12 | 23 | 0 | 0
2017-12-06 | 12 | 0 | 0 | 0
2017-12-06 01:00 | 12 | 1 | 0 | 0
2017-12-06 02:00 | 12 | 2 | 0 | 0
2017-12-06 03:00 | 12 | 3 | 0 | 0
2017-12-06 04:00 | 12 | 4 | 0 | 0
2017-12-06 05:00 | 12 | 5 | 0 | 0
2017-12-06 06:00 | 12 | 6 | 0 | 0
2017-12-06 07:00 | 12 | 7 | 538.9417 | 538.9417
2017-12-06 08:00 | 12 | 8 | 1117.6942 | 1117.6942
2017-12-06 09:00 | 12 | 9 | 2594.0009 | 2594.0009
2017-12-06 10:00 | 12 | 10 | 1474.3678 | 1474.3678
2017-12-06 11:00 | 12 | 11 | 2542.2705 | 2542.2705
2017-12-06 12:00 | 12 | 12 | 2204.8398 | 2204.8398
2017-12-06 13:00 | 12 | 13 | 270.7238 | 270.7238
2017-12-06 14:00 | 12 | 14 | 689.7815 | 689.7815
2017-12-06 15:00 | 12 | 15 | 148.3362 | 148.3362
2017-12-06 16:00 | 12 | 16 | 0 | 0
2017-12-06 17:00 | 12 | 17 | 0 | 0
2017-12-06 18:00 | 12 | 18 | 0 | 0
2017-12-06 19:00 | 12 | 19 | 0 | 0
2017-12-06 20:00 | 12 | 20 | 0 | 0
2017-12-06 21:00 | 12 | 21 | 0 | 0
2017-12-06 22:00 | 12 | 22 | 0 | 0
2017-12-06 23:00 | 12 | 23 | 0 | 0
2017-12-07 | 12 | 0 | 0 | 0
2017-12-07 01:00 | 12 | 1 | 0 | 0
2017-12-07 02:00 | 12 | 2 | 0 | 0
2017-12-07 03:00 | 12 | 3 | 0 | 0
2017-12-07 04:00 | 12 | 4 | 0 | 0
2017-12-07 05:00 | 12 | 5 | 0 | 0
2017-12-07 06:00 | 12 | 6 | 0 | 0
2017-12-07 07:00 | 12 | 7 | 161.8499 | 161.8499
2017-12-07 08:00 | 12 | 8 | 441.6437 | 441.6437
2017-12-07 09:00 | 12 | 9 | 294.2677 | 294.2677
2017-12-07 10:00 | 12 | 10 | 490.6912 | 490.6912
2017-12-07 11:00 | 12 | 11 | 1618.6135 | 1618.6135
2017-12-07 12:00 | 12 | 12 | 1486.8488 | 1486.8488
2017-12-07 13:00 | 12 | 13 | 2476.0328 | 2476.0328
2017-12-07 14:00 | 12 | 14 | 457.033 | 457.033
2017-12-07 15:00 | 12 | 15 | 1135.1454 | 1135.1454
2017-12-07 16:00 | 12 | 16 | 0 | 0
2017-12-07 17:00 | 12 | 17 | 0 | 0
2017-12-07 18:00 | 12 | 18 | 0 | 0
2017-12-07 19:00 | 12 | 19 | 0 | 0
2017-12-07 20:00 | 12 | 20 | 0 | 0
2017-12-07 21:00 | 12 | 21 | 0 | 0
2017-12-07 22:00 | 12 | 22 | 0 | 0
2017-12-07 23:00 | 12 | 23 | 0 | 0
2017-12-08 | 12 | 0 | 0 | 0
2017-12-08 01:00 | 12 | 1 | 0 | 0
2017-12-08 02:00 | 12 | 2 | 0 | 0
2017-12-08 03:00 | 12 | 3 | 0 | 0
2017-12-08 04:00 | 12 | 4 | 0 | 0
2017-12-08 05:00 | 12 | 5 | 0 | 0
2017-12-08 06:00 | 12 | 6 | 0 | 0
2017-12-08 07:00 | 12 | 7 | 1088.5762 | 1088.5762
2017-12-08 08:00 | 12 | 8 | 3394.7218 | 3394.7218
2017-12-08 09:00 | 12 | 9 | 5156.6563 | 5156.6563
2017-12-08 10:00 | 12 | 10 | 6228.4506 | 6228.4506
2017-12-08 11:00 | 12 | 11 | 6621.1549 | 6621.1549
2017-12-08 12:00 | 12 | 12 | 6383.3625 | 6383.3625
2017-12-08 13:00 | 12 | 13 | 5475.5387 | 5475.5387
2017-12-08 14:00 | 12 | 14 | 3855.8603 | 3855.8603
2017-12-08 15:00 | 12 | 15 | 1616.149 | 1616.149
2017-12-08 16:00 | 12 | 16 | 0 | 0
2017-12-08 17:00 | 12 | 17 | 0 | 0
2017-12-08 18:00 | 12 | 18 | 0 | 0
2017-12-08 19:00 | 12 | 19 | 0 | 0
2017-12-08 20:00 | 12 | 20 | 0 | 0
2017-12-08 21:00 | 12 | 21 | 0 | 0
2017-12-08 22:00 | 12 | 22 | 0 | 0
2017-12-08 23:00 | 12 | 23 | 0 | 0
2017-12-09 | 12 | 0 | 0 | 0
2017-12-09 01:00 | 12 | 1 | 0 | 0
2017-12-09 02:00 | 12 | 2 | 0 | 0
2017-12-09 03:00 | 12 | 3 | 0 | 0
2017-12-09 04:00 | 12 | 4 | 0 | 0
2017-12-09 05:00 | 12 | 5 | 0 | 0
2017-12-09 06:00 | 12 | 6 | 0 | 0
2017-12-09 07:00 | 12 | 7 | 1147.4309 | 1147.4309
2017-12-09 08:00 | 12 | 8 | 3470.0732 | 3470.0732
2017-12-09 09:00 | 12 | 9 | 5188.5252 | 5188.5252
2017-12-09 10:00 | 12 | 10 | 6240.6762 | 6240.6762
2017-12-09 11:00 | 12 | 11 | 6600.2306 | 6600.2306
2017-12-09 12:00 | 12 | 12 | 6301.7872 | 6301.7872
2017-12-09 13:00 | 12 | 13 | 5351.5284 | 5351.5284
2017-12-09 14:00 | 12 | 14 | 3735.622 | 3735.622
2017-12-09 15:00 | 12 | 15 | 1522.002 | 1522.002
2017-12-09 16:00 | 12 | 16 | 0 | 0
2017-12-09 17:00 | 12 | 17 | 0 | 0
2017-12-09 18:00 | 12 | 18 | 0 | 0
2017-12-09 19:00 | 12 | 19 | 0 | 0
2017-12-09 20:00 | 12 | 20 | 0 | 0
2017-12-09 21:00 | 12 | 21 | 0 | 0
2017-12-09 22:00 | 12 | 22 | 0 | 0
2017-12-09 23:00 | 12 | 23 | 0 | 0
2017-12-10 | 12 | 0 | 0 | 0
2017-12-10 01:00 | 12 | 1 | 0 | 0
2017-12-10 02:00 | 12 | 2 | 0 | 0
2017-12-10 03:00 | 12 | 3 | 0 | 0
2017-12-10 04:00 | 12 | 4 | 0 | 0
2017-12-10 05:00 | 12 | 5 | 0 | 0
2017-12-10 06:00 | 12 | 6 | 0 | 0
2017-12-10 07:00 | 12 | 7 | 901.8127 | 901.8127
2017-12-10 08:00 | 12 | 8 | 3099.4167 | 3099.4167
2017-12-10 09:00 | 12 | 9 | 765.7953 | 765.7953
2017-12-10 10:00 | 12 | 10 | 1410.2162 | 1410.2162
2017-12-10 11:00 | 12 | 11 | 1626.5588 | 1626.5588
2017-12-10 12:00 | 12 | 12 | 1292.5724 | 1292.5724
2017-12-10 13:00 | 12 | 13 | 1296.5744 | 1296.5744
2017-12-10 14:00 | 12 | 14 | 1521.8329 | 1521.8329
2017-12-10 15:00 | 12 | 15 | 407.974 | 407.974
2017-12-10 16:00 | 12 | 16 | 0 | 0
2017-12-10 17:00 | 12 | 17 | 0 | 0
2017-12-10 18:00 | 12 | 18 | 0 | 0
2017-12-10 19:00 | 12 | 19 | 0 | 0
2017-12-10 20:00 | 12 | 20 | 0 | 0
2017-12-10 21:00 | 12 | 21 | 0 | 0
2017-12-10 22:00 | 12 | 22 | 0 | 0
2017-12-10 23:00 | 12 | 23 | 0 | 0
2017-12-11 | 12 | 0 | 0 | 0
2017-12-11 01:00 | 12 | 1 | 0 | 0
2017-12-11 02:00 | 12 | 2 | 0 | 0
2017-12-11 03:00 | 12 | 3 | 0 | 0
2017-12-11 04:00 | 12 | 4 | 0 | 0
2017-12-11 05:00 | 12 | 5 | 0 | 0
2017-12-11 06:00 | 12 | 6 | 0 | 0
2017-12-11 07:00 | 12 | 7 | 52.9908 | 52.9909
2017-12-11 08:00 | 12 | 8 | 408.6111 | 408.6111
2017-12-11 09:00 | 12 | 9 | 1109.0105 | 1109.0105
2017-12-11 10:00 | 12 | 10 | 2008.6164 | 2008.6164
2017-12-11 11:00 | 12 | 11 | 707.1327 | 707.1327
2017-12-11 12:00 | 12 | 12 | 597.755 | 597.755
2017-12-11 13:00 | 12 | 13 | 934.6188 | 934.6188
2017-12-11 14:00 | 12 | 14 | 50.7426 | 50.7426
2017-12-11 15:00 | 12 | 15 | 0 | 0
2017-12-11 16:00 | 12 | 16 | 0 | 0
2017-12-11 17:00 | 12 | 17 | 0 | 0
2017-12-11 18:00 | 12 | 18 | 0 | 0
2017-12-11 19:00 | 12 | 19 | 0 | 0
2017-12-11 20:00 | 12 | 20 | 0 | 0
2017-12-11 21:00 | 12 | 21 | 0 | 0
2017-12-11 22:00 | 12 | 22 | 0 | 0
2017-12-11 23:00 | 12 | 23 | 0 | 0
2017-12-12 | 12 | 0 | 0 | 0
2017-12-12 01:00 | 12 | 1 | 0 | 0
2017-12-12 02:00 | 12 | 2 | 0 | 0
2017-12-12 03:00 | 12 | 3 | 0 | 0
2017-12-12 04:00 | 12 | 4 | 0 | 0
2017-12-12 05:00 | 12 | 5 | 0 | 0
2017-12-12 06:00 | 12 | 6 | 0 | 0
2017-12-12 07:00 | 12 | 7 | 849.1117 | 849.1117
2017-12-12 08:00 | 12 | 8 | 3154.266 | 3154.266
2017-12-12 09:00 | 12 | 9 | 5004.7195 | 5004.7195
2017-12-12 10:00 | 12 | 10 | 6180.2978 | 6180.2978
2017-12-12 11:00 | 12 | 11 | 6611.6432 | 6611.6432
2017-12-12 12:00 | 12 | 12 | 6366.9037 | 6366.9037
2017-12-12 13:00 | 12 | 13 | 5299.9532 | 5299.9532
2017-12-12 14:00 | 12 | 14 | 3747.4544 | 3747.4544
2017-12-12 15:00 | 12 | 15 | 1573.5243 | 1573.5243
2017-12-12 16:00 | 12 | 16 | 0 | 0
2017-12-12 17:00 | 12 | 17 | 0 | 0
2017-12-12 18:00 | 12 | 18 | 0 | 0
2017-12-12 19:00 | 12 | 19 | 0 | 0
2017-12-12 20:00 | 12 | 20 | 0 | 0
2017-12-12 21:00 | 12 | 21 | 0 | 0
2017-12-12 22:00 | 12 | 22 | 0 | 0
2017-12-12 23:00 | 12 | 23 | 0 | 0
2017-12-13 | 12 | 0 | 0 | 0
2017-12-13 01:00 | 12 | 1 | 0 | 0
2017-12-13 02:00 | 12 | 2 | 0 | 0
2017-12-13 03:00 | 12 | 3 | 0 | 0
2017-12-13 04:00 | 12 | 4 | 0 | 0
2017-12-13 05:00 | 12 | 5 | 0 | 0
2017-12-13 06:00 | 12 | 6 | 0 | 0
2017-12-13 07:00 | 12 | 7 | 1112.1524 | 1112.1524
2017-12-13 08:00 | 12 | 8 | 3498.4886 | 3498.4886
2017-12-13 09:00 | 12 | 9 | 5370.807 | 5370.807
2017-12-13 10:00 | 12 | 10 | 6486.1495 | 6486.1495
2017-12-13 11:00 | 12 | 11 | 6884.7349 | 6884.7349
2017-12-13 12:00 | 12 | 12 | 6450.2649 | 6450.2649
2017-12-13 13:00 | 12 | 13 | 5568.6852 | 5568.6852
2017-12-13 14:00 | 12 | 14 | 3962.1709 | 3962.1709
2017-12-13 15:00 | 12 | 15 | 1725.7705 | 1725.7705
2017-12-13 16:00 | 12 | 16 | 0 | 0
2017-12-13 17:00 | 12 | 17 | 0 | 0
2017-12-13 18:00 | 12 | 18 | 0 | 0
2017-12-13 19:00 | 12 | 19 | 0 | 0
2017-12-13 20:00 | 12 | 20 | 0 | 0
2017-12-13 21:00 | 12 | 21 | 0 | 0
2017-12-13 22:00 | 12 | 22 | 0 | 0
2017-12-13 23:00 | 12 | 23 | 0 | 0
2017-12-14 | 12 | 0 | 0 | 0
2017-12-14 01:00 | 12 | 1 | 0 | 0
2017-12-14 02:00 | 12 | 2 | 0 | 0
2017-12-14 03:00 | 12 | 3 | 0 | 0
2017-12-14 04:00 | 12 | 4 | 0 | 0
2017-12-14 05:00 | 12 | 5 | 0 | 0
2017-12-14 06:00 | 12 | 6 | 0 | 0
2017-12-14 07:00 | 12 | 7 | 47.9515 | 47.9515
2017-12-14 08:00 | 12 | 8 | 454.963 | 454.963
2017-12-14 09:00 | 12 | 9 | 806.3788 | 806.3788
2017-12-14 10:00 | 12 | 10 | 1602.7906 | 1602.7906
2017-12-14 11:00 | 12 | 11 | 558.2491 | 558.2491
2017-12-14 12:00 | 12 | 12 | 604.4871 | 604.4871
2017-12-14 13:00 | 12 | 13 | 735.1249 | 735.1249
2017-12-14 14:00 | 12 | 14 | 284.7101 | 284.7101
2017-12-14 15:00 | 12 | 15 | 45.9781 | 45.9781
2017-12-14 16:00 | 12 | 16 | 0 | 0
2017-12-14 17:00 | 12 | 17 | 0 | 0
2017-12-14 18:00 | 12 | 18 | 0 | 0
2017-12-14 19:00 | 12 | 19 | 0 | 0
2017-12-14 20:00 | 12 | 20 | 0 | 0
2017-12-14 21:00 | 12 | 21 | 0 | 0
2017-12-14 22:00 | 12 | 22 | 0 | 0
2017-12-14 23:00 | 12 | 23 | 0 | 0
2017-12-15 | 12 | 0 | 0 | 0
2017-12-15 01:00 | 12 | 1 | 0 | 0
2017-12-15 02:00 | 12 | 2 | 0 | 0
2017-12-15 03:00 | 12 | 3 | 0 | 0
2017-12-15 04:00 | 12 | 4 | 0 | 0
2017-12-15 05:00 | 12 | 5 | 0 | 0
2017-12-15 06:00 | 12 | 6 | 0 | 0
2017-12-15 07:00 | 12 | 7 | 495.7535 | 495.7535
2017-12-15 08:00 | 12 | 8 | 2815.0528 | 2815.0528
2017-12-15 09:00 | 12 | 9 | 645.4869 | 645.4869
2017-12-15 10:00 | 12 | 10 | 304.4935 | 304.4935
2017-12-15 11:00 | 12 | 11 | 3151.3047 | 3151.3047
2017-12-15 12:00 | 12 | 12 | 1765.7675 | 1765.7675
2017-12-15 13:00 | 12 | 13 | 4549.0147 | 4549.0147
2017-12-15 14:00 | 12 | 14 | 3868.2504 | 3868.2504
2017-12-15 15:00 | 12 | 15 | 1584.7701 | 1584.7701
2017-12-15 16:00 | 12 | 16 | 0 | 0
2017-12-15 17:00 | 12 | 17 | 0 | 0
2017-12-15 18:00 | 12 | 18 | 0 | 0
2017-12-15 19:00 | 12 | 19 | 0 | 0
2017-12-15 20:00 | 12 | 20 | 0 | 0
2017-12-15 21:00 | 12 | 21 | 0 | 0
2017-12-15 22:00 | 12 | 22 | 0 | 0
2017-12-15 23:00 | 12 | 23 | 0 | 0
2017-12-16 | 12 | 0 | 0 | 0
2017-12-16 01:00 | 12 | 1 | 0 | 0
2017-12-16 02:00 | 12 | 2 | 0 | 0
2017-12-16 03:00 | 12 | 3 | 0 | 0
2017-12-16 04:00 | 12 | 4 | 0 | 0
2017-12-16 05:00 | 12 | 5 | 0 | 0
2017-12-16 06:00 | 12 | 6 | 0 | 0
2017-12-16 07:00 | 12 | 7 | 229.3595 | 229.3595
2017-12-16 08:00 | 12 | 8 | 2406.9937 | 2406.9937
2017-12-16 09:00 | 12 | 9 | 5041.8346 | 5041.8346
2017-12-16 10:00 | 12 | 10 | 6104.591 | 6104.591
2017-12-16 11:00 | 12 | 11 | 6504.8255 | 6504.8255
2017-12-16 12:00 | 12 | 12 | 6214.7506 | 6214.7506
2017-12-16 13:00 | 12 | 13 | 5272.3302 | 5272.3302
2017-12-16 14:00 | 12 | 14 | 3697.9434 | 3697.9434
2017-12-16 15:00 | 12 | 15 | 1565.4317 | 1565.4317
2017-12-16 16:00 | 12 | 16 | 0 | 0
2017-12-16 17:00 | 12 | 17 | 0 | 0
2017-12-16 18:00 | 12 | 18 | 0 | 0
2017-12-16 19:00 | 12 | 19 | 0 | 0
2017-12-16 20:00 | 12 | 20 | 0 | 0
2017-12-16 21:00 | 12 | 21 | 0 | 0
2017-12-16 22:00 | 12 | 22 | 0 | 0
2017-12-16 23:00 | 12 | 23 | 0 | 0
2017-12-17 | 12 | 0 | 0 | 0
2017-12-17 01:00 | 12 | 1 | 0 | 0
2017-12-17 02:00 | 12 | 2 | 0 | 0
2017-12-17 03:00 | 12 | 3 | 0 | 0
2017-12-17 04:00 | 12 | 4 | 0 | 0
2017-12-17 05:00 | 12 | 5 | 0 | 0
2017-12-17 06:00 | 12 | 6 | 0 | 0
2017-12-17 07:00 | 12 | 7 | 588.0536 | 588.0536
2017-12-17 08:00 | 12 | 8 | 1435.7324 | 1435.7324
2017-12-17 09:00 | 12 | 9 | 2228.8989 | 2228.8989
2017-12-17 10:00 | 12 | 10 | 3021.5238 | 3021.5238
2017-12-17 11:00 | 12 | 11 | 1378.0542 | 1378.0542
2017-12-17 12:00 | 12 | 12 | 1501.3308 | 1501.3308
2017-12-17 13:00 | 12 | 13 | 1214.9267 | 1214.9267
2017-12-17 14:00 | 12 | 14 | 469.7819 | 469.7819
2017-12-17 15:00 | 12 | 15 | 101.3656 | 101.3656
2017-12-17 16:00 | 12 | 16 | 0 | 0
2017-12-17 17:00 | 12 | 17 | 0 | 0
2017-12-17 18:00 | 12 | 18 | 0 | 0
2017-12-17 19:00 | 12 | 19 | 0 | 0
2017-12-17 20:00 | 12 | 20 | 0 | 0
2017-12-17 21:00 | 12 | 21 | 0 | 0
2017-12-17 22:00 | 12 | 22 | 0 | 0
2017-12-17 23:00 | 12 | 23 | 0 | 0
2017-12-18 | 12 | 0 | 0 | 0
2017-12-18 01:00 | 12 | 1 | 0 | 0
2017-12-18 02:00 | 12 | 2 | 0 | 0
2017-12-18 03:00 | 12 | 3 | 0 | 0
2017-12-18 04:00 | 12 | 4 | 0 | 0
2017-12-18 05:00 | 12 | 5 | 0 | 0
2017-12-18 06:00 | 12 | 6 | 0 | 0
2017-12-18 07:00 | 12 | 7 | 117.7508 | 117.7508
2017-12-18 08:00 | 12 | 8 | 2869.6605 | 2869.6605
2017-12-18 09:00 | 12 | 9 | 4742.8679 | 4742.8679
2017-12-18 10:00 | 12 | 10 | 5894.9011 | 5894.9011
2017-12-18 11:00 | 12 | 11 | 6297.7726 | 6297.7726
2017-12-18 12:00 | 12 | 12 | 6009.3388 | 6009.3388
2017-12-18 13:00 | 12 | 13 | 5242.0565 | 5242.0565
2017-12-18 14:00 | 12 | 14 | 3609.9432 | 3609.9432
2017-12-18 15:00 | 12 | 15 | 1419.6692 | 1419.6692
2017-12-18 16:00 | 12 | 16 | 0 | 0
2017-12-18 17:00 | 12 | 17 | 0 | 0
2017-12-18 18:00 | 12 | 18 | 0 | 0
2017-12-18 19:00 | 12 | 19 | 0 | 0
2017-12-18 20:00 | 12 | 20 | 0 | 0
2017-12-18 21:00 | 12 | 21 | 0 | 0
2017-12-18 22:00 | 12 | 22 | 0 | 0
2017-12-18 23:00 | 12 | 23 | 0 | 0
2017-12-19 | 12 | 0 | 0 | 0
2017-12-19 01:00 | 12 | 1 | 0 | 0
2017-12-19 02:00 | 12 | 2 | 0 | 0
2017-12-19 03:00 | 12 | 3 | 0 | 0
2017-12-19 04:00 | 12 | 4 | 0 | 0
2017-12-19 05:00 | 12 | 5 | 0 | 0
2017-12-19 06:00 | 12 | 6 | 0 | 0
2017-12-19 07:00 | 12 | 7 | 910.7034 | 910.7034
2017-12-19 08:00 | 12 | 8 | 3187.5746 | 3187.5746
2017-12-19 09:00 | 12 | 9 | 4993.7531 | 4993.7531
2017-12-19 10:00 | 12 | 10 | 6034.3133 | 6034.3133
2017-12-19 11:00 | 12 | 11 | 6426.6784 | 6426.6784
2017-12-19 12:00 | 12 | 12 | 6159.0343 | 6159.0343
2017-12-19 13:00 | 12 | 13 | 5326.3227 | 5326.3227
2017-12-19 14:00 | 12 | 14 | 3798.6202 | 3798.6202
2017-12-19 15:00 | 12 | 15 | 1660.2101 | 1660.2101
2017-12-19 16:00 | 12 | 16 | 0 | 0
2017-12-19 17:00 | 12 | 17 | 0 | 0
2017-12-19 18:00 | 12 | 18 | 0 | 0
2017-12-19 19:00 | 12 | 19 | 0 | 0
2017-12-19 20:00 | 12 | 20 | 0 | 0
2017-12-19 21:00 | 12 | 21 | 0 | 0
2017-12-19 22:00 | 12 | 22 | 0 | 0
2017-12-19 23:00 | 12 | 23 | 0 | 0
2017-12-20 | 12 | 0 | 0 | 0
2017-12-20 01:00 | 12 | 1 | 0 | 0
2017-12-20 02:00 | 12 | 2 | 0 | 0
2017-12-20 03:00 | 12 | 3 | 0 | 0
2017-12-20 04:00 | 12 | 4 | 0 | 0
2017-12-20 05:00 | 12 | 5 | 0 | 0
2017-12-20 06:00 | 12 | 6 | 0 | 0
2017-12-20 07:00 | 12 | 7 | 77.1144 | 77.1144
2017-12-20 08:00 | 12 | 8 | 1269.5551 | 1269.5551
2017-12-20 09:00 | 12 | 9 | 4582.2831 | 4582.2831
2017-12-20 10:00 | 12 | 10 | 5634.0041 | 5634.0041
2017-12-20 11:00 | 12 | 11 | 4467.8489 | 4467.8489
2017-12-20 12:00 | 12 | 12 | 3269.5914 | 3269.5914
2017-12-20 13:00 | 12 | 13 | 2464.0486 | 2464.0486
2017-12-20 14:00 | 12 | 14 | 1589.7002 | 1589.7002
2017-12-20 15:00 | 12 | 15 | 466.6849 | 466.6849
2017-12-20 16:00 | 12 | 16 | 0 | 0
2017-12-20 17:00 | 12 | 17 | 0 | 0
2017-12-20 18:00 | 12 | 18 | 0 | 0
2017-12-20 19:00 | 12 | 19 | 0 | 0
2017-12-20 20:00 | 12 | 20 | 0 | 0
2017-12-20 21:00 | 12 | 21 | 0 | 0
2017-12-20 22:00 | 12 | 22 | 0 | 0
2017-12-20 23:00 | 12 | 23 | 0 | 0
2017-12-21 | 12 | 0 | 0 | 0
2017-12-21 01:00 | 12 | 1 | 0 | 0
2017-12-21 02:00 | 12 | 2 | 0 | 0
2017-12-21 03:00 | 12 | 3 | 0 | 0
2017-12-21 04:00 | 12 | 4 | 0 | 0
2017-12-21 05:00 | 12 | 5 | 0 | 0
2017-12-21 06:00 | 12 | 6 | 0 | 0
2017-12-21 07:00 | 12 | 7 | 825.7644 | 825.7644
2017-12-21 08:00 | 12 | 8 | 3107.0527 | 3107.0527
2017-12-21 09:00 | 12 | 9 | 3293.738 | 3293.738
2017-12-21 10:00 | 12 | 10 | 5860.5656 | 5860.5656
2017-12-21 11:00 | 12 | 11 | 6202.7987 | 6202.7987
2017-12-21 12:00 | 12 | 12 | 3152.6974 | 3152.6974
2017-12-21 13:00 | 12 | 13 | 3871.8694 | 3871.8694
2017-12-21 14:00 | 12 | 14 | 1563.3272 | 1563.3272
2017-12-21 15:00 | 12 | 15 | 1325.0771 | 1325.0771
2017-12-21 16:00 | 12 | 16 | 0 | 0
2017-12-21 17:00 | 12 | 17 | 0 | 0
2017-12-21 18:00 | 12 | 18 | 0 | 0
2017-12-21 19:00 | 12 | 19 | 0 | 0
2017-12-21 20:00 | 12 | 20 | 0 | 0
2017-12-21 21:00 | 12 | 21 | 0 | 0
2017-12-21 22:00 | 12 | 22 | 0 | 0
2017-12-21 23:00 | 12 | 23 | 0 | 0
2017-12-22 | 12 | 0 | 0 | 0
2017-12-22 01:00 | 12 | 1 | 0 | 0
2017-12-22 02:00 | 12 | 2 | 0 | 0
2017-12-22 03:00 | 12 | 3 | 0 | 0
2017-12-22 04:00 | 12 | 4 | 0 | 0
2017-12-22 05:00 | 12 | 5 | 0 | 0
2017-12-22 06:00 | 12 | 6 | 0 | 0
2017-12-22 07:00 | 12 | 7 | 184.0046 | 184.0046
2017-12-22 08:00 | 12 | 8 | 2792.2115 | 2792.2115
2017-12-22 09:00 | 12 | 9 | 4520.7236 | 4520.7236
2017-12-22 10:00 | 12 | 10 | 3603.1604 | 3603.1605
2017-12-22 11:00 | 12 | 11 | 3715.6431 | 3715.6431
2017-12-22 12:00 | 12 | 12 | 3451.2983 | 3451.2983
2017-12-22 13:00 | 12 | 13 | 3110.7695 | 3110.7695
2017-12-22 14:00 | 12 | 14 | 1044.4185 | 1044.4185
2017-12-22 15:00 | 12 | 15 | 283.1806 | 283.1806
2017-12-22 16:00 | 12 | 16 | 0 | 0
2017-12-22 17:00 | 12 | 17 | 0 | 0
2017-12-22 18:00 | 12 | 18 | 0 | 0
2017-12-22 19:00 | 12 | 19 | 0 | 0
2017-12-22 20:00 | 12 | 20 | 0 | 0
2017-12-22 21:00 | 12 | 21 | 0 | 0
2017-12-22 22:00 | 12 | 22 | 0 | 0
2017-12-22 23:00 | 12 | 23 | 0 | 0
2017-12-23 | 12 | 0 | 0 | 0
2017-12-23 01:00 | 12 | 1 | 0 | 0
2017-12-23 02:00 | 12 | 2 | 0 | 0
2017-12-23 03:00 | 12 | 3 | 0 | 0
2017-12-23 04:00 | 12 | 4 | 0 | 0
2017-12-23 05:00 | 12 | 5 | 0 | 0
2017-12-23 06:00 | 12 | 6 | 0 | 0
2017-12-23 07:00 | 12 | 7 | 0 | 0
2017-12-23 08:00 | 12 | 8 | 86.1683 | 86.1683
2017-12-23 09:00 | 12 | 9 | 777.9646 | 777.9646
2017-12-23 10:00 | 12 | 10 | 2004.3522 | 2004.3522
2017-12-23 11:00 | 12 | 11 | 2688.3193 | 2688.3193
2017-12-23 12:00 | 12 | 12 | 4073.354 | 4073.3541
2017-12-23 13:00 | 12 | 13 | 3112.2737 | 3112.2737
2017-12-23 14:00 | 12 | 14 | 3324.3809 | 3324.3809
2017-12-23 15:00 | 12 | 15 | 1396.2138 | 1396.2138
2017-12-23 16:00 | 12 | 16 | 0 | 0
2017-12-23 17:00 | 12 | 17 | 0 | 0
2017-12-23 18:00 | 12 | 18 | 0 | 0
2017-12-23 19:00 | 12 | 19 | 0 | 0
2017-12-23 20:00 | 12 | 20 | 0 | 0
2017-12-23 21:00 | 12 | 21 | 0 | 0
2017-12-23 22:00 | 12 | 22 | 0 | 0
2017-12-23 23:00 | 12 | 23 | 0 | 0
2017-12-24 | 12 | 0 | 0 | 0
2017-12-24 01:00 | 12 | 1 | 0 | 0
2017-12-24 02:00 | 12 | 2 | 0 | 0
2017-12-24 03:00 | 12 | 3 | 0 | 0
2017-12-24 04:00 | 12 | 4 | 0 | 0
2017-12-24 05:00 | 12 | 5 | 0 | 0
2017-12-24 06:00 | 12 | 6 | 0 | 0
2017-12-24 07:00 | 12 | 7 | 2.1091 | 2.1091
2017-12-24 08:00 | 12 | 8 | 553.1051 | 553.1051
2017-12-24 09:00 | 12 | 9 | 708.9152 | 708.9152
2017-12-24 10:00 | 12 | 10 | 1163.0548 | 1163.0548
2017-12-24 11:00 | 12 | 11 | 1305.649 | 1305.649
2017-12-24 12:00 | 12 | 12 | 869.3827 | 869.3827
2017-12-24 13:00 | 12 | 13 | 422.9447 | 422.9447
2017-12-24 14:00 | 12 | 14 | 465.0531 | 465.0531
2017-12-24 15:00 | 12 | 15 | 169.2501 | 169.2501
2017-12-24 16:00 | 12 | 16 | 0 | 0
2017-12-24 17:00 | 12 | 17 | 0 | 0
2017-12-24 18:00 | 12 | 18 | 0 | 0
2017-12-24 19:00 | 12 | 19 | 0 | 0
2017-12-24 20:00 | 12 | 20 | 0 | 0
2017-12-24 21:00 | 12 | 21 | 0 | 0
2017-12-24 22:00 | 12 | 22 | 0 | 0
2017-12-24 23:00 | 12 | 23 | 0 | 0
2017-12-25 | 12 | 0 | 0 | 0
2017-12-25 01:00 | 12 | 1 | 0 | 0
2017-12-25 02:00 | 12 | 2 | 0 | 0
2017-12-25 03:00 | 12 | 3 | 0 | 0
2017-12-25 04:00 | 12 | 4 | 0 | 0
2017-12-25 05:00 | 12 | 5 | 0 | 0
2017-12-25 06:00 | 12 | 6 | 0 | 0
2017-12-25 07:00 | 12 | 7 | 22.6998 | 22.6998
2017-12-25 08:00 | 12 | 8 | 356.8726 | 356.8726
2017-12-25 09:00 | 12 | 9 | 94.1896 | 94.1896
2017-12-25 10:00 | 12 | 10 | 63.9216 | 63.9216
2017-12-25 11:00 | 12 | 11 | 620.0604 | 620.0604
2017-12-25 12:00 | 12 | 12 | 224.5708 | 224.5708
2017-12-25 13:00 | 12 | 13 | 344.2744 | 344.2744
2017-12-25 14:00 | 12 | 14 | 1965.5478 | 1965.5478
2017-12-25 15:00 | 12 | 15 | 1514.3361 | 1514.3361
2017-12-25 16:00 | 12 | 16 | 0 | 0
2017-12-25 17:00 | 12 | 17 | 0 | 0
2017-12-25 18:00 | 12 | 18 | 0 | 0
2017-12-25 19:00 | 12 | 19 | 0 | 0
2017-12-25 20:00 | 12 | 20 | 0 | 0
2017-12-25 21:00 | 12 | 21 | 0 | 0
2017-12-25 22:00 | 12 | 22 | 0 | 0
2017-12-25 23:00 | 12 | 23 | 0 | 0
2017-12-26 | 12 | 0 | 0 | 0
2017-12-26 01:00 | 12 | 1 | 0 | 0
2017-12-26 02:00 | 12 | 2 | 0 | 0
2017-12-26 03:00 | 12 | 3 | 0 | 0
2017-12-26 04:00 | 12 | 4 | 0 | 0
2017-12-26 05:00 | 12 | 5 | 0 | 0
2017-12-26 06:00 | 12 | 6 | 0 | 0
2017-12-26 07:00 | 12 | 7 | 24.288 | 24.288
2017-12-26 08:00 | 12 | 8 | 652.9803 | 652.9803
2017-12-26 09:00 | 12 | 9 | 1739.3577 | 1739.3577
2017-12-26 10:00 | 12 | 10 | 1460.9979 | 1460.9979
2017-12-26 11:00 | 12 | 11 | 623.998 | 623.998
2017-12-26 12:00 | 12 | 12 | 2460.2697 | 2460.2697
2017-12-26 13:00 | 12 | 13 | 2131.3893 | 2131.3893
2017-12-26 14:00 | 12 | 14 | 427.6907 | 427.6907
2017-12-26 15:00 | 12 | 15 | 23.8935 | 23.8935
2017-12-26 16:00 | 12 | 16 | 0 | 0
2017-12-26 17:00 | 12 | 17 | 0 | 0
2017-12-26 18:00 | 12 | 18 | 0 | 0
2017-12-26 19:00 | 12 | 19 | 0 | 0
2017-12-26 20:00 | 12 | 20 | 0 | 0
2017-12-26 21:00 | 12 | 21 | 0 | 0
2017-12-26 22:00 | 12 | 22 | 0 | 0
2017-12-26 23:00 | 12 | 23 | 0 | 0
2017-12-27 | 12 | 0 | 0 | 0
2017-12-27 01:00 | 12 | 1 | 0 | 0
2017-12-27 02:00 | 12 | 2 | 0 | 0
2017-12-27 03:00 | 12 | 3 | 0 | 0
2017-12-27 04:00 | 12 | 4 | 0 | 0
2017-12-27 05:00 | 12 | 5 | 0 | 0
2017-12-27 06:00 | 12 | 6 | 0 | 0
2017-12-27 07:00 | 12 | 7 | 822.4961 | 822.4961
2017-12-27 08:00 | 12 | 8 | 3101.0049 | 3101.0049
2017-12-27 09:00 | 12 | 9 | 4876.8372 | 4876.8372
2017-12-27 10:00 | 12 | 10 | 5997.8871 | 5997.8871
2017-12-27 11:00 | 12 | 11 | 6454.9868 | 6454.9868
2017-12-27 12:00 | 12 | 12 | 6269.3952 | 6269.3952
2017-12-27 13:00 | 12 | 13 | 5447.006 | 5447.006
2017-12-27 14:00 | 12 | 14 | 4009.6026 | 4009.6026
2017-12-27 15:00 | 12 | 15 | 1982.3056 | 1982.3056
2017-12-27 16:00 | 12 | 16 | 0 | 0
2017-12-27 17:00 | 12 | 17 | 0 | 0
2017-12-27 18:00 | 12 | 18 | 0 | 0
2017-12-27 19:00 | 12 | 19 | 0 | 0
2017-12-27 20:00 | 12 | 20 | 0 | 0
2017-12-27 21:00 | 12 | 21 | 0 | 0
2017-12-27 22:00 | 12 | 22 | 0 | 0
2017-12-27 23:00 | 12 | 23 | 0 | 0
2017-12-28 | 12 | 0 | 0 | 0
2017-12-28 01:00 | 12 | 1 | 0 | 0
2017-12-28 02:00 | 12 | 2 | 0 | 0
2017-12-28 03:00 | 12 | 3 | 0 | 0
2017-12-28 04:00 | 12 | 4 | 0 | 0
2017-12-28 05:00 | 12 | 5 | 0 | 0
2017-12-28 06:00 | 12 | 6 | 0 | 0
2017-12-28 07:00 | 12 | 7 | 778.3027 | 778.3027
2017-12-28 08:00 | 12 | 8 | 3057.4475 | 3057.4475
2017-12-28 09:00 | 12 | 9 | 4867.452 | 4867.452
2017-12-28 10:00 | 12 | 10 | 5917.7344 | 5917.7344
2017-12-28 11:00 | 12 | 11 | 6319.6421 | 6319.6421
2017-12-28 12:00 | 12 | 12 | 6113.7415 | 6113.7415
2017-12-28 13:00 | 12 | 13 | 5345.2897 | 5345.2897
2017-12-28 14:00 | 12 | 14 | 2120.5781 | 2120.5781
2017-12-28 15:00 | 12 | 15 | 813.3134 | 813.3134
2017-12-28 16:00 | 12 | 16 | 0 | 0
2017-12-28 17:00 | 12 | 17 | 0 | 0
2017-12-28 18:00 | 12 | 18 | 0 | 0
2017-12-28 19:00 | 12 | 19 | 0 | 0
2017-12-28 20:00 | 12 | 20 | 0 | 0
2017-12-28 21:00 | 12 | 21 | 0 | 0
2017-12-28 22:00 | 12 | 22 | 0 | 0
2017-12-28 23:00 | 12 | 23 | 0 | 0
2017-12-29 | 12 | 0 | 0 | 0
2017-12-29 01:00 | 12 | 1 | 0 | 0
2017-12-29 02:00 | 12 | 2 | 0 | 0
2017-12-29 03:00 | 12 | 3 | 0 | 0
2017-12-29 04:00 | 12 | 4 | 0 | 0
2017-12-29 05:00 | 12 | 5 | 0 | 0
2017-12-29 06:00 | 12 | 6 | 0 | 0
2017-12-29 07:00 | 12 | 7 | 597.9459 | 597.9459
2017-12-29 08:00 | 12 | 8 | 2810.7288 | 2810.7288
2017-12-29 09:00 | 12 | 9 | 4587.6202 | 4587.6202
2017-12-29 10:00 | 12 | 10 | 5653.9945 | 5653.9945
2017-12-29 11:00 | 12 | 11 | 6090.3471 | 6090.3471
2017-12-29 12:00 | 12 | 12 | 5912.6778 | 5912.6778
2017-12-29 13:00 | 12 | 13 | 5147.4276 | 5147.4276
2017-12-29 14:00 | 12 | 14 | 3763.674 | 3763.674
2017-12-29 15:00 | 12 | 15 | 1751.0636 | 1751.0636
2017-12-29 16:00 | 12 | 16 | 0 | 0
2017-12-29 17:00 | 12 | 17 | 0 | 0
2017-12-29 18:00 | 12 | 18 | 0 | 0
2017-12-29 19:00 | 12 | 19 | 0 | 0
2017-12-29 20:00 | 12 | 20 | 0 | 0
2017-12-29 21:00 | 12 | 21 | 0 | 0
2017-12-29 22:00 | 12 | 22 | 0 | 0
2017-12-29 23:00 | 12 | 23 | 0 | 0
2017-12-30 | 12 | 0 | 0 | 0
2017-12-30 01:00 | 12 | 1 | 0 | 0
2017-12-30 02:00 | 12 | 2 | 0 | 0
2017-12-30 03:00 | 12 | 3 | 0 | 0
2017-12-30 04:00 | 12 | 4 | 0 | 0
2017-12-30 05:00 | 12 | 5 | 0 | 0
2017-12-30 06:00 | 12 | 6 | 0 | 0
2017-12-30 07:00 | 12 | 7 | 2.3725 | 2.3725
2017-12-30 08:00 | 12 | 8 | 874.2449 | 874.2449
2017-12-30 09:00 | 12 | 9 | 380.305 | 380.305
2017-12-30 10:00 | 12 | 10 | 1093.0428 | 1093.0428
2017-12-30 11:00 | 12 | 11 | 1993.4491 | 1993.4491
2017-12-30 12:00 | 12 | 12 | 5773.1437 | 5773.1437
2017-12-30 13:00 | 12 | 13 | 3280.3416 | 3280.3416
2017-12-30 14:00 | 12 | 14 | 829.7572 | 829.7572
2017-12-30 15:00 | 12 | 15 | 1697.3241 | 1697.3241
2017-12-30 16:00 | 12 | 16 | 0 | 0
2017-12-30 17:00 | 12 | 17 | 0 | 0
2017-12-30 18:00 | 12 | 18 | 0 | 0
2017-12-30 19:00 | 12 | 19 | 0 | 0
2017-12-30 20:00 | 12 | 20 | 0 | 0
2017-12-30 21:00 | 12 | 21 | 0 | 0
2017-12-30 22:00 | 12 | 22 | 0 | 0
2017-12-30 23:00 | 12 | 23 | 0 | 0
2017-12-31 | 12 | 0 | 0 | 0
2017-12-31 01:00 | 12 | 1 | 0 | 0
2017-12-31 02:00 | 12 | 2 | 0 | 0
2017-12-31 03:00 | 12 | 3 | 0 | 0
2017-12-31 04:00 | 12 | 4 | 0 | 0
2017-12-31 05:00 | 12 | 5 | 0 | 0
2017-12-31 06:00 | 12 | 6 | 0 | 0
2017-12-31 07:00 | 12 | 7 | 565.9311 | 565.9311
2017-12-31 08:00 | 12 | 8 | 2797.6395 | 2797.6395
2017-12-31 09:00 | 12 | 9 | 3887.1713 | 3887.1713
2017-12-31 10:00 | 12 | 10 | 2820.9523 | 2820.9523
2017-12-31 11:00 | 12 | 11 | 1156.8839 | 1156.8839
2017-12-31 12:00 | 12 | 12 | 4115.8258 | 4115.8258
2017-12-31 13:00 | 12 | 13 | 5343.2691 | 5343.2691
2017-12-31 14:00 | 12 | 14 | 3930.9771 | 3930.9771
2017-12-31 15:00 | 12 | 15 | 1886.046 | 1886.046
2017-12-31 16:00 | 12 | 16 | 0 | 0
2017-12-31 17:00 | 12 | 17 | 0 | 0
2017-12-31 18:00 | 12 | 18 | 0 | 0
2017-12-31 19:00 | 12 | 19 | 0 | 0
2017-12-31 20:00 | 12 | 20 | 0 | 0
2017-12-31 21:00 | 12 | 21 | 0 | 0
2017-12-31 22:00 | 12 | 22 | 0 | 0
2017-12-31 23:00 | 12 | 23 | 0 | 0
|  |  | 14989.8981 | 14989.8981
Formulas:
Date-time = [Date-time, row above]+1/24